## Slide 1: Buckingham Park Water District
Tracer Study
2/10/16
By Guy Schott

## Slide 2
200K Clearwell
30-ft Diameter; 37.8 ft. Baffle Height

## Slide 4
Inlet Riser
12 ft Ht.
6” x 4” Reducer
Baffle Curtain
Nozzle Velocity:
5.1 ft/sec

## Slide 5
Inlet Side of Clearwell

## Slide 6
Inlet Side of Clearwell
Baffle Curtain

## Slide 7
Flow

## Slide 8
Outlet

## Slide 9
Outlet Side of Clearwell
Leaking baffle

## Slide 10
Leaking baffle
Outlet

## Slide 11
Outlet

## Slide 12
Baffling Factor: 0.13
Flow (inlet/outlet): 200 gpm; HRT: 867 minutes (14.4 hrs)

## Slide 13
1.5 ft
16.5 ft
31 ft
1.73 mg/L
1.81 mg/L
1.82 mg/L
1.81 mg/L
1.73 mg/L
1.86 mg/L
Clearwell
Chlorine Residual
Inlet Side
Outlet Side
Depth
Operating Tank
Level: 31.8 ft.