## Slide 1: Surfwood Mutual Water Corporation CA2300590 Mendocino County Jar Test
by Guy Schott, P.E
July 24, 2023

## Slide 2: Source Water: Jack Peter’s Creek Roughing Filter followed by Multi-Media Filtration
Source Water Characteristics
Turbidity: 2.77 NTU
UVT: 69.6%
UVA: 0.157/cm
0.4 um Filtered
Turbidity: 0.40 NTU
UVT: 75.8%
UVA: 0.12/cm

## Slide 3: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 4: Applied Coagulants for Jar Testing (1)
960 (NTU Technologies)
33% Polyaluminum Hydroxychlorosulfate
67% Water
SG = 1.29
NSF limit: 250 mg/L as Product
961 (NTU Technologies)
~32% Polyaluminum Hydroxychlorosulfate
2% pDADMAC
66% Water
SG = 1.29
NSF limit: 255 mg/L as Product

## Slide 5: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Preparation of coagulant stock solutions are generally 2.0, 1.0 or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 6: Filtrate and %UVT/UVA Analysis
For this study, all jars were samples for Filtrate and %UVT/UVA analysis immediately at the end of the flocculation period.

## Slide 7: Surfwood MWC; Jar Test 1 - 8 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | 960 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction
J1 | 40 | 0.04 | 95.3 | 0.020 | 83.3
J2 | 50 | 0.07 | 96.0 | 0.017 | 85.8
J3 | 60 | 0.03 | 96.8 | 0.013 | 89.2
J4 | 70 | 0.03 | 97.2 | 0.012 | 90.0
J5 | 60 | 0.03 | 97.0 | 0.013 | 89.2
J6 | 65 | 0.03 | 97.1 | 0.012 | 90.0
J7 | 70 | 0.03 | 97.4 | 0.011 | 90.8
J8 | 75 | 0.03 | 97.6 | 0.010 | 91.7

## Slide 8: Surfwood MWC; Jar Test 9 - 16 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | 960 mg/L | 961 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction
J9 | - | 60 | 0.04 | 96.8 | 0.014 | 88.3
J10 | - | 65 | 0.04 | 97.3 | 0.011 | 90.8
J11 | - | 70 | 0.03 | 97.4 | 0.011 | 90.8
J12 | - | 75 | 0.03 | 97.6 | 0.010 | 91.7
J13 | 65 | - | 0.03 | 97.3 | 0.011 | 90.8
J14 | 70 | - | 0.03 | 97.4 | 0.011 | 90.8
J15 | - | 65 | 0.05 | 97.2 | 0.012 | 90.0
J16 | - | 70 | 0.04 | 97.3 | 0.011 | 90.8

## Slide 9: Jars 1-4 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant 960

## Slide 10: Jars 1-4: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
40 mg/L 960
Filtrate 0.04 NTU
UVT: 95.3%
UVA: 0.020/cm
UVA Reduction: 83.3%
50 mg/L 960
Filtrate 0.07 NTU
UVT: 96.0%
UVA: 0.017/cm
UVA Reduction: 85.8%
60 mg/L 960
Filtrate 0.03 NTU
UVT: 96.8%
UVA: 0.013/cm
UVA Reduction: 89.2%
65 mg/L 960
Filtrate 0.03 NTU
UVT: 97.2%
UVA: 0.012/cm
UVA Reduction: 90.0%

## Slide 11: Jars 5-8 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant 960

## Slide 12: Jars 5-8: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
60 mg/L 960
Filtrate 0.03 NTU
UVT: 97.0%
UVA: 0.013/cm
UVA Reduction: 89.2%
65 mg/L 960
Filtrate 0.03 NTU
UVT: 97.1%
UVA: 0.012/cm
UVA Reduction: 90.0%
70 mg/L 960
Filtrate 0.03 NTU
UVT: 97.4%
UVA: 0.011/cm
UVA Reduction: 90.8%
75 mg/L 960
Filtrate 0.03 NTU
UVT: 97.6%
UVA: 0.010/cm
UVA Reduction: 91.7%

## Slide 13: Jars 9-12 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant 961

## Slide 14: Jars 9-12: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
60 mg/L 961
Filtrate 0.04 NTU
UVT: 96.8%
UVA: 0.014/cm
UVA Reduction: 88.3%
65 mg/L 961
Filtrate 0.04 NTU
UVT: 97.3%
UVA: 0.011/cm
UVA Reduction: 90.8%
70 mg/L 961
Filtrate 0.03 NTU
UVT: 97.4%
UVA: 0.011/cm
UVA Reduction: 90.8%
75 mg/L 961
Filtrate 0.03 NTU
UVT: 97.6%
UVA: 0.010/cm
UVA Reduction: 91.7%

## Slide 15: Jars 13-16 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant 961

## Slide 16: Jars 13-16: End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
65 mg/L 961
Filtrate 0.05 NTU
UVT: 97.2%
UVA: 0.012/cm
UVA Reduction: 90.0%
70 mg/L 961
Filtrate 0.04 NTU
UVT: 97.3%
UVA: 0.011/cm
UVA Reduction: 90.8%
65 mg/L 960
Filtrate 0.03 NTU
UVT: 97.3%
UVA: 0.011/cm
UVA Reduction: 90.8%
70 mg/L 960
Filtrate 0.03 NTU
UVT: 97.4%
UVA: 0.011/cm
UVA Reduction: 90.8%

## Slide 17: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 20-30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate). For this study, samples were taken immediately at the end of flocculation process.
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 18: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 19: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 20: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 21: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 22: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Jar Test Results/Procedures for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Jar Testing Done Right video training https://youtu.be/aGByyxhelkI
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732