## SEWER001
Tracking No. | Regional Board Contact Notified (Name, or "VOICE MAIL", or "FAX") | Date & Time Reported | Reported By | Phone No. | Agency | Start Date & Time | End Date & Time | Total Overflow Volume (Gallons) | Overflow Volume Recovered (Gallons) | SSO Location -- Street Address | SSO Location -- City | SSO County SD, RV, OR | SSO Zip Code | SSO Structure I.D. | No. of Overflows in past 12 months | SSO Cause (Short Description) | SSO Cause (Detailed Description) | SSO Correction and Prevention | Reach Surface Waters? (Y or N) | Entered Storm Drain? (Y or N) | Initial Receiving Waters | Secondary Receiving Waters | Final Sewage Destination | Local Health Services Agency Notified (Y or N) | OES Notified (Y or N) | Warning Signs Posted (Y or N) | No. of Days Signs Posted | Remarks | RB staff review comments
1001 | Brian Kelley | 2001-03-08 15:30 | Doug Brown | (619) 670-2271 | Otay Water District | 2001-03-08 09:30 | 2001-03-08 11:00 | 900 | 100 | Forcemain easement 1/4mi. South of plant | Spring Valley | SD | 91978 | 3' X 3 1/2' concrete air vac housing | 0 | corrosion | A small hole developed in the 2" nipple supporting a 2" air vac assembly | The 2" nipple and associated piping were replaced with new materials | N | N | Sweetwater River | Sweetwater Lake | Absorption into roadway and shrubbed hillside | N | N | N | 0 | Chlorinated tertiary effluent was quickly absorbed into the ground
10501 | FAX | 010501 12:01 PM | BRIAN WALTHER | (619) 691-5027 | City of Chula Vista | 2001-01-05 12:01 | 2001-01-05 12:51 | 250 | 0 | 560 AUTO PARK DRIVE | CHULA VISTA | SD | 91910 | MANHOLE | 0 | PUMP STATION FAILURE | CONTROL FAILURE | REPAIRED CONTOLER | Y | Y | POND ON OTAY RIVER WATER WAY SOUTH OF PUMP STATION | N/A | N/A | Y | N/A | Y | 4 | NA
10204 | FAX | 010204 10:30 AM | JOSEPH BURGOS | (619) 691-5027 | City of Chula Vista | 2001-02-04 | 2001-02-04 | 200 | 50 | 254 BONITA GLEN DR. | CHULA VISTA | SD | 91910 | MANHOLE | 0 | GREASE | GREASE BUILD UP IN SEWER MAIN | CLEANED AND FLUSHED SEWER MAIN | N/A | Y | NA | N/A | STORM DRAIN @ BONITA GLEN | Y | NA | N | NA | NA
10213 | FAX | 010213 9:15 AM | JESSE GOMEZ | (619) 691-5027 | City of Chula Vista | 2001-02-13 | 2001-02-13 | 50 | 25 | OTAY LAKES ROAD& RIDGEBACK | CHULA VISTA | SD | 91910 | MANHOLE | 0 | GREASE | GREASE BUILD UP IN SEWER MAIN | CLEANED AND FLUSHED SEWER MAIN | N/A | Y | NA | NA | OPEN UNLINED STORM CHANNEL @ CANYON DR. & OTAY LKS. RD. | N | NA | N | NA | NA
001018 | Fax to RWQCB | 1/2/01; 0830 | Allen Briski | (619) 556-6243 ext. 364 | US Navy | 2001-01-02 11:15 | 2001-01-02 02:15 | 50 | 0 | 8543 Hurlbut St. | San Diego | SD | 92123 | Sewer Cleanout in alley behind 8543 Hurlbut and Afton | 0 | Blockage | Resident reported children and friends used excess amount of toilet paper which blocked line. | Contractor confined area with sand, cleared stoppage, removed solids from area, sprayed disinfectant throughout area. | No | Yes | N/A | N/A | N/A | Yes | Y | N/A | 0 | Sewage stayed in the catch basin and did not travel downstream.
001019 | Not reportable | 01/03/01; 0715 | J. Ching, Code 662 | (619) 545-9146 | US Navy | 2001-01-03 07:15 | 2001-01-03 07:30 | 100 | 75 | Navy Outlying Field, Near Bldg. 193 | San Diego | SD | 91312 | Manhole overflowing | 3 | Vandalism | Main electrical switches were turned off at pump station 4949. | Put locking devices on Electrical panels, enclose lift station. | No | No | N/A | N/A | N/A | Yes, notified Clay Clifton on 01/03/01; 0955. | N | N/A | 0 | Most of the sewage was removed by Vac-truck, site was de-contaminated as per PWC SOP.
001020 | Not reportable | 1/4/2001; 0905 | PWC Duty Desk | (619) 556-7349 | US Navy | 2001-01-04 09:05 | 2001-01-04 09:25 | 15 | 10 | Naval Amphibious Base, Bldg. 905 | Coronado | SD | 92135 | Manhole near Bldg. 605 | 0 | Pump Station Failure | Lift station float failed. | Repaired float | No | No | N/A | N/A | N/A | No | N | N/A | 0 | Float failed at lift station.
001021 | Fax to RWQCB | 1/8/2001; 1515 | Mike Good, N&MCSD Safety | (619) 532-6018 | US Navy | 2001-01-08 06:00 | 2001-01-08 07:15 | 2000 | 1800 | Naval Hospital, Bldg. 26, Farenholt | San Diego | SD | 92134 | None, overflow from inside building | 0 | Blockage | Internal building plumbing backup caused overflow inside Bldg. 26. Backup rose above door threshold and flowed out of Bldg. And into street 200 gallons of which ended up in storm drain. | Blockage removed, 1,800 gallon of sewage recovered. | No | Yes | Possibly Florida Canyon. | San Diego Bay | Pacific Ocean | Yes, notified Clay Clifton on 01/03/01; 0955. | Yes, spoke with "Mr. Jeff" OES # 01-0137 | N/A | 0 | Blockage from building flowed out into the street. Conservative estimate is that 200 gallons went into storm drain.
001022 | Phone call to Victor Vasquez, and Fax to RWQCB | 1/17/01; 1440 | Jack Salerno, Naval Station San Diego | (619) 556-1319 | US Navy | 2001-01-17 12:49 | 2001-01-17 13:10 | 400 | 0 | Naval Station Pier 6 | San Diego | SD | 92136 | 8 inch pipe coupling under pier 6. | 0 | Pipe coupling under the pier separated. | Pipe coupling under the pier separated causing the leak. Leak estimated at 20 gpm for 20 min. | re-routed pier sewer line until coupling could be fixed. | Yes | No | San Diego Bay | Pacific Ocean | San Diego Bay | Yes, Notified Clay Clifton on 01/17/01 at 1440. | Yes, #01-0358 | No | N/A | none.
001029 | Voice Mail to Victor Vasquez, and Fax to RWQCB | 06/10/01; 2200 | Regional Dispatch Security | (619) 524-2030 | US Navy | 2001-06-10 18:37 | 2001-06-10 | 200 | 50 | Building 193, NOLF | Imperial Beach | SD | 92132 | lift station 4949 | 2 | Grease blockage in bubbler sensor | overflow ocurred because of faulty lift station that was clogged with grease. | Cleaned Line | No | No | N/A | N/A | N/A | y | No | No | N/A | Overflow was intermittent and not continuous. That is why the 5 gpm and the duration of the overflow does not equal 200 gallons.
001024 | Phone call to Victor Vasquez, and Fax to RWQCB | 01/26/01; 1140 | Tim Cuoto, PWC ASW Base | (619) 553-4144 | US Navy | 2001-01-26 09:53 | 2001-01-26 10:40 | 300 | 280 | ASW Base, Building #1 | San Diego | SD | 92147 | Sewer Manhole | 0 | Root Blockage | Roots probably blocked the line causing sewer overflow. | Cleared line with cutter. | No | No | N/A | N/A | N/A | Yes, Notified Clay Clifton on 01/26/01; 1040 | No | No | N/A | Remaining 20 gallons was absorbed into the asphalt / evaporated. This was not the galley spill which happened on 1/29/01. Galley spill was not reportable under order 96-04.
001025 | Phone call to Victor Vasquez, and Fax to RWQCB | 02/04/01; 1835 | Ron from the City of San Diego | (858) 654-4142 | City of San Diego | 2001-02-04 11:00 | 2001-02-04 12:38 | 16800 | 8400 | Murphy Canyon Housing | San Diego | SD | 92124 | Sewer Manholes | 1 | Vandalism | Rocks and Metal debris found in manhole | Cleared rocks and metal from manhole. | Unknown | Yes | San Diego River | N/A | N/A | Yes, Notified Clay Clifton on 02/04/01, 1840. | Yes, OES # 01-0745 | No | N/a | City of San Diego first responded to spill. City diverted spill to their tank farm. Navy PWC relieved City to finish repair/ cleanup. Spill was in remote canyon and was disinfected. RWQCB does not consider the collection of overflow into tank farm as containment so initial overflow volume reported was modified.
001026 | Phone call to Victor Vasquez, and Fax to RWQCB | 2001-02-20 | Mr. Simon, Harbor View base club | (619) 553-7160 | US Navy | 2001-02-20 11:09 | 2001-02-20 14:00 | 120 | 100 | Bldg. 530 cleanout, Naval Base Point Loma | San Diego | SD | 92106 | Bldg. 530 Sewer Clean out. | 1 | Grease Blockage | Building lateral clogged by grease causing overflow out of clean-out. | Cleaned / Hydroblasted lateral. | Yes | Yes | San Diego Bay | Pacific Ocean | Pacific Ocean | Yes, Notified Clay Clifton on 2/20/01; 1500, phone / fax. | Yes, OES # 01-1059 | No | N/A | 20 gallons of the overflow was not recovered and went in to the storm drain and then in to the Bay. Spill was located at the tip of the Point Loma base.
001027 | Not reportable | N/a | Base Security | Navy Outlying Landing Field | US Navy | 2001-03-01 06:23 | 2001-03-01 06:45 | 100 | 90 | NOLF Building 193 | San Diego | SD | 91312 | Manhole F26-4141 | 1 | Debris and Grease | Pump Controls in Wet Well blocked by excessive Debris. Pumped down manually. | Removed debris, need to install a device to cut up debris (commutator). | No | No | N/A | N/A | N/A | Yes, Notified Clay Clifton on 03/01/01; 0900 | No | No | N/a | Spill went into the street and parking lot. Remaining 10 gallons absorbed into the asphalt/evaporated. Site was dis-infected.
001028 | Voice Mail to Victor Vasquez, and Fax to RWQCB | 03/03/01; 1900 | Kevin, City of San Diego | City of San Diego Trouble Desk | US Navy | 2001-03-03 14:45 | 2001-03-03 17:15 | 3750 | 2625 | Murphy Canyon Housing | San Diego | SD | 92124 | Sewer Manhole | 0 | Grease Blockage | grease blockage in pipes/line between manholes | Hydroblasted line clear, increase frequency of maintenance | Yes | Yes | Storm drain southwest of I-15 and Aero Drive | San Diego River | Pacific Ocean | Yes, Notified Clay Clifton on 03/03/2001; 1900 phone/fax. | Yes, OES #01-1290 | No | N/A | 1,125 gallons entered the Storm Drain System. Area was cleaned and disinfected. City of San Diego waited on site. Diverted flow to lower manhole.
001-001 | N/A | 7/07/2000 0900 | Mr. Clemete | (619) 423-9068 | City of Imperial Beach | 2000-07-07 09:00 | 7/07/00 09:45 | 20 | 20 | 100 Block Citris Ave. MH# 68 | Imperial Beach | CA | 92132 | MH#68 | 0 | Grease/Small Roots | Grease blockage in line between MH#67 and MH#68. | Vactor truck used to clear line from MH# 67 to MH# 68. | N | N | N/A | N/A | Vactor to Sewer | N | N | N | 0 | Line was last cleaned on April 19, 2000. There is absolutely no reason this line should have an overflow in this short amount of time.
001-003 | N/A | 9/16/2000 0949 | Fire Dept Capt Smith | 911 | City of Imperial Beach | 2000-09-16 09:49 | 2000-09-16 10:15 | 50 | 50 | 221 Donax M/H#53 | Imperial Beach | CA | 92132 | M/H#53 | 0 | Grease/Small Roots | Roots and Grease found in line. 221 Donax has an underground garage that is the low spot in the line.Gargage sump pump sent sewerage to street. Spill ran to catch basin @ Palm and Seacoast leading to the storm drain wet-well. Storm drain wet-well was pumped to sewer. | Vactor truck jetted from M/H#52 to M/H#53 to alleviate blockage. Vactor then sent to Palm and Seacoast catch basin to recover. Gutters cleaned by fresh water wash-down from fire hydrant and broomed from spill site to Vactor. | N | Y | N/A | N/A | Vactor to Sewer | N | N | N | 0 | Sewerage from this part of town will never reach surface waters. Storm drain wet-well will collect and then be pumped to the sewer.
001-004 | N/A | 9/23/00 1730 | Sheriff Dept | 911 | City of Imperial Beach | 2000-09-23 17:20 | 2000-09-23 18:15 | 75 | 75 | 740 Seventh M/H#107 | Imperial Beach | CA | 92132 | M/H#107 | 0 | Large Towel/Rag | Towel in line allowed water to flow past towel but slowed solids to the point where a blockage was created. | Trailer jetter cleared the line and then provided fresh water to wash sewerage to Vactor. | N | N | N/A | N/A | Vactor to Sewer | N | N | N | 0 | Lines inspected again Monday 25Sep00 and was jetted again to achieve a full cleaning.
001-005 | Phone and Fax | 11/30/00 1600 | Mary Blair by Coronado Police | (619) 423-8311 | City of Imperial Beach | 2000-11-30 10:00 | 2000-11-30 16:30 | 1080 | 25 | 700 Block 8th Street in alley | Imperial Beach | Ca | 92132 | M/H#118 | 1 | Pumps "off" | Pumps were discovered in the "off" position. It is possible that the maintenance man failed to reset the pumps to "auto" mode following routine valve maintenance in the pump station on the day prior, November 29, 2000. If so, the pumps would not have kicked on at the present wet well water level, allowing the wet well to rise to the overflow condition some time around 10:00 A.M. Thursday, November 30, 2000. | Turned pumps on. Secured the storm drain, jetted S.D. lines and cleaned the entire site. Plan on installing locking lid on M.H. | Y | Y | Otay River | San Diego Bay | N/A | Y | Y | N | 0 | Dept of Health notified. They did not require signage.
001-006 | N/A | N/A | Alan J. Moeller | (619) 628-1372 | City of Imperial Beach | 2000-12-06 07:55 | 2000-12-06 08:05 | 10 | 10 | 100 Block Calla Ave | Imperial Beach | Ca | 92132 | M/H#70 | 1 | Pump Station Failure | Pump Station 5 failed and was found flooded. Sewerage was bypassed to P.S. 1A, and then 10gals were spilled. Failure occurred during a Level 3 electrical emergency state wide. It is possible that a low voltage condition caused the motor to draw more than the 27 AMP circuit breaker would allow, thus shutting down the station. | Alarm system will be installed during the next thirty days. | N | N | N/A | N/A | Vactor to Sewer | N | N | N | 0 | All 90s and "S" turns leading to this station jetted to prevent back-ups as a result of the lines being full.
001-007 | N/A | N/A | Mary Blair by Homeowner | (619) 423-8311 | City of Imperial Beach | 2001-03-29 17:55 | 2001-03-29 18:45 | 10 | 10 | 340 Citrus Ave | Imperial Beach | CA | 92132 | M/H#156 | 0 | Root Ball | Four residents on this line had plumbers out thi week. It is believed that plumbers pushed roots from laterals causing a partially self-relieving blockage. | Jetted line/Cleaned spill//Following day jetted adjacent lines as a precaution. | N | N | N/A | N/A | Vactor to Sewer | N | N | N | 0 | Resident responed quickly calling in resulting in a small spill.
00112 | N/A | N/A | N/A | N/A | City of Coronado | 2001-01-19 07:00 | 2001-01-19 09:00 | 100 | 100 | 336 Palm Avenue | Coronado | SD | 92118 | Sewer main | 0 | Grease | Grease from unknown source blocked sewer main | Used Vactor to clear line, cleaned line | N | N | N/A | N/A | N/A | N | N | N | N/A
00113 | N/A | N/A | N/A | N/A | City of Coronado | 2001-02-14 19:00 | 2001-02-14 19:30 | 15 | 15 | 950 Country Club Lane | Coronado | SD | 92118 | Sewer main | 0 | Debris | Toilet paper blocked sewer main | Cleaned sewer line | N | N | N/A | N/A | N/A | N | N | N | N/A
00114 | Fax | 2001-02-16 11:30 | Charles Kamenides | (619) 522-7387 | City of Coronado | 2001-02-16 10:00 | 2001-02-16 10:25 | 120 | 100 | 1201 First Street | Coronado | SD | 92118 | Private lateral | 1 | Grease | Grease from restaurant power-washing lateral. Operator did not clean entire line, thus causing blockage | Instructed property manager to clean and videotape lateral. Met with restaurant owners and instructed them to develop preventive maintenance schedule. | Y | Y | San Diego Bay | None | N/A | Y | N | Y | 3
00115 | N/A | N/A | N/A | N/A | City of Coronado | 2001-02-19 08:30 | 2001-02-19 09:30 | 100 | 100 | Orange/RH Dana Place | Coronado | SD | 92118 | Private lateral | 0 | Grease | Company employees cleaned sewer lateral; released water/grease onto street, ponding along curb/gutter | Instructed company to keep water from running off private property onto public property. | N | N | N/A | N/A | N/A | N | N | N | N/A
001002 | Rebecca Stewart | 2001-03-13 15:00 | Martin Holmes | (619) 258-4706 | Padre Dam MWD | 2001-03-12 12:30 | 03/12/01 13:15 | 300 | 300 | 10400 Second St. | Santee | SD | 92071 | Manhole #1089 and Manhole #1090 on 8" VCP | 0 | Grease | Manholes 1089 & 1090 backed up causing 4" lateral inside Santana High School parking lot to overflow. All sewage pooled in lower parking lot adjacent to Auto Shop. | Vactor truck cleared blockage of grease from MH #1088. Cleaned lower parking lot of all debris and material. Vactored up all sewage pooled in parking lot and washed down parking lot. Vactored up wash-down water. | N | N | None | None | Confined to lower parking lot. | Y | NA | N | 0 | Area of spill was coned off to prevent public contact.
001003 | FAX & Victor Vasquez | 2001-03-19 17:23 | City of Lemon Grove | (619)825-3810 | Lemon Grove | 2001-03-19 08:00 | 2001-03-19 11:30 | 3150 | 2100 | 1500 block Arthur Neil Ct, Rear Easement | Lemon Grove | SD | 91945 | 8" vc | 0 | Vandals:rocks,limbs,debris in manhole | MH cover removed, 30-40 rocks, fan palm fronds,sections of tree branch recovered. | All manholes along rear easement were cemented closed.Debris cleaned up, area raked and sanitized. | N | N | unmaintained open ditch | Chollas Creek/ SD Bay | 1000 feet of unmaintained open ditch . | Y | Y | N | NA
159126 | Fax 571-6972 | January 2, 2001/11:07am | Denise Steele | 6544160 | City of San Diego | 2001-01-02 08:19 | 2001-01-02 09:01 | 630 | 0 | 65th & Broadway | San Diego | SD | 92114 | 8" VC | 1 | Roots | Root blockage in 8" VC canyon main | Flushed 8" VC main to relieve stoppage. | Y | N | Canyon area | Canyon area | Absorbed into canyon ground | Y | N | N | N/A | N/A
159429 | Fax 571-6972 | January 3, 2001/1:25pm | Eric Swanson | 6544160 | City of San Diego | 2001-01-03 09:15 | 2001-01-04 09:45 | 1102.5 | 75 | 2972 Wing Street | San Diego | SD | 92106 | 6" VC | 1 | Debris | Parcel blocked line from debris & roots | Removed blockage, vactored, put on Root I. 6" VC | Y | N | Went down 400' & soaked into ground | N/A | N/A | Y | Y | N | N/A | N/A
159886 | Fax 571-6972 | January 5, 2001/4:31pm | Eric Swanson | 6544160 | City of San Diego | 2001-01-05 14:04 | 2001-01-05 14:30 | 260 | 260 | 4042 Illinois Street | San Diego | SD | 92104 | 6" VC | 1 | Grease | Heavy grease in main | Crews responded, vactored to contain total overflow. 6" VC | N | N | Alley/street surface | Puddle at end of alley | Vactored | Y | N/A | N | N/A | N/A
159903 | Fax 571-6972 | January 5, 2001/7:22pm | Doug Branco | 6544160 | City of San Diego | 2001-01-05 15:52 | 2001-01-05 16:45 | 53 | 0 | 210 Coast Blvd | San Diego | SD | 92037 | 6" VC | 1 | Roots | Root blockage | Flushed line to relieve stop. 6" VC | Y | N | Flowed into underground garage & entered private drain, drained on beach & sand | Pacific Ocean | N/A | Y | Y | N | N/A | N/A
159834 | Fax 571-6972 | January 5, 2001/2:04pm | Eric Swanson | 6544160 | City of San Diego | 2001-01-05 07:40 | 2001-01-05 10:30 | 95 | 45 | 3788 Dove Street | San Diego | SD | 92103 | 6" VC | 1 | Debris | Blocked w/ debris | TV section of main, cleaned, vactored 45 gallons of sewer. 6" VC | Y | N | Puddle on side of house | Soaked into ground | Next to house | Y | Y | N | N/A | N/A
160101 | Fax 571-6972 | January 6, 2001/3:36pm | Doug Branco | 6544160 | City of San Diego | 2001-01-06 11:53 | 2001-01-06 13:15 | 41 | 26 | 2415 Winship Lane | San Diego | SD | 92101 | 8" VC | 1 | Debris | Blocked from debris consisting of wood & cement | Flushed line to relieve stop. 8" VC | N | N | Overflow seepage trapped in drainage vault & vactored | N/A | Dried in street | Y | N/A | N | N/A | N/A
160711 | Fax 571-6972 | January 10, 2001/8:00am | Epikopo Semo | 6544160 | City of San Diego | 2001-01-09 08:03 | 2001-01-09 09:57 | 2850 | 500 | 754 Bonair Street | San Diego | SD | 92037 | 8" VC | 1 | Roots | Root blockage on 350' section, rod main to relieve blockage | Will be televised. 8" VC | Y | Y | Entered storm drain | Outlet pipe | Pacific Ocean | Y | Y | Y | 3 | 7 signs posted
160933 | Fax 571-6972 | January 11, 2001/12:00pm | Gary Richardson | 6544160 | City of San Diego | 2001-01-10 16:44 | 2001-01-10 18:01 | 616 | 120 | 4804 60th Street | San Diego | SD | 92113 | 6" VC | 1 | Roots | Roots in main | Rodded 6" VC main to relieve stoppage, vactored overflow. | Y | Y | San Diego River | N/A | Pacific Ocean | Y | Y | N | N/A | N/A
160907 | Fax 571-6972 | January 10, 2001/12:30pm | Epikopo Semo | 6544160 | City of San Diego | 2001-01-10 10:41 | 2001-01-10 11:15 | 34 | 0 | 3714 Mac Tibby Street | San Diego | SD | 92117 | 8" VC | 1 | Grease | Flushed main to relieve grease stop | Televise 8" VC main, will refer to FEWD for grease | Y | Y | Storm drain | 34 gallons dissipated into storm drain | N/A | Y | Y | N | N/A | N/A
161118 | Fax 571-6972 | January 12, 2001/9:30am | Gary Neel | 6544160 | City of San Diego | 2001-01-11 09:00 | 2001-01-12 13:45 | 128250 | 0 | Genesee Ave & Calgary | San Diego | SD | 92145 | 15" VC | 1 | Surchrg/Rain | Heavy infiltration @ airbase caused main to surcharge, directly related to heavy rains | Set up by pass pumps to relieve overflow, refer to Engineering. 15" VC | Y | N | Rose Creek | Mission Bay | Pacific Ocean | Y | Y | Y | Unknown | N/A
161261 | Fax 571-6972 | January 12, 2001/12:20pm | Les Finch | 6544160 | City of San Diego | 2001-01-12 08:49 | 2001-01-12 09:30 | 123 | 25 | 8th Ave & G st. | San Diego | SD | 92101 | 10" VC | 1 | Grease | Grease stoppage | Clean & TV for source of grease. 10" VC | Y | Y | Storm drain | San Diego Bay | N/A | Y | Y | N | N/A | N/A
161519 | Fax 571-6972 | January 13, 2001/3:53pm | Doug Branco | 6544160 | City of San Diego | 2001-01-13 08:51 | 2001-01-13 11:30 | 1590 | 0 | 3972 Jackdaw Street | San Diego | SD | 92103 | 8" Unknown | 1 | Roots | Root blockage | Contained overflow, vactored system. 8" | Y | Y | Soaked into hillside & dissipated in system | San Diego Bay/Pacific Ocean | N/A | Y | Y | N | N/A | N/A
161591 | Fax 571-6972 | January 14, 2001/3:10pm | Doug Branco | 6544160 | City of San Diego | 2001-01-14 13:23 | 2001-01-14 13:50 | 54 | 0 | 6170 Durant Street | San Diego | SD | 92122 | 8" VC | 1 | Roots | Root blockage | Flushed line to relieve root stop. 8" VC | Y | Y | Entered storm drain & dissipated in system | Rose Creek/San Diego Bay | N/A | Y | Y | N | N/A | N/A
161779 | Fax 571-6972 | January 16, 2001/2:30pm | Les Finch | 6544160 | City of San Diego | 2001-01-16 09:15 | 2001-01-16 12:30 | 195 | 0 | 1829 31st Street | San Diego | SD | 92102 | 6" CP | 1 | Roots | Roots & grease caused partial blockage | Evaluate maintenance site, 6" CP | N | N | N/A | N/A | Soaked into canyon | Y | Y | N | N/A | N/A
162165 | Fax 571-6972 | January 22, 2001/2:00pm | Kent Vian | 6544160 | City of San Diego | 2001-01-17 07:27 | 2001-01-17 10:52 | 2050 | 0 | Jackson Dr. & Navajo Rd. | San Diego | SD | 92120 | 8" VC | 1 | Debris | Blockage caused by disposable diapers | Will TV and put on 12 month MC schedule. 8" VC | N | N | Canyon behind Patrick Henry H.S. | N/A | Dried in canyon | Y | Y | N | N/A | N/A
162435 | Fax 571-6972 | January 18, 2001/2:00pm | Gary Richardson | 6544160 | City of San Diego | 2001-01-18 10:34 | 2001-01-18 11:20 | 230 | 200 | 4064 Monroe Ave | San Diego | SD | 92116 | 6" CP | 2 | Gravity Break | Overflow caused by a break in the main | Flushed, rodded, turned over to construction.6" CP | Y | Y | Storm drain | N/A | Dissipated into system | Y | Y | N | N/A | N/A
162673 | Fax 571-6972 | January 19, 2001/1:45pm | Les Finch | 6544160 | City of San Diego | 2001-01-19 09:06 | 2001-01-19 09:40 | 34 | 30 | 3660 Richmond Street | San Diego | SD | 92103 | 8" VC | 1 | Gravity Break | Break in main caused blockage from roots, rocks & debris | Refered for construction. 8" VC | Y | Y | Storm drain | Pooled @ storm drain exit | N/A | Y | Y | N | N/A | N/A
162980 | Fax 571-6972 | January 20, 2001/5:04pm | Doug Branco | 6544160 | City of San Diego | 2001-01-20 13:52 | 2001-01-20 15:38 | 530 | 0 | 17809 Pueblo Vista Lane | San Diego | SD | 92127 | 8" PVC | 1 | Grease | Blockage caused by roots & grease | Machine rodded to relieve stop. Cleaned roots. 8" PVC | Y | N | Flowed into canyon & soaked into floor | Lake Hodges | N/A | Y | Y | N | N/A | N/A
162956 | Fax 571-6972 | January 20, 2001/8:22pm | Doug Branco | 6544160 | City of San Diego | 2001-01-20 09:09 | 2001-01-20 09:56 | 23 | 0 | 3725 Federal Blvd | San Diego | SD | 92101 | 6" VC | 1 | Roots | Root blockage | Flushed line to relieve blockage. 6" VC | Y | Y | Entered storm drain & dissipated into system | Chollas Creek/San Diego Bay | N/A | Y | Y | N | N/A | N/A
163044 | Fax 571-6972 | January 21, 2001/5:00pm | Doug Branco | 6544160 | City of San Diego | 2001-01-21 13:52 | 2001-01-21 15:09 | 100 | 0 | 3175 B Street | San Diego | SD | 92102 | 6" VC | 1 | Roots | Overflowed & soaked into backyard | Flushed line to relieve stop. 6" VC | N | N | Overflowed into canyon & soaked into hillside | N/A | Soaked into canyon & back yard | Y | N/A | N | N/A | N/A
163126 | Fax 571-6972 | January 22, 2001/1:25pm | Les Finch | 6544160 | City of San Diego | 2001-01-22 08:40 | 2001-01-22 09:45 | 65 | 40 | 2980 Worden Street | San Diego | SD | 92110 | 8" VC | 1 | Roots | Heavy roots caused partial stoppage | Put main on maint. site, applied root inhibitor. 8" VC | Y | N | Dried in gutter | N/A | Dried in gutter | Y | Y | N | N/A | N/A
163442 | Fax 571-6972 | January 24, 2001/12:30am | Jeff Wilder | 6544160 | City of San Diego | 2001-01-23 15:15 | 2001-01-23 15:48 | 66 | 20 | 1405 Diamond Street | San Diego | SD | 92109 | 6" CP Main | 1 | Roots | Root blockage | Vacuum overflow. Rod main to relieve stop. TV main. 6" CP | N | N | N/A | N/A | Vactored 20 gal. that puddled /remainder soaked into ground | Y | Y | N | N/A | N/A
163903 | Fax 571-6972 | January 25, 2001/6:30pm | Rick Donahue | 6544160 | City of San Diego | 2001-01-25 08:30 | 2001-01-25 17:30 | 90 | 60 | 4243 Ingraham Street | San Diego | SD | 92109 | 6" CP | 1 | Gravity Break | Partial collapse on main caused partial blockage | Flushed by machine to relieve stoppage. 6" CP | Y | Y | N/A | N/A | Dried in parking lot & dissipated into storm drain | Y | Y | N | N/A | N/A
164362 | Fax 571-6972 | January 27, 2001/7:27pm | Doug Branco | 6544160 | City of San Diego | 2001-01-27 16:50 | 2001-01-27 17:35 | 1350 | 0 | 6808 Potomac Street | San Diego | SD | 92139 | 10" PVC | 1 | Rocks | Blockage caused by rocks & debris | Flushed line to relieve stop. 10" PVC | N | Y | Entered storm drain | N/A | Flowed down valley & dissipated into system | Y | Y | N | N/A | N/A
164413 | Fax 571-6972 | January 28, 2001/7:17pm | Doug Branco | 6544160 | City of San Diego | 2001-01-28 17:25 | 2001-01-28 18:00 | 35 | 0 | 6020 Wanda Ct. | San Diego | SD | 92120 | 8" VC | 2 | Grease | Grease blockage | Flushed line to relieve stop. 8" VC | N | Y | Entered storm drain | N/A | Dissipated into storm drain | Y | Y | N | N/A | N/A
164408 | Fax 571-6972 | January 28, 2001/4:57pm | Doug Branco | 6544160 | City of San Diego | 2001-01-28 14:36 | 2001-01-28 15:40 | 32 | 0 | 3360 Nutmeg Street | San Diego | SD | 92104 | 6" CP | 1 | Roots | Root blockage | Flushed line after relieving stop. 6" CP | N | Y | Entered storm drain & flowed into canyon hillside | N/A | Soaked into canyon | Y | Y | N | N/A | N/A
165134 | Fax 571-6972 | February 1, 2001/3:30pm | Rick Donahue | 6544160 | City of San Diego | 2001-01-31 13:21 | 2001-01-31 14:20 | 59000 | 60000 | Olivera & San Jacinto | San Diego | SD | 92113 | 6" CP, 8" CP, 8" VC | 1 | Construction | Water main broke, water entered system causing a surcharge | Flushed. 6" CP, 8" CP, 8" VC | Y | Y | Entered storm drain @ several locations | N/A | Flowed into dry creek bed, pumped back into system | Y | Y | N | N/A | N/A
166156 | Fax 571-6972 | February 2, 2001/1:30pm | Les Finch | 6544160 | City of San Diego | 2001-02-02 08:20 | 2001-02-02 09:55 | 50 | 0 | 2610 Covington Rd | San Diego | SD | 92104 | 8" CP | 1 | Grease | Heavy grease caused partial blockage | 8" CP, Hand rodded in canyon, flushed & rodded from street. | N | N | N/A | N/A | Soaked into ground | Y | Y | N | N/A | N/A
166128 | Fax 571-6972 | February 2, 2001/2:30pm | Denise Steele | 6544160 | City of San Diego | 2001-02-02 10:27 | 2001-02-02 12:15 | 216 | 116 | 783 Manning Way | San Diego | SD | 92154 | 8" VC | 1 | Roots | Root blockage | 8" VC, Flushed to relieve stop, had confine space crew clean MH116,refer TV | N | N | N/A | N/A | Vactored spill, remaining absorbed into soil in back yard | Y | Y | N | N/A | N/A
166263 | Fax 571-6972 | February 2, 2001/11:00pm | Doug Branco | 6544160 | City of San Diego | 2001-02-02 20:24 | 2001-02-02 10:02 | 294 | 0 | 421 61st Street | San Diego | SD | 92114 | 8" PVC | 1 | Roots | Heavy roots in manhole | 8" PVC, Flushed line to remove blockage, cleaned roots from channel | N | Y | Entered storm drain & dissipated into system | N/A | Dissipated into system | Y | Y | N | N/A | N/A
166409 | Fax 571-6972 | February 3, 2001/6:08pm | Doug Branco | 6544160 | City of San Diego | 2001-02-03 08:02 | 2001-02-03 08:55 | 75 | 0 | Blue Lake Dr & Cowles Mtn Blvd | San Diego | SD | 92119 | 8" VC | 1 | Other | Stoppage unknown | 8" VC, Rodded main for protection, refer to area supervisor | N | Y | Entered storm drain | N/A | Dissipated into storm drain | Y | Y | N | N/A | N/A
167344 | Fax 571-6972 | February 10, 2001/8:00am | Gary Richardson | 6544160 | City of San Diego | 2001-02-08 16:38 | 2001-02-08 18:45 | 1016 | 520 | 330 S. Royal Oak Dr. | San Diego | SD | 92114 | 8" VC Main | 1 | Grease | Grease in main | 8" VC, Vacuum Overflow, flush to relieve stoppage & clean main. | Y | Y | Entered storm drain | N/A | Dissipated into system | Y | Y | N | N/A | N/A
167541 | Fax 571-6972 | February 9, 2001/7:14pm | Doug Branco | 6544160 | City of San Diego | 2001-02-09 13:09 | 2001-02-09 15:25 | 136 | 0 | 9885 Carroll Canyon Road | San Diego | SD | 92131 | 10" PVC | 1 | Roots | Root blockage | 10" PVC, Cleaned roots from Channel of MH to relieve stop, Rod line. | N | N | Flowed into property drain & soaked into the ground | N/A | Soaked into ground on property | Y | Y | N | N/A | N/A
167767 | Fax 571-6972 | February 10, 2001/12:38pm | Doug Branco | 6544160 | City of San Diego | 2001-02-10 09:14 | 2001-02-10 10:10 | 10 | 0 | 4066 Loma Alta Drive | San Diego | SD | 92115 | 6" VC | 1 | Roots | Root blockage | Machine rodded to relieve stop. Refer to area supervisor. 6" VC | N | N | Dried in curb | N/A | Dried in curb | Y | Y | N | N/A | N/A
167813 | Fax 571-6972 | February 11, 2001/4:45pm | Doug Branco | 6544160 | City of San Diego | 2001-02-11 12:40 | 2001-02-11 14:22 | 1020 | 0 | 3013 Village Pine Drive | San Diego | SD | 92173 | 8" VC | 1 | Grease | Grease blockage | Flushed line to relieve stop, vactor MH for heavy grease, refer to supr. 8" VC | N | Y | Entered storm drain & dissipated into system | N/A | Dissipated into system | Y | Y | N | N/A | N/A
161096 | Fax 571-6972 | February 14, 2001/3:30pm | Rick Donahue | 6544160 | City of San Diego | 2001-02-13 22:30 | 2001-02-14 02:30 | 480 | 0 | Rose Creek between Genesee Av & 805 | San Diego | SD | 92122 | 15" VC | 2 | Surcharge | Heavy infiltration from air station caused surcharge in main, caused by ruptured discharge hose | Shut down pump at low flow, replaced hose, started bypass opr. 15" VC | Y | N | Rose Creek | Mission Bay | Pacific Ocean | Y | Y | N | N/A | N/A
168252 | Fax 571-6972 | February 14, 2001/12:42pm | Eric Swanson | 6544160 | City of San Diego | 2001-02-14 07:04 | 2001-02-14 08:30 | 60 | 0 | 5582 Cambria Court | San Diego | SD | 92120 | 8" VC | 1 | Roots | Roots in main caused partial back-up | Clean Section of main for TV inspection of main. 8" VC | N | Y | Entered storm drain | N/A | Dissipated into storm drain | Y | Y | N | N/A | N/A
168291 | Fax 571-6972 | February 14, 2001/10:14pm | Jeff Wilder | 6544160 | City of San Diego | 2001-02-14 13:01 | 2001-02-14 14:33 | 450 | 0 | 839 S. 32d Street | San Diego | SD | 92113 | 8" CI | 1 | Grease | Grease build-up | Flushed main relieved stoppage, add to cleaning schedule vactor puddles. 8"CI | N | N | N/A | Street surface (dirt road) | Soaked into ground | Y | Y | N | N/A | N/A
168516 | Fax 571-6972 | February 15, 2001/12:00pm | Epikopo Semo | 6544160 | City of San Diego | 2001-02-15 08:03 | 2001-02-15 09:20 | 1155 | 500 | 6314 Friars Road | San Diego | SD | 92108 | 8" VC | 1 | Roots | Roots & grease caused blockage | 8'VC, will refer main for TV. | Y | Y | Storm drain | San Diego River | Pacific Ocean @ dog beach | Y | Y | Y | Unknown | 7 signs were posted
168995 | Fax 571-6972 | March 1, 2001/3:00pm | Gary Richardson | 6544160 | City of San Diego | 2001-02-18 10:44 | 2001-02-18 13:35 | 25650 | 18450 | 5041 Tierra Baja Way | San Diego | SD | 92115 | 8" VC | 1 | Gravity Break | Blockage caused by a section of missing pipe that allowed roots to enter | 8" VC, Tape shows missing pipe, referred to construction for repair. | Y | Y | Entered storm drain | San Diego River | Pacific Ocean @ dog beach | Y | Y | N | N/A | N/A
170589 | Fax 571-6972 | March 1, 2001/4:30pm | Rick Donahue | 6544160 | City of San Diego | 2001-02-19 12:00 | 2001-02-28 16:30 | 1500000 | 0 | Mt. Acadia & Snead Av. | San Diego | SD | 92111 | 15" | 1 | Rocks | Debris & rags caused partial blockage | 15", Rodded main by hand and machine, TV. | Y | N | Tecolote Creek | Mission Bay | Pacific Ocean | Y | Y | Y | over 100 | 2 signs posted
169041 | Fax 571-6972 | February 19, 2001/2:10pm | Mike Bedard | 6544160 | City of San Diego | 2001-02-19 12:26 | 2001-02-19 13:00 | 170 | 100 | 4502 Melissa Way | San Diego | SD | 92117 | 8" VC | 1 | Roots | Root blockage | 8" VC, Removed roots and recovered sewage. | Y | Y | Entered storm drain | Canyon | Dreid in canyon | Y | Y | N | N/A | N/A
169867 | Fax 571-6972 | February 23, 2001/4:15pm | Doug Branco | 6544160 | City of San Diego | 2001-02-23 13:41 | 2001-02-23 14:50 | 690 | 0 | 2445 Hidden Valley Road | San Diego | SD | 92037 | 8" VC | 1 | Roots | Root blockage | 8" VC, Flushed line to relieve blockage. Refer to area supervisor. | Y | Y | Entered storm drain behind address | Pacific Ocean | N/A | Y | Y | Y |  | 8 signs posted
| Fax 571-6972 | February 26, 2001/3:20pm | Johnny Mitchell | 6544160 | City of San Diego | 2001-02-26 12:51 | 2001-02-26 12:58 | 700 | 200 | 2200 W. Citracado Parkway | San Diego | SD | 92025 | N/A | 0 | Surcharge | Additional flow pumped into main and caused gravity line to back-up | Pump Sta. 77a&77 Booster, reinstalled lockdown screws to MH. | Y | Y | Escondido Creek | N/A | N/A | Y | Y | N | N/A | PRIVATE SPILL
170054 | Fax 571-6972 | February 26, 2001/9:45pm | Jeff Wilder | 6544160 | City of San Diego | 2001-02-26 10:32 | 2001-02-26 12:20 | 540 | 0 | 10405 San Diego Mission Road | San Diego | SD | 92108 | 8" VC | 1 | Debris | Flat main & debris caused back-up | 8" VC, Cleaned main and placed on PM site for cleaning. | Y | Y | San Diego River | Pacific Ocean | N/A | Y | Y | N | N/A | N/A
170374 | Fax 571-6972 | February 27, 2001/11:40am | Denise Steele | 6544160 | City of San Diego | 2001-02-27 07:00 | 2001-02-27 10:01 | 1810 | 0 | Toyon Road & Yerba Santa | San Diego | SD | 92115 | 8" VC | 1 | Grease | Grease blockage | 8" VC, Rodded to reliev stop. | Y | Y | Storm drain | Alvarado Creek/San Diego River | Pacific Ocean | Y | Y | Y | 1 | 10 signs posted
170591 | Fax 571-6972 | February 28, 2001/4:20pm | Les Finch | 6544160 | City of San Diego | 2001-02-28 13:00 | 2001-02-28 13:45 | 90 | 0 | 2934 F Street, in alley | San Diego | SD | 92102 | 6" VC | 1 | Grease | Heavy grease caused partial blockage | 6" VC, Cleaned main, TV, refer for Grease program. | Y | Y | Storm drain | Street & San Diego Bay | N/A | Y | Y | N | N/A | N/A
170748 | Fax 571-6972 | March 1, 2001/11:06pm | Jeff Wilder | 6544160 | City of San Diego | 2001-03-01 16:43 | 2001-03-01 19:07 | 2880 | 740 | 4211 Swift | San Diego | SD | 92104 | 6" CP Main | 1 | Gravity Break | Main break | 6" CP, Vacuum overflow, rod main, setup by-pass pump. | Y | Y | Storm channel along 805 | San Diego Bay | N/A | Y | Y | N | N/A | N/A
171258 | Fax 571-6972 | March 5, 2001/12:03pm | Eric Swanson | 6544160 | City of San Diego | 2001-03-05 07:34 | 2001-03-05 09:15 | 65 | 0 | 5929 Ridgemoor Dr. | San Diego | SD | 92120 | 8" VC | 2 | Roots | Roots caused partial blockage | 8" VC, Relieve stoppage. TV main Root-I main. | N | N | Soaked into ground | N/A | Soaked into ground | Y | Y | N | N/A | N/A
172201 | Fax 571-6972 | March 8, 2001/10:05pm | Jeff Wilder | 6544160 | City of San Diego | 2001-03-08 16:30 | 2001-03-08 19:00 | 2250 | 0 | 6206 Oakridge Rd. | San Diego | SD | 92120 | 8" VC Main | 1 | Roots | Root blockage | MH36 8"VC main, Rod main, Cleaned Roots- Refer to have MH cleaned. | N | N | N/A | N/A | Soaked into canyon | Y | Y | N | N/A | N/A
172021 | Fax 571-6972 | March 8, 2001/11:35am | Les Finch | 6544160 | City of San Diego | 2001-03-08 06:33 | 2001-03-08 07:55 | 410 | 0 | 515 San Gorgonio St. | San Diego | SD | 92106 | 6" CP | 1 | Other | Rags & paper stuck on broken screw caused partial stop | 6" CP main, TVing to evaluate main condition and maint. schedule. | Y | Y | San Diego Bay | San Diego Bay | N/A | Y | Y | Y | Unknown | 11 signs posted
172217 | Fax 571-6972 | March 9, 2001/11:30am | Les Finch | 6544160 | City of San Diego | 2001-03-09 07:30 | 2001-03-09 08:40 | 70 | 0 | 855 32nd St. | San Diego | SD | 92102 | 8" VC | 1 | Debris | Debris & large rocks caused partial stop | 8" VC main, TV main & evaluate for maint. site. Washed area & recovered. | Y | N | Soaked into dirt | Storm drain inlet | N/A | Y | Y | N | N/A | N/A
172265 | Fax 571-6972 | March 9, 2001/6:30pm | Les Finch | 6544160 | City of San Diego | 2001-03-09 14:19 | 2001-03-09 15:30 | 142 | 50 | 2860 Chatsworth Blvd. | San Diego | SD | 92133 | 8" CP | 1 | Roots | Roots & grease caused partial stoppage | 8" CP main, TV & evaluate for freguency of cleaning. | Y | N | Dried in curb | Beachline & storm drain | N/A | Y | Y | N | N/A | N/A
172416 | Fax 571-6972 | March 10, 2001/8:22am | Jose Oropeza | 6544160 | City of San Diego | 2001-03-10 08:22 | 2001-03-10 09:12 | 1000 | 0 | 4301 Collwood Lane | San Diego | SD | 92105 | 12" VC | 1 | Other | Plumber snake, rags & paper caused blockage | 12' VC main, Rodded sewer main, TV 12" sewer line. | Y | Y | Storm drain | San Diego River | Mission Bay Channel/Pacific Ocean | Y | Y | N | N/A | N/A
172438 | Fax 571-6972 | March 10, 2001/7:42pm | Doug Branco | 6544160 | City of San Diego | 2001-03-10 16:07 | 2001-03-10 17:25 | 78 | 0 | 10935 Barbados Way | San Diego | SD | 92126 | 8" VC | 1 | Grease | Grease blockage | 8" VC main, Machine Rodded - Refer to area supervisor. | Y | Y | Storm drain | N/A | Dissipated into system | Y | Y | N | N/A | N/A
172509 | Fax 571-6972 | March 11, 2001/10:57pm | Doug Branco | 6544160 | City of San Diego | 2001-03-11 20:40 | 2001-03-11 21:03 | 230 | 0 | 2860 Chatsworth Blvd | San Diego | SD | 92106 | 8" CP | 1 | Roots | Rodding line, line backed up, machine malfunctioned, overflowed before assistance could set up | 8" CP main, Contain overflow, rodded main, refer to area supervisor. | Y | Y | Storm drain/flowed into San Diego Bay | N/A | San Diego Bay | Y | Y | N | N/A | N/A
172833 | Fax 571-6972 | March 13, 2001/11:52pm | Carl Mickelson | 6544160 | City of San Diego | 2001-03-13 17:57 | 2001-03-13 18:58 | 30 | 15 | 5518 Elgin Avenue | San Diego | SD | 92120 | 8" VC | 1 | Gravity Break | Broken sewer main | 8" VC main, TV main for possible repairs. | Y | N | Street | N/A | Dried in gutter | Y | Y | N | N/A | N/A
173068 | Fax 571-6972 | March 14, 2001/10:00pm | Jeff Wilder | 6544160 | City of San Diego | 2001-03-14 17:40 | 2001-03-14 19:27 | 100 | 0 | 5620 Trinadad Way | San Diego | SD | 92113 | 6" CP Main | 1 | Roots | Roots in main | 6" CP main, Hand Rod, put on PM site, called for cleanup crew. | N | N | N/A | N/A | Puddled & soaked into ground | Y | Y | N | N/A | N/A
172995 | Fax 571-6972 | March 14, 2001/12:01pm | Denise Steele | 6544160 | City of San Diego | 2001-03-14 08:47 | 2001-03-14 09:35 | 1200 | 1200 | 927 La Huerta Way | San Diego | SD | 92154 | 8" VC | 1 | Grease | Grease build-up in main | 8" VC main, Flushed, washed, and vactored. | Y | Y | Storm drain | N/A | Vactored out of storm drain & returned to system | Y | Y | N | N/A | N/A
173997 | Fax 571-6972 | March 18, 2001/6:10pm | Doug Branco | 6544160 | City of San Diego | 2001-03-18 15:41 | 2001-03-18 16:30 | 25 | 0 | 1439 Savoy Circle | San Diego | SD | 92107 | 6" VC | 1 | Rocks | Rocks left in main | 6" VC main, Vactor, Flush line. | N | N | Dried in curb | N/A | Dried in curb | Y | Y | N | N/A | N/A
174092 | Fax 571-6972 | March 22, 2001/10:00am | Robert York | 6544160 | City of San Diego | 2001-03-21 12:45 | 2001-03-21 21:00 | 19800 | 12600 | El Paseo Grande & Discovery Way | San Diego | SD | 92037 | 8" VC Sewer Main | 1 | Construction | Main damaged by private contractor | Sewer main repair completed. | Y | Y | Storm drain | Pacific Ocean | Pacific Ocean | Y | Y | Y | Still posted | 18 signs posted
174694 | Fax 571-6972 | March 21, 2001/11:10pm | Carl Mickelson | 6544160 | City of San Diego | 2001-03-21 15:16 | 2001-03-21 17:15 | 1190 | 0 | 2648 Island Avenue | San Diego | SD | 92113 | 6" VC | 1 | Roots | Roots growing in main | 6" VC main, refer to area supervisor for maintenance. | Y | Y | Storm drain | San Diego Bay | San Diego Bay | Y | Y | N | N/A | N/A
175033 | Fax 571-6972 | March 30, 2001/10:00am | Rick Donahue | 2218728 | City of San Diego | 2001-03-22 15:36 | 2001-03-22 17:21 | 525 | 20 | 3731 Aragon Drive | San Diego | SD | 92115 | 6" VC | 1 | Roots | Roots growing in main | 6" VC main, refer to unit 8792 for PM sched. after TV review. | Y | Y | Storm drain | Dissipated into storm drain | N/A | Y | Y | N | N/A | N/A
175334 | Fax 571-6972 | March 23, 2001/10:47am | Doug Branco | 6544160 | City of San Diego | 2001-03-23 17:16 | 2001-03-23 20:15 | 2685 | 1130 | 4987 Acuna Street | San Diego | SD | 92117 | 10" VC | 1 | Vandalism | Vandalism (manhole strap, rocks, wood & bricks) | 10" VC main, Setup pump, rod line, probe MH. will return for followup. | Y | Y | Dissipated in Tecolote Creek | N/A | Dissipated in canyon creek | Y | Y | N | N/A | N/A
175317 | Fax 571-6972 | March 23, 2001/3:45pm | Les Finch | 6544160 | City of San Diego | 2001-03-23 13:50 | 2001-03-23 14:15 | 10 | 0 | 1318 Bush St. | San Diego | SD | 92103 | 4" CP | 1 | Roots | Root blockage | 4" CP main, Relieved main & TV to evaluate condition. | N | N | N/A | N/A | Soaked into ground | Y | Y | N | N/A | N/A
175612 | Fax 571-6972 | April 2, 2001/1:00pm | Rick Donahue | 6544160 | City of San Diego | 2001-03-25 08:10 | 2001-03-27 14:10 | 41100 | 41100 | 5700 Genesee Avenue | San Diego | SD | 92117 | 10" VC | 1 | Roots | Root blockage | 10" VC main, Rodded by machine, Televise and evaluate. | Y | N | San Clemente Creek | Mission Bay | Flowed to interceptor & returned to system | Y | Y | Y | 3 days | 15 signs posted
175637 | Fax 571-6972 | March 28, 2001/9:25am | Les Finch | 6544160 | City of San Diego | 2001-03-25 18:04 | 2001-03-25 20:07 | 12300 | 0 | 29th & Broadway (in canyon) | San Diego | SD | 92102 | 10" VC | 1 | Construction | 48" piece of PVC pipe & roots in manhole, rocks in main | 10" VC main, Cleaned, TV'd. | Y | Y | Storm drain & flowed into San Diego Bay | N/A | San Diego Bay | Y | Y | Y | Still posted | 5 signs posted
175756 | Fax 571-6972 | March 26, 2001/8:53pm | Jeff Wilder | 6544160 | City of San Diego | 2001-03-26 18:03 | March 26, 201 6:56 pm | 265 | 75 | 3621 Aragon Drive | San Diego | SD | 92115 | 6" VC Main | 2 | Roots | Roots in main | 6" VC main, Flush main relieved stop, cleaned up street & gutters. | Y | Y | NE corner of Livingston & Aragon | Dried in storm culvert | N/A | Y | Y | N | N/A | N/A
176660 | Fax 571-6972 | March 29, 2001/1:40pm | Les Finch | 6544160 | City of San Diego | 2001-03-29 09:37 | 2001-03-29 10:40 | 126 | 0 | 2904 Market Street | San Diego | SD | 92101 | 6" PVC/VC | 1 | Gravity Break | Hill gave way, took PVC & caused main to leak | 6" PVC/VC main, called construction crew for repairs, cleaned storm drain. | N | Y | Storm drain | San Diego Bay | N/A | Y | Y | N | N/A | N/A
176722 | Fax 571-6972 | March 30, 2001/12:27am | Gary Ward | 6544160 | City of San Diego | 2001-03-29 15:17 | 2001-03-29 16:30 | 146 | 146 | 7760 Girard Avenue | San Diego | SD | 92037 | 6" CP | 1 | Gravity Break | Main break in alley | 6" CP main, Vactored overflow, called crew for repair. | Y | N | Contained in alley | N/A | Contained in alley | Y | Y | N | N/A | N/A
176718 | Fax 571-6972 | March 30, 2001/8:30am | Rick Donahue | 6544160 | City of San Diego | 2001-03-29 14:30 | 2001-03-29 16:10 | 155 | 0 | 2581 Quivira Ct. | San Diego | SD | 92109 | 8" VC | 1 | Debris | Inlet main blocked with tampon applicators | 8" VC main, Flushed, TV'd, inlet main. | Y | Y | Mission Bay | Pacific Ocean | Flowed through storm drain into bay | Y | Y | Y | Still posted | 119 signs posted
176879 | Fax 571-6972 | March 30, 2001/4:00pm | Rick Donahue | 6544160 | City of San Diego | 2001-03-30 10:30 | 2001-03-30 13:15 | 825 | 150 | 5031 Tierra Baja Way | San Diego | SD | 92115 | 8" CP | 1 | Gravity Break | Deteriorated main caused heay roots to partially stop main | Flushed and machine rodded, TV'd main and evaluated for PM schedule. | Y | Y | N/A | N/A | Flowed in gutter, dissipated in storm drain, vactored 150 gal., returned to system | Y | Y | N | N/A | N/A
176953 | Fax 571-6972 | March 31, 2001/9:45pm | Doug Branco | 6544160 | City of San Diego | 2001-03-31 17:12 | 2001-03-31 19:24 | 30 | 0 | 111 Las Flores Terrace | San Diego | SD | 92114 | 6" CP | 1 | Roots | Root blockage in M/H | Machine rodded, cleaned roots from MH, refer to area supervisor. | N | N | Dried in gutter | N/A | Dried in gutter | Y | Y | N | N/A | N/A
990041 | Voice Mail | 07/05/00 1725 | Mark Patnode | 7604355840 | Water Utilities Dept. City of Oceanside | 2000-07-05 15:52 | 07/05/00 1625 | 1500 | 1000 | Wooster Street Easement | Oceanside | SD | 92054 | City Manhole | 0 | Debris | Unknown debris in the city line. | City line was rodded by city crews. 100# chlorine was put into the system to burn off any debris left in line after rodding. | Y | N | Loma Alta Creek | Loma Alta Lagoon | N/A | Y | Y | Y | Three | Crew responded w/ vactor to contain & clean up. Most spill soaked into ground. Vactor sent downstream to recover spill & dilution water.
990042 | Victor Vasques | 07/21/00 1040 | Guss Pennell | 7609668795 | Water Utilities Dept. City of Oceanside | 2000-07-21 07:35 | 07/21/00 0750 | 80 | 30 | 915 North Pacific Street | Oceanside | SD | 92054 | 6 Inch Force Main | 0 | Line Break | Spill location is at an old repair to the 6 inch force main. Repair was made with two rubber couplings. The gaskets to the couplings blew out on the bottom of pipe. | Repair to 6 inch line was made with new couplings and new gaskets. Repairs were encased in concrete. | N | Y | Storm Drain | None | Soaked into sandy soil 70 yards from SLR River. | Y | Y | N | N/A | Collections crew recovered 30 gallons from the storm drain. Two tankers were called out to keep the P.S. wet well down until final repairs can be completed.
990043 |  |  | Michael Dumas | 7609414975 | Water Utilities Dept. City of Oceanside | 2000-08-02 15:27 | 08/02/00 1652 | 425 | 0 | 3344 Golf Crest Drive Easement | Oceanside | SD | 92056 | City Manhole | 0 | Debris | Grease & debris created a blockage. | Line was rodded and put on immediate inspection list for Tving. | N | N | N/A | N/A | Soaked into soil around manhole. | Y | N/A | N/A | N/A
990044 |  |  | Jeremy Kemp | 7604355842 | Water Utilities Dept. City of Oceanside | 2000-08-16 11:20 | 08/16/00 1200 | 100 | 0 | El Camino Golf Course Easement | Oceanside | SD | 92054 | City Manhole | 0 | Roots | Roots and debris blocked line. | Rodded line to break stopage. Will TV line to repair problem. | N | N | N/A | N | Soaked into soil around manhole. | Y | N/A | N/A | N/A
990045 |  |  | Mark Patnode | 7604355840 | Water Utilities Dept. City of Oceanside | 2000-08-30 10:45 | 08/30/00 1055 | 60 | 60 | Vista Campana North, #5 | Oceanside | SD | 92054 | City Manhole | 0 | Debris | Diapers and other rags in the city line. | Rodder broke stopage. Vactor cleaned it out. | N | N | N/A | N/A | Soaked into sidewalk & grass. | Y | N/A | N/A | N/A | The line will be checked by TV crew for possible problems.
990046 |  |  | Jeremy Kemp | 7604355842 | Water Utilities Dept. City of Oceanside | 2000-09-05 09:15 | 09/05/00 1230 | 100 | 100 | 4131 Tiberon Drive | Oceanside | SD | 92056 | Private Clean Out | 0 | Unknown | Stoppage in private apartment lateral. Residents popped the cap off the clean out and let it flow. We responded to keep it out of storm drain. | City vactor recovered spill. Plumber broke stoppage. City jetted the City Main to chasr the debris. | N | N | N/A | N | Recovered. | Y | N/A | N/A | N/A | Private spill contained and recovered.
990047 | Victor Vasques | 09/06/00 1240 | Jeremy Kemp | 7604355842 | Water Utilities Dept. City of Oceanside | 2000-09-06 09:05 | 09/06/00 0940 | 14000 | 0 | 4220 La Tiera Drive | Oceanside | SD | 92056 | 10 inch Force Main | 0 | Line Break | Home Owner was digging in his back yard with a Back Hoe and ripped out a 16 foot section of our Force Main | Lift Station was shut down & tanker trucks called to "bypass flow". Force Main was "marked out", but owner did not specify where in back yard he was digging. | N | Y | N/A | N/A | Soaked into the dirt sides and bottom of the storm drain channel. | Y | Y | N | N/A | Washed down streets and flushed storm drains.
990048 | Voice Mail | 09/30/00 1830 | Ed Calhoun | 7604355870 | Water Utilities Dept. City of Oceanside | 2000-09-30 15:45 | 09/30/00 1630 | 75 | 0 | 310 North Tremont | Oceanside | SD | 92054 | Private Toilet | 0 | Grease | Private house lateral is a 350 Ft. run to starter manhole. Spill flowed from toilet to floor to driveway to curb & gutter. | Routine jetting and/or rodding of area. | N | Y | N/A | N | Evaporation and soaked into debris in storm drain. | Y | N/A | N/A | N/A | No access to storm drain by public or vehicles.
00-001 | N/A | 2001-08-01 00:01 | N/A | N/A | City of Encinitas | 2000-08-29 10:00 | 2000-08-29 10:30 | 750 | 250 | 3488 Fortuna Ranch Road | Encinitas | SD | 92024 | T-96 | 0 | Rocks, Blockage, and Vandalism | Upon arrival, found manhole to be full of 3/4-inch rock; someone had removed manhole cover and filled manhole with rocks. | Removed all rock from manhole and normal flow was restored. | N | N | None | None | Saturated into ground | N | N | N | N/A | Spill was in remote area of Olivenhain which people do not normally visit.
000-01 | 2000-08-09 | 2000-08-07 | San Elijo JPA | 760 753-6203 | San Elijo JPA/City of Solana Beach | 2000-08-07 06:40 | 8/7/00 @ 16:48 | 7500 | 3000 | Solana Beach Pump Station | Solana Beach | SD | 92075 | Pump Station | 1 | Air compressors that control bubbler system failed, pumps did not start | Pressure switch on compressors were insulated by ants. Contacts couldn't close. Wetwell level reached high leverl, gravity line surcharged. Sewage spilled out overflow pipe into spill basin. | Pressure switch and one compressor replaced. More effective ant control. Approx 3,000 gal was pumped back into system. Remainder of sewage leached into sand | N | N | None | None | Designated holding pond | Y | N/A | N | N/A | Report from Gary Masters, San Elijo Water Reclamation Facility | Discharger reported total SSO volume as "<7,500"; changed to 7500 by RB staff for database consistency
000-02 | 2000-08-10 | 2000-08-10 | Neil Cole | 858 720-2470 | City of Solana Beach | 2000-08-10 10:15 | 8/20/00 @ 11:30 | 7500 | 5000 | APN 26301132 &33 Vacant land | Solana Beach | SD | 92075 | Sewer Manhole | 1 | Sewer line clogged | Sewer line clogged. Clog was removed |  | N | N | None | None | Flow was contained within an old containment area at the south west end of San Elijo Lagoon area and within berms constructed around the manhole after spill was discovered. | Y | N/A | N | N/A
001-001 | Victor Vasquez V-858-636-3155 F-858-571-6972 | 09/11/00 08:45 | Patrick Jackson | 619-441-1658 | City Of El Cajon | 2000-09-10 11:30 | 09/10/00 12:00 | 300 | 0 | 690 N Second St | El Cajon | SD | 92020 | MH 25-125 | 0 | Debris | A broken wooden broom handle was found in trough of manhole, causing debris to build up. | Since the manhole is near a sewer syphon, we have added it to our 3 month cleaning schedule. | Y | Y | Forester Creek Channel | None | NA | Y | NA | N | NA | Forester Creek Channel is completely fenced and not accessible to the public.
001-002 | Victor Vasquez V-858-636-3155 F-858-571-6972 | 09/18/00 09:15 | Patrick Jackson | 619-441-1658 | City Of El Cajon | 2000-09-16 08:00 | 09/17/00 11:30 | 23500 | 7800 | 2000 Block East Main St | El Cajon | SD | 92020 | MH 36-026 | 0 | Debris | Overflow was caused by plastic construction material not normally found in sewer mains. The material may have been used as a temporary plug in new sewer line installed by developer. | Currently, we televise new construction of sewer mains during the construction process. We will televise new mains a second time prior to final inspection. | Y | Y | Forester Creek Channel | S.D. River | NA | Y | Y | N | NA | Forester Creek Channel is completely fenced and not accessible to the public. | Per phone call from Pat Jackson on 10/2/00, MH 32-026 was changed to MH 36-026 for spill #2 by RB staff.
000101 | N/A | N/A | N/A |  | City of Poway | 2000-09-04 11:30 | 09/04/00 - 1230 | 480 | 300 | 14521 Lake Poway Rd | Poway | San Diego | 92064 | Sewer manhole | 1 | Other | Inorganic sludge (silt, clay) from Water Treatment Plant was discharged into sanitary sewer system causing sewer main to discharge. | Sanitary sewer system was jet-rodded and cleared. Removed as much debris as possible on surface area. Set up containment barrier; contained and flushed surface area (road, curb, gutter) and vacuumed. | No | No | None | None | Inorganic materials contained/vacuumed; remainder percolated into soil or evaporated. | Yes | No | No | N/A | Follow-up video inspection and put mainline on monthly maintenance book.
000001 | RWQCB fax: 571-6972 | 2000-07-14 | Mr. Stephenson Code 662 | (619) 553-4114 | US Navy | 2000-07-14 08:30 | 07/14/2000, 1020 | 2750 | 0 | Naval SUBASE B-513, semi-remote access trail | San Diego | SD | 92106 | Man Hole 13-8 | 0 | Blockage | Root intrusion | Line cleared by hydroblasting | N | N | N/A | N/A | N/A | Y | Y | N/A | N/A | 2,750 gallons; recovered 0 gallons, infiltrated into the soil. Spill soaked into the soil. Spill is in a natural resource sensitive area. Working with Navy Botanist to remove tree causing the blockage. | Total and recovered volume with comments copied into first sentence in remarks column by RB staff for database consistency.
000002 | RWQCB fax: 571-6972 | 2000-07-17 | Mr. Patrias | (619) 556-8946 | US Navy | 2000-07-17 10:20 | 7/17/00, 1135 | 375 | 325 | Building 262, Near Sylverster Road. | San Diego | SD | 92106 | Manhole 10/4 | 1 | Blockage | Root intrusion | Line cleared by hydroblasting | N | N | N/A | N/A | N/A | Y | None | N/A | N/A | 375 gallons; recovered 325 gallons, remaining 50 gallons soaked into soil. Spill Soaked into the soil. Spill is in a natural resource sensitive area. Working with Navy Botanist to remove tree causing the blockage. This spill is up stream of the 7/14/00 event. | Total and recovered volume with comments copied into first sentence in remarks column by RB staff for database consistency.
000003 | e-mail report to Victor Vasquez (was not reportable quantity but sent it anyway) | 2000-07-23 | Mr. McMeans | (619) 556-7352 | US Navy | 2000-07-23 11:43 | 7/23/00, 1318 | 150 | 25 | NAB, Tulagi road by building 504. | Coronado | SD | 92118 | Manhole K-5-1 and Building 4 grease trap | 0 | Root Blockage | Massive clump of tree roots resulted in sewage overflow | Line cleared by hydroblasting | N | N | N | N | N/A | Y, Clay Clifton at DEH. | Not under 1,000 gallons or didn't enter storm drain | N/A | N/A | 150 gallons; recovered 25 gallons vacumed up, rest of it percolated into soil. Sewage percolated into soil. Only 25 gallons were recovered by vacuuming the grassy area surrounding the spill. | Total and recovered volume with comments copied into first sentence in remarks column by RB staff for database consistency.
000004 | Victor Vasquez, 467-2952 | 2000-07-24 | Mr. Warfe | (619) 545-6793 | US Navy | 2000-07-24 07:56 | 7/24/00, 1000 | 155 | 130 | NOLF, Building 193, near Gatlin Road | San Diego | SD | 91932 | F 26-4141 | 1 | Other | Sewer pump station 4949 wetwell indicator failure. | Bubbler cleared and pump level controller fixed. | N | Y | N | N | N/A | Y, Clay Clifton at DEH. | N | N/A | N/A | 155 gallons; 130 gallons evaporated from the asphalt, about 25 gallons entered storm drain. A secondary level controller is planed for installation and roving patrol will check controllers more frequently. Area was swept down and disinfected. | Total and recovered volume with comments copied into first sentence in remarks column by RB staff for database consistency.
0000005 | Victor Vasquez, 467-2952 | 2000-07-31 | Mr. Quintua | (619) 553-4144 | US Navy | 2000-07-31 10:00 | 7/31/00, 1634 | 400 | 0 | Guijaros Road, near buildings 530 and 38 | San Diego | SD | 92106 | Clean out for building 530 | 0 | Pump Station Failure | Pump station bubbler failed preventing pumps from turning on | Bubbler repaired, backup alert to bubbler will be installed | Y | Y | San Diego Bay | Pacific Ocean | Pacific Ocean | Y, Clay Clifton at DEH. | No, under 1,000 gallons | No | N/A | 400 gallons; 0 recovered. Bubbler repaired, will install backup alert to bubbler, surface areas cleaned and disinfected. When pump didn't kick on backup flowed out a sewer cleanout. | Total and recovered volume with comments copied into first sentence in remarks column by RB staff for database consistency.
0000006 | faxed to (858) 571-6972 | 2000-08-05 | Joe Patrias, Code 660 | (619) 556-8946 | US Navy | 2000-08-05 17:40 | 8/5/00, 1800 | 200 | 200 | Lift Station 4949 | Imperial Beach | SD | 91932 | Broken Sewer Line | 0 | Line Break | Excavation hit lateral line causing spill | Repaired line that was broken | N | N | None | N/A | N/A | N/A | N/A, not reportable | No | N/A | 200 gallons; 200 gallons recovered. Sewer Line repaired. Sewage was contained within the hole that was being dug when like was broken. Pumped truck came and vacuumed the captured sewage. | Total and recovered volume with comments copied into first sentence in remarks column by RB staff for database consistency.
0000007 | Not reportable, | 2000-08-06 | Mr. Quintua | (619) 553-4144 | US Navy | 2000-08-06 09:35 | 8/6/00, 1030 | 40 | 35 | West of Bldg. 52 Kerrick Road | San Diego | SD | 92106 | M H 11-6 | 0 | roots | Tree roots caused blockage. Hydroblasted to clean | Hydroblasted line clear | N | N | None | N/A | N/A | N/A | N/A, not reportable | No | N/A | 40 gallons; 35 gallons, 5 gallons evaporated on roadway. Did not meet reporting limits but was included in quarterly monitoring report. | Total and recovered volume with comments copied into first sentence in remarks column by RB staff for database consistency.
0000008 | faxed to (858) 467-2952 | 2000-08-29 | Joe Patrias, Code 660 | (619) 556-8946 | US Navy | 2000-08-29 18:38 | 8/29/00, 2030 | 200 | 25 | South side of North Avenue, and McCain Street | Coronado | SD | 92118 | M/H near Building 614 | 0 | grease | grease clogged line causing overflow in manhole | Pumper truck to pick up spillage. Sand bags used to stop runoff, hydroblaster used to clear blockage | N | Y | None, went into storm drain but probably wasn't enough volume to reach waters. | n/a | Storm Drain system on base | Y, left message with DEH duty Desk | N/A | No | N/A | 200 GALLONS; 25 gallons recovered. Spill was intermittent at a max rate of 5 gpm and min rate of 0. Volume of 200 gallons was reported as worst case volume. Line services base pizza parlor. Will check frequency of grease maint. Program. | Total and recovered volume with comments copied into first sentence in remarks column by RB staff for database consistency.
0000009 | Not reportable, | 2000-09-01 | Johansen, Facilities Manager | (619) 545-4180 | US Navy | 2000-09-01 14:36 | 09/01/00; exact time unknown | 25 | 0 | NASNI, SW of Read and 3rd St. | Coronado | SD | 92135 | Portable head facility #422 | 0 | Blockage | portable trailer head facility #422, which serves building M-3 and M-5 sewer lateral overflowed at cleanout. Someone removed cleanout cap and didn't properlty replace it. | PWC Code 510 personnel "rodding out" line and will vacuum up debris and disinfect spill area. Code 510 will also ensure cleanout cap is properly installed. | N | N | N/A | N/A | N/A | N/A, not reportable quantity | n/a, not reportable quantity | N/A | N/A | 20-30 gallons; none, discharge flowed on to hot asphalt and evaporated. Spill went on to empty asphalt parking lot. It was a hot day and the liquid evaporated almost as fast as it came. Solids were removed and site was disinfected. | Total and recovered volume with comments copied into first sentence in remarks column by RB staff for database consistency.
0000010 | Not reportable, | 2000-09-19 | Stine, PWC Utilities | (619) 556-1881 | Pier 6 Naval Station | 2000-09-19 10:48 | 09/19/00; 1105 | 5 | 5 | Naval Station, Pier 6 CHT riser | San Diego | SD | 92136 | CHT riser 2N on Pier 6 | 0 | leaking drain plug | CHT riser drain plug was leaking by. Leaking sewage was contained in berm around riser. | PWC fixed the drain plug. | N | N | N/A | N/A | N/A | N/A, not reportable | n/a, not reportable | N/A | N/A | 5 gallons; 5 gallons recovered. Spill was contained within the CHT riser berm. About 5-gal. Spilled and none entered the bay, or stormdrain system. | Total and recovered volume with comments copied into first sentence in remarks column by RB staff for database consistency.
00001 | N/A | N/A | N/A | N/A | City of Coronado | 2000-07-16 17:00 | 7-16-00,17:45 | 50 | 50 | 300 PALM AVENUE | CORONADO | SD | 92118 | SEWER LINE | 0 | DEBRIS IN LINE | UNIDENTIFIABLE DEBRIS IN SEWER LINE | REMOVED DEBRIS | N | N | N/A | N/A | N/A | N | N | N | N/A |  | Tracking # changed by RB staff to conform with Order 96-04. Units (gallons) were removed from total and recovered volume entries by RB staff for database consistency.
001003 | N/A | N/A | N/A | N/A | City of Coronado | 2000-08-11 09:00 | 8-11-00, 10:30 | 50 | 50 | 1301 FIRST STREET | CORONADO | SD | 92118 | SEWER LATERAL | 0 | GREASE IN LINE | GREASE IN LATERAL CAUSED STOPPAGE | REMOVED GREASE, DIRECTED MGMT TO PERFORM REGULAR MAINTENANCE | N | N | N/A | N | N/A | N | N | N | N/A |  | Tracking # changed by RB staff to conform with Order 96-04. Units (gallons) were removed from total and recovered volume entries by RB staff for database consistency. Spill #001002 was deleted by RB staff - not reportable under Order 96-04.
001004 | N/A | N/A | N/A | N/A | City of Coronado | 2000-08-19 12:00 | 8-19-00,14:30 | 20 | 20 | 1100 BLK FIRST ST | CORONADO | SD | 92118 | SEWER LINE | 1 | DEBRIS IN LINE | RAGS AND GREASE IN MAIN LINE | REMOVED RAGS AND GREASE | N | N | N/A | N | N/A | N | N | N | N/A |  | Tracking # changed by RB staff to conform with Order 96-04. Units (gallons) were removed from total and recovered volume entries by RB staff for database consistency.
001005 | N/A | N/A | N/A | N/A | City of Coronado | 2000-08-20 17:25 | 8-20-00,18:00 | 25 | 25 | 711 FIFTH ST | CORONADO | SD | 92118 | SEWER LATERAL | 0 | DEBRIS IN LINE | STOPPAGE IN PRIVATE LATERAL | CLEANED UP OVERFLOW, SPOKE WITH RESIDENTS | N | N | N/A | N | N/A | N | N | N | N/A |  | Tracking # changed by RB staff to conform with Order 96-04. Units (gallons) were removed from total and recovered volume entries by RB staff for database consistency.
001006 | N/A | N/A | N/A | N/A | City of Coronado | 2000-09-11 09:15 | 9-11-00, 11:00 | 50 | 50 | 160 C AVENUE | CORONADO | SD | 92118 | SEWER LINE | 1 | GREASE IN LINE | GREASE IN MAIN LINE CAUSED STOPPAGE | REMOVED GREASE, WILL INCREASE SEWER CLEANING MAINTENANCE ON SEWER MAIN LINE. HAVE CONTACTED BOTH RESTAURANTS IN THE AREA AND INSTRUCTED THEM IN PROPER DISPOSAL OF GREASE AND GREASE TRAP MAINTENANCE. | N | N | N/A | N | N/A | N | N | N | N/A |  | Tracking # changed by RB staff to conform with Order 96-04. Units (gallons) were removed from total and recovered volume entries by RB staff for database consistency.
000101 | CLAY CLIFTON - FAX | 07/17/00 - 6:30 P.M.. | DON WASKO | 438-2722 X 7138 | CMWD | 2000-07-17 18:00 | 7/17/2000 - 6:30 p.m. | 7 | N/A | 3245 VALLEY STREET | CARLSBAD | SD | 92008 | CLEAN OUT ON SIDE OF HOUSE | 1 | GREASE | MANHOLE STOPPAGE. | CLEANED SEWER MAIN. | N | N | NONE | NONE | SIDE YARD OF RESIDENCE, PERCOLATED INTO SOIL. | Y | N/A | NO | N/A | NONE
000102 | CLAY CLIFTON - FAX | 7/26/2000 - 1:00 P.M. | DON WASKO | 438-2722 X 7138 | CMWD | 2000-07-26 13:00 | 07/26/00 - 1:30 P.M. | 30 | 0 | 4934 LOMA LAGUNA | CARLSBAD | SD | 92008 | 24" MANHOLE | 1 | ROOTS AND GREASE | BLOCKAGE IN SEWER MAIN | VACTOR OUT BLOCKAGE | N | Y | NONE | POND AT FOOT OF PARK DRIVE AND KELLY DRIVE. NO HUMAN CONTACT | POND IN UNINCORPORATED AREA | Y | N/A | NO | N/A | NONE
000103 | CLAY CLIFTON - FAX | 08/24/00 - 15:30 | DON WASKO | 438-2722 X 7138 | CMWD | 2000-08-24 09:30 | 08/24/00 - 10:00 A.M. | 45 | 45 | 4075 SUNNYHILL | CARLSBAD | SD | 92008 | INSIDE RESIDENCE | 1 | ROOTS AND GREASE | SEWER MAIN BACK-UP CAUSED SEWAGE TO BACK UP INTO DOWNSTAIRS BATHROOM. IT SPREAD OUT INTO HALLWAY AND ADJACENT BEDROOMS. *CONTRACTOR WAS CALLED TO DO CLEAN UP. | ROUTINE CLEANING TO PREVENT ROOTS/GREASE. | N | N | NONE | NONE | BATHROOM IN 4075 SUNNYHILL | Y | N/A | NO | N/A | NONE
000104 | CLAY CLIFTON - FAX | 9/12/00 - 2:00 P.M. | DON WASKO | 438-2722 X 7138 | CMWD | 2000-09-12 12:30 | 09/12/00 - 1:00 P.M. | 20 | 10 | TAMARACK AND JEFFERSON | CARLSBAD | SD | 92008 | 4" SEWER CLEANOUT | 1 | UNKNOWN | STOPPAGE WAS NOT SEWER MAIN STOPPAGE. IT WAS THE SEWER LATERAL AT GAS STATION. WE DID JETVAC MAIN. RODDED LATERAL & CLEARED. |  | Y | Y | STORM DRAIN BOX CORNER OF JEFFERSON AND TAMARACK | NONE | VERY SMALL AMOUNT (5-10 GALLONS) MADE IT TO STORM DRAIN. | Y | N/A | NO | N/A | VERY LITTLE OVERFLOW - UNKNOWN CAUSE. DEBRIS WAS VACTORED OUT OF STORM AC1DRAIN BOX.
101 | Quarterly Report | 2000-07-05 10:00 | Richard Andrews | 858 755-3294 | City of Del Mar | 2000-07-04 09:00 | 2000-07-04 11:30 | 450 | 300 | 1245 Cuchara | Del Mar | SD | 92014 | Manhole B-8, No.25 | 0 | roots | roots | rod main | n | n | none | none | most recovered, dissipated in dirt at road edge | y | n | n | 0 | none
102 | Ros Dimenstein | 2000-08-14 09:20 | Terry Hartnet | 858 755-3294 | City of Del Mar | 2000-08-14 06:30 | 2000-08-14 10:20 | 1200 | 0 | 1136 Cuchara | Del Mar | SD | 92014 | Manhole B-8, No.23 | 1* | roots | palm tree roots infiltrating into manhole, plugging invert | remove palm tree | y | y | Pacific Ocean | none | Pacific Ocean | y | y | y | 3 | *Number of other occurences in last 12-months should read as "1", not "2" as earlier reported incorrectly on hardcopy of SSO report, line-item #16.
103 | Quarterly Report | 2000-09-14 13:30 | Mike Emerson | 858 755-3294 | City of Del Mar | 2000-09-14 13:05 | 2000-09-14 13:30 | 60 | 60 | 119 11th Street | Del Mar | SD | 92014 | Private 4" sump drain | 0 | private plumber | plumber cited for pumping water from adjacent sump pump wet well into outside drain | Contractor was cited and responsible for all clean-up costs; also advised to confirm source of receiving drain prior to work. | n | y | none | none | pooled in storm drain, blocked by silt and debris | y | n | y | 1 | beach posted
4 | CRW QCB SD Dept FNV Health | 07/31/00 @8:30AM | Steven Maurer | 619-667-1488 | City of La Mesa | 2000-07-30 15:30 | 2000-07-30 18:00 | 1500 | 0 | 8855 Dallas St./La Mesita Park | La Mesa | San Diego | 91942 | 8" | 2 | Rocks, Con- struction | They were clearing debris from the sewer main, and it entered the line after they knocked off several manhole frames. | Cal Trans is currently working on the problem. | No | Yes | None | None | Most of it soaked into the park grassy area. A small amount ran into the stormdrain, which eventually runs into the Alvarado Channel | Yes | N/A | No | N/A | Affected area has been barricaded and chemically treated.
5 |  | 8/1/00 @2:00PM | Steven Maurer | 619-667-1488 | City of La Mesa | 2000-07-31 13:00 | Continuing | 2000 | 2000 | 8855 Dallas St./La Mesita Park | La Mesa | San Diego | 91942 | 8" vc | 3 | Rocks, Con- struction | Cal Trans continues to have a problem removing debris from sewer main. Debris entered line after several manholes were knodked off during grading | Cal Trans continues to work on problem of clearing the line | No | No | None | None | Above ground open ditch to down- stream sewer manhole | Yes | N/A | Yes |  | This is a continuation of the spill which began on 7/30/00. However, since the overflow stopped on the 30th and started up again on the 1st. Follow up report. | City reported total spill volume as 10gal/min with 100% recovery. RB staff changed these to 2000 gal with 2000 gal recovered per Caltrans response to NOV 2000-205
1001 | Victor Vasquez | 2000-07-25 14:30 | Ted Eich | (909) 674-3146, ex 203 | Elsinore Valley Municipal Water District | 2000-07-25 10:30 | 2000-07-25 11:30 | 4500 | 4500 | Intersection of Colony Dr. and Avenida Florita | Murrieta | RI | 92562 | Sewer Manhole | 1 | Rocks, Debris, Other | A combination of debris (concrete, plywood, and 2x4s), rocks and plastic visquene plugged the entrance to a metering manhole located on Avenida Florita approximately 150 feet from the intersection of Colony Dr. and Avenida Florita. Raw sewage within the | Corrective Actions Taken: Blockage was relieved to stop the spill. All debris was recovered utilizing a vacuum truck. Upstream and downstream sewer lines were rodded and flushed and the spill area was disinfected using Lysol. | N | Y | None | None | N/A | Y | Y | N | N/A | To ensure that the spilled sewage was removed from the storm drain system, the District set up a recovery process whereby a joint team of District Staff and White House Sanitation Pumpers employees flushed and vacuumed the storm drain recovering 14,000 ga | RB staff changed overflow volume recovered from 14,000 to 4500
O00101 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2000-07-20 14:00 | 2000-07-20 14:10 | 2 | 0 | 414 S. Main Street | Fallbrook | SD | 92028 | Cleanout | 1 | Roots | Roots in lateral. | Ran cutter 35 feet down lateral. | N | N | NA | NA | Around cleanout | N | N | N | NA | Recovered paper only from around cleanout.
O00102 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2000-08-05 16:15 | 2000-08-05 16:30 | 10 | 0 | 205 E. Kalmia | Fallbrook | SD | 92028 | Cleanout | 1 | Blockage | Some kind of blockage. | Ran rodder 60 feet into mainline and hit an obstruction at about 20-25 feet. Cleared obstruction. | N | N | NA | NA | Percolated into ground around cleanout | N | N | N | NA | Disinfected area around cleanout.
O00103 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2000-08-18 16:10 | 2000-08-18 16:25 | 2 | 0 | 420 S. Summitt | Fallbrook | SD | 92028 | Cleanout | 1 | Roots | Roots about 8 feet east of cleanout. | Rodded lateral and unplugged. Also ran out to the mainline. | N | N | NA | NA | About 2 feet around the cleanout box | N | N | N | NA | Cleanout box was not overflowing when arrived. Sprayed disinfectant around cleanout box.
O00104 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2000-08-29 11:30 | 2000-08-29 15:00 | 25 | 0 | 400 W. Elder Street | Fallbrook | SD | 92028 | Manhole | 1 | Roots | Manhole backed up with roots. | Rodded main line and cleared roots. | N | N | NA | NA | Percolated into ground and grassy area around manhole. | Y | N | Y | 3 | Notified SD County Health since overflow occurred at Maie Ellis Elementary School. Removed contaminated soil and replace with clean material.
001001 | Environmental Health only | 2000-07-03 16:15 | Lance Lauricha | 760-839-4347 | City of Escondido | 2000-07-03 12:00 | 7/3/00 1330 | 90 | 25 | 725 N. Fig St. | Escondido | SD | 92025 | Private cleanout | 0 | Grease | Grease stoppage in private lateral. | Referred to Pretreatment Inspector for further investigation. | N | N | N/A | N/A | Absorbed to soil. | Y | N | N | N/A | N/A
001003 | Environmental Health only | 2000-07-12 14:00 | Mike Schultz | 760-839-4255 | City of Escondido | 2000-07-12 05:00 | 7/12/00 900 | 240 | 100 | 1570 W. Valley Pkwy. | Escondido | SD | 92025 | Private cleanout | 0 | Grease | Albertson's called a plumber to clear blockage. We assisted by washing and vacuuming at the storm drain. We disinfected the contaminated area. The storm system was flushed and vacuumed for recovery purposes. | The Pretreatment Inspector investigated and issued a Notice of Correction to Albertson's manager. | Y | Y | Escondido Creek | San Elijo Lagoon | Pacific Ocean | Y | N | N | N/A | Samples were not taken. | Spill #001002 is july 2000 HARRF spill; not reportable under Order 96-04; deleted by RB staff.
001004 | Environmental Health only | 2000-08-17 10:00 | John Vaught | 760-839-4323 | City of Escondido | 2000-08-16 13:00 | 8/16/00 1720 | 560 | 280 | 710 E. Grand Ave | Escondido | SD | 92025 | Private cleanout | 0 | Roots | Large root mass in private service lateral. | Our Pretreatment Inspector is investigating the situation and will make recommendations. | Y | Y | Escondido Creek | San Elijo Lagoon | Pacific Ocean | Y | N | Y | 1 day | Samples were not taken.
001005 | Environmental Health only | 2000-09-11 10:45 | John Vaught | 760-839-4323 | City of Escondido | 2000-09-09 12:30 | 9/9/00 1800 | 1110 | 900 | 360 E. Washington Ave. | Escondido | SD | 92025 | Private cleanout | 1 | Grease | Private system overflow due to grease and poor maintenance. | The Pretreatment Inspector will investigate and issued a Notice of Correction if warranted. Educational material will also be distributed to the manager and residents. | Y | Y | Escondido Creek | San Elijo Lagoon | Pacific Ocean | Y | N | Y | 1 day | Samples were not taken.
001006 | Environmental Health only | 2000-09-22 13:40 | Jim Miller | 760-839-4347 | City of Escondido | 2000-09-22 07:00 | 9/22/00 730 | 300 | 300 | 1204 N. Escondido Blvd. | Escondido | SD | 92025 | Private cleanout | 0 | Unknown | Cause of discharge is unknown, this is a private system. | All documentation was turned over to Code Enforcement for code violation. | Y | Y | N/A 100% recovered | N/A | N/A | Y | N | N | N/A | Samples were not taken.
001007 | Victor Vasquez | 2000-09-26 16:15 | Lance Lauricha | 760-839-4347 | City of Escondido | 2000-09-26 10:00 | 9/26/00 1450 | 1160 | 305 | 360 E. Washington Ave. | Escondido | SD | 92026 | Private cleanout | 2 | Grease | Grease stoppage in private lateral. | The information was referred to Code Enforcement and Pretreatment office. | Y | Y | Escondido Creek | San Elijo Lagoon | Pacific Ocean | Y | Y | Y | 2 days | Samples were not taken.
001008 | Environmental Health only | 2000-09-28 15:45 | Romero Gonzalez | 760-839-4347 | City of Escondido | 2000-09-28 15:30 | 9/28/00 1550 | 100 | 25 | Old San Pasqual Rd. | Escondido | SD | 92025 | Forcemain air release valve from sta. 13 | 0 | Construction debris | Construction debris caused air release valve to malfunction and stick open. | This unit is being inspected every month to ensure reliability. | N | N | N/A | N/N | Absorbed to soil. | Y | N | N | N/A | Samples were not taken.
101 | VICTOR VASQUEZ | 2000-07-12 10:40 | COLLEEN ECKENROAD | 7607259761 | MCB, CAMP PENDLETON | 2000-07-12 06:30 | 2000-07-12 08:25 | 1800 | 100 | ACROSS FROM BLDGS 210567 AND 21564 | CAMP PENDLETON | SD | 920555008 | MH 13Y191 AND MH 13Y192 | 1 | GREASE | DEL MAR LIFT STATION 21537 PUMPS FAILED TO COME ON DUE TO GREASE & DEBRIS BUILD-UP ON FLOAT WHICH KEPT THE FLOAT FROM OPERATING PROPERLY IN CONJUNCTION WITH POOR DESIGN. | CORR: RECOVERED 100 GALS, HOSED GREASE OFF FLOAT TO RESUME PROPER OPERATION. PUMPED GREASE&SOLIDS OUT OF LS ON 7-13-00. PREV: CONTINUE TO HOSE OFF FLOATS DAILY,IR#43429 TO INSTALL ULTRASONIC SENSOR | Y | N | DEL MAR BOAT BASIN | PACIFIC OCEAN |  | Y | Y | Y | 3+ | 1770 GALLONS OVERFLOWED MH13Y192 TRAVELED 50' OVER DIRT INTO DEL MAR BOAT BASIN. 30 GALLONS SPILLED FROM MH13Y191 & PERC'D INTO DIRT AROUND MH. 35 SIGNS POSTED AROUND BOAT BASIN, ADDT'L SIGNS POSTED AT NORTH HALF OF OCEANSIDE HARBOR BEACH. SAMPLES WILL BE COLLECTED FROM THE BOAT BASIN & FROM THE NORTH HALF OF THE OCEANSIDE HARBOR BEACH UNTIL CLEARED TO REMOVE SIGNS. OCEANSIDE HARBOR REOPENED ON 7-13-00 BY DEH BASED ON SAMPLE RESULTS COLLECTED ON 7-12-00. DEL MAR BOAT BASIN WAS CLEARED ON 7-15-00.
102 | ELECTRONIC QTLY RPT | 2000-07-30 12:00 | KARL VOGEL | 7607259762 | MCB, CAMP PENDLETON | 2000-07-30 05:20 | 2000-07-30 08:20 | 900 | 850 | BLDG 2394 USMCAS | CAMP PENDLETON | SD | 920555008 | CLEANOUT | 1 | PUMP STATION FAILURE | LIFT STATION 2387 PUMP FAILED | CORRECTIVE: RESET PUMP PREVENTATIVE: ENGR SERVICE REQUEST TO PWO FOR PERMANENT REPAIRS | N | Y | NONE | NONE | 8' ACROSS ASPHALT TO CONTRCTORS TRENCH-PONDED 50'. | Y | N | Y | 3 | FLOWED FROM CLEANOUT, 8' ACROSS ASPHALT TO CONTRACTORS TRENCH AND PONDED. 50' INTO STM DRN AND 50' TO MH WHERE FLOW WAS STOPPED AND RECOVERED
103 | CLAY CLIFTON | 2000-08-01 16:00 | CPL TINGLE D.K. | 7607259761 | MCB, CAMP PENDLETON | 2000-07-31 10:30 | 2000-07-31 11:30 | 700 | 400 | BUILDING 51055 | CAMP PENDLETON | SD | 920555008 | MH 11Y216 | 1 | GREASE | GREASE BALL FROM HOUSING AREA. | CORRECTIVE: CLEARED THE BLOCKAGE WITH THE JETTTER. PREVENTATIVE: CONTINUAL EDUCATION OF THE HOUSING TENANTS. | Y | Y | DRY CREEK BED | SANA MARGARITA RIVER | NO FLOW TO ACTUAL SURFACE WATER | Y | NA | N | 0 | NO ACTUAL FLOW TO SURFACE WATER FLOW TRAVELED 100 FT TO STORM DRAIN, 100 FT IN STORM DRAIN WERE MIXED WITH SAND IN STORM DRAIN AND PERC INTO BARE SANDY EARTH
104 | ELECTRONIC QTRLY RPT | 2000-08-04 15:28 | COLLEEN ECKENROAD | 7607259761 | MCB, CAMP PENDLETON | 2000-08-03 07:00 | 2000-08-03 07:40 | 350 | 0 | NEAR BLDG 62521, CAMP CRISTIANITOS | CAMP PENDLETON | SD | 920555008 | MANHOLE 12-Y-31 BETWEEN BARRACKS | 1 | ROOTS | TREE ROOTS CAUSED A BLOCKAGE IN A 10" CLAY LINE. | CORRECTIVE: RAM JET LINE, CUT TREES & REMOVED POSTS IN THE WAY TO ACCESS THE MH. PREVENTATIVE: TV & FOAM SEWER LINE, TAKE ACTION BASED ON VIDEO RESULTS. | Y | N | SAN MATEO CREEK | PACIFIC OCEAN | NO FLOW TO ACTUAL SURFACE WATER | Y | NA | N | NA | 2 FLOWS; FIRST TRAV FROM BLDG 62520 TO 62534 TO 62528 WHICH IS A DIST OF 455', SECOND TRAV FROM BLDG 62520 TO STREET PAST 62534 TO 62528 WHICH WAS 1166', TOTAL TRAV DIST 1621'. NO EXPECTED PUBLIC CONTACT OR FLOW TO ACTUAL SURFACE WATER.
105 | VICTOR VASQUEZ | 2000-08-22 07:00 | CPL TINGLE D.K. | 7607259761 | MCB, CAMP PENDLETON | 2000-08-21 18:55 | 2000-08-21 20:30 | 2600 | 1200 | BLDG 2408 | CAMP PENDLETON | SD | 920555008 | CLEANOUT NEAR BUILDING 2408 | 1 | ROOTS | TREE ROOTS | CORRECTIVE: USED ROOT CUTTERS TO CLEAN UP THE CLEAN OUT. PREVENTATIVE: P.M. SEWER LINE. | Y | Y | SANTA MARGARITA RIVER | PACIFIC OCEAN | PERC AND PUMPED NO FLOW TO ACTUAL SURFACE WATERS | Y | Y | Y | 3 | FROM CLEANOUT 30' TO ASPHALT AND GRASSY AREA, 120' ACROSS ASPHALT TO CONCRETE DITCH, 250' IN DITCH TO VANDEGRIFT, 500' IN CIRB TO STORM DRAIN, AND 500' IN THE STORM DRAIN.
106 | VICTOR VASQUEZ | 2000-09-13 15:35 | KARL VOGEL | 7607259762 | MCB, CAMP PENDLETON | 2000-09-06 08:00 | 2000-09-13 18:00 | 2730000 | 0 | STUART MESA BRIDGE | CAMP PENDLETON | SD | 920555008 | 6" CLEANOUT ON 12" FORCE MAIN | 1 | BLOCKAGE | SAND, GRIT, AND DEBRIS BLOCKAGE IN 12" PVC FORCE MAIN, AN EST 300' SOUTH OF BRIDGE, CAUSED 6" PVC CLEANOUT CAP TO BLOW OUT | CORR: 3 PUMPER TRUCKS, 3 JETTERS RESPONDED, SECURED WATER SUPPLY TO STUART MESA HOUSING, PUMPERS PUMPING 2 LIFT STATIONS UPSTREAM TO PREVENT SPILL, JETTED BLOCKAGE CLEAR. PREV: BASE REQUESTING HQ FUNDING FOR ENGINEERING ASSESSMENT/REPAIR OF ALL SEWAGE LINES CROSSING/ADJ TO WATER WAYS, IR FOR VALVES ON CLEANOUTS NEAR STREAMS & VIDEO OF AFFECTED FM TO ID POT PROB W/IN 6 MONTHS. | Y | N | SANTA MARGARITA RIVER | PACIFIC OCEAN | FLOW DID NOT ACTUALLY REACH OCEAN | Y | Y | Y | 3+ | PONDED AND PERC APPROX 200' NORTH OF CLEANOUT PARALLEL TO STUART MESA ROAD. SPILL FROM CLEAN OUT 15' THROUGH SAND BAR TO RIVER
107 | VICTOR VASQUEZ | 2000-09-25 15:15 | KARL VOGEL | 7607259762 | MCB, CAMP PENDLETON | 2000-09-23 16:50 | 2000-09-23 20:00 | 505 | 500 | N/W OF STUART MESA BRIDGE | CAMP PENDLETON | SD | 920555008 | 6" PVC CLEANOUT ON 12' PVC FORCEMAIN | 2 | OTHER | ABS THREADS DID NOT SEAL CORRECTLY WITH STAINLESS THREADS ON COUPLING ALLOWING MIST OF SEWAGE TO ESCAPE | CORR: PREV FOR CORRECTION WAS TO BERM ON RIVER SIDE FOR CONTAINMENT. WATER TO STUART MESA HOUSING SECURED AT APPROX. 1730 + RESTORED AT APPROX 0030. PUMPER TRUCK STARTED RECOVERING SEWAGE IMMEDIATELY AFTER CAP WAS REMOVED PREV: REPLACE ABS CAP W/ GAVL. CAP WHICH SERVES AS A PREVENTATIVE MEASURE FOR FUTURE SPILLS FROM CLEANOUT. | Y | N | SANTA MARGARITA RIVER | PACIFIC OCEAN | FLOW DID NOT ACTUALLY REACH RIVER | Y | NA | N | 12+ | SIGNS STILL POSTED FROM PREVIOUS SPILL. SPILL TRAVELED 10 FT TOTAL AND PERC'D INTO SAND A RADIUS OF 5 FT FROM CLEANOUT
114426 | Fax 571-6972 | 07/09/00 08:46 | M. Bedard | 6544160 | City of San Diego | 2000-07-01 23:15 | 07/02/00 12:45 | 7383 | 0 | Aldine Dr. & Fairmount Av.( in canyon) | San Diego | SD | 92116 | 8"VC MAIN | ONE | Roots | This call was backed due to a odor. Original call caused by roots which caused overflow | Flushed line to relieve stoppage- 8"vc main- put on cleaning schedule | Y | Y | NONE | Soaked into hillside. | N/A | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
114429 | Fax 571-6972 | 07/02/00 16:34 | D. A Branco | 6544160 | City of San Diego | 2000-07-02 11:08 | 07/02/00 14:40 | 106 | 0 | 3110 Gregory St. | San Diego | SD | 92104 | 6"VC MAIN | ONE | Grease | Blockage was caused by grease. | Rodden 6" cp main. Refered for scheduled maintenance. | Y | N | Dried in curb on Redwood St. and Mckinley. | San Diego Bay/ Pacific Ocean. | N/A | Y | N | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
114733 | Fax 571-6972 | 07/05/00 10:15 | J. Mitchell | 6544160 | City of San Diego | 2000-07-04 12:40 | 07/04/00 14:08 | 2400 | 0 | 2423 Fairmount | San Diego | SD | 92105 | 8"VC MAIN | ONE | Roots | Roots in manhole #397 and grease and debris. | Flushed 8" vc main, refered to Area Supervisor for cleaning | Y | Y | Storm channel near spill site | N/A | N/A | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
114724 | Fax 571-6972 | 07/05/00 10:20 | J. Mitchell | 6544160 | City of San Diego | 2000-07-04 08:30 | 07/04/00 10:30 | 720 | 0 | 1743 Midvale Dr. | San Diego | SD | 92105 | 8" VC Main | One | Roots | Roots and debris in the main | Flushed and hand rodded 8" vc main. | Y | Y | Storm drain run off | N/A | N/A | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
114744 | Fax 571-6972 | 07/05/00 10:00 | J. Mitchell | 6544160 | City of San Diego | 2000-07-04 19:30 | 07/04/00 20:50 | 48 | 48 | 2612 Byer Blvd. | San Diego | SD | 92173 | 6"VC MAIN | ONE | Grease | Grease and debris in main. | Flushed 6"vc main, disenfected sidewalk and curb area around manhole. | N | N | None | None | Recovered at curbside. | Y | N | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
114848 | Fax 571-6972 | 07/15/00 22:54 | C. Mickelson | 6544160 | City of San Diego | 2000-07-05 22:54 | 07/05/00 16:53 | 5 | 0 | 4383 Beta St. | San Diego | SD | 92113 | 6"VC MAIN | TWO | Roots | Roots blocked 250' section causing overflow from crack in street pavement end of main plug | Rodded 6" vc main, refered to TV section. | Y | N | N/A | N/A | Dried up in curb in front of 4364 Beta Street | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
115784 | Fax 571-6972 | 07/09/00 14:26 | D. A Branco | 6544160 | City of San Diego | 2000-07-07 18:00 | 07/09/00 13:52 | 45520 | 0 | 17855 Bernardo Trails Place | San Diego | SD | 92128 | 8"PVC MAIN | ONE | Roots | Blockage was caused by roots; machine rodded; probed m/h with bar; heavy roots in M/H; romoved roots and relieved stop | 8" pvc main, Rodded & probed M/H to releive stoppage. | Y | N | Dry creek behind 17855 Bernardo Trails. | Soaked into ground near Pepper Tree Nursery. | N/A | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
115595 | Fax 571-6972 | 07/08/00 11:01 | D. A Branco | 6544160 | City of San Diego | 2000-07-08 11:01 | 07/07/00 20:00 | 40 | 0 | 1905 Mission Cliff Dr. | San Diego | SD | 92116 | 6"VC MAIN | ONE | Roots | Blockage was caused by roots. | 6" vc main, Flushed line to relieve stop, referred for PM. | Y | Y | Entered storm drain in front of address and dissipated in system. | San Diego River/ Pacific Ocean. | N/A | Y | N | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
115600 | Fax 571-6972 | 07/08/00 13:11 | D. A Branco | 6544160 | City of San Diego | 2000-07-08 13:11 | 07/08/00 11:15 | 170 | 0 | 4260 Randolph St. | San Diego | SD | 92103 | 8"VC MAIN | ONE | Roots | Blockage was caused by roots. | Rodded 8" vc main to relieve root blockage. | Y | Y | Entered storm drain in front of 4320 Randolph and dissipated. | San Diego River/ Pacific Ocean. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
115789 | Fax 571-6972 | 07/09/00 21:55 | D. A Branco | 6544160 | City of San Diego | 2000-07-08 19:00 | 07/09/00 19:10 | 1450 | 1450 | 729 Ostend Ct. | San Diego | SD | 92109 | 6"VC MAIN | ONE | Grease | Blockage was caused by grease. | Rodded 6" vc main. | N | Y | Entered storm drain at Santa Clara and Mission Blvd. | Interceptor V44 | Interceptor V44 | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
115893 | Fax 571-6972 | 07/10/00 14:00 | G. Richardson | 6544160 | City of San Diego | 2000-07-10 12:00 | 07/10/00 13:09 | 15 | 10 | 3452 Arthur Av. & 35th St. | San Diego | SD | 92116 | 6"VC MAIN | ONE | Grease | Grease build-up in the main causing the overflow. | Rodded 6" vc main to relieve stoppage. | Y | N | Alley at spill site. | Dried up in alley. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
117272 | Fax 571-6972 | 07/15/00 18:44 | D. A Branco | 6544160 | City of San Diego | 2000-07-15 15:17 | 07/15/00 17:05 | 1620 | 0 | 595 Hotel Circle South | San Diego | SD | 92108 | 10"VC MAIN | ONE | Roots | Blockage was caused by roots. | Flushed line to relieve stoppage on 10" vc. | Y | Y | Entered storm drain on Hotel Circle South about 150-W of Bachman pc and dissipated in system at Hanolery Hotel. | San Diego River/ Pacific Ocean. | N/A | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
117409 | Fax 571-6972 | 07/17/00 14:40 | L. Finch | 6544160 | City of San Diego | 2000-07-17 08:50 | 07/17/00 10:15 | 128.5 | 100 | Dewey St. & Newton Av. | San Diego | SD | 92113 | 6"VC MAIN | ONE | Debris | Main partically blocked by deris appeared to be fish scales and sea erichen spines. We back tracked and found no commerical type places that work with seafood possible illegally pumped in M/H- we didn't find any evidence in any man holes. | Reflush MC Site, Vactored 6" vc.. | Y | N | Vactured at curb and washed. | Storm drain/ San Diego Bay. |  | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
117420 | Fax 571-6972 | 07/17/00 13:30 | L. Davis | 6544160 | City of San Diego | 2000-07-17 10:25 | 07/17/00 11:20 | 364 | 60 | 5221 Quemado Court | San Diego | SD | 92124 | 8"VC MAIN | ONE | Roots | Grease build-up in manhole and roots down stream. | 8" vc - Additional cleaning and added to cleaning schedule | Y | Y | Storm drain at 5221 Quemado Ct. | Canyon area South of Quemado Ct. | Dried up in canyon area. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
117484 | Fax 571-6972 | 07/17/00 02:37 | J. Hernandez | 6544160 | City of San Diego | 2000-07-17 16:53 | 07/17/00 17:54 | 122 | 38 | 1743 Midvale Dr. | San Diego | SD | 92105 | 8"VC MAIN | TWO | Roots | Roots infiltracting and growing in sewer main. | 8" vc Schedule for cleaning | Y | Y | Curb in front of 1743 Miduale Dr. | Storm drain in front of 1743 Miduale Dr. dissipated in storm drain Home Ave. | North of Federal Blvd. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
117786 | Fax 571-6972 | 07/18/00 21:05 | C. Mickelson | 6544160 | City of San Diego | 2000-07-18 15:53 | 07/18/00 17:05 | 144 | 0 | 1506 Plumosa Way | San Diego | SD | 92103 | 6"CP MAIN | TWO | Roots | Roots infiltrating and growing in sewer main. | 6" cp main, Rodded main to relieve root stoppage. Schedule periodic cleaning | Y | N | Canyon hillside behind 1506 Plumosa Way. |  | Soaked into canyon hillside 1506 Plumosa way. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
117727 | Fax 571-6972 | 07/18/00 14:00 | L. Finch | 6544160 | City of San Diego | 2000-07-18 09:20 | 07/18/00 11:20 | 60 | 60 | 1956 Linwood St. | San Diego | SD | 92103 | 6"CP MAIN | ONE | Roots | Main was partically blocked by roots. Causing overflow out of c/o 1956 Linwood St. | 6" cp, Cleaned main , vactored, main will be replaced Sept. 2000 | Y | N | Guter at 1956 Linwood St. | San Diego Bay |  | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency. Discharger reported recovered volume as "60+", changed to "60 " by RB staff.
118482 | Fax 571-6972 | 07/20/00 23:45 | C.Mickelson | 6544160 | City of San Diego | 2000-07-20 20:30 | 07/20/00 20:30 | 40 | 0 | 7526 Rock Canyon Dr. | San Diego | SD | 92126 | 8"PVC MAIN | ONE | Grease | Grease build-up in sewer main. | 8" pvc, Flushed mains to remove grease, refer for periodic maint. | Y | Y | Curb at 7526 Rock Canyon Dr. | Storm dain inlet box at NE corner of Rock Canyon Dr. /Rock Canyon CT. | Sewage dissipated in box. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
118850 | Fax 571-6972 | 07/22/00 13:54 | D. A Branco | 6544160 | City of San Diego | 2000-07-22 11:02 | 07/22/00 11:53 | 26 | 0 | 3276 Rosecrans Street | San Diego | SD | 92103 | 8"CP MAIN | ONE | Roots | Blockage was caused by roots. | 8" cp, Machine rodded to relieve stoppage. | Y | Y | Entered storm drain in parking lot, behind address and dissipated in drain | San Diego Bay/ Pacific Ocean. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
118910 | Fax 571-6972 | 07/23/00 12:59 | D. A Branco | 6544160 | City of San Diego | 2000-07-23 08:37 | 07/23/00 09:10 | 175 | 175 | Bacon St. & Long Branch | San Diego | SD | 92107 | 15"CP MAIN | ONE | Other | No 7-33 upon arrival; cause of brief overflow unknown; sludge in line; possible surge. | Rodded main for City protection, Flushedand Vactored. 15" cp | N | Y | Entered storm drain on East side of Bacon and Long Branch and puddled in storm drain not flowing. | N/A | [6 empty] | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
119612 | Fax 571-6972 | 07/25/00 00:30 | J. Wilder | 6544160 | City of San Diego | 2000-07-24 18:44 | 07/24/00 20:20 | 20 | 0 | 6232 Calle Vera Cruz | San Diego | SD | 90237 | 8"VC | ONE | Roots | Roots infiltracting and growing in sewer main. | 8" vc, relieved root stop, cleaned main with blade | Y | Y | Curb in front of 6232 Calle Vera Cruz. | Storm drain at 6204 Calle Vera Cruz. | Dissipated in same storm drain box. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
119740 | Fax 571-6972 | 07/25/00 23:30 | J. Wilder | 6544160 | City of San Diego | 2000-07-25 16:25 | 07/25/00 21:55 | 4200 | 0 | 3010 Briand Av. | San Diego | SD | 92122 | 8"VC MAIN | ONE | Roots | Roots in main caused overflow. | 8" vc, Rod main, Relieved stoppage. | Y | N | Dried up in canyon. | N/A | Dried up in canyon. | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
120377 | Fax 571-6972 | 07/27/00 13:40 | M. Bedard | 6544160 | City of San Diego | 2000-07-26 19:05 | 07/26/00 19:15 | 10000 | 4000 | Canyon Crest Drive | San Diego | SD | 92115 | 21 VC | ONE | Other | Contractors 6" discharge hose came out of manhole while by pass pumping. Pump ran for 10 minutes discharging sewage onto the grounds of parking lot. 4,000 gallons was contained on job site and hosed back into manhole. | 21"vc, Set up pumps in concrete channel, | Y | Y | Storm drain. | Alvarado Creek/ San Diego River | Pacific Ocean | Y | Y | Y | To be determinded by County Health | Twenty Five signs were posted in one day. | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
120436 | Fax 571-6972 | 07/27/00 14:45 | L. Davis | 6544160 | City of San Diego | 2000-07-27 10:10 | 07/27/00 11:45 | 190 | 0 | 4500 Block of Orcutt St. | San Diego | SD | 92126 | 8"VC | ONE | Other | Unknown- Possible sampling bottle tied up in the manhole caused a partial blockage. | Cleaned /added to PM schedule, notified FEWD. | Y | Y | Storm drain behind Kaiser Hospital. | Dried up in storm drain. | Storm drain East of 4500 Orcutt Street. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
120502 | Fax 571-6972 | 07/28/00 11:25 | K. Gensler | 6544160 | City of San Diego | 2000-07-27 16:36 | 07/27/00 18:22 | 5300 | 0 | 18695 Pomerado Rd ** | San Diego | SD | 92128 | Pump Sta. 76 | ONE | Power Out. | S.D.G & E Power outage in area caused pump station failure. | Pump Sta. 76- Vactored overflow, mobile generator restored power to Sta. | N | N | N/A | N/A | Soaked into drain culvert 110' from pump station. | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
120407 | Fax 571-6972 | 07/27/00 08:55 | G. Richardson | 6544160 | City of San Diego | 2000-07-27 06:39 | 07/27/00 07:15 | 180 | 0 | 54th St. & Collwood | San Diego | SD | 92115 | 8"CP | ONE | Gravity Break | A main break caused the overflow. | 8" cp, Rodded/Flushed to relieve stoppage, referred to construction. | Y | Y | Storm drain at spill site to flowing creek. | San Diego River | Pacific Ocean | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
121142 | Fax 571-6972 | 08/01/00 11:45 | L. Finch | 6544160 | City of San Diego | 2000-07-28 10:00 | 07/30/00 19:25 | 34450 | 0 | 409 28th Street | San Diego | SD | 92102 | 8"VC MAIN | ONE | Grease | Blockage caused by heavy grease. (SR 120764) earlier investigate it, did not find cause of BSO. | 8" vc main, flushed & rodded line. Heavy grease, refer for Schd. Maint. | N | Y | Entered storm drain behind 2778 C St. and emptied into San Diego Bay via Switzer St. | N/A | San Diego Bay | Y | Y | Y | Posted signs on 7.31.00 | 7 signs were posted | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
121035 | Fax 571-6972 | 07/31/00 13:45 | E. Semo | 6544160 | City of San Diego | 2000-07-28 15:00 | 07/31/00 12:00 | 3 | 0 | Pico St. & Garnet | San Diego | SD | 92109 | 12"PVC MAIN | ONE | Other | Deterioration on expansion joint- leak on inverted syphon along Garnet Bridge- rubber leaking due to deterioration on rubber joint. | 12" pvc main, Concreted problem area, refer for joint replacement | N | N | Soaked into soil below pipe. | N/A | Soaked into ground below innerted syphon at Pico and Garnet. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
121077 | Fax 571-6972 | 07/29/00 16:03 | D. A Branco | 6544160 | City of San Diego | 2000-07-29 10:20 | 07/29/00 10:45 | 125 | 0 | 6102 La Pintura Dr. | San Diego | SD | 92037 | 8"VC | ONE | Roots | Blockage was caused by roots. | 8" vc main, Flushed line to relieve Blockage. | Y | N | Soaked into hillside in canyon behind address. | Pacific Ocean. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
121060 | Fax 571-6972 | 07/29/00 15:54 | D. A Branco | 6544160 | City of San Diego | 2000-07-29 09:52 | 07/29/00 10:40 | 24 | 0 | Niagara & SunsetCliff Blvd at Pier | San Diego | SD | 92107 | Sump Pump | ONE | Other | Sump pump on Ocean Beach Pier malfunctioned; pump maintained by city plumbers. | Started Pump, pump would not work on Auto. | Y | N | Pacific Ocean | N/A | Pacific Ocean. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
121067 | Fax 571-6972 | 07/29/00 16:08 | D. A Branco | 6544160 | City of San Diego | 2000-07-29 11:12 | 07/29/00 12:50 | 470 | 0 | 1551 Acheson Street | San Diego | SD | 92111 | 8"VC | ONE | Roots | Blockage was caused by roots. | 8" vc main, Flushed line to relieve stop, clean roots, refer for Schd. Maint. | Y | Y | Entered storm drain in alley 50- East of Linda Vista Rd. and Archeson St. and dissipated in system. | San Diego River/ Pacific Ocean. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
121843 | Fax 571-6972 | 08/02/00 13:30 | G. Richardson | 6544160 | City of San Diego | 2000-08-02 09:26 | 08/02/00 10:11 | 47 | 0 | 6988 Park Vistal Ct. | San Diego | SD | 92114 | 6"PVC MAIN | ONE | Grease | Grease build-up caused the overflow. | Flushed 6" PVC to relieve stoppage. | Y | N | Culdesac on Park Vista CT. | N/A | Dried up on pavement | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
121831 | Fax 571-6972 | 08/02/00 10:30 | L. Finch | 6544160 | City of San Diego | 2000-08-02 07:26 | 08/02/00 08:30 | 640 | 400 | Texas St. and University Av. | San Diego | SD | 92104 | 8"VC MAIN | ONE | Debris | Heavy rags, 24" metal rod and light grease. | Washed down, recovered, deoderized area. TV main - 8" vc | Y | Y | Storm drain 3240 Arizona disspated in system. | Switzar St and San Diego Bay. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
122421 | Fax 571-6972 | 08/08/00 10:20 | L. Finch | 6544160 | City of San Diego | 2000-08-04 17:40 | 08/04/00 19:20 | 200 | 0 | Robinson Av. & SB163 | San Diego | SD | 92101 | 8"CI MAIN | ONE | Other | Blockage was caused by unknown source; possible rock in line. | Flushed line to relieve stoppage. 8" ci | Y | Y | Entered storm drain 100's of WYH513 AND dissipated in system. | San Diego Bay/ Pacific Ocean. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
122696 | Fax 571-6972 | 08/05/00 16:36 | D. A Branco | 6544160 | City of San Diego | 2000-08-05 12:31 | 08/05/00 15:00 | 149 | 149 | 4233 Cherokee St. | San Diego | SD | 92104 | 6"VC MAIN | ONE | Gravity Break | Blockage caused by break in pipe. | Flushed line- 6" vc- Vactored puddled sewage. | N | N | Flowed down alley between 37th and Cherokee into sink hole at end of alley; pudded sewage vactored. | N/A | Flowed down alley between 37th and Cherokee. Back inot system, puddled sewage in alley vactored. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
122764 | Fax 571-6972 | 08/06/00 13:57 | D. A Branco | 6544160 | City of San Diego | 2000-08-06 11:44 | 08/06/00 12:15 | 62 | 0 | 5516 Rutgers | San Diego | SD | 92037 | 8"VC MAIN | ONE | Roots | Blockage was caused by roots. | 8" vc, Flushed main to relieve stoppage. | Y | Y | Entered storm drain at 5476 Rutgus dissipated in system. | Pacific Ocean | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
122830 | Fax 571-6972 | 08/07/00 12:50 | G. Neel | 6544160 | City of San Diego | 2000-08-07 10:08 | 08/07/00 11:20 | 730 | 730 | 7713 Esterel Drive | San Diego | SD | 92037 | 8"VC MAIN | TWO | Roots | Blockage was caused by roots after one bearcide application. | 8" vc, Machine rodded to clear stoppage. | Y | Y | Curb at 7713 Esterel Dr. | Entered storm drain at 2556 Azure Coast Dr. | Intercepted at Aud De La Playa at valve #3. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
124610 | Fax 571-6972 | 08/03/00 19:58 | D. A Branco | 6544160 | City of San Diego | 2000-08-07 22:04 | 08/13/00 19:30 | 4243 | 0 | 1889 Whaley Av. | San Diego | SD | 92104 | 6"CP MAIN | ONE | Gravity Break | Sewer line 6" cp broke in cayon. | 6" cp, Investigate BSO in canyon. Locate 11-61, notified standby to send crew. | Y | N | Soaked into chocolate canyon East of Gregory and South of Ivy St. | Chollas Creek/San Diego Bay. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
122870 | Fax 571-6972 | 08/07/00 14:50 | L. Finch | 6544160 | City of San Diego | 2000-08-07 12:25 | 08/07/00 13:25 | 20 | 0 | 805 Otesgo Dr. | San Diego | SD | 92103 | 6"CP MAIN | ONE | Roots | Roots caused a partical stoppage with paper products. | 6" cp, Evaluate main put on man cleaning root inhibitor site. | Y | N | Dried in street. | N/A | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
123716 | Fax 571-6972 | 08/09/00 10:30 | E. Semo | 6544160 | City of San Diego | 2000-08-09 08:15 | 08/09/00 08:40 | 125 | 0 | 3143 Carnegie Ct. | San Diego | SD | 92122 | 8"VC MAIN | TWO | Roots | Heavy roots in main rod to relieve stop. Washed down and vaccumed street. | 8" vc, Schedule main for TV. | Y | Y | Storm drain at Carnegie Ct. | Dissipated into storm drain system, outlet dry. | N/A | Y | N | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
124145 | Fax 571-6972 | 08/11/00 09:30 | L. Finch | 6544160 | City of San Diego | 2000-08-10 19:58 | 08/10/00 20:38 | 20 | 0 | 918 21st St. | San Diego | SD | 92101 | 6"VC/ 8"PVC | ONE | Construction | Contractors temporary connection of flex pipe caused construction debris to build up and stop main. | 6"/8" pvc, Sandbag gutter & vacuumed, Notified resident engineer. | Y | N | Dissipated in guttter, didn't enter storm drain. | N/A | N/A | Y | N | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
123996 | Fax 571-6972 | 08/10/00 14:15 | L. Finch | 6544160 | City of San Diego | 2000-08-10 10:20 | 08/10/00 11:35 | 525 | 600 | 2099 Morley Field Dr. | San Diego | SD | 92101 | 6' Main | ONE | Vandalism | Vanpals destroyed existing hold down straps, put that material and rocks in main. Blockage was in M/H not main. | 6", Restrap all manholes in canyon. | N | Y | Canyon dirt channel storm drain, dried in channel. | Switzler Rd. at San Diego Bay. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
124240 | Fax 571-6972 | 08/11/00 14:30 | G. Neel | 6544160 | City of San Diego | 2000-08-11 11:17 | 08/11/00 13:20 | 615 | 0 | 3246 Erie St. | San Diego | SD | 92117 | 8"VC MAIN | TWO | Gravity Break | Erusion caused main back next to old break. Large rock fell on main. Broke 8"vc main. | Temp repairs, cut out bad section and cut in new 8" pvc pipe. | Y | N | Entered drainage ditch in canyon. | Dried up in canyon. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
124633 | Fax 571-6972 | 08/13/00 17:34 | D. A Branco | 6544160 | City of San Diego | 2000-08-13 10:36 | 08/13/00 13:30 | 8700 | 0 | 12360 Black Mtn Rd. | San Diego | SD | 92129 | 8"PVC MAIN | ONE | Roots | Blockage was caused by roots. | 8" pvc, Flushed line to relieve stoppage. | Y | Y | Entered storm drain 150 south of overflowing MH on Black Mtn Rd. and into Pacifc Ocean. | Penasquitos Canyon Creek and soaked into Creek. | Creek runs dry 9/10 of mile from Black Mtn Rd. | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
124721 | Fax 571-6972 | 08/14/00 14:20 | E. Semo | 6544160 | City of San Diego | 2000-08-14 14:20 | 08/14/00 13:20 | 228 | 228 | 3780 Mission Blvd. | San Diego | SD | 92109 | 96"VC MAIN | ONE | Grease | Grease stop on main. | 6" vc, Televised. | Y | Y | Into storm drain. | Santa Clara Pt. | N/A | Y | N | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
124837 | Fax 571-6972 | 08/15/00 00:09 | J. Wilder | 6544160 | City of San Diego | 2000-08-14 18:47 | 08/14/00 22:20 | 4260 | 1000 | 14071 Mango Dr. | San Diego | SD | 92014 | 10"VC MAIN | ONE | Roots | Roots in main, caught paper towels, etc. causing stoppage. | 10" vc, Rodded & Flushed easement main to relieve stoppage. | Y | Y | Storm drain system on West side of I-5. | N/A | N/A | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
125352 | Fax 571-6972 | 08/16/00 12:00 | L. Finch | 6544160 | City of San Diego | 2000-08-16 08:06 | 08/16/00 09:20 | 37 | 20 | 606 Washington St. | San Diego | SD | 92103 | 6"VC MAIN | ONE | Debris | Heavy paper debris caused partically blockage of 6"vc main in manhole outlet. | 6" vc, Cleaned up/down stream, washed, deoderized, recovered. | Y | Y | Storm drain 606 Washington dissipated before reaching 6 main storm channel | San Diego River/ Pacific Ocean. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
125425 | Fax 571-6972 | 08/17/00 00:50 | J. Wilder | 6544160 | City of San Diego | 2000-08-16 16:31 | 08/16/00 19:59 | 416 | 0 | 3027 30th St. | San Diego | SD | 92104 | 6"CP MAIN | ONE | Roots | Roots in main. | 6" cp, Hand rod main to relieve stoppage. | N | N | N/A | N/A | Dried up in canyon. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
125541 | Fax 571-6972 | 08/18/00 15:30 | R. Donahue | 6544160 | City of San Diego | 2000-08-16 19:51 | 08/18/00 14:30 | 341 | 0 | 3780 Voltaire St. | San Diego | SD | 92107 | C/O at 3780 Voltoire | ONE | Construction | Design problem with invert elevation caused sewage from address to flow out of c/o. Contractor installed lateral with reverse flow. | Flushed lateral | Y | Y | Storm drain in front of address. | Dissipated in storm drain. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
125920 | Fax 571-6972 | 08/18/00 15:30 | K. Vain | 6544160 | City of San Diego | 2000-08-18 11:00 | 08/18/00 12:00 | 100 | 0 | 8024 Tommy Dr. | San Diego | SD | 92119 | 8"VC MAIN | ONE | Roots | Root caused stoppage in main. | Clean easement main, TV, and put on Root Foam site. | N | N | Soaked into cons backyard. | N/A | Soaked into cons backyard. | Y | N | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
125956 | Fax 571-6972 | 08/18/00 22:03 | D. A Branco | 6544160 | City of San Diego | 2000-08-18 16:28 | 08/18/00 17:35 | 20 | 0 | 2117 Torrey Pines Rd. | San Diego | SD | 92037 | 6"VC MAIN | ONE | Roots | Blockage was caused by roots. | 6" vc, machine rodded D/E main to relieve root stoppage. | N | N | Dried in street. | N/A | Dried in street. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
125891 | Fax 571-6972 | 08/18/00 11:30 | G. Neel | 6544160 | City of San Diego | 2000-08-18 08:09 | 08/18/00 09:25 | 380 | 0 | 11480 North Torrey Pines Rd. | San Diego | SD | 92121 | 8"VC MAIN | ONE | Roots | Blockage was caused by roots. | Rodded 8" vc main to clean root stoppage. | N | N | Soaked into grass surrounding M/H. | N/A | Soaked into grass on Golf Coarse. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
125894 | Fax 571-6972 | 08/18/00 15:07 | M. A Whelan | 6544160 | City of San Diego | 2000-08-18 10:03 | 08/18/00 11:00 | 171 | 20 | 3485 Kenyon St. | San Diego | SD | 92110 | 8"VC MAIN | N/A | Roots | Roots and grease caused blockage which caused overflow. | 8" vc main, Rodded M.H. 266 to 265, Vactored. | Y | Y | Ran 1/2 blk. Kenyon Ct. 1/2 blk Kenyon St to enter storm drain 3300 blk. Kenyon St. | Storm drain runs towards Intercepter Sta. I-10. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
126069 | Fax 571-6972 | 08/19/00 14:42 | D. A Branco | 6544160 | City of San Diego | 2000-08-19 09:59 | 08/19/00 10:30 | 20 | 0 | 1805 Crepo Dr. | San Diego | SD | 92037 | 6"VC MAIN | ONE | Roots | Blockage caused by roots. | 6" vc, Flushed line to relieve root stoppage. | Y | N | Soaked into ground in dirt gravel area near manhole. | Pacific Ocean. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
126135 | Fax 571-6972 | 08/21/00 00:45 | D. A Branco | 6544160 | City of San Diego | 2000-08-20 21:00 | 08/21/00 00:30 | 420 | 0 | 4918 Cresita Dr. | San Diego | SD | 92115 | 6"CP MAIN | ONE | Roots | Blockage was caused by roots. | 6" cp, Highlined into canyon. Hand rodded main. | Y | N | Soaked into canyon behind address. | San Diego Bay/ Pacific Ocean. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
126172 | Fax 571-6972 | 08/21/00 08:36 | M. A Whelan | 6544160 | City of San Diego | 2000-08-21 09:32 | 08/21/00 12:28 | 234 | 20 | 3122 Gregory St. | San Diego | SD | 92104 | 6"CP MAIN | TWO (3110 Gregory St., 7-2-00) | Roots | Roots in main caused grease build up which blocked main and caused private c/o to back up and overflow. | 6" cp, 747 rodded main w/machine, 728 vacuumed, 747 rod w/blade & rod M.Hs | Y | N | Flowed from c/o in backyard of 3122 Gregory St. down drive way drain to gutter, flowed down Gregory St. about 150' to corner where it was vacuumed up. | N/A | Did not reach storm drain. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
126243 | Fax 571-6972 | 08/22/00 00:19 | J. Wilder | 6544160 | City of San Diego | 2000-08-21 17:06 | 08/21/00 17:55 | 49 | 0 | 3411 Poe St. | San Diego | SD | 92106 | 6"CP MAIN | ONE | Roots | Roots in Eastment main. | Hand rod main, cleaned up area. | Y | Y | Dissipated in gutter at storm drain. | N/A | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
126387 | Fax 571-6972 | 08/23/00 14:30 | G. Richardson | 6544160 | City of San Diego | 2000-08-22 15:11 | 08/22/00 22:15 | 45 | 0 | Aldine Dr. & Fairmont Av. in canyon | San Diego | SD | 92116 | 8"VC MAIN | ONE | Roots | Roots in main. | Hand rod main , 8" vc main. | N | N | N/A | N/A | Soaked into canyon. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
126501 | Fax 571-6972 | 08/24/00 12:30 | R. Donahue | 6544160 | City of San Diego | 2000-08-23 07:06 | 08/23/00 08:06 | 4200 | 4200 | 595 Hotel Circle South | San Diego | SD | 92108 | 10" VC | TWO | Roots | Root build up in main caused overflow. | Machine rodded, vactored gutter and sewage from down stream inlet. | Y | Y | Storm drain at address. | S.S. O. contained in storm drain, vactored and returned to system. | N/A | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
125541 | Fax 571-6972 | 08/23/00 17:38 | M. A Whelan | 6544160 | City of San Diego | 2000-08-23 11:00 | 08/23/00 12:00 | 30 | 0 | 3790 Voltaire St. | San Diego | SD | 92107 | C/O at 3780 Voltaire St. | TWO | Construction | Design problem with invert elevation caused sewage from address to flow out of c/o. Contractor installed lateral with reverse flow. | Flushed lateral, connect temp containment. | Y | Y | Storm drain on Worden. | Dissipated in storm drain. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
126504 | Fax 571-6972 | 08/23/00 10:00 | G. Richardson | 6544160 | City of San Diego | 2000-08-23 07:51 | 08/23/00 08:30 | 39 | 0 | 4490 47th & Monroe | San Diego | SD | 92116 | 6"VC MAIN | TWO | Grease | Grease build up in the main caused the overflow. | Rodded 6' vc main to remove grease. | Y | N | Street around the manhole. | N/A | Dried up in street and curb. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
126601 | Fax 571-6972 | 08/23/00 22:17 | J. Welder | 6544160 | City of San Diego | 2000-08-23 15:58 | 08/23/00 16:37 | 147 | 30 | Froude St. & Newport Av. | San Diego | SD | 92107 | 6"CP MAIN | ONE | Roots | Roots in main. | Rod main (6" cp). | Y | Y | Dissipated in storm drain system. | N/A | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
126947 | Fax 571-6972 | 08/28/00 14:00 | L. Davis | 6544160 | City of San Diego | 2000-08-25 12:00 | 08/25/00 13:10 | 2100 | 2000 | 9977 Lemonwood Lane | San Diego | SD | 92124 | M/H on 8"VC | ONE | Roots | Root blockage in 8"vc main in canyon East of Lemonwood Lane. Root build up in manhole | M/H on 8" vc, Clean and add to Root Foaming schedule | N | N | Canyon area around manhole 104. | Ponced up in canyon area. Pumped back into main. | Dried up in canyon area. | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency. Total volume was reported as "Aprox. 2100 Gallons in canyon" by discharger, changed to 2100 by RB staff for database consistency.
126989 | Fax 571-6972 | 08/25/00 20:29 | D. A Branco | 6544160 | City of San Diego | 2000-08-25 14:47 | 08/25/00 15:50 | 31 | 0 | 3738 Mission Blvd. | San Diego | SD | 92109 | 6"VC MAIN | ONE | Grease | Blockage caused by grease. | 6" vc, Flushed, rodded line. | Y | Y | Entered storm drain in alley at portsmouth CT and dissipated in system. | Mission Bay/ Pacific Ocean. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
127048 | Fax 571-6972 | 08/26/00 17:26 | D. A Bronco | 6544160 | City of San Diego | 2000-08-26 12:20 | 08/26/00 13:45 | 85 | 0 | Meadowbrook Dr. & Royal Oak Dr. | San Diego | SD | 92114 | 8"VC MAIN | ONE | Grease | Blockage was caused by grease. | Flush line to relieve grease stoppage. 8" vc | Y | Y | Entered storm drain in front of 355 Royal Oak Dr. | Sweetwater River/ San Diego Bay. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
127037 | Fax 571-6972 | 08/26/00 21:00 | D. A Branco | 6544160 | City of San Diego | 2000-08-26 11:03 | 08/26/00 20:30 | 567 | 500 | 30th & Palm (in canyon) | San Diego | SD | 92104 | 8"CP MAIN | TWO | Gravity Break | Machine rod; flush. Line has rocks in it ; possible break in pipe. | Flush, rod, 8"cp, contacted construction crew. | Y | N | Overflowed from manhole 197 and flowed 300 down the canyon into manhole 192. | San Diego Bay/ Pacific Ocean. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
127200 | Fax 571-6972 | 08/28/00 14:30 | R. Donahue | 6544160 | City of San Diego | 2000-08-28 10:56 | 08/28/00 12:41 | 1575 | 1575 | 950 Hotel Circle North | San Diego | SD | 92108 | 8"VC MAIN | ONE | Grease | Grease build up in main caused stoppage. | Flushed line, will TV to determine source of grease. 8" vc | Y | Y | Entered storm drain in front of address. | Flowed through system and paled on golf course. | Vactored and returned to system. | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
127951 | Fax 571-6972 | 08/30/00 13:00 | K. Vian | 6544160 | City of San Diego | 2000-08-30 10:19 | 08/30/00 11:06 | 94 | 0 | 5762 Del Cerro Blvd. | San Diego | SD | 92120 | 8"VC MAIN | ONE | Roots | Stoppage of roots 92' us from manhole 71. | 8" vc, Rodded main from M/H 71 to 77. | Y | Y | Storm drain at 5762 at Del Cerro Blvd. | Dried in storm drain. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
127969 | Fax 571-6972 | 08/30/00 18:08 | J. Wilder for J. Hernandez | 6544160 | City of San Diego | 2000-08-30 13:16 | 08/30/00 16:20 | 92 | 92 | 2955 K St. | San Diego | SD | 92102 | 6"CP MAIN | ONE | Gravity Break | 6" cement pipe break caused sewer to back up at consumers property. | 6" cp, investigate M.H.s, wash and vactor alley. Called constr. crew for repairs. | Y | N | Alley behind 2955 K Street. | None | Sewer puddled in alley, recovered 100%. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
128096 | Fax 571-6972 | 08/30/00 22:06 | J. Wilder | 6544160 | City of San Diego | 2000-08-30 18:50 | 08/30/00 20:30 | 50 | 0 | 3516 Tony Dr. | San Diego | SD | 92122 | 8"VC MAIN | ONE | Roots | Roots in main mixed with greased caused stoppage. | 8" vc, 739 11-11 area confirmed 7-31 to be 7-33, 677 flushed main. | N | N | Soaked into backyard of address. | N/A | Soaked into backyard of address. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
128611 | Fax 571-6972 | 09/02/00 21:46 | D. A Branco | 6544160 | City of San Diego | 2000-09-02 18:29 | 09/02/00 20:45 | 1360 | 0 | Flanders & Dancy | San Diego | SD | 92126 | 8"PVC MAIN | ONE | Grease | Blockage was caused by grease. | Flushed line to releive grease stop. 8" PVC | Y | Y | Entered storm drain at Flanders and Dancy and dissipated in system. | Carroll Canyon Creek/ Pacific Ocean. | N/A | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
128656 | Fax 571-6972 | 09/05/00 15:00 | L. Davis | 6544160 | City of San Diego | 2000-09-05 11:45 | 09/05/00 12:30 | 23 | 0 | Intersect. Avenida Magnifica & Handrich | San Diego | SD | 92131 | 8"PVC Stop was in the manhole | ONE | Grease | Grease blockage in the manhole. | Additional Cleaning and added to cleaning schedule. 8" pvc | Y | Y | Curbline in 11900 block of Handrich. | Storm drain at 11951 Handrich. | Dried up in storm drain. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
128990 | Fax 571-6972 | 09/06/00 22:30 | J. Wilder | 6544160 | City of San Diego | 2000-09-06 18:06 | 09/06/00 19:39 | 1395 | 1000 | 4011 Idaho St. | San Diego | SD | 92104 | 6"VC MAIN | ONE | Grease | Grease build up in main. | Vactored overflow, Rod to relieve stop. 6" vc | Y | Y | Dissipated in storm system. | N/A | N/A | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
129145 | Fax 571-6972 | 09/07/00 12:30 | G. Richardson | 6544160 | City of San Diego | 2000-09-07 07:49 | 09/07/00 08:50 | 255 | 4 | 2344 Altadena Av. | San Diego | SD | 92105 | 8"PVC MAIN | ONE | Grease | Grease build up in the main caused the overflow. | Flushed to relieve stoppage, referred to TV. 8" pvc | Y | N | The canyon behind the address. | N/A | Soaked into the address. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
129207 | Fax 571-6972 | 09/07/00 22:50 | J. Wilder | 6544160 | City of San Diego | 2000-09-07 14:50 | 09/07/00 16:21 | 150 | 0 | 5682 Dartford Wy | San Diego | SD | 92120 | 8"VC MAIN | ONE | Roots | Roots in Eastment Main | Highline flusher hose to relieve stop. 8" vc | Y | N | N/A | N/A | Saturated ground around manhole 76. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
129214 | Fax 571-6972 | 09/07/00 23:04 | J. Wilder | 6544160 | City of San Diego | 2000-09-07 20:05 | 09/07/00 20:21 | 32 | 32 | 219 Hensley St. | San Diego | SD | 92101 | 6"CP MAIN | TWO | Grease | Grease in 6" main. | Rod to relieve stop, vacuum to recover overflow, cleaned gutter. 6" cp | Y | N | Vacuum overflow from gutter. | N/A | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
129431 | Fax 571-6972 | 09/08/00 21:00 | M. A Whelan | 6544160 | City of San Diego | 2000-09-08 06:59 | 09/08/00 11:09 | 2500 | 1000 | 3093 C St | San Diego | SD | 92102 | 8"VC MAIN | ONE | Grease | Roots and grease caused blockage. Note: BSO in same area but not found earlier that above call is included. Time is for earlier call. | Machine rod to relieve stoppage, and vactored at stormdrain. | Y | Y | Entered storm drain in canyon at 3093 C St. and dissipated in storm drain. | Didn't reach San Diego Bay. | N/A | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
130271 | Fax 571-6972 | 09/13/00 04:20 | J. Wilder | 6544160 | City of San Diego | 2000-09-11 23:54 | 09/13/00 00:32 | 960 | 0 | 738 Rosecrans St. | San Diego | SD | 92106 | 6"VC MAIN | TWO | Roots | Per consumer overflow started on 09/11/00 in am. Running (on & off) since then. Roots in main cause stop. | Hand rod main relieve root stop. Refer-Main Machine Rod & MHS raised. 6" vc | Y | Y | San Diego Bay. | Pacific Ocean. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
130100 | Fax 571-6972 | 09/12/00 16:05 | M. A Whelan | 6544160 | City of San Diego | 2000-09-12 10:32 | 09/12/00 12:37 | 375 | 0 | 3655 Cactusridge Ct. | San Diego | SD | 92105 | 8"VC MAIN | ONE | Grease | Grease build up caused stoppage, overflow. | Hand rodded 30' in 8" vc main to relieve stop. Referred to TV. | Y | Y | Flowed into storm channel along and dried up and/or soaked into ground. | N/A | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
130312 | Fax 571-6972 | 09/13/00 11:30 | L. Davis | 6544160 | City of San Diego | 2000-09-13 09:10 | 09/13/00 10:28 | 156 | 100 | 10381 Matador Ct. | San Diego | SD | 92124 | 8"VC MAIN | ONE | Roots | Blockage on 8"vc main. | Cleaned and added to maintenance schedule. 8" vc | Y | N | Curbline at 10381 Matador Ct. | Concrete drain channel North of 10381 Matador Ct. | Canyon area East of Matador Court. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
130596 | Fax 571-6972 | 09/14/00 15:00 | R. Donahue | 6544160 | City of San Diego | 2000-09-14 15:00 | 09/14/00 13:54 | 53 | 0 | 2861 Arnoldson Av. | San Diego | SD | 92122 | 8"VC MAIN | ONE | Debris | Paper products (toilet paper and tampons) built D/S of manhole #274 causing partical stoppage in main. | Flushed, cleaned 2 sections will TV and re-evaluate. 8" vc | Y | Y | Storm drain on Trovers Way. | Flowed approxiamately 1/2 mile thru storm drain | Dried in canyon behind 6158 Trovers Way. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
136351 | Fax 571-6972 | 09/15/00 16:15 | M. A Whelan | 6544160 | City of San Diego | 2000-09-15 10:02 | 09/15/00 10:31 | 145 | 40 | 3rd Av. & Maple St. | San Diego | SD | 92101 | 6"VC MAIN | ONE | Roots | Root build up in main causing stoppage and overflow. | Machine rodded, vactored, referred to TV and Weekend Shift. 6" vc | Y | Y | One stream entered storm drain at Albatross and Maple St. which flowed to the canyon, soaked into the ground. | Flow went down 3rd Ave. where 725 vactored before entering and reaching storm drain. | The rest dried in gutter. | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
137055 | Fax 571-6972 | 09/15/00 15:42 | J. Mitchell | 6544160 | City of San Diego | 2000-09-15 09:28 | 09/15/00 09:50 | 3880 | 0 | 15900 Camino Crisalida** | San Diego | SD | 92128 | SPS #84 | TWO | Power Failure | Technician working at the station installing temporary power generator. Left panel in off position which did not allow pumps to start at high. High wet well level. | Advised staff to ensure systems were restored to proper status. SPS #84 | N | Y | Abandoned rock quarry. | None | Old rock bed quarry. | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
136387 | Fax 571-6972 | 09/15/00 19:42 | J. Fernandez (OCA) | 6544160 | City of San Diego | 2000-09-15 16:36 | 09/15/00 17:34 | 290 | 0 | Huntington Av. & Wilbee Ct. | San Diego | SD | 92108 | 8"VC MAIN | ONE | Roots | Blockage caused by roots. | Rodded main, removed roots, referred to Supervisor for Scheduled cleaning.8"vc | N | Y | Entered storm drain at 9120 Huntington Ave | San Diego River/ Pacific Ocean. | Soaked into canyon dirt, at storm drain outlet. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
136685 | Fax 571-6972 | 09/18/00 09:34 | R. Donahue | 6544160 | City of San Diego | 2000-09-18 09:34 | 09/18/00 11:00 | 430 | 430 | 4204 Dakota Dr. | San Diego | SD | 92109 | 8"VC MAIN | TWO | Roots | Roots in between manhole 211 and 212 going into Dakota Canyon. | 6 month PM site, currently in design stage to repair or replace. 8' vc | Y | Y | Storm drain in front of address. | Flowed thru storm drain, intercepted at D. V. #2 | Returned to system. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
136647 | Fax 571-6972 | 09/20/00 11:00 | E. Semo (OCA) | 6544160 | City of San Diego | 2000-09-18 08:09 | 09/18/00 09:30 | 243 | 243 | 3094 Olive St. | San Diego | SD | 92104 | 8"CP MAIN | THREE | Vandalism | Contractor working on sewer mains left manhole lids off of cones. Rock and debris were thrown into manhole #197 causing main to overflow. | City crews restrapped lids. 8" cp | Y | N | Pooled in canyon. | Crew vaccumed up overflow and debris caused by stoppage. | All overflow recaptured back into system. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
136683 | Fax 571-6972 | 09/18/00 13:30 | R. Donahue | 6544160 | City of San Diego | 2000-09-18 09:10 | 09/18/00 10:11 | 3050 | 1350 | 685 Turquoise & La Jolla Blvd. | San Diego | SD | 92037 | 10"PVC MAIN | ONE | Construction | Large moss of roots broke free from possible upstream laterals and collected on construction rock in main, causing complete stoppage on 10"PCV main. | Flush by machine, TV, Inspected. Put on insp. sched. 10" pvc | Y | Y | Storm drain in front on 2556 La Jolla Blvd. | Pacific Ocean. | 1350 gallons flowed south on street and intercepted at tourmaline. 1700 gallons flowed north on street, entered ocean at Sea Ridge and Linda Way, P. B. point. | Y | Y | Y | Signs still posted at the time of report. | 10 signs posted at the time of report. | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
137040 | Fax 571-6972 | 09/19/00 13:20 | E. Semo | 6544160 | City of San Diego | 2000-09-19 11:09 | 09/19/00 11:35 | 145 | 145 | Intersection K St. & Hoitt St. | San Diego | SD | 92101 | 6"CP MAIN | ONE | Grease | Grease and debris stop on 6" C.P. caused 270' section to overflow. | Will have main televised to determine cleaning frequency. 6" cp | Y | N | Overflow pooled along curb. | Side, was able to recapture. | All of oveflow back into system. | Y | N | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
137022 | Fax 571-6972 | 09/19/00 10:00 | E. Semo | 6544160 | City of San Diego | 2000-09-19 07:50 | 09/19/00 09:10 | 210 | 0 | 1801 Sheridan Ave. | San Diego | SD | 92103 | Hi Line | ONE | Other | Contractor working on city sewer mains. Sewer hi line leaking, car drove over coupling. | Hi line repaired by contractor. | Y | Y | Entered storm at Lyndon and Sheridan. | N/A | Dissipated into canyon. | Y | N | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
137471 | Fax 571-6972 | 09/21/00 11:00 | E. Semo | 6544160 | City of San Diego | 2000-09-21 07:43 | 09/21/00 09:05 | 364 | 0 | 4220 Ampudia St. & Whitman St. | San Diego | SD | 92103 | 6"CP 300' SEC. | ONE | Roots | Flushed main to relieve root. Stopped on easement main. | Will have main TV, 6" cp | Y | Y | Storm drain at Ampudia St. and Witman St. | Soaked into canyon with thick vegatation. | No public access. | Y | N | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
137475 | Fax 571-6972 | 09/21/00 14:40 | M. Dawson | 6544160 | City of San Diego | 2000-09-21 08:16 | 09/21/00 09:30 | 148 | 0 | 6355 Lorca Dr. | San Diego | SD | 92115 | 6"VC MAIN | ONE | Roots | Roots in 6" clay pipe. | Will put on preventive maintenance site. | N | N | N/A | N/A | Absorbating into ground. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
137486 | Fax 571-6972 | 09/22/00 08:15 | M. Dawson | 6544160 | City of San Diego | 2000-09-21 09:07 | 09/21/00 10:40 | 930 | 0 | 2215 Susan Pl. | San Diego | SD | 92105 | 6"VC MAIN | ONE | Roots | Stoppage caused by roots. | Will add on to preventive maint. site in area. 6" vc | Y | N | N/A | N/A | Soaked into dirt in canyon. | Y | N | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
137508 | Fax 571-6972 | 09/21/00 14:15 | E. Semo | 6544160 | City of San Diego | 2000-09-21 12:02 | 09/21/00 12:30 | 28 | 0 | 3502 Wanona Dr. | San Diego | SD | 92107 | 6"CP MAIN | THREE | Roots | Root stop on Easement main. Rod main to relieve stop. | Will change to 6 months Rod, also TV main. 6" cp | Y | Y | Storm drain at Clove and Oliphant. | Dissipated into storm drain system. | Overflow dissipated in storm pipe. | N | N | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
137539 | Fax 571-6972 | 10/02/00 13:10 | J. Wilder | 6544160 | City of San Diego | 2000-09-21 16:20 | 09/21/00 18:13 | 2260 | 0 | Murray Prk Dr. & Park Ridge Blvd. | San Diego | SD | 92119 | 8"VC MAIN | ONE | Rocks | Rocks and sludge in main caused stoppage. | Flushed, TV, referred to have easement cleaned & put on PM. 8" vc | Y | Y | Alvarado Creek. | Pacific Ocean. | N/A | Y | Y | Y | 1 day | 20 signs posted at the time of report. | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
137778 | Fax 571-6972 | 09/22/00 14:30 | M. Dawson | 6544160 | City of San Diego | 2000-09-22 07:37 | 09/22/00 08:37 | 300 | 250 | 153 Sellsway | San Diego | SD | 92173 | 6"VC MAIN | ONE | Vandalism | Vandalism to exposed clean out in vacant lot. Rocks and debris reached main. | Will cover up C/O and plug opening. 6" vc | Y | N | N/A | N/A | Wash and swepted puddles back into manhole. | Y | N | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
138020 | Fax 571-6972 | 09/23/00 14:31 | D. A Branco | 6544160 | City of San Diego | 2000-09-23 09:56 | 09/23/00 10:50 | 270 | 0 | 4037 South Hempstead Cr. | San Diego | SD | 92116 | 6"VC MAIN | ONE | Grease | Blockage was caused by grease. | Flushed line to relieve grease stop. 6" cp | y | Y | Flowed into storm drain infront of 4036 So. Hempstead and dissipated in system. | San Diego River/ Pacific Ocean. | N/A | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
138042 | Fax 571-6972 | 09/23/00 20:35 | D. A Branco | 6544160 | City of San Diego | 2000-09-23 15:37 | 09/23/00 17:45 | 3200 | 2800 | 3802 49th St | San Diego | SD | 92105 | 8"VC MAIN | ONE | Roots | Blockage was caused by grease and roots. | Machine Rod, refer for accelerated PM schedule site. 8" vc | Y | Y | Soaked into ground in canyon and in yard behind 3802 49th St. Flow that reached storm drain was vactored and returned to system. | Chollas Creek/ San Diego Bay. | N/A | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
138207 | Fax 571-6972 | 09/27/00 16:45 | J. Wilder | 6544160 | City of San Diego | 2000-09-25 18:34 | 09/25/00 19:50 | 38 | 38 | 4276 Oceanview Blvd. | San Diego | SD | 92113 | 10"VC MAIN | TWO | Grease | Grease build up in main. | Vactor overflow, Rod main, refer to have put on PM site. 10" main | Y | N | Gutter at that address. | NA | Sandbag gutter and vaccumed overflow. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
138615 | Fax 571-6972 | 09/26/00 10:45 | M. Dawson | 6544160 | City of San Diego | 2000-09-26 08:26 | 09/26/00 09:38 | 124 | 0 | Cielo & "S" 65th St. | San Diego | SD | 92114 | 8"VC MAIN | ONE | Grease | Grease blockage. | Rodded to relieve stoppage. 8" vc | Y | Y | Canyon at 65th and Skyline. | N/A | Absorbing into ground. | Y | N | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
138651 | Fax 571-6972 | 09/26/00 16:33 | E. Semo | 6544160 | City of San Diego | 2000-09-26 13:30 | 09/26/00 13:50 | 50 | 0 | 4800 North Harbor Dr. | San Diego | SD | 92133 | 8"VC MAIN | ONE | Grease | Grease, rod main to relieve stop. Manhole was not overflowing upon arrival. Evidence of overflow around manhole 50 gallons is an estimated. Per County Health post signs for 2 days. | Flush main and TV, 8" vc | Y | Y | Storm drain on North Harbor Dr. | San Diego Bay. | Pacific Ocean. | Y | N | Y | 2 days per County | 4 signs were posted. | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
139318 | Fax 571-6972 | 09/28/00 14:30 | J. Becker | 6544160 | City of San Diego | 2000-09-28 12:34 | 09/28/00 14:05 | 1365 | 0 | 4920 Southcrest Ave. | San Diego | SD | 92110 | 8"VC MAIN | ONE | Other | Debris caused overflow and alarm that was supposed to alert us wasn't functioning. | Fix overflow sensor, rod with 3 prong in future. | Y | N | Absorb into canyon. | Soaked into canyon. | Soaked into canyon. | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
139296 | Fax 571-6972 | 09/20/00 14:30 | J. Becker | 6544160 | City of San Diego | 2000-09-28 09:53 | 09/28/00 12:50 | 2655 | 2655 | 5038 Edgeworth Rd. | San Diego | SD | 92037 | 8"VC MAIN | ONE | Roots | Roots in main caused main stoppage. | Rodded & TV in a.m. 8" vc | Y | Y | Entered storm drain at multi locatins. | Intercepted at Interceptor I- 8. | Interecepted at Interceptor I- 8. | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
139656 | Fax 571-6972 | 09/29/00 15:00 | L. Davis | 6544160 | City of San Diego | 2000-09-29 11:04 | 09/29/00 13:20 | 68 | 0 | 13254 Entreken Av. | San Diego | SD | 92129 | 8"PVC MAIN | ONE | Roots | Root in manhole. | Additional cleaning of the area and add to cleaning schedule. | Y | Y | Curbline at 13300 block of Entreken Ave. | Storm drain at Entreken Ave. and Sedbrus St. | Dried up in storm drain area. | Y | N/A | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
139646 | Fax 571-6972 | 09/29/00 15:20 | J. Oropeza | 6544160 | City of San Diego | 2000-09-29 10:35 | 09/29/00 13:45 | 675 | 575 | 2625 Ariane Pl | San Diego | SD | 92117 | 10"VC MAIN | ONE | Roots | Blockage was caused by roots. Origanal call was a stoppage only, which turned into and overflow at 13:00, 575 gallons were recovered by interceptor. 100 gallons were lost sue to soaking into dirt channel. | Flushed & Rodded 10" vc referred to area supervisor. | Y | Y | Entered storm drain at Morena Blvd. and Ariane Dr. | Rose Creek/ Mission Bay | Interceptor # IPS1 | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
139634 | Fax 571-6972 | 09/29/00 14:30 | J. Becker | 6544160 | City of San Diego | 2000-09-29 08:12 | 09/29/00 09:20 | 680 | 100 | 2451 Ellentown Rd. | San Diego | SD | 92037 | 8"VC MAIN | ONE | Roots | Root blockage in 8 inch VC main caused sewage to come out of property. Cleaned out spilling into storm drain then reaching the Pacific Ocean. | Rodded, flushed, recovered 100 gallons, TV main ASAP. 8" vc | Y | Y | Spill site storm drain. | N/A | Pacific Ocean. | Y | Y | Y | 1 Day | 6 signs were posted. | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
140180 | Fax 571-6972 | 09/30/00 18:25 | M. Bedard | 6544160 | City of San Diego | 2000-09-30 15:47 | 09/30/00 16:35 | 279 | 135 | 5484 Resevoir Rd. | San Diego | SD | 92120 | 8"VC MAIN | TWO | Roots | Roots blocked 8" vc main. | Relieved stop, set up berm, cleaned storm channel. 8" vc | Y | Y | Concrete channel at Alvarado Rd. and Reservoir Dr. | San Diego River | Pacific Ocean. | Y | Y | N | N/A |  | Units (gallons) were deleted by RB staff from Total and recovered volumes reported by discharger for database consistency.
816 | FAX 8/16/00 | 2000-08-16 10:00 | STEVEN GONZALES | (619)691-5027 | City of Chula Vista | 2000-08-16 10:00 | 2000-08-16 14:00 | 200 | 160 | 1680 BROADWAY | CHULA VISTA | SD | 91910 | CLEAN OUT | 0 | BLOCKAGE | GREASE | PRIVATE PROPERTY-PLUMBER CORRECTED PROBLEM | NO | NO | N/A | N/A | CONTAINED / PARKING LOT | NO | N/A | NO | N/A | CONTAINED SPILL BY VACUUMING
908 | FAX 9/8/00 | 2000-09-08 14:30 | STEVE PADILLA | (619)6915027 | City of Chula Vista | 2000-09-08 14:30 | 2000-09-08 15:00 | 300 | 250 | 410 EAST H ST | CHULA VISTA | SD | 91910 | CLEAN OUT | 0 | BLOCKAGE | GREASE & ROOTS | CONTAINED/ VACUUMED /FLUSHED MAIN & TV LINE | NO | YES | N/A | N/A | CATCH BASIN | NO | N/A | NO | N/A | CONTAINED SPILL BY VACUUMING
924 | FAX 9/24/00 | 2000-09-24 16:05 | TONY CONTRERAS | (619)6915027 | City of Chula Vista | 2000-09-24 16:05 | 2000-09-24 18:00 | 300 | 150 | 681 COLORADO | CHULA VISTA | SD | 91910 | MAN HOLE | 0 | BLOCKAGE | GREASE | CONTAINED/ VACUUMED /FLUSHED MAIN & TV LINE | YES | YES | YES | YES | CENTRAL BASIN | YES | NO | YES | 5 | CONTAINED SPILL BY VACUUMING | Discharger reported Total volume as "200 to 300"; changed by RB staff to 300 for database consistency.
OOO101 | 858 571 6972 | 070500 1250 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2000-07-05 12:35 | 070500 1330 | 800 | 800 | Heisler Park 330 Cliff Drive | Laguna Beach | Orange | 92651 | Restrooms at Heisler Park | 0 | Construction | City contractor Doty Bros. Were installing a 12 inch pipe and operating on a by-pass pump. They turned off the pump for about two hours or more. This caused sewage to back up in the 18 inch trunk line and overflowed at the restrooms in Heisler Park | City crews sand bagged off the spill area and vacuumed up all sewer water. Washed down with clean water to the vacuum truck. We recovered all 800 gallons. No sewage made it to the storm drain or the beach. | No | No | None | None | Heisler Park/Jasmine Street | Yes | Yes | No | None
OOO102 | 858 571 6972 | 070700 1300 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2000-07-07 13:00 | 070700 1400 | 500 | 500 | Cliff Drive | Laguna Beach | Orange | 92651 | Restrooms at Heisler Park | 1 | Construction | Contractors by-pass pump was not keeping up with the flow due to rages on the suction screen | Contractor added a second pump. City crews stopped all sewage at the restrooms by vacuuming all sewer water. No sewage went into the storm drain or beach | No | No | None | None | Heisler Park/Jasmine Street | Yes | Yes | No | None | Doty. Bros have two by-pass pumps on line and manned at all times.
OOO103 | 858 571 6972 | 071700 1400 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2000-07-15 13:30 | 071500 1730 | 40 | 20 | Gaviota/Oak Street | Laguna Beach | Orange | 92651 | Lateral Line at 1099 S. Coast Hwy | 0 | Construction | The main line on Gaviota Drive was lined on 2/23/00. At that time, the lateral line to 1099 S. Coast Hwy was not cut open. The lateral has a leak so small that water usage did not cause any visible problems on 7/15/00. The property owner used enough wa | 20 gallon plus entered the storm drain and went to the beach. The storm drain outlet was bermed and the catch basin blocked with sand bags. The sewage at the beach soaked into the sand. About 20 gallons in the street was vacuumed up. The lateral line | Yes | Yes | Pacific Ocean | Pacific Ocean | Pacific Ocean | Yes | Yes | Yes | Three
OOO104 | 858 571 6972 | 072600 2015 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2000-07-26 20:00 | 072600 2015 | 10 | 10 | 658 S. Coast Hwy | Laguna Beach | Orange | 92651 | Private Lateral 658 S. Coast Hwy | 0 | Roots | Tree roots | Homeowner called a plumber to open the stoppage. City personnel called Orange County Health Dept. respond. Alan Reynolds at (714) 667-3632 did a follow up report. This was on 7/27/00 at 1000+- | No | No | None | None | Sidewalk area only | Yes | Yes | No | None
OOO105 | 858 571 6972 | 072800 0935 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2000-07-28 09:00 | 072800 0945 | 2500 | 2500 | 592 Mystic Way | Laguna Beach | Orange | 92651 | Manhole #30 | 0 | Roots | Private sewer lateral roots plugged at City sewer manhole #30 from an unknown location | City crews cleaned the main line to open the blockage. Then finished rodding to the downstream mnahole 145ft. Also cleaned the upstream section of sewer main line at 385ft. Flushed the storm drain with chlorine from the hydrant 25 min. All sewer and w | No | Yes | None | None | From the diversion box into the City sewer system. | Yes | Yes | No | None | OES # 00-3376
OOO106 | 858 571 6972 | 081000 1615 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2000-08-04 14:30 | 080600 1000 | 5 | 5 | 1980 San Remo | Laguna Beach | Orange | 92651 | 4" Private Lateral / Donna Drive | 0 | Blockage | Debris in Private Sewer Lateral caused a leak at the joint | The homeowner called a plumber to repair the problem. City crews contained the leak on private property | No | No | None | None | Private property | Yes | No | No | None | Private Sewer Lateral
OOO107 | 858 571 6972 | 092100 0815 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2000-09-21 08:15 | 092100 0835 | 500 | 500 | Manhole #3 at Ocean Avenue/Coast Hwy | Laguna Beach | Orange | 92651 | Manhole #3 | 0 | Grease | City 10 inch sewer line was plugged with grease from upstream business | City crews used a jetter/vacuum truck to open the stoppage and recover all sewage silled into the storm drain. This line is cleaned each year at this time. | No | Yes | None | None | Collected in the storm drain | Yes | No | No | None | Collected in the storm drain and vacuumed up by City Crews
001003 | Fax | 2000-08-11 13:00 | Dave Seymour | (949)459-6540 | Santa Margarita Water District | 2000-08-11 06:00 | 2000-08-11 08:00 | 2400 | 1200 | Coto Drive at Oso Parkway | Coto de Caza | OR | 92679 | Force Main Air Relief Line | 0 | Plastic Air Relief | PVC line between force main and air-vac cracked. | Temporarily isolated the line. The line will be replaced with coated steel. | Y | Y | Coto de Caza Creek | N/A | N/A | Y | Y | N | N/A | None.
001004 | Fax | Quarterly Report | Dave Seymour | (949)459-6540 | Santa Margarita Water District | 2000-08-24 11:00 | 2000-08-24 11:00 | 300 | 300 | Chiquita WRP, 28793 Ortega Hwy | San Juan Capistrano | OR | 92675 | Sludge Truck | 0 | Truck Landing Gear Collapsed | Contractor's truck gear collapsed causing the truck to shift away from the conveyor belt. | Had the contractor replace the trailer. | N | N | None | N/A | N/A | Y | N | N | N/A | None.
001005 | Fax | 2000-09-18 11:30 | Dave Seymour | (949)459-6540 | Santa Margarita Water District | 2000-09-16 12:50 | 2000-09-16 13:50 | 200 | 200 | Camino Pedriza/Altea | Talega Valley | OR | 92672 | Gravity Manhole 060352 | 0 | Construction Debris | The line was blocked with debris in a new construction area. | Placed sandbags to contain the spill. Used Vactor truck to clean line and remove debris. | N | Y | Dry Creek Bed | N/A | N/A | Y | N | N | N/A | None.
001006 | Fax | 2000-09-26 16:10 | Dave Seymour | (949)459-6540 | Santa Margarita Water District | 2000-09-26 13:15 | 2000-09-26 13:45 | 17610 | 9960 | Puerta de Luz/Trabuco Road | Mission Viejo | OR | 92692 | Sewer Force Main | 0 | Construction | Contractor installing sewer by-pass hit the force main during excavation. | Contractor called SMWD. Our crews shut off the lift station, bermed the storm drain, and recovered the remaining sewage. | Y | Y | Storm Drain | Trabuco Creek | N/A | Y | Y | N | N/A | Flow did not reach the beach. Berm in place at Doheney.
001-001 | SIRT (FAX) | 2000-08-18 13:30 | Larry Dees | 949-425-3537 | Moulton Niguel Water | 2000-08-18 10:40 | 2000-08-18 16:15 | 3600 | 3400 | 26750 Avery Parkway | Mission Viejo | OR | 92691 | 6" PVC forcemain | 2 | Line break | Pipe split longitudinally for about 10 feet. | Repaired forcemain. Lift station is being bypassed by a new gravity sewer to San Juan Capistrano system. Sewer construction should be completed by 9/30/00. | N | N | N/A | N/A | Vactor truck - 3,400 gals; surrounding soil - 200 gals. | Y | N | N | N/A | N/A
001-002 | SIRT (FAX) | 2000-08-15 11:00 | Brad Bruington | 949-425-3543 | Moulton Niguel Water | 2000-08-15 07:15 | 2000-08-15 07:35 | 700 | 700 | La Plata/Vista Plaza | Laguna Niguel | OR | 92677 | 8" PVC gravity pipe | 1 | Debris, Construction | Downstream side of manhole 50% blocked due to concrete from original construction. Private sewer root ball and debris hung-up on concrete protrusion. | Concrete protrusion removed after video inspection of line. | Y | Y | Sulphur Creek at La Plata & Crown Valley Pkwy. | None | Wastewater was pumped from Sulphur Creek catch basin into MNWD sewer. 100% recovery. | Y | N | N | N/A | N/A
001-003 | SIRT (FAX) | 2000-08-10 16:30 | Brad Bruington | 949-425-3543 | Moulton Niguel Water | 2000-08-10 07:10 | 2000-08-10 07:20 | 2000 | 1200 | 28386 Alicia Parkway | Laguna Niguel | OR | 92677 | Lift Station | 1 | Power failure | Power failure to programmable logic controller caused pumps to idle. Dialer called telephone service but call went unanswered due to equipment failure at service. | Station is being upgraded at present time, including programmable logic controller that failed. Power circuits will be separated to both emergency dialers and alarms. | Y | Y | Sulphur Creek from storm drain | Aliso Creek to diversion dam, pumped into AWMA outfall line. | AWMA outfall line. | Y | N | N | N/A | N/A
001001 | Voice Mail | 9/2/2000 1140 | Noah C. Sanchez | 949 830-0580 | Los Alisos W.D. | 2000-09-02 08:00 | 9/2/00 0830 | 25 | 0 | 23442 El Toro Rd. | Lake Forest | OR | 92630 | cleanout/manhole | 0 | blockage | Plumber's snake found in sewer line. | Cleared blockage and cleaned line. | N | Y | None | None | Storm drain | Y | N | N | NA | 25 gal of raw sewage spread out and began evaporating as it reached the storm drain 50 ft. away.
990009 | Mike Golina | 27 Oct 00 17:00 Hrs | Jay Elston | 949.366.1553 | CSC | 2000-07-24 12:00 | 27 July 00 15:00 Hrs | 288 | 0 | 380 Avenida Pico | San Clemente | OR | 92672 | 1" Reclaim Irrigation Line | 0 | Line Break | Broken irrigation line | Closed valve; landscape contractor made repairs | Y |  | MO 2 Drainage Channel | Pacific Ocean | Pacific Ocean | Y | N | N | N/A | Leak was discovered on 27 July 00 at 15:00 hrs, staff estimate the line broke approximately at 12 noon on 24 July 00, the date when last observed that line was intact. Flow exiting was estimated at 3 gal per minute during each operating cycle at the irrigation station.
990011 | FAX | 24 Oct 00 13:00 Hrs | Jay Elston | 949.366.1553 | CSC | 2000-08-14 | 14 Aug 00 11:40 Hrs | 400 | 0 | Easement line between South Ola Vista and 300 Blk West Alessandro | San Clemente | OR | 92672 | SMH D8238 | 0 | Cause Unknown | Obstruction relieved itself before ColSys ops arrival to site. | Colsys ops rodded line and found no unusual condition. Line was last clean 17 May 00 and historically has not been a trouble spot. Crews will video line for deficiencies. | N | N | N/A | N/A | Spill soaked into soil around manhole and dry area of canyon | Y | N | N | N/A
990-004 | Clay Clifton | 7/20/20 0930 | Ron Gunnett | 760-788-2252 | Ramona Water District | 2000-07-20 06:45 | 7/20/00 0715 | 3000 | 3000 | Rangeland Road | Ramona Calif. | San Diego | 92065 | 8" forcemain | 1 | Mechanical Joint | Mechanical Joint Failure | Restraints were installed on pipe | no | no | yes | no | no | yes | no | no | n/a | Spill entered ravine into a cow pasture where the discharge was recovered
990-05 | n/a | 9/2/00 1942 | n/a | 760-788-2252 | Ramona Water District | 2000-09-02 19:42 | 2000-09-03 | 1000 | 1000 | Hanson Lane | Ramona Calif. | San Diego | 92065 | 8" Main | 1 | Roots | Root intrusion through joints. | Jetted pipeline and removed material from pipeline. | no | no | no | no | no | no | no | no | n/a | Spill was contained within the house
2000-11 | (858) 571-6972 (SIRT) | 2000-07-05 10:15 | MIKE DUNBAR | (949)499-4555 | SOUTH COAST WATER DISTRICT | 2000-07-01 10:20 | 2000-07-01 11:00 | 10 | 0 | Westley Apartments | LAGUNA BEACH | OR | 92651 | MANHOLE | 0 | LINE PLUGGED WITH LARGE AMOUNTS OF PAPER | LARGE AMOUNTS OF PAPER WAS REMOVED FROM THE SEWER PIPELINE. SMALL AMOUNT OF FLOW LEAKED OUT OF HOLE INTO MANHOLE | REMOVED ROOTS AND CLEANED LINE | N | N | NONE | NONE | PUDDLED AROUND MANHOLE | Y | N | N
2000-12 | (858) 571-6972 (SIRT) | 2000-08-07 10:45 | MIKE DUNBAR | (949)499-4555 | SOUTH COAST WATER DISTRICT | 2000-08-05 18:00 | 2000-08-05 19:35 | 1500 | 0 | 24796 SUN STAR | DANA POINT | OR | 92629 | MANHOLE | 0 | LINE PLUGGED WITH ROOTS | ROOTS IN MAIN LINE CAUSED BLOCKAGE. SANITARY PERSONNEL REC'D CALL AT 8:26 P.M. UPON ARRIVING AT SITE THEY WERE TOLD FLOW HAD BEEN RUNNING ON & OFF SINCE ABOUT 6:00 P.M. | CLEANED LINE | Y | Y | D.P. HARBOR | PACIFIC OCEAN | PACIFIC OCEAN | Y | Y | Y |  | AREA ALREADY POSTED DUE TO HIGH BACTERIA COUNT
2000-13 | (858) 571-6972 (SIRT) | 2000-08-09 15:00 | MIKE DUNBAR | (949)499-4555 | SOUTH COAST WATER DISTRICT | 2000-08-09 12:15 | 2000-08-09 12:45 | 10 | 10 | 22212 RICO ROAD | LAGUNA BEACH | OR | 92651 | MANHOLE | 0 | LINE PLUGGED WITH ROOTS | ROOTS OBSTRUCTING FLOW BUT NOT STOPPING FLOW. FOAM COMING OUT OF MANHOLE CAUSING SMALL PUDDLE ALONG CURB | CLEANED LINE | N | N | NONE | NONE | RETURNED FLOWS TO COLLECTION LINE | Y | Y | N
2000-14 | (858) 571-6972 (SIRT) | 2000-09-03 10:00 | MIKE DUNBAR | (949)499-4555 | SOUTH COAST WATER DISTRICT | 2000-09-02 12:15 | 2000-09-02 13:15 | 3000 | 0 | CALLE PORTOLA/CALLE VELEZ | CAPO BEACH | OR | 92624 | MANHOLE | 0 | LINE PLUGGED WITH TREE ROOTS | ROOTS BLOCKED MAIN SEWER COLLECTION LINE CAUSING MANHOLE TO OVERFLOW | CLEANED LINE | N | Y | NONE | NONE | SMALL AMOUNT REACHED SAND | Y | N | Y |  | DOHS POSTED "ADVISORY" ONLY AT EXIT OF STORM DRAIN
001007 | Fax | 2000-11-04 18:45 | Dave Seymour | (949)459-6540 | Santa Margarita Water District | 2000-11-04 14:00 | 2000-11-04 14:23 | 82814 | 64500 | Chiquita WRP, 28793 Ortega Highway | San Juan Capistrano | OR | 92675 | Influent Lift Station | 1 | Power Failure | A crow flew into the power lines and shorted out SDG&E commercial power. Our emergency generators started automatically and ran the influent pumps and treatment plant. After about 20 minutes, a radiator hose broke on the generator for the influent pumps causing the generator and pumps to shut down. | Staff started an emergency backup pump, then isolated the heat exchanger and restarted the generator. | Y | N | Chiquita Creek, adjacent to the lift station | N/A | N/A | Y | Y | N | 0 | There is a large pond where the sewage spilled into the creek. Much of the spill was contained within that pond and returned to the sewer system. Water in the creek must flow approx. 1 1/2 miles downstream through dense cattails and other vegetation, until it meets the confluence with San Juan Creek. At the time of the spill, the flows were soaking into the ground prior to reaching San Juan Creek.
001-004 | SIRT (Attn: Gloria Fulton) | 2000-10-16 08:00 | Brad Bruington | 949-425-3543 | Moulton Niguel Water | 2000-10-13 13:00 | 2000-10-13 14:15 | 300 | 300 | Laguna Niguel Regional Park | Laguna Niguel | OR | 92677 | 24" techite forcemain | 1 | Line Break | 24" techite forcemain was cracked. | Contractor placed a repair clamp on pipe. | N | N | None | None | 300 gallons vacuumed from ground to Vac-Con truck | Y | N | N | 0
001-005 | SIRT (Attn: Gloria Fulton) | 2000-11-27 08:00 | Brad Bruington | 949-425-3543 | Moulton Niguel Water | 2000-11-26 12:00 | 2000-11-26 12:45 | 90 | 40 | Preston/Felton | Laguna Niguel | OR | 92677 | 8" gravity sewer line at drop manhole structure | 1 | Roots | Possible root blockage in vertical section of drop manhole. Upper overflow pipe failed to handle flow. | Manhole structure was video inspected and repaired. Exposed areas were washed down and vacuumed by combo trucks. | Y | Y | Flow entered catch basin on Niguel Rd. near Alicia Pkwy. Flow continued to J03P01 | Sulphur Creek Reservoir |  | Y | N | N | 0
001-006 | SIRT (Attn: Gloria Fulton) | 2000-12-11 07:30 | Brad Bruington | 949-425-3543 | Moulton Niguel Water | 2000-12-10 11:00 | 2000-12-10 12:00 | 200 | 0 | Puerta De Oro | Mission Viejo | OR | 92691 | 8" VCP sewer line easement to street below | 1 | Roots | Tree roots intruded in three pipe joints on easement line. | Easement line was video inspected. Roots have been removed. Line will be repaired by replacement or pipe-bursting. | Y | Y | 48" storm drain to Oso Creek | San Juan Creek |  | Y | N | N | 0
1016 | (858) 571-6972 (SIRT) | 2000-12-26 15:30 | MIKE DUNBAR | (949)499-4555 | SOUTH COAST WATER DISTRICT | 2000-12-23 08:40 | 2000-12-23 10:30 | 500 | 500 | VALIDO/WEST STREET | LAGUNA BEACH | OR | 92651 | MANHOLE | 1 | STICKS/DEBRIS WERE FORCED THRU MANHOLE COVER | STICKS/DEBRIS WERE FORCED THRU MANHOLE COVER PICK HOLE CAUSING WASTEWATER TO BACKUP & OVERFLOW. APPEARS TO BE VANDALISM. | SANITARY CREW WILL EVALUATE COLLECTION SYSTEM TO SEAL MANHOLE COVER & PLUG PICK HOLE | N | N | NONE | NONE | DIVERTED TO DOWNSTREAM M.H. | Y | N | N
990012 | Rebecca Stewart | 26 Oct 00 1135 | A J Howard | 949.361.8253 | CSC | 2000-10-26 09:35 | 26 Oct 00 0945 | 300 | 0 | 178 Avenida De La Paz | San Clemente | OR | 92672 | SMHD6113 | 0 | Private Lateral Cut Root Ball | A cut root ball 4" diameter by 22" long originating from a private lateral becam lodged in the outlet manhole in SMHD6141 causing a partial flow blockage and subsequent overflow at SMHD6113. | ColSys crews rodded line, dislodged and later removed cut root ball. | Y | Y | Bonita Canyon Drainage | County Drainage Channel MO2 | Pacific Ocean | Y | N | Y | 6 Days | Sanitary sewer overflow combined with storm water flows could not be contained or diverted back into sanitary sewer system.
990013 | Rebecca Stewart | 12 Nov 00 1655 | J Elston | 949.361.8231 | CSC | 2000-11-12 12:15 | 12 Nov 00 1305 | 375 | 200 | 170 Avenida Baja | San Clemente | OR | 92672 | SMHE7542 | 0 |  | Cause Unknown. Crews to video | ColSys crews rodded line, dislodged obstruction to restore flow | Y | Y | Salvador Canyon Drainage | N/A | Soil | Y | N | N | N/A | ColSys crews arrived on site and contained overflow stopping discharge to drainage system. Vactor on site cleared unknow obstruction and vacuum contained flow. Video revealed slight sag. No other deficiencies observed. Continue to monitor
PL99001 | FAX | 22 Oct 00 1445 | J Elston | 949.361.8231 | CSC | 2000-10-21 07:30 | 21 Oct 00 1430 | 30 | 0 | 330 Paseo De Cristobal | San Clemente | OR | 92672 | PRIVATE LATERAL | 0 | Unknown blockage in private lateral |  | Plumber cleared | Y | Y | Street gutter | Storm drainage system | Soil on east side of OCTA Railroad Tracks | Y | N | N | N/A | ColSys crews arrived on site and placed sandbags to contain overflow on private property. Crews vacuumed contained flow until plumber arrived to relieve obstruction.
PL99002 | FAX | 30 Oct 00 1457 | A J Howard | 949.361.8253 | CSC | 2000-10-27 14:57 | 27 Oct 00 1515 | 100 | 50 | 205 Avenida Del Mar | San Clemente | OR | 92672 | PRIVATE LATERAL | 0 | Unknown blockage in private lateral |  | Plumber cleared | Y | Y | Street gutter | Storm drainage system | Pacific Ocean | Y | N | N | N/A | ColSys crews responded and set Vactor to contain flow from entering strom drain.Postal Service contract plumber was a no show. Crews remained on site for 2 hours then turned off and lock water service until plumber corrected obstruction.
PL99003 | FAX | 14 Dec 00 1420 | A J Howard | 949.361.8253 | CSC | 2000-12-05 00:45 | 6 Dec 00 0830 | 200 | 200 | 115 West Mariposa | San Clemente | OR | 92672 | PRIVATE LATERAL | 0 | Unknown blockage in private lateral |  | Plumber cleared | Y | N | Street gutter | N/A | Vactor/Sanitary Sewer System | Y | N | N | N/A | Intermittent discharge from 6 apartments was contained at 2 locations 2/10ths mile downstream of 115 W Mariposa. ColSys crew responded with 2 Vactors to vaccum up estimated 200 gallons of sewage and 400 gallons of flush water to clean gutters. Crews remained on site with Vactor to collect sewage until 2nd contract plumber responded.
140370 | Fax 571-6972 | 10-02-00 14:00 | E. Semo | 6544160 | City of San Diego | 2000-10-01 22:15 | 10-02-00 9:30 | 337.5 | 0 | 3065 Eagle | San Diego | SD | 92103 | 8" CP | 1 | Roots | Root stop in main | Will TV to see what type of P.M. site to put it on. 8" cp | Y | Y | Storm drain at Eagle & 3000 block of Reynard | Dissipated into the storm drain system | N/A | Y | Y | N | N/A
140257 | Fax 571-6972 | 10-01-00 12:49 | D. Branco | 6544160 | City of San Diego | 2000-10-01 10:22 | 10-01-00 11:16 | 270 | 0 | 3815 Mt. Brundagie Ave | San Diego | SD | 92111 | 8" VC | 1 | Grease | Blockage caused by grease & some roots | Flushed main to relieve grease, 8" vc, Refer for accel. cleaning | Y | Y | Entered storm drain adjacent to M/H at 3800 block of Mt. Brundage Ave. | Soaked into adjacent canyon | Mission Bay/Pacific Ocean | Y | Y | N | N/A
140411 | Fax 571-6972 | 10-02-00 12:30 | R. Donahue | 6544160 | City of San Diego | 2000-10-02 08:48 | 10-02-00 10:10 | 246 | 246 | 2205 Camto Preciosa | San Diego | SD | 92037 | 8" VC | 1 | Roots | Previously treated roots broke loose & caused blockage @ M/H 244 | Will inspect MH on addtional 6 month cycle. 8" vc | Y | Y | Storm drain at Soledad Mtn. Rd. & Camto. Preciosa Norte | N/A | 100 gallon vactored from brow ditch, 146 gallons flowed to Int. I-8, returned to system | Y | Y | N | N/A
140876 | Fax 571-6972 | 10-04-00 2:45 | J. Wilder | 6544160 | City of San Diego | 2000-10-03 18:54 | 10-03-00 20:34 | 5000 | 4950 | 2454 Geranium St | San Diego | SD | 92109 | 8" VC Main | 1 | Roots | Roots & grease & broken screw in main caused blockage | Rod main, vacuum Recommend PM site. 8" vc main | Y | Y | Gutter in front of 2454 Geranium Street | Intercepted and put back into system at I-9 | N/A | Y | Y | N | N/A
141044 | Fax 571-6972 | 10-04-00 14:30 | R. Donahue | 6544160 | City of San Diego | 2000-10-04 13:15 | 10-04-00 14:15 | 2 | 2 | 6755 Draper Ave | San Diego | SD | 92037 | 5" Lined | 1 | Roots | Partial stoppage on 5" lined pipe caused approx. 2 gallons to surge out of private clean out | TV, eval tape, adjust p.m. schedule. 5" lined (Rick Donahue) | Y | N | Apron of driveway at 6755 Draper | N/A | Dried in apron of driveway/cleaned up | Y | Y | N | N/A
141775 | Fax 571-6972 | 10-07-00 13:03 | D. Branco | 6544160 | City of San Diego | 2000-10-07 09:23 | 10-07-00 10:45 | 820 | 0 | 5604 Albemarle | San Diego | SD | 92139 | 8" VC | 1 | Roots | Blockage caused by roots | Hi-lined hose & flused line to relieve stop. 8" vc | Y | N | Soaked into ground behind 5536 Albemarle | Sweetwater River/San Diego Bay | N/A | Y | Y | N | N/A
141772 | Fax 571-6972 | 10-07-00 17:04 | D. Branco | 6544160 | City of San Diego | 2000-10-07 08:44 | 10-07-00 10:00 | 25 | 0 | 3662 Rose Lawn St. | San Diego | SD | 92105 | 6" CP | 1 | Grease | Blockage caused by heavy grease, evidence of overflow prior to arrival, no overflow upon arrival | Flused line to releive stoppage. 6" cp | N | N | Soaked into ground behind 3662 Roselawn Ave. | N/A | Soaked into ground behind address | Y | N | N | N/A
141873 | Fax 571-6972 | 10-08-00 16:28 | D. Branco | 6544160 | City of San Diego | 2000-10-08 10:19 | 10-08-00 11:00 | 82 | 0 | 2934 Inglelow St. | San Diego | SD | 92107 | 8" PVC | 1 | Grease | Blocakge was caused by grease | Flushed ilne, refer for accel. cleaning. 8" pvc | Y | Y | Entered storm drain @ Scott St. & Ingelow St. & dissipated in pipe | San Diego Bay/Pacific Ocean | N/A | Y | Y | N | N/A
141875 | Fax 571-6972 | 10-10-00 12:05 | M. Bedard | 6544160 | City of San Diego | 2000-10-08 10:25 | 10-08-00 13:45 | 5000 | 4875 | 3810 Winona Ave | San Diego | SD | 92105 | 8" VC | 1 | Vandalism | Vandalism, found evidence of wood from construction cuttings of 2"x4" etc., wood used by crew currently working on remodeling of apt. complex at this location | Vactored, TV, add lock down materials 8" vc | Y | Y | Flowed into storm drain channel | Chollas Creek | Pacific Ocean | Y | Y | N | N/A
142488 | Fax 571-6972 | 10-11-00 18:45 | J. Wilder | 6544160 | City of San Diego | 2000-10-11 15:05 | 10-11-00 17:17 | 132 | 57 | 2045 Winnett St. | San Diego | SD | 92114 | 8" VC Main | 1 | Roots | Blockage caused by roots in main | Vac, Rod, Recommend area to be put on PM site. 8" vc | Y | Y | Chollas Creek | Dissipated in creek | N/A | Y | Y | N | N/A
142438 | Fax 571-6972 | 10-18-00 9:30 | M. Dawson | 6544160 | City of San Diego | 2000-10-11 08:52 | 10-11-00 14:30 | 6640 | 5360 | Adams Ave & I 15 | San Diego | SD | 92116 | 8" VC | 1 | Roots | Root blockage in 8" VC Main | Diverted sewage into system through manhole. 8" vc | Y | N | In canyon | Soaked into ground | Pacific Ocean | Y | Y | N | N/A
143290 | Fax 571-6972 | 10-15-00 16:18 | D. Branco | 6544160 | City of San Diego | 2000-10-15 12:27 | 10-15-00 13:12 | 23 | 0 | 4476 Ampudia St. | San Diego | SD | 92103 | 6" CP | 1 | Roots | Blockage caused by roots | Machine Rodded, refer for accel. maintenance. 6" cp | N | N | Soaked into ground around M/H behind address | N/A | Soaked into ground behind address | Y | Y | N | N/A
143679 | Fax 571-6972 | 10-17-00 23:17 | J. Wilder | 6544160 | City of San Diego | 2000-10-17 15:57 | 10-17-00 17:19 | 82 | 52 | 653 S. 42nd St. | San Diego | SD | 92113 | 8" VC Main | 1 | Grease | Grease accumulation restricted flow in main | Vactored, Rodded, Flused, recommend for PM site. 8" vc | Y | Y | Dried creek bed behind address | Soaked into ground | N/A | Y | Y | N | N/A
143604 | Fax 571-6972 | 10-23-00 11:30 | E. Matta | 6544160 | City of San Diego | 2000-10-17 08:51 | 10-17-00 09:57 | 40 | 40 | 6324 Lorca Dr. | San Diego | SD | 92115 | 6" CP | 1 | Roots | Root blockage on 6" easement main | Machine Rod. 6" cp | N | N | N/A | N/A | Vactor truck vacuumed spill | Y | N | N | N/A
143979 | Fax 571-6972 | 10-19-00 13:00 | J. Peay | 6544160 | City of San Diego | 2000-10-19 07:27 | 10-19-00 08:27 | 60 | 60 | 1741 60th St. | San Diego | SD | 92105 | 4" Lateral | 1 | Roots | Heavy roots between M/H 354 & 384 | Refer for 6 Month cleaning site. 8" vc | N | N | N/A | N/A | Vactored sewer spill | Y | Y | N | N/A
144416 | Fax 571-6972 | 10-21-00 15:45 | D. Branco | 6544160 | City of San Diego | 2000-10-21 11:46 | 10-21-00 12:37 | 1275 | 0 | Campanile Dr. & Murylane Drive | San Diego | SD | 92115 | 8" VC | 1 | Roots | Blocakge was caused by roots & rags | Machine Rodded, refer for scheduled maintenance. 8" vc | Y | Y | Entered storm drain at Baha Dr. & Campanile Dr. & dissipated in system prior to Montezuma @ Collwood | San Diego Bay/Pacific Ocean | N/A | Y | Y | N | N/A
144520 | Fax 571-6972 | 10-22-00 16:10 | D. Branco | 6544160 | City of San Diego | 2000-10-22 12:41 | 10-22-00 13:56 | 37 | 0 | 4460 Alamo Way | San Diego | SD | 92115 | 6" CP | 1 | Roots | Blockage was caused by roots | Machine Rod, refer for scheduled maintenance. 6" cp | N | N | Soaked into ground around M/H | N/A | Soaked into ground around M/H located behind address | Y | Y | N | N/A
144516 | Fax 571-6972 | 10-22-00 13:08 | D. Branco | 6544160 | City of San Diego | 2000-10-22 10:48 | 10-22-00 11:45 | 1710 | 1600 | 5014 Triana St. | San Diego | SD | 92117 | 10" VC | 1 | Vandalism | Manhole cover removed by vandals & filled with large rocks, wood, plant material & other misc. debris | Relieved stop w/ bar, contained OV with pump. 10" vc | Y | N | Retained in long trench beside M/H, crews pumped majority of overflow back into system | Tecolote Creek/Mission Bay | N/A | Y | Y | N | N/A
145138 | Fax 571-6972 | 10-25-00 13:30 | J. Peay | 6544160 | City of San Diego | 2000-10-25 10:50 | 10-25-00 11:10 | 100 | 0 | 5400 Hewlett Dr. | San Diego | SD | 92182 | 8" VC | 1 | Roots | Heavy roots between M/H 283 & 285 | Sewer will be put on a 3 Month cleaning site. 8" vc | N | N | N/A | N/A | Soaked in dirt 20' of M/H 283 | Y | Y | N | N/A
145162 | Fax 571-6972 | 10-27-00 15:00 | G. Richardson | 6544160 | City of San Diego | 2000-10-25 15:28 | 10-25-00 17:17 | 763 | 0 | 1783 Sunset Blvd. | San Diego | SD | 92103 | 8" VC | 1 | Construction | Contractor was cleaning mains using wayne ball, debris from cleaning collected on roots downstream & caused the overflow | Rodded main, TV & found roots / offset joint. 8" vc | N | N | Day creek behind address | N/A | Soaked into creek bed in canyon | Y | Y | N | N/A
145698 | Fax 571-6972 | 10-27-00 16:00 | L. Davis | 6544160 | City of San Diego | 2000-10-27 09:31 | 10-27-00 11:15 | 525 | 0 | 14455 Penasquitos Dr. | San Diego | SD | 92129 | 8" VC | 1 | Roots | Root blockage in main | Additional cleaning, refer for cleaning schedule. 8" vc | Y | Y | Grassy area on golf course absorbed most of spill | Storm drain on golf course | Canyon area W of I-15 & N of Carmel Mtn. Rd. | Y | Y | N | N/A
146045 | Fax 571-6972 | 10-28-00 17:42 | D. Branco | 6544160 | City of San Diego | 2000-10-28 13:51 | 10-28-00 14:20 | 20 | 0 | Brentwood Ave & Westonhill Dr. | San Diego | SD | 92126 | 8" VC | 1 | Other | No 7-32 or 7-33 upon arrival, rodded for city protection, nothing found in main to cause, stop evidence of slight 7-33 upon arrival | Rodded main, 8" vc | Y | N | Dried in street around M/H & at curb | Carroll Canyon/Pacific Ocean | N/A | Y | Y | N | N/A
146040 | Fax 571-6972 | 10-28-00 19:22 | D. Branco | 6544160 | City of San Diego | 2000-10-28 12:53 | 10-28-00 14:50 | 25 | 0 | 1625 Glencoe Dr. | San Diego | SD | 91945 | 8" VC | 1 | Roots | Overflow caused by flusher cleaning line, stop was caused by roots, no overflow until work began on line | Hand Rod, Flushed, Refer for scheduled maintenance. 8" vc | N | N | Soaked into ground around M/H | N/A | Soaked into ground around M/H | Y | Y | N | N/A
146110 | Fax 571-6972 | 10-29-00 17:12 | D. Branco | 6544160 | City of San Diego | 2000-10-29 14:35 | 10-29-00 15:40 | 650 | 0 | 65th & Shaules | San Diego | SD | 92114 | 8" VC | 2 | Roots | Blockage was caused by roots | Flushed, called for Rodder. 8" vc | Y | Y | Flowed down hill & entered storm drain @ 6145 Imperial Ave./dissipated in street/in storm drain | Chollas Creek/San Diego Bay | N/A | Y | Y | N | N/A
146461 | Fax 571-6972 | 11-3-00 10:58 | J. Wilder/J. Hernandez | 6544160 | City of San Diego | 2000-10-31 15:00 | 10-31-00 15:30 | 15 | 10 | Alley next to 1764 Bacon St. | San Diego | SD | 92107 | Ground | 1 | Construction | City contractor missed connection of lateral during project | Vactored, referred to resident engineer | Y | N | Formed a puddle on the street | N/A | S/W corner of Bacon St. & Narragansett St./vactored & deodorized | Y | Y | N | N/A
146791 | Fax 571-6972 | 11-01-00 19:32 | J. Wilder | 6544160 | City of San Diego | 2000-11-01 15:21 | 11-01-00 16:50 | 178 | 52 | 5018 Cervantes | San Diego | SD | 92113 | 8" VC | 1 | Grease | Grease blockage in main | Relieve grease stop, 8" VC main, Refer for periodic cleaning | Y | Y | N/A | N/A | Dissipated in storm channel N of YMCA Wy. | Y | Y | N | N/A
147448 | Fax 571-6972 | 11-04-00 13:28 | D. Branco | 6544160 | City of San Diego | 2000-11-04 09:12 | 11-04-00 09:45 | 33 | 0 | Ardath Ln & Azure Coast Dr. | San Diego | SD | 92037 | 8" VC | 1 | Roots | Blockage was caused by roots, M/H stopped overflowing & C/O @ 2440 Azure Coast Dr. began to overflow | Machine Rod 8" vc main, refer for Schd. Cleaning. | Y | Y | Entered storm drain @ Ardath Ln. & Azure Coast Dr./dissipated in system/on street, 7-31 C/O soaked into yard behind 2440 Azure Coast Dr. | Pacific Ocean | N/A | Y | Y | N | N/A
147646 | Fax 571-6972 | 11-06-00 14:45 | K. Vian | 6544160 | City of San Diego | 2000-11-06 07:00 | 11-06-00 13:14 | 1122 | 45 | 6970 Mission Gorge Rd. | San Diego | SD | 92120 | 15" VC | 1 | Grease | Grease build up in main | Flush 15" vc main, to remove stoppage. | Y | Y | Storm channel | Storm drain @ D.E Old Cliffs Rd. | Dried in storm drain/dirt drainage | Y | Y | N | N/A
147696 | Fax 571-6972 | 11-07-00 10:21 | J. Hernandez | 6544160 | City of San Diego | 2000-11-16 14:09 | 11-16-00 15:00 | 180 | 0 | 207 30th St. | San Diego | SD | 92102 | 6" VC | 1 | Grease | Heavy grease build up in 130 6" VC main, stopped normal sewer flow causing it to overflow out of M/H | 6" vc main, Flushed, cleaned & vactored | Y | Y | Street surface (alley) | Storm drain at S/E corner of 30th & K | Dissipated in storm drain | Y | Y | N | N/A
148226 | Fax 571-6972 | 12-06-00 9:00 | M. Bedard | 6544160 | City of San Diego | 2000-11-08 13:42 | 11-09-00 09:45 | 176.5 | 10 | 3005 Rogers | San Diego | SD | 92106 | 6" VC | 1 | Roots | Roots in 6" VC easement main | Clean, TV, and locate MH's | Y | N | Soaked into open construction | Trench @ 690 Rosecrans | Pacific Ocean | Y | Y | N | N/A
148397 | Fax 571-6972 | 11-09-00 01:05 | J. Wilder | 6544160 | City of San Diego | 2000-11-08 19:11 | 11-08-00 21:01 | 550 | 160 | Riverdale St. & Vandever | San Diego | SD | 92120 | 8" VC Main | 2 | Grease | Very heavy grease in main | Vactored, Rod 8" vc main, recommend adjust frequency of PM site. | Y | Y | San Diego River | Pacific Ocean | N/A | Y | Y | N | N/A
148186 | Fax 571-6972 | 11-08-00 12:06 | K. Vian | 6544160 | City of San Diego | 2000-11-08 07:44 | 11-08-00 08:48 | 320 | 0 | 8370 Capricorn Way | San Diego | SD | 92126 | 8" VC | 1 | Roots | Blockage caused by roots | Flush 8" vc main, removed roots & grease, will add to PM site. | Y | Y | Curb @ 8370 Capricorn Wy. | Storm drain 100 to 150' from M/H | Majority of SSO dried on street due to heavy vehicle traffic, remainder dried in storm drain | Y | Y | N | N/A
148209 | Fax 571-6972 | 11-08-00 13:57 | J. Hernandez | 6544160 | City of San Diego | 2000-11-08 09:58 | 11-08-00 10:30 | 160 | 0 | 3859 Z St. | San Diego | SD | 92113 | 8" VC | 1 | Grease | Upon arrival to clean main found stoppage, main surcharge caused overflow | Machine rodded 8" vc main to relieve stoppage refer to TV & FEWD. | Y | Y | Flood control channel at 3859 2 Street | Flood control at 3859 2 Street | Dissipated in channel | Y | Y | N | N/A
148792 | Fax 571-6972 | 11-12-00 10:07 | J. Oropeza | 6544160 | City of San Diego | 2000-11-11 17:07 | 11-11-00 23:15 | 11100 | 0 | 30th St. & Palm Ave. | San Diego | SD | 92104 | 8" VC | 2 | Vandalism | M/H 106 in canyon was vandalized, blocking 8" VC with firewood and rocks | 8" vc main, MH's in canyon refer to crew for straps & for PM sched. | Y | Y | Storm drain @ Pershing Dr. & 26th Street | Canyon area N of Balboa golf course | Dried in canyon N of Balboa golf course | N | Y | Y | 3
148935 | Fax 571-6972 | 12-06-00 9:00 | M. Bedard | 6544160 | City of San Diego | 2000-11-12 16:50 | 11-13-00 10:55 | 800 | 0 | 3300 Kellogg Wy | San Diego | SD | 92106 | 8" VC | 1 | Roots | Root stoppage/intrusion caused sewer main to break | Refer to Supervisor for TV main. 8" vc main | Y | Y | Storm drain San Berginto Wy. & Kellogg St. | San Diego Bay | San Diego Bay | Y | Y | Y | Unknown
149544 | Fax 571-6972 | 11-15-00 16:00 | M. Bedard | 6544160 | City of San Diego | 2000-11-13 10:48 | 11-15-00 11:04 | 227 | 0 | Hortensia & Whitman | San Diego | SD | 92103 | 8" PVC | 1 | Roots | Root blockage, called in 11-13-00, upon arrival no spill, 11-15-00 consumer called in spill, intermittent spill, could not contact consumer, 12 homes upstram of problem | Remove blockage 8" pvc main, create cleaning site. | Y | Y | Storm drain at location of spill | Soaked into ground at bottom of street on Whitman | N/A | Y | Y | N | N/A
150265 | Fax 571-6972 | 11-18-00 02:00 | R. Donahue | 6544160 | City of San Diego | 2000-11-17 22:24 | 11-17-00 23:30 | 1650 | 0 | 8308 Regents Rd. | San Diego | SD | 92122 | 10" PVC | 1 | Construction | Plastic sheeting, piece of PVC pipe & rocks from construction @ intersection caused stoppage on 10" PVC main | Rodded 10" pvc main,TV and investigate. Placed on PM | Y | Y | N/A | N/A | Entered storm drain at address, flowed aprox. 1 1/2 miles, dried in canyon by La Jolla Colony Dr. | Y | Y | N | N/A
150066 | Fax 571-6972 | 11-17-00 12:00 | J. Peay | 6544160 | City of San Diego | 2000-11-17 08:47 | 11-17-00 08:57 | 500 | 0 | 4501 54th St. | San Diego | SD | 92115 | 8" CP | 2 | Rocks | Heavy rocks & debris between M/H 354 & 327, 713 located 733, relieved stop, called into Station 38 | Refer 8" cp main over to TV crew | N | N | N/A | N/A | Storm drain @ 4570 54 St./soaked in creek bed in canyon @ 4570 54 St. | Y | Y | N | N/A
150367 | Fax 571-6972 | 11-19-00 17:05 | J. Oropeza | 6544160 | City of San Diego | 2000-11-19 13:41 | 11-19-00 14:48 | 67 | 45 | W Seaward Av & W Park Av | San Diego | SD | 92173 | 8" VC | Unknown | Grease | Blockage caused by grease | Refer to supervisor to add to PM site. 8" vc main | Y | N | Dirt St. @ 250 E Park Ave. | Dirt railroad tracks | Soaked @ (trolley) railroad tracks | Y | Y | N | N/A
150359 | Fax 571-6972 | 11-19-00 17:15 | J. Oropeza | 6544160 | City of San Diego | 2000-11-19 11:58 | 11-19-00 12:50 | 520 | 520 | W Knoll Dr & W Knoll Lane | San Diego | SD | 92109 | 8" VC | 1 | Roots | Blockage caused by roots | Refer 8" vc main to supervisor for PM | Y | Y | Storm drain @ S/W/C Vickie Dr. & Castle Hill | N/A | Intercepted @ Tourmaline/returned to system | Y | Y | N | N/A
150442 | Fax 571-6972 | 11-20-00 15:30 | R. Donahue | 6544160 | City of San Diego | 2000-11-20 10:30 | 10-20-00 13:11 | 5635 | 5555 | Flintkote Av & Estuary Wy | San Diego | SD | 92121 | 15" VC | 1 | Roots | Roots in M/H on 15" VC, SSO noticed by Mike Kelly, called to State Parks/County Health, County notified City | Cleaned roots from MH, will TV, 15" vc main. | Y | Y | N/A | N/A | Flowed in storm drain/contained by City w/berm/returned to system | Y | Y | N | N/A
150906 | Fax 571-6972 | 11-21-00 17:30 | R. Donahue | 6544160 | City of San Diego | 2000-11-21 13:46 | 11-21-00 13:56 | 100 | 0 | 7021 Draper Ave | San Diego | SD | 92037 | 8" VC | 1 | Construction | Asphalt from construction, replacing mains plugged 8" PVC, causing surcharge/discharge of sewage | Flushed by machine 8" pvc main, notify RE for install MH per book of standards | Y | N | N/A | N/A | Sewage flowed approx. 1000' down street & dried/crews cleaned | Y | Y | N | N/A
150845 | Fax 571-6972 | 11-21-00 10:45 | G. Richardson | 6544160 | City of San Diego | 2000-11-21 07:06 | 11-21-00 08:15 | 50 | 0 | 4033 South Hempstead Circle | San Diego | SD | 92116 | 6" CP | 1 | Roots | Roots & debris | Flushed 6" cp main, refer to TV. | Y | Y | Storm drain @ spill site | N/A | Dissipated in storm drain | Y | Y | N | N/A
151101 | Fax 571-6972 | 11-22-00 13:00 | R. Donahue | 6544160 | City of San Diego | 2000-11-22 07:06 | 11-22-00 10:45 | 7200 | 7000 | Camino Lindoo & Camino Noguera | San Diego | SD | 92122 | 8" VC | 1 | Roots | Large mass of roots in M/H 29 caused stoppage on 8" VC main, bermed front of storm drain w/dirt, pumped back into system | Machine rodded 8" vc main, cleaned, chemical herbicide | Y | Y | Rose Creek | N/A | Ponded in Canyon Creek/bermed/returned to system/200 gal. absorption ratio | Y | Y | Y | Unknown (still posted)
151174 | Fax 571-6972 | 11-22-00 23:00 | C. Mickelson | 6544160 | City of San Diego | 2000-11-22 16:24 | 11-22-00 18:50 | 5840 | 4200 | 175 69th St. | San Diego | SD | 92114 | 8" VC | 1 | Roots | Heavy roots growing into sewer main between M/H 95 & 83 | Cleaned 8" vc main MH83 to 95 and 85 to 93 w/full blade. | Y | Y | Gutter in front of 175 69th St. | Storm drain inlet @ SE corner Sychar & 69th St. | Ponded in storm culvert on E side of 68th St., S of Jamacha Rd. | Y | Y | N | N/A
151491 | Fax 571-6972 | 11-25-00 14:59 | D. Branco | 6544160 | City of San Diego | 2000-11-25 09:10 | 11-25-00 09:30 | 100 | 50 | 1552 Tarbox | San Diego | SD | 92114 | 8" VC | 1 | Other | Unknown, stopped itself, unit rodding for City protection, removed some grease, poss. cause | Flushed 8" vc main, vactoredsewage & cleaned | N | N | Dried in street @ Hilger St. & Madera | N/A | Dried in street | Y | N/A | N | N/A
151559 | Fax 571-6972 | 11-26-00 11:37 | D. Branco | 6544160 | City of San Diego | 2000-11-26 10:18 | 11-26-00 10:45 | 20 | 0 | 5520 Fontaine St. | San Diego | SD | 92120 | 8" VC | 1 | Grease | Heavy grease | Rodded 8" vc main, refer for scheduled maintenance | N | N | Dried @ 5520 Fontaine Street | N/A | Dried in street | Y | N/A | N | N/A
151643 | Fax 571-6972 | 11-28-00 11:00 | G. Richardson | 6544160 | City of San Diego | 2000-11-27 14:54 | 11-27-00 17:00 | 1890 | 1000 | Cumburland & Morningside | San Diego | SD | 92139 | 8" VL | 1 | Grease | Grease in sewer main between M/H 581 & 70 | Rodded 8" vc main | Y | Y | Storm drain @ spill site | N/A | Dissipated in storm drain | Y | Y | N | N/A
151851 | Fax 571-6972 | 11-28-00 11:00 | K. Vian | 6544160 | City of San Diego | 2000-11-28 07:32 | 11-28-00 09:42 | 260 | 50 | 13106 Avnda Del General | San Diego | SD | 92128 | 8" VC | 1 | Roots | Roots in M/H | 8" vc main, Inspect MH's refer for TV.. | Y | Y | Curb @ 13106 Avenida Del General | Storm drain @ Calle De Los Ninos & Avenida Del General | Majority of SSO dried in gutter/balance dried in storm drain | Y | Y | N | N/A
151850 | Fax 571-6972 | 11-28-00 10:35 | D. Lelroy | 6544160 | City of San Diego | 2000-11-28 07:19 | 11-28-00 08:22 | 315 | 150 | 1622 Blaine St. | San Diego | SD | 92103 | 6" VC Main | 2 | Roots | Root intrusion held back debi (toilet paper,napkins,etc.) causing backup and eventually overflow | Rodded 6" vc main, vactored, cleaned & deoderized. | Y | Y | Street surface @ 1622 Blaine St. | Storm drain @ 3909 Centre St. | Dissipated into storm drain | Y | Y | N | N/A
152683 | Fax 571-6972 | 11-30-00 01:20 | J. Wilder | 6544160 | City of San Diego | 2000-11-29 21:43 | 11-29-00 22:26 | 86 | 24 | 2094 Laurinda Place | San Diego | SD | 92105 | 8" VC | 1 | Roots | Roots in main | Vacuum overflow, Rod 8" vc main, clean & deoderize. | Y | Y | Storm drain @ 2094 Laurinda Place | Soaked into dry creek bed | N/A | Y | Y | N | N/A
153201 | Fax 571-6972 | 12-01-00 19:56 | D. Branco | 6544160 | City of San Diego | 2000-12-01 19:25 | 12-01-00 19:26 | 50 | 0 | 6491 Bishop Dr. | San Diego | SD | 92114 | 8" VC | 1 | Roots | Rodding machine relieved stopped line downstream, M/H overflowed, stop was originally between M/H 210 & 280 | Relieved root stop btwn MH's 210&280. 8" VC Refer to Sup. for Schd Maint. | Y | Y | Entered storm drain @ 65th & Skyline/dissipated in system | Sweetwater River/San Diego Bay | N/A | Y | Y | N | N/A
153126 | Fax 571-6972 | 12-01-00 11:30 | D. Steele | 6544160 | City of San Diego | 2000-12-01 09:40 | 12-01-00 10:25 | 450 | 0 | 4321 53RD ST. | San Diego | SD | 92115 | 6" VC | 1 | Roots | Stoppage of roots on 6" VC main | Clean two 6" VC sections up and two sections down, TV main, Adj. Freq Clean | N | Y | Curb @ 4321 53rd Street | Storm drain @ 52nd & Trojan | Dried in storm drain | Y | Y | N | N/A
153451 | Fax 571-6972 | 12-02-00 15:35 | D. Branco | 6544160 | City of San Diego | 2000-12-02 12:16 | 12-02-00 12:57 | 410 | 0 | Cartagena Dr. & Tarragona Dr. | San Diego | SD | 92115 | 6" VC | 1 | Roots | Blockage caused by roots | Machine Rodded to relieve stop, refer to area Supervisor. 6" VC | Y | Y | Entered storm drain @ Cartagena & University/dissipated in system | Chollas Creek/San Diego Bay | N/A | Y | Y | N | N/A
153428 | Fax 571-6972 | 12-02-00 11:02 | D. Branco | 6544160 | City of San Diego | 2000-12-02 08:25 | 12-02-00 09:04 | 20 | 0 | 4067 Adams Ave. | San Diego | SD | 92116 | 8" VC | 2 | Grease | Blockage caused by heavy grease | Flushed line to relieve stop, Refer to area Supervisor for Accl. Cleaning. 8" VC | Y | Y | Entered storm drain on 4600 block of Terrace Dr. about 50' S of Adams/dissipated in system | San Diego River/Pacific Ocean | N/A | Y | Y | N | N/A
153507 | Fax 571-6972 | 12-03-00 14:12 | D. Branco | 6544160 | City of San Diego | 2000-12-03 10:31 | 12-03-00 12:10 | 495 | 0 | 3920 Thorn St. | San Diego | SD | 92105 | 8" PVC | 1 | Grease | Blockage caused by heavy grease | Flushed line to relieve stop refer to area supervisor for schd. maint. 8" PVC | Y | Y | Entered storm drain behind 3920/flowed up 39th/dissipated in system | San Diego Bay/Pacific Ocean | N/A | Y | Y | N | N/A
153604 | Fax 571-6972 | 12-04-00 13:41 | E. Swanson | 6544160 | City of San Diego | 2000-12-04 11:26 | 12-04-00 12:05 | 19.5 | 0 | Goldfinch St. & Goldfinch Place | San Diego | SD | 92103 | 6" VC | 1 | Grease | Grease buildup in 6" VC Main caused sewer to back up & overflow | Rod & Vactor, referred to TV and FEWD. 6" VC. | Y | Y | Storm drain located @ Goldfinch Place & Goldfinch Street | Dissipated into storm drain @ Goldfinch Place & Goldfinch Street | N/A | Y | Y | N | N/A
154078 | Fax 571-6972 | 12-05-00 23:48 | J. Wilder | 6544160 | City of San Diego | 2000-12-05 15:28 | 12-05-00 22:05 | 198.5 | 70 (estimated) | 6460 El Cajon Blvd. | San Diego | SD | 92115 | 8" VC Main | 1 | Roots | Roots in main caused stop | Vacuum overflow, Rod/Clean main Recommend put on PM site. 8" VC | N | N | N/A | N/A | Contained in yard around & under trailer behind church | Y | Y | N | N/A
154289 | Fax 571-6972 | 12-20-00 11:00 | K. Vian | 6544160 | City of San Diego | 2000-12-06 15:43 | 12-06-00 16:01 | 50 | 0 | 10776 Scripps Ranch Blvd. | San Diego | SD | 92131 | 8" PVC | 1 | Construction | Contractor clearing lot for new business park, hit sewer main when looking for water service, causing breakage | 8" PVC, Flush, remove debri, repair broken main. | N | N | N/A | N/A | Soaked into ground around M/H | Y | Y | N | N/A
155176 | Fax 571-6972 | 12-09-00 16:31 | D. Branco | 6544160 | City of San Diego | 2000-12-09 13:24 | 12-09-00 16:09 | 82 | 0 | 4399 10th Ave. | San Diego | SD | 92103 | 6" VC | 1 | Roots | Blockage caused by heavy roots | Machine Rod, Refer to area supervisor for Sched. maint. 6" VC | N | Y | Entered storm drain next to M/H, flowed into canyon adjacent to Hwy 163/soaked into ground | San Diego Bay/Pacific Ocean | N/A | Y | N/A | N | N/A
155211 | Fax 571-6972 | 12-11-00 10:23 | D. Branco | 6544160 | City of San Diego | 2000-12-11 07:31 | 12-11-00 08:33 | 930 | 0 | 2490 Hopkins St. | San Diego | SD | 92139 | 8" VC | 1 | Roots | Blockage caused by roots | Flushed line, Cleaned heavy roots from MH 45. 8" VC | Y | Y | Entered storm drain in 2200 block of Rachael Ave/dissipated in canyon area adjacent to drain entrance in Nat'l City | Sweetwater River/San Diego Bay | N/A | Y | Y | N | N/A
155314 | Fax 571-6972 | 12-11-00 15:00 | G. Richardson | 6544160 | City of San Diego | 2000-12-11 10:48 | 12-11-00 13:00 | 150 | 100 | 5199 University Ave. | San Diego | SD | 92105 | 6" VC | 1 | Roots | Overflow caused by roots in main | Rodded 6" VC main and vactored. | Y | N | Vacant lot at spill site | N/A | Recovered 100 gal. by vactor/remaining soaked into the ground | Y | Y | N | N/A
155341 | Fax 571-6972 | 12-11-00 18:39 | J. Wilder | 6544160 | City of San Diego | 2000-12-11 14:37 | 12-11-00 17:12 | 20 | 0 | 3733 Elliot St. | San Diego | SD | 92106 | 6" CP Main | 1 | Roots | Main stoppage caused by roots & grease | Flushed 6" CP main, notified consumer, refer 2 sections up & down cleaning.PM | N | N | N/A | N/A | Contained on private property @ 3733 Elliott Street | Y | Y | N | N/A
155361 | Fax 571-6972 | 12-12-00 11:30 | G. Neel | 2218728 | City of San Diego | 2000-12-11 17:30 | 12-11-00 20:36 | 4650 | 375 | 5861 Desert View Dr. | San Diego | SD | 92037 | 8" VC Main | 1 | Roots | Stoppage caused by roots in main | Rod main, vacuum overflow. 8" VC | Y | Y | Soaked into canyon floor | N/A | Interceptor #1 @ Damon Ave. | Y | Y | N | N/A
155588 | Fax 571-6972 | 12-12-00 09:00 | G. Neel | 6544160 | City of San Diego | 2000-12-12 06:28 | 12-12-00 07:55 | 609 | 0 | 2370 Cardinal Dr. | San Diego | SD | 92123 | 8" VC Main | 1 | Roots | Blockage caused by roots | Flushed 8" VC main, put on area PM site. | Y | Y | Entered storm drain @ 2350 Cardinal Dr. | Flowed into Murray Canyon, soaked into ground | San Diego River/Pacific Ocean | N/A | Y | Y | N/A
155904 | Fax 571-6972 | 12-19-00 08:30 | G. Richardson | 6544160 | City of San Diego | 2000-12-13 13:12 | 12-13-00 14:19 | 5 | 0 | 63rd & El Cajon Blvd | San Diego | SD | 92115 | 6" VC | 1 | Grvty Break | Broken sewer main | Rodded/ Flushed 6" VC main, Televised, referred to construction. | Y | N | Street around M/H | N/A | Dried up on the street | Y | Y | N | N/A
156172 | Fax 571-6972 | 12-15-00 10:17 | E. Swanson | 6544160 | City of San Diego | 2000-12-14 12:48 | 12-14-00 15:00 | 500 | 0 | 4460 Teralta Place | San Diego | SD | 92103 | 6" CP | 1 | Roots | Roots in main | Rodded 6" CP main | Y | N | Canyon @ spill site | N/A | Soaked into ground | Y | Y | N | N/A
156464 | Fax 571-6972 | 12-15-00 19:38 | D. Branco | 6544160 | City of San Diego | 2000-12-15 14:54 | 12-15-00 16:35 | 505 | 450 | Dove & West Maple St. | San Diego | SD | 92101 | 8" CP | 1 | Grvty Break | Collapsed main, construction in area, storm drains sandbagged, break possibly caused by previous work | 8" CP main, Vactored, called for construction crew to repair break. | Y | Y | Flowed to storm drain @ W Maple St. & Reynard Wy./was contained by sandbags due to earlier construction | San Diego Bay/Pacific Ocean | N/A | Y | Y | N | N/A
156640 | Fax 571-6972 | 12-16-00 15:07 | D. Branco | 6544160 | City of San Diego | 2000-12-16 12:42 | 12-16-00 13:58 | 38 | 0 | 4589 Contour Blvd | San Diego | SD | 92115 | 6" CP | 1 | Roots | Blockage caused by roots | 6" CP main, Machine rodded, refer to area supervisor for sched. maint. | Y | Y | Out of ground @ 52nd & Contour Blvd./dried in street/some reached storm drain/some dissipated in system | Chollas Creek/San Diego Bay | N/A | Y | Y | N | N/A
156798 | Fax 571-6972 | 01-04-01 13:25 | E. Swanson | 6544160 | City of San Diego | 2000-12-18 11:06 | 12-18-00 12:45 | 940 | 0 | Bernice Dr. & Catalina Blvd. | San Diego | SD | 92107 | 8" PVC | 1 | Construction | City of San Diego contractor hit water main while excavating lateral water main/water filled trench/went into lateral pipe/dirt went down sewer main/blocked flow/sewer & water main came out of 4" clean outs | 8" PVC | N | Y | Entered storm drain by M/H/soaked into ground | San Diego Bay/Pacific Ocean | N/A | Y | Y | N | N/A
157424 | Fax 571-6972 | 12-21-00 12:44 | E. Swanson | 6544160 | City of San Diego | 2000-12-21 08:30 | 12-21-00 10:40 | 650 | 0 | 1892 33rd St. | San Diego | SD | 92104 | 6" VC | 1 | Roots | Roots in main | 6" VC main, Rod and refer to Root Foam | Y | N | Canyon @ spill site | N/A | Soaked into ground | Y | Y | N | N/A
157646 | Fax 571-6972 | 12-22-00 23:20 | D. Branco | 6544160 | City of San Diego | 2000-12-22 19:00 | 12-22-00 19:45 | 8030 | 0 | Bernardo Cntr Dr. & Bernardo Hghts Pkwy | San Diego | SD | 92113 | 6" VC | 1 | Rocks | Blockage caused by grease | ES unit located overflow, refer to Flusher and area supervisor. 8" PVC | N | N | Dried in street in front of address | N/A | Dried in street | Y | N/A | N/A | N/A
157690 | Fax 571-6972 | 12-23-00 15:31 | D. Branco | 6544160 | City of San Diego | 2000-12-22 09:04 | 12-23-00 11:50 | 20 | 0 | 2821 Clay Ave. | San Diego | SD | 92128 | 8" PVC | 1 | Grease | Blockage caused by rocks & broken PVC pipe | Flushed line, refer to area supervisor for sched. maint. 6" VC | Y | Y | Flowed down Bernardo Center Dr. & Rancho Bernardo Rd. to Pomerado & dissipated in system | San Diego Penasquitos Creek/Pacific Ocean | N/A | Y | Y | N | N/A
157792 | Fax 571-6972 | 12-23-00 14:51 | D. Branco | 6544160 | City of San Diego | 2000-12-23 09:54 | 12-23-00 10:22 | 1400 | 500 | 4523 Bancroft | San Diego | SD | 92116 | 8" VC | 1 | Grease | Blockage caused by heavy grease | Machine rod, refer to area super for sched. maint. 8" VC main | Y | Y | Entered storm drain @ 4411 Bancroft St./dissipated in system | Chollas Creek/San Diego Bay | N/A | Y | Y | N | N/A
157835 | Fax 571-6972 | 12-24-00 14:40 | D. Branco | 6544160 | City of San Diego | 2000-12-24 10:27 | 12-24-00 11:35 | 680 | 0 | Beaver Lake Dr. & Beaver Lake Ct. | San Diego | SD | 92119 | 8" VC | 1 | Grease | Blockage caused by grease | Flushed, refer to area supervisor. 8" VC | Y | Y | Entered storm drain @ Beaver Lake Dr. & Beaver Lake Ct./dissipated in system | San Diego River/Pacific Ocean | N/A | Y | Y | N | N/A
157840 | Fax 571-6972 | 12-24-00 14:47 | D. Branco | 6544160 | City of San Diego | 2000-12-24 11:53 | 12-24-00 13:10 | 385 | 0 | 4134 Cam. Tacino | San Diego | SD | 92122 | 8" VC | 1 | Grease | Blockage caused by grease | Flushed, refer to area supervisor. 8" VC | Y | Y | Entered storm drain @ Cam. Ticino & Cam. Lita/dissipated in system | Rose Creek/Mission Bay | N/A | Y | Y | N | N/A
157831 | Fax 571-6972 | 12-24-00 18:21 | D. Branco | 6544160 | City of San Diego | 2000-12-24 10:37 | 12-24-00 11:19 | 21 | 0 | 3707 Columbia St. | San Diego | SD | 92103 | 6" CP | 1 | Roots | Blockage caused by roots | Machine rodded, refer to area supervisor. 6" CP main | Y | Y | Entered storm drain on Winder & India/dissipated in system | San Diego Bay/Pacific Ocean | N/A | Y | Y | N | N/A
157935 | Fax 571-6972 | 12-26-00 23:45 | C. Mickelson | 6544160 | City of San Diego | 2000-12-26 16:58 | 12-26-00 19:27 | 5 | 0 | 1634 Crespo | San Diego | SD | 92037 | 6" VC | 1 | Roots | Root blockage on city sewer main M/H 53 to 54 | Rodded main, referred to area super for sched. maint. 6" VC | Y | N | Dried on street | N/A | N/A | Y | Y | N | N/A
158075 | Fax 571-6972 | 12-27-00 23:56 | C. Mickelson | 6544160 | City of San Diego | 2000-12-27 18:03 | 12-27-00 20:28 | 4350 | 4000 | 2580 46th St. | San Diego | SD | 92105 | 8" VC | 1 | Grease | Grease & roots causing blockage in sewer main | Refer for maintenance cleaning, more frequent. 8" VC | Y | Y | Entered storm drain in backyard @ 2580 46th St. | Dissipated in storm channel @ Federal Ave. W of Home Ave. | N/A | Y | Y | N | N/A
158233 | Fax 571-6972 | 12-29-00 10:00 | G. Richardson | 6544160 | City of San Diego | 2000-12-28 14:50 | 12-28-00 17:40 | 8500 | 7000 | 7673 Woodbine Way | San Diego | SD | 92114 | 8" VC | 1 | Vandalism | Vandals dropped rocks in the M/H | Set-up Bypass pumping, refer to Constr. 8" VC | Y | Y | Dry creek bed @ spill site | N/A | Dried up in creek bed | Y | Y | N | N/A
158829 | Fax 571-6972 | 12-30-00 19:08 | D. Branco | 6544160 | City of San Diego | 2000-12-30 14:32 | 12-30-00 15:25 | 10 | 0 | 1819 Bancroft St. | San Diego | SD | 92104 | 6" CP | 2 | Roots | Blockage caused by roots | Machine Rod, refer to area supervisor. 6" CP | N | N | Seepage around M/H behind address/soaked into ground | N/A | Soaked into ground around M/H | Y | N/A | N/A | N/A
158846 | Fax 571-6972 | 12-31-00 14:52 | D. Branco | 6544160 | City of San Diego | 2000-12-31 10:48 | 12-31-00 11:55 | 335 | 30 | 4202 National Ave. | San Diego | SD | 92113 | 8" VC | 1 | Grease | Blockage caused by grease | Flushed line, vactored, refer to area supervisor. 8" VC | Y | Y | Dried in cement storm drain channel in 4000 block of National Ave. | San Diego Bay/Pacific Ocean | N/A | Y | Y | N | N/A
158857 | Fax 571-6972 | 12-31-00 17:54 | D. Branco | 6544160 | City of San Diego | 2000-12-31 16:12 | 12-31-00 17:03 | 1275 | 0 | 15900 Camino Del Norte | San Diego | SD | 92128 | 8" PVC | 1 | Construction | Blockage caused by grease & sludge trapped behind a cleanout cover, which traveled down the line, trapped in M/H 72 | Flushed line, refer to area supervisor. 8" PVC | Y | Y | Entered storm drain at Cam. Del Norte & Paseo Lucido/dissipated in system in Poway | Los Penasquitos Canyon Creek/Pacific Ocean | N/A | Y | Y | N | N/A
158859 | Fax 571-6972 | 12-31-00 19:20 | D. Branco | 6544160 | City of San Diego | 2000-12-31 17:24 | 12-31-00 18:45 | 81 | 0 | S Euclid Ave. & Holly St. | San Diego | SD | 92113 | 8" VC | 1 | Grease | Blockage caused by grease | Flushed line, refer to area supervisor. 8" VC | N | N | Soaked into dirt lot @ 5011 Holly St. | N/A | Soaked into dirt lot | Y | N/A | N | N/A
001001 | RWQB - Rebecca Steward; Co. Health - voice mail; | 2000-10-23 11:10 | Jim Guzman | (760)726-1340, ext-1665 | City of Vista | 2000-10-23 11:23 | 2000-10-23 11:30 | 50 | 50 | 1959 Yetteford | Vista | SD | 92083 | B13/ SMH #186; AP 183-131 | 1 | Roots | Roots blockage from private lateral attached from 1959 Yetterford. Location verified by CCTV inspection. Owner was notified at time of last blockage and CCTV verification to clean lateral. | Root cut with chain-flail, Root-X foam, and notify resident to clean lateral again. | N | N | None | None | 100 yards along the curb and gutter, then to the Vacuum truck; 100% recovered. | Y | N/A | N | 0 | Private spill from cleanout
001002 | Co. Health - voice mail; | 2000-11-02 11:10 | UPS driver |  | City of Vista | 2000-11-02 11:10 | 2000-11-02 11:10 | 100 | 0 | 1925 W. Vista Way | Vista | SD | 92083 | Private sewer cleanout | 1 | Blockage | Unknown | Notified tenant at spill location to call plumber immediatelly; Reported to Co. Health. | N | N | None | None | Iceplant | Y | N/A | N | 0 | Private spill from cleanout
001003 | S.D. County Health -Clay Clifton, L.M./ RWQB - Rebecca Stewart, L.M. | 2000-11-06 07:45 | Jim Guzman | (760)726-1340, ext-1665 | City of Vista | 2000-11-04 08:00 | 11/04/2000 1600 | 10000 | 2400 | 881 Softwind d. | Vista | SD | 92083 | Private sewer manhole | 3 | Roots | Roots in sewer manhole created blockage; manhole located within the Bree Hill Apartments; Manhole channel was full of roots -- ladder was cover by roots; | Because this was a private sewer line, the City of Vista Vactor was setup out in the public right of way at storm drain location to help minimize Buena Vista Creek contamination; On-site Assistant Manager and Maintenece Manager were notified to call a jetter ASAP due to prop. 65 & 96-04; Their contractor was late (3:30 pm); I told them (& Todd), Co. HazMat to call someone else; They did but cancelled twice; Street Dep't supervisor/ Storm Water program coordinator was on site to field inspect for water contamination; no samples of the creek water were taken -- storm water prevention technician does not respond on weekends. | Y | Y | None | Buena Vista Creek | N/A | Y | Yes -(Control #005163) | Y |  | PRIVATE SPILL FROM MANHLE; Breeze Hill Apt. Manager didn't respond properly to the incident, causing serious and possibly major enviromentsal damage to the creek area; As of 11/06/2000, signs were still up;
001004 | S.D. County Health, RWQB | 2000-11-16 16:15 | Judy Miller | (760)726-1340, ext-1665 | City of Vista | 2000-11-16 15:00 | 2000-11-16 15:30 | 750 | 750 | Intersection of Escondido Ave. and So. Santa Fe Ave. | Vista | SD | 92083 | V24/ SMH #52A | 1 | Grease | Grease in manhole caused blockage and overflow. | Two Vactors responded; one vactor was stationed near the storm drain to vacuum spilled sewege, the other near the manhole to clear the blockage; staff returned to site to chain flail all connecting sewer lines up and downstream of the incident. | N | N | None | None | Vacuum prior to entering the storm drain. | Y | N/A | N | 0 | Several restaurants and grocery stores are located upstream of the manhole were the blockage occurred; Grease traps inspections may be needed; because these are private properties, we may need assistance from the S. D. County Health.
001005 | S.D. County Health, RWQB | 2000-11-22 16:53 | George Solano | (760)726-1340, ext-1662 | City of Vista | 2000-11-22 15:15 | 2000-11-22 15:45 | 330 | 200 | Intersection of No. Citrus and Orange Ave. | Vista | SD | 92084 | V05/ SMH #59, AP 163-271 | 1 | Roots | Roots in sewer main created blockage | Two Vactors responded; one vactor was stationed downstream near the storm drain to vacuum spilled sewege, the other near the manhole to clear the blockage; recover overflowing sewage, and wash out surface; no surface contamination. | N | Y | None | None | Storm Drain, then recovered by Vactor | Y | N/A | N | 0 | Overflow sewage did not leave storm drain system; overflow did not reach Creek area; residual sewage within the storm drain system was washed cleaned and vacuumed.
001006 | S.D. County Health -Clay Cliffrod, L.M./ RWQB - Rebecca Steward, L.M. | 2000-11-28 08:00 | Jim Guzman | (760)726-1340, ext-1665 | City of Vista | 2000-11-27 10:00 | 2000-11-27 10:30 | 50 | 0 | 1106 Vista Bonita Dr. | Vista | SD | 92083 | V26/ SMH #223 | 1 | Roots, Grease | Roots and grease in sewer main created blockage; Poor easement access during last rain fall, prevented routine maintenace on schedule. | Cleared blockage, chain flailed line, and CCTV inspected the sewer line for condition; Returned on 11/28/2000 with mechanical rodder to perform more extensive root cutting; | N | N | None | None | Low volume spill; sewage was absorved by ground | Y | N/A | N | 0 | None
001007 | S.D. County Health -Clay Cliffrod, L.M./ RWQB - Rebecca Steward, L.M. | 2000-11-28 08:00 | Jim Guzman | (760)726-1340, ext-1665 | City of Vista | 2000-11-27 16:30 | 2000-11-27 18:00 | 5 | 3 | 1212 Olive Ave. | Vista | SD | 92083 | V03/ SMH #35 | 1 | Roots, Grease | Roots and grease in sewer main created blockage; Poor access due to current construction activity of the Street widening and sewer line recostruction project. | Clear blockage, chain flail main line. A new sewer amin has been installed, and the lateral tie-ins should be completed within a month. Vacuum puddle, and washed down area. | N | N | None | None | Sewage ponded in front yard of private property. | Y | N/A | N | 0 | Line replacement should be completed within two months.
001008 | S.D. County Health -C Cliffrod, L.M./ RWQB - V. Vasquez, L.M. | 2000-12-06 07:30 | Jim Guzman | (760)726-1340, ext-1665 | City of Vista | 2000-12-06 07:00 | 2000-12-06 07:15 | 3000 | 500 | 304 N. Melrose Dr. | Vista | SD | 92083 | V05/ SMH #59, AP 163-271 | 1 | Roots | Roots in sewer main created blockage | Broke blockage ASAP. Second Vactor at catch basin for storm drain. Chain Flied main twice. Sewer amin CCTV today. | Y | Y | Buena Vista Creek | None | N/A | Y | Yes -(Control #00-5746) Danielle | Y | 6 | Posted signs from N. Melrose Dr. to Emerald Dr.
001009 | S.D. County Health | 2000-12-18 12:08 | David Brookbank | (760)726-1340, ext-1663 | City of Vista | 2000-12-18 12:08 | 2000-12-18 13:10 | 1160 | 700 | 243 Pala Vista Dr. | Vista | SD | 92083 | Private sewer cleanout | 1 | Unknown | Unknown | Notify Manager of their responsibility; City's storm water technician issued a warning. | Y | Y | storm drain system | Buena Vista Creek | N/A | Y | N/A | Y | 1 | PRIVATE SPILL --- 3 signs were posted at the end of covered strom drains, approx. 1.2 miles from spill.
1001 | Victor Vasquez | 2000-11-06 08:30 | Anne Briggs | (909) 928-3777 | E.M.W.D. | 2000-11-06 06:55 | 2000-11-06 12:00 | 60000 | 54000 | Intersection Solana/Ynez | Temecula | RV | 92590 | Manhole | 0 | Blockage | Manhole backed up because of sand blockage | Removed sand. Asked the local newspaper to report the incident and ask anyone with information on the origin of the sand to repot it to Eastern. The District is developing agreements with neighboring communities regarding traffic control and strom drain mapping information. | Y | Y | Tributar to Murrieta Creek | Murrieta Creek | N | Y |  | Y | y
1002 | Jim Gillis | 2000-11-17 13:30 | Anne Briggs | (909) 928-3777 | E.M.W.D. | 2000-11-17 09:30 | 2000-11-17 12:30 | 1800 | 1800 | Rancho CA Road | Temecula | RV | 92510 | Private Manhole | 0 | Line Break | Contractor crushed EMWD owned lateral serving private system and caused overflow | EMWD blocked storm drain while private pumper pumped down manhole. Contractor repaired lateral. | N | Y | Thomas Guide page 958 H-6 |  |  |  | Y | Y | Y
1003 | Roger Workkman | 2000-11-18 | Anne Briggs | (909) 928-3777 | E.M.W.D. | 2000-11-17 10:00 | 2000-11-18 14:10 | 5000 | 0 | Wolf Valley Road, Rancho CA | Temecula | RV | 92590 | Manhole #00307 | 0 | Blockage | Manhole was restricted and blocked by a 5 gallon can covered in asphalt | Line pumped down and Vactor Truck was used to clear blockage down stream. One manhole drained and rock grabbers were used to remove debris. Will add site to inspection route. Will weld lids to prevetn vandalism. | N | N |  |  | N | Y | Y |  | Y
OOO109 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2000-10-07 17:15 | 2000-10-07 17:25 | 10 | 0 | 1147 Gearald Way | Fallbrook | SD | 92028 | Cleanout | 1 | Roots | Hair line root. | 4" cleanout plugged with roots 25' down. | N | N | NA | NA | Soaked into ground. | N | N | N | NA
OOO110 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2000-10-07 22:45 | 2000-10-07 23:15 | 20 | 0 | 140 1/2 E. View | Fallbrook | SD | 92028 | Cleanout | 1 | Roots | Hair line root. | 4" cleanout plugged with roots 25' down. | N | N | NA | NA | Evaporated down driveway. | N | N | N | NA | Sprayed disinfectant around box and driveway.
OOO111 | 858-571-6972 | 2000-10-12 11:45 | Patti S. Page | (760)723-5640 | Fallbrook Public Utility District | 2000-10-11 15:30 | 2000-10-11 16:10 | 70 | 20 | 450 Ammunition Road | Fallbrook | SD | 92028 | Cleanout | 1 | Grease | Grease in sewer lateral. | Rodded lateral with 2" cutter then 6" cutter. Blocked off storm drain. | N | Y | Fallbrook Creek | Lake O'Neil | Entered storm drain culvert. | Y | N | N | NA | Blocked up downstream culvert, flushed, and vacuumed storm drain. None of overflow actually reached the creek due to plug in storm drain culvert.
OOO112 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2000-10-11 16:15 | 2000-10-11 17:00 | 0 | 0 | 1079 S. Mission Road | Fallbrook | SD | 92028 | Cleanout | 1 | Grease | Cleanout overflow from grease and roots in manhole. Unknown overflow volume because it had already dried up. | Cleaned up grease and roots along side of road. Sewer had already opened itself up before we arrived. | N | N | NA | NA | Dried up around cleanout & along street. | N | N | N | NA | Noticed a strong odor. Stopped and noticed grease from the cleanout that had overflowed, but had already opened itself up. Cleaned up grease and dirt.. Flushed mainline to maked sure it was clear. | District reported "? Already Dried" in Total Overflow Volume field
OOO113 | 858-571-6972 | 2000-10-16 08:50 | Patti S. Page | (760)723-5640 | Fallbrook Public Utility District | 2000-10-14 13:30 | 2000-10-14 14:00 | 50 | 30 | Shady Lane Lift Station | Fallbrook | SD | 92028 | Lift Station | 1 | Pump Station Failure | Air compressor went out on bubbler system. | Replaced compressor. Completed 10/14/00. | N | N | NA | NA | Dried up on ground around lift station. | Y | N | Y | 3 | Removed contaminated soil.
OOO114 | 619-338-2848 | 2000-10-23 09:40 | Patti S. Page | (760)723-5640 | Fallbrook Public Utility District | 2000-10-21 21:30 | 2000-10-21 22:00 | 400 | 250 | Shady Lane Lift Station | Fallbrook | SD | 92028 | Lift Station | 2 | Pump Station Failure | Mercury switch failed. | Put pump on "hand", and pumped down. | N | N | NA | NA | Dried up on ground around lift station & open field. | N | N | Y | 3 | Diverted overflow and vactored 250 galllons. Remaining overflow immediately percolated in fenced field. Posted field.
OOO115 | 619-338-2848 | 2000-10-25 10:00 | Patti S. Page | (760)723-5640 | Fallbrook Public Utility District | 2000-10-24 07:10 | 2000-10-24 07:20 | 60 | 50 | Shady Lane Lift Station | Fallbrook | SD | 92028 | Lift Station | 3 | Pump Station Failure | Float stuck on debris. Bubbler system had failed and installed float for temporary use. | Moved float system and pump started pumping. Will be installing electronic sensor system in the future. | N | N | NA | NA | Diverted & contained flow using sand bag in ditch beside pump station. | Y | N | Y | 3 | We are in the process of rehabilitation of this lift station and hope to complete this within 2 weeks. We are also looking into an emergency overflow tank to prevent any future spills.
OOO116 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2000-11-03 14:50 | 2000-11-03 15:30 | 30 | 0 | 1010 S. Stage Coach | Fallbrook | SD | 92028 | Cleanout | 1 | Roots | Roots in lateral. | Rodded lateral and it opened at about 10 feet. | N | N | NA | NA | Soaked in ground around cleanout. Removed paper and solids. | N | N | N | NA
OOO117 | 858-571-6972 | 2000-11-15 09:45 | Patti S. Page | (760)723-5640 | Fallbrook Public Utility District | 2000-11-14 11:30 | 2000-11-14 12:30 | 25 | 25 | 1412 E. Mission Road | Fallbrook | SD | 92028 | Cleanout | 1 | Roots | Roots in lateral. | Rodded lateral and it opened at about 25 feet. | Y | N | Fallbrook Creek | Lake O'Neil | Did not reach secondary waters. | Y | N | Y | 3 | Tried to open sewer lateral. Homeowner had tied into District cleanout. Had to remove pipe and water drain from house in ditch. Vactored out standing water in creek. 100 gallons total of ponded water recovered. This includes 25 gallons of overflow an
OOO118 | 858-571-6972 | 2000-11-22 11:05 | Patti S. Page | (760)723-5640 | Fallbrook Public Utility District | 2000-11-21 11:00 | 2000-11-21 11:25 | 125 | 0 | 2800 Block Overland Trail | Fallbrook | SD | 92028 | 10" Pressure Line | 2* | Line break. | About a 6" crack in pipe with 3 little holes, where water was coming out. Pipe failure. | Dug up and replaced with 4 1/2' joint of pipe. | Y | N | Ostrich Creek | San Luis Rey River |  | Y | N | Y | 3 | Turned pumps off and drained line so it would not keep overflowing. Estimated only 25-30 gallons went to creek. The rest of it soaked into ground. This is the 2nd spill on the 2800 block of Overland Trail, but at a different location on pipe. Related
OOO119 | 858-571-6972 | 2000-11-22 14:30 | Patti S. Page | (760)723-5640 | Fallbrook Public Utility District | 2000-11-21 19:00 | 2000-11-21 20:10 | 12000 | 12000 | 2800 Block Overland Trail | Fallbrook | SD | 92028 | 10" Pressure Line | 2* | Line break. | See #000118 - this is same cause/overflow, but at a different final destination. Force main broke and valve in manhole was not closed all the way at Plant 2, sending flow to equalization basin. | Closed vavle in manhole at Plant 2. | N | N | NA | NA | Equalization basin at Plant 2 Pump Station. | Y | N | Y | 3 | See #000118 above. This is same cause/overflow but to different final destination due to diverting actions. This entered the emergency pond. The valve in the manhole that caused this spill will be locked out and red tagged from now on. See Regional Bo
OOO120 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2000-12-04 20:40 | 2000-12-04 20:55 | 25 | 5 | 818 E. Alvarado | Fallbrook | SD | 92028 | Cleanout | 1 | Blockage | Hair line root, grease, & hair. | Ran cutter down 6" cleanout about 15' where it cleared stoppage. | N | N | NA | NA | Soaked into ground near cleanout box. | N | N | N | NA
OOO121 | 858-571-6972 | 2000-12-07 08:30 | Patti S. Page | (760)723-5640 | Fallbrook Public Utility District | 2000-12-06 18:30 | 2000-12-06 20:00 | 200 | 0 | 1225 Aves Lane | Fallbrook | SD | 92028 | Cleanout | 1 | Roots | Bockage caused by roots. | Tried to clear mainline stoppage with flush truck but truck didn't have needed power to make it up line. Tried for 45 minutes and finally cleared it with rodder from District cleanout with extra cable. | Y | Y | None. Percolated into ground of dry dirt culvert. | NA | Soaked into ground of dry dirt culvert. | Y | N | Y | 3 | Due to poor equipment (power), clear time for stoppage was extended. Vactor truck was out for service and couldn't recover overflow. Overflow percolated into ground very quickly.
OOO122 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2000-12-09 08:35 | 2000-12-09 09:25 | 500 | 200 | 610 N. Main Street | Fallbrook | SD | 92028 | Manhole | 1 | Grease & Debris | Grease and debris in manhole. A couple bricks and a stick about 2' long. | Flushed mainline and unblocked. Then cleaned manhole with water hose, then flushed and vacuumed mainline. | N | N | NA | NA | Was standing in yard. Most of it soaked into the grass, but we did recover about 200 gallons. | N | N | N | NA | Mainlines above and below manhole B-137 should be flushed and vacuumed ASAP. Manhole is located in the backyard of 610 N. Main.
OOO123 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2000-12-14 19:10 | 2000-12-14 19:11 | 15 | 0 | 316 E. Clemmens | Fallbrook | SD | 92028 | Cleanout | 1 | Roots | Major roots in lateral wye and mainline. | Rodded lateral. | N | N | NA | NA | Ran out of cleanout box into ice plant and soaked in the ground 5' to 8' around cleanout box. | N | N | N | NA | Didn't overflow until lid was removed, which is why overflow duration was only 1 minute.
OOO124 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2000-12-16 10:04 | 2000-12-16 10:20 | 35 | 0 | 308 Sunbeam Lane | Fallbrook | SD | 92028 | Cleanout | 1 | Roots & Other | Roots and tampons. | Rodded line. Hit obstruction about 10' to 15' down. Cleared line. Sanitized entire spill area to end of standing water in street. | N | N | NA | NA | Dried up on pavement. | N | N | N | NA
OOO125 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2000-12-15 11:20 | 2000-12-15 11:40 | 3 | 0 | 818 E. Alvarado | Fallbrook | SD | 92028 | Cleanout | 2 | Roots | Roots in cleanout. | Rodded lateral with 3 different cutters. Unplugged lateral. Roots are caused from about 5 big trees on easement and over mainline. | N | N | NA | NA | Water soaked into the dirt around cleanout about 5'-7'. | N | N | N | NA | Water was not running out of cleanout box when arrived. It was about 8-10 inches from top of pipe. Sanitized entire area. Major roots were cause of stoppage.
OOO126 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2000-12-21 10:45 | 2000-12-21 10:50 | 20 | 0 | 262 Via Cassandra | Fallbrook | SD | 92028 | Cleanout | 1 | Roots | Roots in lateral. | Rodded line. Hit roots at about 15' to 20' out. Disinfected area when done. | N | N | NA | NA | Dried up on pavement. | N | N | N | NA
OOO127 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2000-12-23 09:37 | 2000-12-23 11:30 | 40 | 0 | 130 Alva Lane | Fallbrook | SD | 92028 | Cleanout | 1 | Blockage | Mainline blockage downstream from cleanout. | Flushed downstream manhole to upstream manhole. Opened mainline. Posted sign and disinfected area by cleanout. | N | N | NA | NA | Soaked into dry sandy soil. | N | N | Y | 3 | Posted as public precaution.
OOO128 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2000-12-26 09:46 | 2000-12-26 12:00 | 200 | 0 | 148 Palacio Norte | Fallbrook | SD | 92028 | Cleanout | 1 | Roots | Roots in cleanout. | Rodded cleanout and cleaned up yard and around pool. Disinfected entire area and posted signs. | Y | N | Un-known/Un-named | Fallbrook Creek |  | Yes | N | Y | 3 | Cleaned up area. Cut grass to remove toilet paper and as much waste as possible. Disinfected entire area. Posted sign by creek. Unable to access area with vactor to recover overflow or contaminated water.
00-3 | Voice/Fax | 11/18/00 11:00am | Leo Schempp | 760-753-0155 | Leucadia County Water District | 2000-11-18 07:40 | 2000-11-18 07:50 | 1200 | 10 | Intersection of Altisma & Alicante | Carlsbad | SD | 92009 | Manhole | 0 | Grease stoppage | Grease stoppage | Used vactor truck to relieve blockage, vacuum up debris & wash down street with potable water. | Y | Y | Storm drain | San Marcos creek | Ocean | Y | Y | N | NA | Washed down affected area
00-4 | Voice | 11/21/00 8:20pm | Leo Schempp | 760-753-0155 | Leucadia County Water District | 2000-11-21 19:23 | 2000-11-21 20:20 | 420 | 0 | 7614 Calla Madero | Carlsbad | SD | 92009 | Manhole | 0 | Roots/ Grease | Roots/ Grease | Used vactor truck to relieve blockage, TV inspection of main line | N | N | NA | NA | NA | Y | N | N | NA | removed all debris around affected area
00-5 | Voice/Fax | 11/30/00 12:20:pm | Leo Schempp | 760-753-0155 | Leucadia County Water District | 2000-11-30 11:00 | 2000-11-30 11:50 | 500 | 30 | La Calina way | Carlsbad | SD | 92009 | clean out | 0 | Grease stoppage | Grease stoppage | Used vactor truck to relieve blockage, vacuum up sewage containment & wash down street with potable water. | N | Y | Storm drain | NA | NA | Y | N | N | NA | Washed down affected area
001001 |  | 100700 16:54 | City of San Diego | (858)654-4135 | Lemon Grove | 2000-10-07 12:12 | 100700 14:20 | 384 | 0 | Angelus Ave, Lemon Grove & Di Marino, San Diego City | Lemon Grove | SD | 91945 | 8" vc | 0 | roots-LG side.. Grease-SD side | Location is on LG /SD City border and serves both cities. Spill took place on steep downhill easement. Roots on LG side combined with grease caused stoppage | Replacement of the 43' section of 8" vc in Lemon Grove is being replaced in current CIP program in spring 01. Has been placed on 'hot list' for frequest cleaning until that time. | Y | Y | Storm drain 100 ft west of manhole, dissipated in system | Chollas Creek/ SD Bay | 0 | Y | NA | N | NA | Initial stoppage was reported by affected S.D homeowners.City of SanDiego responded as well as Lemon Grove. Spill is on steep easement .
001002 |  |  |  | (619)825-3800 | Lemon Grove | 2000-10-15 09:30 | 101500 12:00 | 150 | 100 | Dirt road on city owned undeveloped land. | Lemon Grove | SD | 91945 | 8" VC | 0 | grease blockage | grease. | jetted and root cut line | N | N | NA | NA | Area diked and pumped back into main line. Small amount absorbed into open field. | N | NA | N | NA | Spill reported by L.G. City crew. Section last cleaned 7-22-00
00107 | N/A | N/A | N/A | N/A | City of Coronado | 2000-11-06 08:15 | 2000-11-06 09:00 | 100 | 100 | 700 SECOND STREET | CORONADO | CA | 92118 | SEWER MAIN | 0 | BREAK IN LINE | OLD SEWER MAIN BROKE, SEWER BUBBLED UP ONTO STREET SURFACE | REPLACED BROKEN CLAY PIPE | N | N | N/A | N/A | N/A | N | N | N/A | N/A
00108 | N/A | N/A | N/A | N/A | City of Coronado | 2000-11-18 10:30 | 2000-11-18 12:00 | 50 | 50 | ORANGE/D ALLEY AT THIRD STREET (1000 BLOCK OF THIRD) | CORONADO | CA | 92118 | SEWER MAIN | 0 | DEBRIS IN LINE | TOILET PAPER IN SEWER MAIN LINE | REMOVED PAPER, CLEANED 270' OF LINE. SCHEDULED MAINTENANCE AND CLEANING TO PREVENT FUTURE OCCURENCES | N | N | N/A | N | N/A | N | N | N/A | N/A
00109 | N/A | N/A | N/A | N/A | City of Coronado | 2000-11-21 11:00 | 2000-11-21 11:20 | 10 | 10 | ORANGE/D ALLEY AT THIRD STREET (1000 BLOCK OF THIRD) | CORONADO | CA | 92118 | SEWER MAIN | 1 | UNKNOWN | BACKUP IN SEWER MAIN LINE, CAUSE UNKNOWN | VIDEOTAPED SEWER LINE TO EVALUATE CAUSE, PLACED ON REPAIR LIST | N | N | N/A | N | N/A | N | N | N/A | N/A
00110 | N/A | N/A | N/A | N/A | City of Coronado | 2000-11-29 21:20 | 2000-11-29 23:30 | 30 | 30 | 421 EIGHTH STREET | CORONADO | CA | 92118 | SEWER MAIN | 0 | UNKNOWN | BACKUP IN SEWER MAIN LINE, CAUSE UNKNOWN | CLEANED AND JETTED SEWER LINE. | N | N | N/A | N | N/A | N | N | N/A | N/A
00111 | N/A | N/A | N/A | N/A | City of Coronado | 2000-11-30 16:00 | 2000-11-30 16:20 | 20 | 20 | FIRST ST BETWEEN ORANGE AND C | CORONADO | CA | 92118 | SEWER MAIN | 2 | POSSIBLE GREASE | BACKUP IN SEWER MAIN LINE, POSSIBLY CAUSED BY GREASE FROM RESTAURANTS | CLEANED AND JETTED SEWER LINE. | N | N | N/A | N | N/A | N | N | N/A | N/A
001-003 | Victor Vasquez V-858-636-3155 F-858-571-6972 | 12/05/00 07:00 | Patrick Jackson | 619-441-1658 | City Of El Cajon | 2000-12-04 08:05 | 12/04/00 08:40 | 600 | 0 | 811 Murray Dr. | El Cajon | SD | 92020 | MH 09-079 | 0 | Roots | T.V. inspection revealed tree roots infiltrating sewer main. | Sewer line will be added to our 6 month rodding list. Manhole is already inspected every three months. Other sewer lines in that area are also rodded. | Y | Y | County Ditch Channel | Forester Creek Channel | NA | Y | NA | N | NA | Most of overflow percolated into the ground. County Ditch and Forester Creek are completely fenced.
001008 | VICTOR VASQUEZ | 2000-10-01 16:00 | COLLEEN ECKENROAD | 7607259761 | MCB, CAMP PENDLETON | 2000-10-01 09:20 | 2000-10-01 10:40 | 400 | 0 | 169 CASTLE, STUART MESA HOUSING | CAMP PENDLETON | SD | 920555008 | MH 13Y463, 8" PVC | 1 | BLOCKAGE | SEWER LINE BLOCKED WITH PAPER TOWELS AND GREASE RESULTING IN SEWAGE OVERFLOWING/WEEPING FROM HOLES ON TOP OF MH COVER, THE MH LID WAS NOT DISPLACED. | CORR: USE JETTER TO CLEAR LINE FROM DOWNSTREAM MH, WASH LIQUIDS (NO SOLIDS) BACK INTO MH. PREV: CONTINUAL EDUCATION OF HOUSING TENANTS OF PROPER DISPOSAL METHODS. | Y | Y | SANTA MARGARITA RIVER | PAC OCEAN(SMR MOUTH CLOSED) | NO FLOW TO ACTUAL WATER, PERC'D INTO MARSH. | Y | NA | N | NA | OVERFLOWED 15' FROM MH TO STREET, 250' TO GUTTER/CURB TO STORM DRAIN, DOWN CONCRETE CULVERT AND ~1 MILE THRU VEGETATED CANYN, INTO MARSH, .25 MI TO RIVER. TOT DIS OVER 1.25 MILE. SPILL PERC'D IN CANYON & INTO MARSH. NO EXPECTED PUBLIC CONTACT.
001009 | VICTOR VASQUEZ | 2000-10-12 12:55 | COLLEEN ECKENROAD | 7607259761 | MCB, CAMP PENDLETON | 2000-10-12 09:45 | 2000-10-12 10:40 | 20 | 0 | BLDG 22190 | CAMP PENDLETON | SD | 920555008 | MH 3-Y-257,6" CLAY PIPE NEAR BLDG 22190 | 1 | ROOTS | FMD WAS WORKING ON CLEARING A BLOCKAGE IN BLDG 22190 AND NOTICED INTERMITTENT WEEPING OF EFFLUENT FROM MANHOLE COVER, BLOCKAGE IN LINE PRESUMABLY FROM TREE ROOTS | CORRECTIVE: RAM JET LINE, PUMPED OUT 2000 GAL. FROM MANHOLE TO PREVENT FURTHER DISCHARGE WHILE RAM JETTING TO CLEAR BLOCKAGE. HOSED DOWN FOR CLEAN UP. PREVENTATIVE: CONTINUAL PM OF LINES AN AREA. | Y | Y | SANTA MARGARITA RIVER | PACIFIC OCEAN | NO ACTUAL FLOW TO WATER, PERC'D INTO EARTHEN DITCH | N | NA | N | NA | OVERFLOWED FROM MH 15' TO STORM DRAIN. APPROX 475' IN STM DN AND EXITED STORM DRAIN AND 5' INTO EARTHEN DITCH, WHERE IT PONDED AND PERCOLATED TOTAL DISTANCE TRAVELED 495'.NO PUBLIC CONTACT EXPECTED.
001010 | VICTOR VASQUEZ | 2000-10-16 16:35 | COLLEEN ECKENROAD | 7607259761 | MCB, CAMP PENDLETON | 2000-10-16 10:00 | 2000-10-16 12:30 | 3000 | 2100 | BLDG 43505 | CAMP PENDLETON | SD | 920555008 | CLEANOUT FOR BLDG 43505 | 1 | BLOCKAGE | SEWAGE BACKED UP INSIDE BLDG 43505 AT 1000, CLEANOUT CAP WAS REMOVED IN INVESTIGATION WHICH RESULTED IN AN OVERFLOW CAUSED BY UNKNOWN BLOCKAGE IN 8" CLAY MAIN LINE | CORRECT: RAM JET LINE TO CLEAR BLOCKAGE, BLOCKED STORM DRAIN A WITH SAND BAGS TO CREATE RECOVERY POND,600 GAL WERE RECOVERED AT POND,1500 GAL IN CLEANOUT AREA. TWO PUMPER TRUCKS RESPONDED FOR RECOVERY. PREVENTATIVE: CONTINUE PM'S OF SEWER MAINS | Y | Y | LAS PLUGAS CREEK | PACIFIC OCEAN | NO FLOW TO ACTUAL WATER, PERC'D INTO SOIL | Y | Y | N | NA | OVERFLOW FROM CLEANOUT, 5'OVER DIRT, 240' DOWN ASPHALT RD TO STORM DRAIN(SD) A, 100 GAL 150'TRU SD, 2' IN EARTH DITCH AND PERC'D FLOW CONT 530' DOWN RD, TO SD B, 140' THRU SD 100' SOUTH IN SAME EARTHEN DITCH AND PER'C BRUSH AREA OF NO EXPECTED PUBLIC CONTACT
001011 | VICTOR VASQUEZ | 2000-10-23 14:12 | COLLEEN ECKENROAD | 7607259761 | MCB, CAMP PENDLETON | 2000-10-23 11:00 | 2000-10-23 13:30 | 9000 | 7000 | 1/4 MILE E. OF LS.31227 | CAMP PENDLETON | SD | 920555008 | 6" CLEANOUT ON 12" FORCE MAIN | 1 | LINE BREAK | BURIED 6" CLEANOUT ON 12" FORCE MAIN BROKE DUE TO HEAVY TRAFFIC OVER CLEANOUT AREA | CORREC: CONTAINED SPILL WITH 5' DIRT BERM AND RECOVERED WITH 3 PUMPER TRUCKS, LIME WAS USE TO DISINFECT ON ROAD WAY WATER WAS SECURED TO STUART MESA AT APPROX. 1230. RESTORED AT 1750. PREVENTATIVE: REMOVED 6'" CLEANOUT FROM ROAD WAY, REPLACED 12" DIAMETER 36" LONG DUCTILE IRON PIPE. | Y | N | UNNAMED TRIBUTARY TO SMR | SANTA MARGARITA RIVER | NO FLOW TO RIVER PERC'D IN SANDY AREA ADJACENT | Y | Y | Y | 3 | SPILL TRAVELED 2 DIRECTIONS;1-FROM CLEANOUT 50'N ACROSS DIRT RD 200'W ALONG RD & 50'S ACROSS RD & INTO SANDY AREA,2-FROM CLEANOUT 50'S INTO SAND BERMED AREA,200' W THRU EXISTING SAND CHANNEL TO SAME FINAL DESTINATION & PERC'D INTO A SANDY AREA APPROX 900' FROM THE SMR TDT 550'
001012 | VICTOR VASQUEZ | 2000-11-02 15:30 | COLLEEN ECKENROAD | 7607259761 | MCB, CAMP PENDLETON | 2000-11-02 10:15 | 2000-11-02 13:30 | 20600 | 20200 | 1 MILE EAST OF LS 51056 ON BASILONE RD | CAMP PENDLETON | SD | 920555008 | 8" PVC FORCE MAIN | 1 | CONSTRUCTION | CONTRACTOR WORKING ON BASILONE RD HIT LINE WITH EXCAVATOR. | CORREC:3 PUMPER TRUCKS ON SITE & AT LIFT STATION 51056 WHILE REPAIRS TO LINE ARE MADE & TRANS TO STP 11.WATER & LS SECURED @1330.REPLACE A 10' BROKEN SEGMENT OF PVC PIPE- DI PIPE. LIMED EXPOSED AREA. PREVENTATIVE: CONTRACTOR TO HAND DIG AREA, AND HAVE LOCATOR TO REMARK UTILITIES | N | N | NONE | NONE | NO FLOW TO ACTUAL WATER, SPILL PERC'D INTO DIRT | Y | Y | N | NA | ENTIRE SPILL WAS CONTAINED WITH 98% RECOVERED, REMAINING PERCOLATED INTO GROUND. BASILONE ROAD WAS CLOSED FOR REPAIRS; THEREFORE, NO PUBLIC CONTACT ACCESS CONCERNS.
001013 | VICTOR VASQUEZ | 2000-11-27 11:25 | Cpl Osunabaez, R | 7607259761 | MCB, CAMP PENDLETON | 2000-11-25 11:00 | 2000-11-25 11:41 | 150 | 0 | BLDG # 310406 BY SUZUKI & PARKER | CAMP PENDLETON | SD | 920555008 | UNNUMBERED MANHOLE IN STUART MESA @SUZUKI & PARKER | 1 | PUMP STATION FAILURE | PUMPS DID NOT COME ON BECAUSE ONE PUMP WAS PLUGGED WITH RAGS AND THE OTHER WAS PARTIALLY PLUGGED, THAT CAUSED THE CIRCUIT BREAKER TO KICK OFF | CORRECT: PUMPS WERE CLEARED AND RESET, THERE WAS NO NEED FOR CLEAN UP IT WAS ONLY LIQUID NO SOLIDS, WATER EVAPORATED. NO NEED FOR DISINFECTION BECAUSE OF UV EXPOSURE. PREVENTATIVE: ELECTRICIAN WILL CHECK ELECTRIC PANEL FOR ANY CIRCUIT BREAKER PROBLEMS | Y | Y | PACIFIC OCEAN | MCB, CPEN | REMAINED IN 4 FT DIAMETER CONCRETE STORM DRAIN | Y | NA | N | NA | FROM MANHOLE FLOW ACROSS PAYMENT 25 FT TO CONCRETE GUTTER 60 FT TO STORM DRAIN 140 FT AND IN SWALE 35 FT TO CONCRETE PIPE 4 FT.
001014 | ELECTRONIC QTLY RPT | NA | Cpl Osunabaez, R | 7607259761 | MCB, CAMP PENDLETON | 2000-12-07 09:45 | 2000-12-07 21:15 | 50 | 30 | CLEANOUT U11974 BY BLDG 1441 | CAMP PENDLETON | SD | 920555008 | CLEANOUT U11974 | 1 | BLOCKAGE | PAPER TOWELS AND ROOTS WERE STUCK IN LINE THAT CAUSE A BACKUP THAT ENDED IN A SPILL IN CLEANOUT U11974. | CORRECTIVE: JET LINE TO CLEAR BLOCKAGE. PREVENTATIVE: WILL SEND ROOT CUTTER TO PM LINE | N | N | NA | NA | FROM CLEAN OUT 250' ACROSS ASPHALT PARKING LOT AND POUNDED | NA | NA | NA | NA | FROM CLEAN OUT 250' ACROSS ASPHALT PARKING LOT AND PONDED PUMPER TRUCK RECOVERED 30 GALLONS OF SEWAGE.
001015 | VICTOR VASQUEZ | 2000-12-15 18:07 | Cpl Osunabaez, R | 7607259761 | MCB, CAMP PENDLETON | 2000-12-15 11:45 | 2000-12-15 13:00 | 1800 | 0 | OFF 11TH ST. BETWEEN 1526 AND SERRA MESA HOUSING | CAMP PENDLETON | SD | 920555008 | MANHOLE 2Y110 | 1 | ROCKS | ROCKS & DEBRIS IN LINE, GREASE FROM THE HOUSING AREA COMBINED TO BLOCK LINE. AND CAUSED THE MANHOLE TO OVERFLOW. | CORRECTIVE: JET LINE CLEAR, NO SOLIDS, LIQUIDS PERCOLATED INTO GROUND. NO NEED FOR DISINFECTION NOT IN AREA OF EXPECTED PUBLIC CONTACT. PREVENTATIVE: WILL PM ALL SERVICE LINES IN AREA AND INSPECT FOR CONDITION | Y | N | PILGRIM CREEK | PACIFIC OCEAN | DID NOT REACH ACTUAL SURFACE WATER | Y | NA | N | NA | FROM MANHOLE 65' DOWN EARTH & VEGETATION TO NATURAL DRAINAGE 1200' THROUGH EARTH & VEGETATION- PERCOLATED INTO GROUND APPROX.2500' FROM DRY PILGRIM CREEK. IN AREA OF NO EXPECTED PUBLIC CONTACT.
001016 | VICTOR VASQUEZ | 2000-12-18 10:00 | Cpl Osunabaez, R | 7607259761 | MCB, CAMP PENDLETON | 2000-12-17 10:00 | 2000-12-17 13:00 | 30 | 0 | BLDG 210597 | CAMP PENDLETON | SD | 920555008 | UNNUMBERED MANHOLE BY BLDG 210597 ADJACENT MH 13Y231 | 1 | BLOCKAGE | CLOGGED SEWER MAINLINE, CLOGGED WITH SAND ROCKS AND WOMAN'S SANITARY PROTECTION ITEMS. | CORRECTIVE: JETTED LINE CLEAR, NO SOLIDS, ALL LIQUID WHICH ALL PERCOLATED INTO SAND. LIMED AREA FOR DISINFECTION AND BARRIER THE INSTALLED TO PREVENT PUBLIC ACCESS. PREVENTATIVE: HYDRO JETTED DEBRIS IN AREA LINES ON 18 DEC 00. | N | N | NONE | NONE | NO FLOW TO ACTUAL SURFACE WATER | Y | NA | Y | 3 | SPILL TRAVEL 65' ON SAND AND PERCOLATED ABOUT 300' FROM OCEAN'S HIGH TIDE LINE.
001017 | VICTOR VASQUEZ | 2000-12-18 15:57 | Cpl Osunabaez, R | 7607259761 | MCB, CAMP PENDLETON | 2000-12-18 11:50 | 2000-12-18 12:00 | 30 | 0 | BLDG 2511 | CAMP PENDLETON | SD | 920555008 | 4" MAIN SEWER LINE | 1 | CONSTRUCTION | CONTRACTOR WAS DIGGING AND HIT THE 4" MAIN SEWER LINE WITH BACK HOE. | CORRECTIVE: THE 4" MAIN SEWER LINE WAS REPLACED, ALL LIQUID NO SOLIDS, IT ALL PERCOLATED INTO GROUND. TREATED SPILL AREA WITH LIME. PREVENTATIVE: A LOCATOR WILL ADVISE ALL CONTRACTORS WORKING IN THE AREA WERE ALL THE SEWAGE LINES ARE LOCATED. | Y | Y | SANTA MARGARITA RIVER | PACIFIC OCEAN | NO FLOW TO ACTUAL SURFACE WATER | Y | NA | N | NA | THE SPILL TRAVELED 10' OVER DIRT FROM THE 4" MAIN LINE AND 10' IN AN EARTHEN DITCH AND PERCOLATED INTO SOIL.
001018 | VICTOR VASQUEZ | 2000-12-23 16:04 | Cpl Osunabaez, R | 7607259761 | MCB, CAMP PENDLETON | 2000-12-22 11:00 | 2000-12-22 15:00 | 500 | 400 | NEAR ABEYATA COURT, SERRA MESA HOUSING | CAMP PENDLETON | SD | 920555008 | MANHOLE 2Y152 | 1 | BLOCKAGE | UNKNOWN CAUSE FOR BLOCKAGE OF MAIN LINE | CORRECTIVE: JETTED LINE CLEAR; WASHED DOWN SPILL AREA & PUMPED PONDED SEWAGE FOR TRANSPORT TO STP FOR TREATMENT; LIMED AREA. PREVENTATIVE: MAIN LINES IN THIS AREA OF SERRA MESA HOUSING WILL BE JETTED IN JAN 01 | Y | N | DRY PILGRIM CREEK | PACIFIC OCEAN | NO FLOW TO CREEK OR ACTUAL SURFACE WATER | Y | NA | Y | 5 | FLOW FROM MH DOWN HILL TOTAL 464' ALL TRU DIRT/GRASS/BRUSH AREA; FLOW 74 ' & PERC'D; SEPARATE FLOW 390' & POND/PERC'D - NO EXPECTED PUBLIC CONTACT-LIMED & POSTED AS PRECAUTION
001009 | Whittney | 2000-10-02 13:15 | Jeremy Kemp | 7604355842 | Water Utilities Dept. City of Oceanside | 2000-10-02 09:30 | 2000-10-02 09:50 | 800 | 300 | Morse St. & Griffin St. | Oceanside | SD | 92054 | City Manhole | 1 | Roots | Vactor crew broke a major stoppage of roots on an easement line that runs under I-5. Had to make an "entry" to recover large root mass. | Line is on a routine maintenance schedule. Will video line to check overall condition. | N | Y | N/A | N/A | Evaporation and Recovery | Y | N | N | 0
001010 | Lisa Brown | 2000-10-05 13:10 | Mark Patnode | 7604355840 | Water Utilities Dept. City of Oceanside | 2000-10-05 09:50 | 2000-10-05 10:03 | 75 | 40 | 3761 Cameo Drive | Oceanside | SD | 92054 | City Manhole | 1 | Grease | Heavy grease in City line caused manhole to overflow at the intersection of Cameo & Brandeis Drive. | Line was jet cleaned and 200 Lbs. Of chlorine was put into line to burn grease down the line. Line put on monthly cleaning schedule. | N | Y | Storm drain @ 3700 block Cameo Drive. | N/A | N/A | Y | N | N | 0 | City cleaned all of Cameo Drive line with Vactor Truck, and line put on monthly cleaning schedule.
001011 | Voice Mail & Fax | 2000-10-09 10:50 | Jeremy Kemp | 7604355870 | Water Utilities Dept. City of Oceanside | 2000-10-09 08:45 | 2000-10-09 09:05 | 800 | 0 | 4706 Cannon Road | Oceanside | SD | 92056 | Sewer Lift Station | 1 | Pump Station Failure | Pumps @ station were tripped. Back up system failed due to "bad" relay. | Station alarms notified crew. Quick response helped to limit spill amount. Station is checked daily. 7/7. | Y | Y | Un-named creek in canyon. | N/A | N/A | Y | Y | Y | 2 | Two vactors on site. Could not recover due to limited access on dirt road in steep canyon covered with brush.
001012 | Voice Mail | 2000-10-31 09:10 | Mark Patnode | 7605350535 | Water Utilities Dept. City of Oceanside | 2000-10-31 06:35 | 2000-10-31 07:17 | 860 | 860 | 5755 Jefferies Ranch Road | Oceanside | SD | 92056 | City Manhole | 1 | Grease | Grease built up in the City line, causing a stoppage. | Crew will add chlorine to burn out grease, and put line on semi-annual jetting schedule. | Y | Y | Storm drain @ 5700 block of Jefferies Ranch Road | Pond and creek runoff on north side of freeway. | Recovered 100% | Y | N | N | 0 | Crew dammed drainage ditch with sand bags, and recovered spill with vactor trucks.
001013 | Voice Mail | 2000-11-03 03:00 | Art Trujillo | 7608011179 | Water Utilities Dept. City of Oceanside | 2000-11-02 21:50 | 2000-11-03 00:30 | 4500 | 1900 | 2900 Blk. College & Marvin | Oceanside | SD | 92054 | City Manhole | 1 | Grease | Roots & grease blocked a 10" sewer line causing upstream manhole to overflow. | Line was jetted, and will be TV'd to find root cause. | Y | Y | Storm Drain on College | Water Hazard on El Camino Golf Course. | Water Hazard on 9th hole. | Y | Y | Y | 3 | Spilled 4500 gal into storm drain on College Blvd. and recovered 1900 gal from storm drain on Cameo Drive & Rancho del Oro Drive. Coliform sample was taken of Water Hazard on Golf Course. No flows leave the pond.
001014 | Voice Mail | 2000-11-24 18:10 | Edwin C. Calhoun | 7604355870 | Water Utilities Dept. City of Oceanside | 2000-11-24 10:00 | 2000-11-24 10:30 | 550 | 250 | 3864 Mission Avenue | Oceanside | SD | 92057 | City Manhole | 1 | Grease | Grease built up in the City line, causing a stoppage. | The line will have chlorine drops made periodically and surrounding grease traps will be checked by Inspector. | Y | Y | Mission Avenue Flood Channel | Fireside Drive Flood Channel | Evaporation and Recovery | Y | Y | N | 0 | Spill did not make it to SLR River. Flood Channel is dry and spill gates into River are closed.
001015 | Voice Mail | 2000-12-12 16:30 | Jeremy Kemp | 7604355840 | Water Utilities Dept. City of Oceanside | 2000-12-12 15:30 | 2000-12-12 16:05 | 350 | 0 | 510 San Luis Rey Drive | Oceanside | SD | 92054 | City Manhole | 1 | Rags | Grease, rags and debris built up in City line, causing a stoppage. | Line to be TV'd on 12/13/00 to see if serious problem in line. | Y | Y | Storm drain at San Luis Rey Drive | San Luis Rey River |  | Y |  | N |  | Permanent signs are posted. No recover possible due to short trip "tween drain & River.
001201 | n/a | 2000-12-09 20:00 | Kevin Miller | (760) 728-1178 | Rainbow MWD | 2000-12-09 16:42 | 2000-12-09 19:00 | 75 | 0 | Via Larga Vista | Bonsall | SD | 92003 | 26G-m050 | 0 | DEBRIS IN LINE | unknown obsturction in sewer line | used jet truckto clear blockage. Scheduled area for line cleaning | n | n | none | none | dissipated | y | n | n | 0 | overflow was not detectedwhen work crew arrived but manhole was full. Used approx 20 gallons of wash water to rinse street.
1210 | FAX | 2000-12-10 10:30 | CHULA VISTA POLICE | (619) 691-5027 | City of Chula Vista | 2000-12-10 10:30 | 2000-12-10 15:30 | 1500 | 0 | OTAY LAKES & LA MEDIA | CHULA VISTA | SD | 91910 | MANHOLE | 0 | DEBRIS | CONSTUCTION DEBRIS ( 2 X 4 LUMBER) | CONTAINED SPILL AND REMOVE DEBRIS ( 2 X 4) | YES | YES | TELEGRAPH CHANNEL | J ST MARINA | J ST MARINA | YES | YES | YES | 3 | ENTIRE SYSTEM IN QUESTION WAS CCTV
000011 | Not reportable | 11/01/00; 0930 | Dennis Causbrook | (619) 556-7352 | US Navy | 2000-11-01 09:30 | 11/01/00; 0950 | 250 | 0 | NASNI, 300' east of Blddg. 873. | Coronado | San Diego | 92135 | Bldg. 713 | 0 | Construction | Sewer pump station #713 is currently being excavated. During the excavation process an abandoned line was cut. Wastewater filled up in the wetwell and flowed out of the "cut" line prior to the pumps "start up" . Wastewater flowed out of the pipe into the excavation, and filtered into the soil. | The level pump controller was lowered so the wetwell would be pumped down before reaching the open pipe. Excavation disinfected. | No | No | n/a | n/a | n/a | Yes, but they considered non-reportable | N/a | N | n/a | none.
000012 | Not reportable | 11/01/00; 1226 | Ms. Leonor | (619) 524-3100-125 | US Navy | 2000-11-01 12:26 | 11/01/00; 1250 | 40 | 25 | NOLF IB, Bldg. 193 | Imperial Beach | San Diego | 91932 | manhole near Bldg. 193 | 1, July 24, 2000 | Debris | Bubbler float alarm failed due to excessive debris in pump station. | Cleared debris from pump station. Investigate where debris is entering the sewer. | No | No | n/a | n/a | n/a | No. Not reportable | No | n/a | n/a | none.
000013 | Not reportable | 11/28/00; 1500 | Miramar Duty Desk | (858) 577-1604 | US Navy | 2000-11-28 15:00 | 11/28/00; 1545 | 50 | 35 | Miramar Way | San Diego | San Diego | 92145 | I-31-3 | 0 | Blockage | Blockage in sewer line between manholes | sewer line was hydroblasted clear. | No | No | n/a | n/a | sewage went on surrounding ground and was cleaned up/absorbed into the soil. | DEH notified as a heads up call. | no | n/a | n/a | manholes up and downstream were hydroblasted.
000014 | Victor Vasquez | 12/04/2000; 0900 | James Olson | (619) 553-4144 | US Navy | 2000-12-04 09:00 | 12/04/2000; 1015 | 200 | 0 | Next to Bldg. 602, White Road | San Diego | San Diego | 92106 | Man hole 11-6 | 0 | Blockage/Debris | Unknown Blockage - Debris in manhole and line. | Hydroblast manholes before and after overflow lacation (manhole 11/6). | Yes | Yes | Storm Drain to San Diego Bay | San Diego Bay near Point Loma | n/a | Yes. | N/a | N/a | n/a | overflow entered storm drain.
000015 | Not reportable | 12/06/2000; 1130 | C.E. Wylie (private contractor) | (619)223-1107 | US Navy | 2000-12-06 11:30 | 12/06/2000; 1150 | 50 | 40 | Rosecrans Bldg. 560, NRAD | San Diego | San Diego | 92120 | Sewer line at Bldg. 560 | 0 | Construction | Contractor hit a 4" forced Main. Contained within Trench | Repaired Line | No | No | n/a | n/a | n/a | No. Not reportable | N/a | n/a | n/a | Remaining 10 gallons that were not recovered infiltrated into the soil of the trench that held the spill.
000016 | Not reportable | 12/11/2000; 1043 | PWC Duty Desk | (619) 556-7349 | US Navy | 2000-12-11 10:43 | 12/11/2000; 1050 | 20 | 20 | Naval Amphib. Base adjacent to Bldg. 605 | Coronado | San Diego | 92155 | Bldg. 605 sewer lift station | 0 | Pump Station Failure | Float Failure | Cleaned Float, cleaned and sanitized the area | No | No | none | none | n/a | No, not reportable | N/a | n/a | n/a | none.
000017 | Victor Vasquez | 12/20/2000; 1950 | Pat at MCAS Miramar trouble desk | (858) 577-1609 | US Navy | 2000-12-20 10:17 | 12/20/00; 1230 | 45000 | 34000 | MCAS Miramar, S/W of Brig Bldg. 9658, West end of De La Garza Rd. | San Diego | San Diego | 92145 | B1-09-3 | 0 | Blockage | Blockage was caused by City of San Diego contractor that plugged the line to stop sewer flow and install a sewer flow meter. | PWC Hydroblasted line clear. | none | No | Dry creek bed of Rose Canyon | none | Dry creek bed of Rose Canyon | Yes | Yes | Yes | 5 | 34,000 gallons were recovered. City of SD contractor plugged the line on purpose to install the meter and then forgot to remove the plug causing the sewer spill.
001001 | Lisa Brown RWQCB | 2000-10-06 16:00 | Kelley Gage | (760)753-6466 | Olivenhain Municipal Water District | 2000-10-05 22:00 | 2000-10-06 07:00 | 4500 | 4500 | 478 Campbell Rd | Rancho Bernardo | San Diego | 92127 | Manhole | 0 | Debris | During grading operations, manhole cover was removed and filled manhole with debris. | Spill was contained to street, vacuum truck recovered all volume, manhole was cleared of debris and cover replaced, volume was discharged to 4S WWTP fro treatment. | N | N | None | None | 4S WWTP | Y | N | N | 0 | Spill occurred within construction zone with no public access. The area is fenced and gated with signs posted for public to keep out.
000105 | CLAY CLIFTON - FAX | 10/01/00 - 9:30 A.M. | DON WASKO | 438-2722 X 7138 | CMWD | 2000-10-01 09:30 | 10/01/00 - 10:00 A.M. | 5 | 5 | 3831 SIERRA MORENA | CARLSBAD | SD | 92008 | MANHOLE | 1 | ROOTS | ROOT BUILD UP IN SEWER MAIN | JET VAC OF SEWER MAIN. CLEANED UP AREA CONTAINED SPILLAGE. | N | N | NONE | NONE | PERCOLATED INTO GROUND AROUND MANHOLE. | YES | N/A | NO | N/A | NONE
000106 | CLAY CLIFTON - FAX | 10/04/00 - 8:30 A.M. | DON WASKO | 438-2722 X 7138 | CMWD | 2000-10-02 15:00 | 10/02/00 - 15:00 | 5 | 300 | 2608 EL CAMINO REAL | CARLSBAD | SD | 92008 | PRIVATE GREASE TRAP - CARL'S JR. RESTAURANT | 1 | GREASE | THE GREASE TRAP AT CARL'S JR. OVERFLOWED. THE MANAGER HAD HIS PEOPLE WASHING DOWN THE DRIVE THRU TO CLEAN UP THE GREASE. I TOLD THEM TO STOP WASHING DOWN AND NOT TO USE WATER. CITY FORCES ASSISTED WITH CLEAN UP OF WASH DOWN WATER THAT MADE IT TO THE GUT5TER. WE VACTORED UP THE WATER BEFORE IT COULD REACH THE STORM DRAIN, ALSO DISINFECTED. | REGULAR MAINTENANCE ON THEIR GREASE TRAP. | N | N | NONE | NONE | WE CAPTURED THE INITIAL WASH DOWN WATER PLUS THE WATER WE USED TO CLEAN AND DISINFECT WITH. | YES | N/A | NO | N/A | NONE
000107 | CLAY CLIFTON - FAX | 11/17/00 - 8:00 A.M. | DON WASKO | 438-2722 X 7138 | CMWD | 2000-11-17 | 11/17/00 - 9:00 A.M. | 50 | 50 | 411-415 CHESTNUT | CARLSBAD | SD | 92008 | MANHOLE | 1 | ROOTS AND GREASE | WHEN WE "AARON ROTHCHILD, RUDY GRACIANO & PEDRO RODRIGUEZ" TRIED TO STOP THE OVERFLOW WITH JET VAC WE NOTICED BIG CHUNKS OF GREASE BEING RELEASED FROM SEWER PIPE UNTIL WE DID NOT SEE GREASE ANY MORE. | AFTER CLEARING ALL THE GREASE, WE RODDERED FOR ABOUT ANOTHER THIRTY MINUTES 200 FEET OF SEWER PIPE TO BE SURE IT WOULDN’T HAPPEN AGAIN. | N | N | NONE | NONE | WE COLLECTED ALL SEWER OVERFLOW WITH VACTOR SINCE ALL SEWER WAS CONTAINED IN PARKING LOT. | NO | N/A | NO | N/A | WE HOSED PARKING LOT AS BEST AS WE COULD & DISINFECTED IT.
000108 | CLAY CLIFTON - FAX | 11/20/00 - 7:30 A.M. | DON WASKO | 438-2722 X 7138 | CMWD | 2000-11-18 09:30 | 11/18/00 - 12:00 P.M. | 75 | 375 | 3090 JEFFERSON | CARLSBAD | SD | 92008 | LATERAL CLEANOUT | 1 | ROOTS | ROOT OBSTRUCTION | WE RODDERED LATERAL CLEAN OUT & PULLED OUT ROOTS FROM SEWER PIPE AND THEN RODDERED A COUPLE MORE TIMES TO BE SURE ALL ROOTS WERE PULLED OUT. WE PLAN TO TV SEWER LINE TO CORRECT FUTURE STOPPAGES. ALL THE ABOVE WAS DONE BY STEVE CORBEIL AND PEDRO RODRIGUEZ. SUPERVISOR DON WASKO WAS NOTIFIED. | N | N | NONE | NONE | WE JET VACCED ALL SEWER FROM STREET GUTTER IN A LOW POINT | NO | N/A | NO | N/A | ALL SEWER WATER WAS RECOVERED WITH JET VAC. IT NEVER REACHED STORM DRAINS OR SURFACE WATERS.
000109 | CLAY CLIFTON - FAX | 11/28/00 - 2:15 P.M. | DON WASKO | 438-2722 X 7138 | CMWD | 2000-11-28 15:10 | 11/28/00 - 3:15 P.M. | 20 | 20 | 3830 MONROE | CARLSBAD | SD | 92008 | LATERAL CLEANOUT | 1 | ROOTS | ROOT BALL 11" LONG, EIGHT FEET IN FROM 4 INCH CLEAN OUT. | HAND RODDED TO REMOVE ROOT BALL AFTER CONTAINING 20 GALLON SPILL AND VACTORING UP SPILL. | N | N | NONE | NONE | VACTORED AT STREET | YES | N/A | NO | N/A | NONE
000110 | CLAY CLIFTON - FAX | 12/21/00 - 11:00 A.M. | DON WASKO | 438-2722 X 7138 | CMWD | 2000-12-19 15:00 | 12/19/00 - 15:10 | 50 | 250 | 5650 EL CAMINO REAL, SUITE 125 | CARLSBAD | SD | 92008 | PRIVATE LIFT STATION | 1 | PUMP STATION FAILURE | PRIVATE LIFT STATION FAILURE. THE MULLER COMPANY (760) 431-9036 | THE COMPANY THAT OWNS THIS PROPERTY MUST PAY FOR PREVENTATIVE MAINTENANCE. | N | Y | STORM DRAIN BOX NEXT TO LIFT STATION. | NONE | WE RECAPTURED OUT OF STORM DRAIN DOWN STREAM. | YES | NO | NO | N/A | "PRIVATE LIFT STATION" WE ASSISTED WITH CLEAN UP.
000111 | CLAY CLIFTON - FAX | 12/21/00 - 16:35 | DON WASKO | 438-2722 X 7138 | CMWD | 2000-12-20 14:00 | 12/20/00 - 15:00 | 300 | 300 | BEACON BAY DRIVE/LIGHTHOUSE | CARLSBAD | SD | 92008 | SEWER MANHOLE | 1 | CONSTRUCTION | IT APPEARED TO BE CONSTRUCTION DEBRIS ABOUT 1/2 MILE DOWNSTREAM ON TURNSTONE ST. | MAKE SURE SEWER SYSTEM IS CLEAR OF ANY OBSTRUCTIONS FROM CONSTRUCTION. THE OVERFLOW ENTERED THE STORM DRAIN AND DUMPED INTO A POND AT THE BOTTOM NEAR BEACON BAY/WHITESAIL. WE RECAPTURED ALL OF THE OVERFLOW. | Y | Y | STORM DRAIN | DESILT BASIN | N/A | YES | N/A | NO | N/A | NONE
000112 | CLAY CLIFTON - FAX | 12/22/00 - 16:00 | DON WASKO | 438-2722 X 7138 | CMWD | 2000-12-22 16:00 | 12/22/00 - 16:45 | 10 | 10 | 4070 HARBOR DRIVE | CARLSBAD | SD | 92009 | TOILET OVERFLOW X 2 | 1 | ROOTS | ROOTS IN LATERAL | SNAKED OUT LATERAL | N | N | NONE | NONE | CARPETING IN THE HOUSE | YES | N/A | NO | N/A | NONE
001-003 | Clay Clifton | 12/8/00 1120 | Ron Gunnett | 760-788-2252 | Ramona Water District | 2000-12-07 14:30 | 2000-12-07 | 55 | 0.5 | Alley behind 578 Main | Ramona Calif. | San Diego | 92065 | 6" VC | 1 | Blockage | Customer pushed material when cleaning causing blockage | A private plumber rodded sewer lateral on customer side | no | no | no | no | no | no | no | no | n/a | Private spill from clean-out
001009 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2000-10-22 16:30 | 10/22/00 1640 | 50 | 50 | 975 Del Dios Hwy. | Escondido | SD | 92025 | Private cleanout | 1 | Debris | Private lateral has a low spot which collects debris. | Advised the manager to have their service lateral cleaned annually. | y | y |  |  |  | y | n | n | N/A | Private spill from clean out. No sampling required.
001010 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2000-10-23 08:20 | 10/23/00 850 | 150 | 150 | 1125 North Broadway | Escondido | SD | 92025 | Private cleanout | 1 | Other | Private system, cause unknown. | Pretreatment Inspector issued the apartment manager a Notice of Correction and will perform a follow-up inspection. | y | y | N/A | N/A | 100% recovered | y | n | n | N/A | Private spill from clean out. No sampling required.
001011 | Fax | 2000-10-24 16:00 | John Vaught | 760-839-4323 | City of Escondido | 2000-10-23 20:00 | 10/24/00 1500 | 1,140 | 100 | 516 South Tulip St. | Escondido | SD | 92025 | Private cleanout | 1 | Other | Private system, cause unknown. | City of Escondido Code Enforcement was on site investigating the incident. Our Pretreatment Inspector issue the property managers a Notice of Correction as well as informative information on how to prevent grease stoppages, which will be past along to the residents. | n | n | N/A | N/A | Soil adsorption and recovery. | y | y | y | 3 | Private spill from clean out. No sampling required.
001012 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2000-11-02 09:00 | 11/2/00 930 | 30 | 30 | 933 Inspiration Lane | Escondido | SD | 92025 | Private cleanout | 1 | Roots | Homeowner experienced excessive root growth in their service lateral which caused a blockage. | Advised the homeowner to have their service lateral cleaned annually. | n | n | N/A | N/A | 100% recovered | y | n | n | N/A | Private spill from clean out. No sampling required.
001013 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2000-11-14 10:00 | 11/14/00 1150 | 55 | 55 | 736 East 3rd St. | Escondido | SD | 92025 | Private cleanout | 2 | Roots | Plumber removed roots from service lateral. | City of Escondido Code Enforcemen was notified of the incident. The property owner was notified and is taking the required steps to rectify the situation. The property owner also met with the City's Collection System Supervisor and assured him that the problem would be rectified. | n | n | N/A | N/A | 100% recovered | y | n | n | N/A | Private spill from clean out. No sampling required.
001014 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2000-11-25 20:30 | 11/25/00 2300 | 450 | 450 | 816 East Washington Ave. | Escondido | SD | 92025 | Private cleanout | 1 | Grease | Grease stoppage in private service lateral. | The incident was reported to our Pretreatment Inspector for further investigation and enforcement. | y | y | N/A | N/A | 100% recovered | y | n | n | N/A | Private spill from clean out. No sampling required.
001015 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2000-11-29 12:10 | 11/29/00 1240 | 90 | 90 | 142 South Grape St. | Escondido | SD | 92025 | Private cleanout | 1 | Roots | Blockage was caused by excessive roots in service lateral. | Pretreatment Inspector issued the property manager a Notice of Correction. | y | y | N/A | N/A | 100% recovered | y | n | n | N/A | Private spill from clean out. No sampling required.
001016 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2000-11-29 |  | 300 | 270 | 213 East 6th. Ave. | Escondido | SD | 92025 | Sewer Atlas 388M5401 | 1 | Roots | Partial blockage in city sewer main caused by root intrusion. | The main line was inspected and will be placed on a three month root maintenance schedule. | y | y | Escondido Creek | San Elijo Lagoon | Pacific Ocean | y | n | n | N/A | No sampling required.
001017 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2000-11-30 17:25 | 11/30/00 1800 | 396 | 200 | 505 West Washington Ave. | Escondido | SD | 92025 | Private cleanout | 1 | Grease | Excessive grease in service lateral. | Our Pretreatment Inspector will issue a Notice of Correction. | y | y | Reidy Creek | Escondido Creek | Pacific Ocean | y | n | n | N/A | Private spill from clean out. No sampling required.
001018 | Victor Vasquez, Fax | 2000-12-13 16:00 | Lance Lauricha | 760-839-4347 | City of Escondido | 2000-12-13 | 12/13/00 1630 | 2000 | 200 | 3907 Sierra Linda Dr. | Escondido | SD | 92025 | Private cleanout | 1 | Line break | Broken and blocked private service lateral. | Homeowner contracted with a plumbing firm to make the necessary repairs. | y | y | Storm drain | N/A | Dissipated into soil | y | y | n | N/A | Private spill from clean out. No sampling required.
001019 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2000-12-17 09:00 | 12/17/00 1030 | 200 | 200 | 623 East Lincoln Ave. | Escondido | SD | 92025 | Private cleanout | 1 | Grease | Grease stoppage in private service lateral. | Our Pretreatment Inspector will investigate and make recommendations. | y | y | N/A | N/A | 100% recovered | y | n | n | N/A | Private spill from clean out. No sampling required.
001020 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2000-12-18 10:00 | 12/18/00 1210 | 130 | 130 | 204 East Clark St. | Escondido | SD | 92025 | Private cleanout | 1 | Roots | Root infiltration causing paper and debris to backup and overflow. | Our Pretreatment Inspector will issue a Notice of Correction to the property manager. | n | n | N/A | N/A | 100% recovered | y | n | n | N/A | Private spill from clean out. No sampling required.
001021 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2000-12-20 10:45 | 12/20/00 1145 | 160 | 160 | 204 East Clark St. | Escondido | SD | 92025 | Private cleanout | 2 | Grease | Excessive grease in service lateral, roots could also be a major factor. Numerous large trees close to service lines. | Our Pretreatment Inspector will issue a Notice of Correction to the property manager. The property manager has been contacted and is trying to address the issues. Steps to be taken are the removal of existing trees, informing residents not to discharge grease in drains and a full video inspection of the sewer pipes in the effected area. Escondido Code Enforcement will also be included in this investigation. | y | y | N/A | N/A | 100% recovered | y | n | n | N/A | Private spill from clean out. No sampling required.
001022 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2000-12-22 16:00 | 12/22/00 1722 | 1 | 0 | 417 North Cedar St. | Escondido | SD | 92025 | Private cleanout | 1 | Roots | Root infiltration caused wastewater to backup and overflow. | We recommend the homeowner clean his service lateral every six months because of large trees near his line. | n | n | N/A | N/A | Soil adsorption | y | n | n | N/A | Private spill from clean out. No sampling required.
001023 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2000-12-23 17:00 | 12/23/00 1720 | 10 | 1 | 602 South Grape St. | Escondido | SD | 92025 | Private cleanout | 1 | Line break | Service lateral was broken while the resident was digging sprinklers lines. | Property owner made the repair. | n | n | N/A | N/A | Soil adsorption / evaporation | y | n | n | N/A | Private spill from clean out. No sampling required.
001002 | Faxed RWQCB, DEH; called OES, OES HazMat, CA Fish/Game | 10/11/00 08:45 | Brad Voorhees | 858/679-5419 | City of Poway | 2000-10-10 15:10 | 10/10/00 15:40 | 1600 | 400 | 15615 Pomerado Road | Poway | San Diego | 92064 | Sewer manhole | 1 | Roots | Root growth in manhole. | Removed root infiltration from the manhole. Cleaned the 8-inch main with Vactor truck. Permanent repair (grout and epoxy seal) of manhole was completed by quarter's end. | Y | Y | Pomerado Channel (paved) | Poway Creek |  | Y | Y | Y | 3 | Signs posted at possible public access points along Pomerado Channel and Poway Creek, approximately three miles. Creek inspected daily; initial inspection showed no signs of debris or odor in storm channel. | Qtr 2/00-01
001008 | 858 571 6972 | 10/08/00 0723 | City of Laguna Beach | 949 497-0765 | Laguna Beach | 2000-10-08 07:20 | 10/08/00 0815 | 30 | 0 | 249 Broadway | Laguna Beach | Orange | 92651 | Private Lateral 249 Broadway | 0 | Grease | Plugged 4 inch lateral with grease from the restaurant | City crews contained and cleaned up the debris on the street. Plumber cleaned the plugged lateral. Police and Fire on scene to seal off the area and close the restaurant. Placed about one pound of chlorine in the gutter line and storm drain box | N | Y | None | None | flood control channel that is blocked off before Main Beach | Yes | No | No | None | Water was spread over a large area and not enough to pickup with a vacuum truck. Private Lateral
001009 | 858 571 6972 | 10/23/00 1610 | City of Laguna Beach | 949 497-0765 | Laguna Beach | 2000-10-23 16:00 | 10/23/00 1655 | 50 | 0 | 1085 Dyer Place | Laguna Beach | Orange | 92651 | 1085 Dyer Place | 0 | Roots | Very large trees next to the City main line on each side of the road | Rodded out the roots and flushed the line to remove the roots. This area (Dyer/Wykoff) will be upgraded to an 8 inch sewer line by July 2001 | N | N | None | None | Water spread out on the street and unable to vacuum | Yes | No | No | None
001010 | 858 571 6972 | 10/28/00 0951 | City of Laguna Beach | 949 497-0765 | Laguna Beach | 2000-10-28 09:51 | 10/28/00 1040 | 150 | 0 | 421 Ledroit | Laguna Beach | Orange | 92651 | 421 Ledroit | 0 | Roots | Root infiltration in the main line | Opened the main line using a rodding machine to remove the obstruction. | N | N | None | None | Wet Pavement | Yes | No | No | None
001011 | 858 571 6972 | 10/31/00 1703 | City of Laguna Beach | 949 497-0765 | Laguna Beach | 2000-10-31 17:03 | 10/31/00 1745 | 50 | 50 | 890 S. Coast Hwy | Laguna Beach | Orange | 92651 | 890 S. Coast Hwy | 0 | Grease/Motor Oil | Grease and motor oil in the City Main Line caused our system to back up. Grease from Marks Restaurant at 858 S. Coast Hwy | Jetted the main line to open up the stoppage. This let the water in the shop floor drain back into the City Sewer. The City Engineer called our Environmental Speciaist Mike Phillips to take action on Pete's Auto to correct all of the drains that are connected to the Sewer Main. | N | N | None | None | Back into the City Sewer | Yes | No | No | None
001012 | 858 571 6972 | 11/14/00 0755 | City of Laguna Beach | 949 497-0765 | Laguna Beach | 2000-11-14 07:45 | 11/14/00 0825 | 50 | 50 | 2488 Irvine Cove Crest | Laguna Beach | Orange | 92651 | Sewer Manhole at Irvine Cove Crest | 0 | Grease/Blockage | grease build up between the 8 inch gravity line and the 15 inch trunk line. There is about 30ft between them. | The City Crew rodded the 8 inch VCP trunk line and then followed up by jetting the same area. Pumped all sewage that spilled into the storm drain back into the City Sewer System. Flushed the street and storm drain with about 1000 gallons of water. | N | Y | None | None | Back into the City Sewer | Yes | No | No | None
001013 | 858 571 6972 | 11/24/00 1030 | City of Laguna Beach | 949 497-0765 | Laguna Beach | 2000-11-24 10:00 | 11/24/00 1130 | 5000 | 0 | 2400 Blk. S. Coast Hwy. | Laguna Beach | Orange | 92651 | Manhole 318 10 inch gravity line | 0 | Roots | City 12 inch trunk sewer line between Moss Street and Fern Street plugged with roots at about 200ft from Moss Street. Jetted to Fern Street. We are unablet to get to the manhole due to a parked vehicle on top of it. | Jetted the main line to open the stoppage. Flushed the storm drain with 4 pounds of chlorine with fresh water. Storm drain dumps onto a non swimming beach. No access. | Y | Y | Pacific Ocean/Rockpile Beach | Pacific Ocean/Rockpile Beach (Private) | Pacific Ocean/Rockpile Beach | Yes | Yes | Yes | 4 | None
001014 | 848 571 6972 | 12/01/00 1000 | City of Laguna Beach | 949 497-0765 | Laguna Beach | 2000-12-01 10:00 | 12/01/00 1010 | 30 | 0 | 277 Bluebird Canyon Dr. | Laguna Beach | Orange | 92651 | Private Sewer Lateral | 0 | Roots | Private 4 inch lateral plugged with tree roots between the City main line on Bluebird Canyon Drive and the home. | City personnel called the rental agent and asked them to get a plumber. They called Scotts Service & Repair to snake out the lateral. The lateral was opened and running ok by 10:55 on 12/1/00 | N | Y | None | None | Bluebird Beach / Water soaked into sand | Yes | No | No | None
01-1488 | 858-467-2952 | 3/12/01, 9:20 am | Juan Camacho | 949-443-6394 | City of San Juan Capistrano | 2001-03-11 17:06 | 3/11/01, 6:50 pm | 750 | 0 | Man hole cover on corner of Marina Rd & Village Rd | San Juan Capistrano | Orange | 92675 | Gravity Line | zero | Roots & Grease | Possible roots in line which caused greese build-up | Monitor sewer line and if necessary, add it on to trouble spot frequency | Y | Y | Storm Drain Catch Basin SD Line to Trabuco Creek | San Juan Creek @ merge 3 miles down stream to Pacific Ocean | Receiving waters were not impacted | Orange County Health Depart-ment | Y | N | n/a
101 | Rebecca Stewart | 12 Jan 01 0900 | A J Howard | 949.366.1553 | CSC | 2001-01-12 05:30 | 14 Jan 01 0330 | 985000 | 889000 | North El Camino Real @ MO2 Drainage Channel | San Clemente | OR | 92672 | Land Outfall Line to SERRA | 0 | Crack in 30 inch Ductile Iron Pipe | Cause still under investigation. John Carollo Engineer issued contract to study cause. | Bryon Crume Pipeline Contractor issued contract to make temporary repairs until actual cause of leak determined. | Y | Y | MO2 Drainage Channel | Pacific Ocean | Pacific Ocean / Treatment Plant | Y | N | Y | 6 | Preliminary SSO written report filed 12 Jan 2001 at 1340; Revised Final written SSO report filed 22 Jan 2001 at 1445; Detailed letter of response to N.O.V. 2001-32 filed on 28 February 2001; Technical Memorandum for the Land Outfall Line to SERRA by John Carollo Engineers detailing the cause and proper corrective action to finalize repairs. A copy shall be issued to the CRWQCB directly upon its completion.
102 | FAX | 3 Feb 01 1630 | J Elston | 949.366.1553 | CSC | 2001-02-03 09:00 | 3 Feb 01 1000 | 600 | 600 | 311 La Rambla | San Clemente | OR | 92672 |  | 0 | Concrete in main line | Residential contractor at 260 Vista Marina poured concrete into the sewer lateral that contractor thought was a yard drain | ColSys ops rodded line with hi velocity root saw for several hours to remove concrete. Video inspection indicates line clear of concrete. | N | Y | N/A | N/A | Vactor / Sanitary Sewer System | Y | N | N/A | N/A | Spilled contents contained in bermed up concrete drainage channel in OCTA Rail Road ROW. ColSys crews vacuumed contents into Vactor for disposal into sanitary sewer system.
103 | FAX | 21 Feb 01 0900 | J Elston | 949.366.1553 | CSC | 2001-02-20 18:00 | 20 Feb 01 1820 | 60 | 60 | 1520 De La Estrella | San Clemente | OR | 92672 | SMH C6407 | 0 | Unknown | Cause unknown. ColSys crews arrived on site, confirmed witness estimated flow rate of 3 GPM. Crews observed exiting flow contained in gutter. Line segment has no history of obstructions.ColSys crews previously cleaned line on 29 Jan 01. | ColSys ops rodded line, washed down street and vacuumed all contents. | N | N | N/A | N/A | Vactor / Sanitary Sewer System | Y | N | N/A | N/A | Spilled contents contained in gutter. ColSys crews vacuumed contents into Vactor for disposal into sanitary sewer system.
104 | FAX | 22 Feb 01 1630 | J Elston | 949.366.1553 | CSC | 2001-02-22 10:00 | 22 Feb 01 1022 | 66 | 66 | Intersection of Ave. Cota and Santa Margarita | San Clemente | OR | 92672 | SMH E8524 | 0 | Lateral Root Ball | SSO cause a result of lateral service root ball cleared from unknown residential service. Root ball removed from manhole SMH E8524. Line segment has no history of obstructions. Line last serviced on 28 November 2000 | ColSys ops repsonded with 2 Vactors; First Vactor crew set up at downstream catch basin ID CB D9418 located on S. El Camino Real to contain spill. Second Vactor set up at spill site and cleared and captured lateral root ball that cause obstruction. | N | N | N/A | N/A | Vactor / Sanitary Sewer System | Y | N | N/A | N/A
105 | FAX | 6 Mar 01 1540 | J Elston | 949.366.1553 | CSC | 2001-03-06 15:18 | 6 Mar 01 1540 | 11 | 3 | Ole Hanson Elementry School | San Clemente | OR | 92672 | Sewer cleanout on school property | 0 | Unknown | Direct cause unknown. ColSys crews previously cleaned line on 29 Jan 01. | ColSys ops rodded line from SMH D6110, cleared partial obstruction, washed down affected school area and vacuumed all contents between clean out and catch basin. | N | Y | N/A | N/A | Vactor / Sanitary Sewer System / Canyon Floor | Y | N | N/A | N/A
106 | FAX | 10 Mar 01 1110 | J Elston | 949.366.1553 | CSC | 2001-03-10 15:31 | 10 Mar 01 1626 | 13 | 13 | 1405 Alcazar | San Clemente | OR | 92672 | Sewer cleanout on private property | 0 | Roots | Roots in main line. | ColSys ops rodded line to clear obstruction and came back with roots. Crews switch to root saw and re rodded line. | N | N | N/A | N/A | Vactor / Sanitary Sewer System | Y | N | N/A | N/A | Spilled contents contained in gutter. ColSys crews vacuumed contents into Vactor for disposal into sanitary sewer system.
107 | FAX | 15 Mar 01 1500 | J Elston | 949.366.1553 | CSC | 2001-03-15 07:30 | 15 Mar 01 0750 | 6000 | 3600 | CSC Reclamation Facility 380 Avenida Pico | San Clemente | OR | 92672 | 1-1/2 inch Recycle Water Line | 0 | Contractor disturbed soil near pipe to be replaced | Contractor replacing all galvanized iron 3-inch and smaller Recycle Water lines. With the amount of line corrosion present the disturbance of soil around line caused its failure before replacement could be completed. | 2 Vactors Crews responded to vacuum contents at outlet structure to MO2 Drainage Channel until plant crews set up diversion to nearby sanitary sewer manhole. Contractor is due to be completed with galvanized pipe replacement project in May 2001. | Y | Y | MO2 Drainage Channel | Pacific Ocean | Pacific Ocean / Treatment Plant | Y | N | N/A | N/A | Reclaimed Water Leak
001-007 | SIRT (FAX) | 2001-01-15 07:45 | Brad Bruington | 949-425-3543 | Camden Development | 2001-01-14 16:40 | 2001-01-14 17:40 | 240 | 140 | La Alameda/El Regatteo | Mission Viejo | OR | 92691 | 8" gravity sewer line at manhole structure | 0 | Rocks, debris, blockage, construction | Removed approx. 1 cubic yard of gravel and plastic Gatorade bottle in sewer line of The Park at Crown Valley | Jetted and removed debris from sewer line. Video inspection of La Alameda and construction site upstream of overflow. No additional debris found. | Y | Y | Oso Creek via storm drain | Oso Creek to San Juan Creek | Pumped and vacuumed sewage into sewer | Y | N | N | 0 | Responsible party is The Park at Crown Valley, Camden Development
001-008 | SIRT (FAX) | 2001-02-06 12:45 | Brad Bruington | 949-425-3543 | Moulton Niguel Water | 2001-02-06 10:30 | 2001-02-06 10:50 | 350 | 350 | 26750 Avery Parkway | Mission Viejo | OR | 92691 | 6" PVC pressure line - forcemain | 3 | Line break | 6" PVC forcemain split approximately one foot from 45 degree fitting | Contractor removed and replaced fifteen feet of 6-inch C-900 pipe. Sewage flow was diverted using vacuum truck during repair. | N | N | None | None | Vacuum truck on site recovered 100% of overflow | Y | N | N | 0 | None
|  | 1/20/01 1550 to OR | John Fox | 949-494-8571 | Emerald Bay Service District | 2001-01-20 10:40 | 01/20/01 1130 | 100 | 100 | Pacific Coast Hwy , Rear of 241 Emerald Bay | Laguna Beach | OR | 92651 | Manhole #340 | 0 | Roots | Root blockage in 6" line. Overflowed lower manhole when blockage cleared. | Used hydrocleaner to cut roots & break blockage. Washed down contaminated area w/potable water to sewer catch basin. Preventive measures - Will TV & increase preventive maintenance. | N | N | None | None | Sewer collection system via runoff catch basin. | Orange County Health Dept. | N | N
001008 | Voice Mail | 2001-01-29 08:00 | Steve Francis | (949)459-6539 | Santa Margarita Water District | 2001-01-27 19:00 | 2001-01-27 20:30 | 100 | 25 | Winslow Street | Ladera Ranch | OR | 92688 | Manhole | 1 | Other | Sewer bulkhead was left in by the contractor when the new housing was released for occupancy. Sewage backed up into the manhole and overflowed through the pick hole into the street. | The bulkhead was removed. Sandbags were placed to contain the overflow upon arrival, and the sewage was removed from the site using the Vactor truck. The street and cub were washed and the water was removed via the Vactor unit. | N | Y | None | None | Water Detention Basin | Y | NA | N | N/A | None.
001009 | N/A | N/A | Steve Francis | (949)459-6539 | Santa Margarita Water District | 2001-02-09 09:00 | 2001-02-09 09:30 | 30 | 10 | 20811 Hidalgo | Mission Viejo | OR | 92691 | Manhole | 1 | Roots | Rootball lodged in an 8-inch sewer line causing a blockage. | Trapped and removed the rootball from the sewer line. Sandbagged the storm drain and vactored the sewage from the manhole and containment area. | N | Y | None | None | Storm Drain | Y | N/A | N | N/A | None.
001010 | Victor | 2001-02-26 09:00 | Steve Francis | (949)459-6539 | Santa Margarita Water District | 2001-02-25 14:00 | 2001-02-25 17:00 | 54000 | 11968 | 94424 Oso Parkway | Las Flores | OR | 92688 | Las Flores Lift Station | 1 | Power Failure | Moisture from the rains shorted out the control power to the pumps at the lift station. The UPS grounded out, disabling all alarms from the station to the District's SCADA system. The failure was discovered by an operator during routine rounds. The operator immediately turned the pumps on through the manual override and pumped down the wetwell. | The District is in the process of replacing the UPS and mounting it in a less vunerable location. We are also investigating the stations electrical logic to find a way to bypass the control power loop to avoid future failures. | Y | Y | Trabuco Creek | Doheny Beach | Pacific Ocean | Y | Y | Y |  | The Health Department was notified and will determine the amount of days the signs will be posted. OES tracking number assigned: #01-1161
001011 | Fax | 2001-03-04 13:30 | Dave Seymour | (949)459-6540 | Santa Margarita Water District | 2001-03-04 08:50 | 2001-03-04 09:55 | 3750 | 3150 | World Cup Soccer Center | Mission Viejo | OR | 92690 | Manhole | 1 | Vandalism | Vandals dumped large rocks and a log into the manhole. | Removed the rocks and log. Cleaned the area and returned the washwater to the sewer. We will install a bolt-down cover in this location. | Y | Y | Oso Creek | Pacific Ocean at Doheny Beach | Pacific Ocean | Y | Y | Y |  | The Health Department was notified and will determine the amount of days the signs will be posted. OES tracking number assigned: #01-1294.
001012 | Quarterly Report | N/A | Dave Seymour | (949)459-6540 | Santa Margarita Water District | 2001-03-10 09:35 | 2001-03-10 09:40 | 75 | 75 | El Paseo near Pacific Park | Mission Viejo | OR | 92690 | Manhole | 1 | Construction | Doty Bros. Construction is performing work on sewers in the area. Their sewer bypass pumps were unable to handle peak flow. | The contractor removed the plug from the line and allowed the sewage to flow by gravity. The contractor and SMWD staff placed sandbags to contain all of the spill. We hosed down the parking lot and recovered all of the spill and wash water. | N | N | None | None | Returned to sewer. | Y | N | N
01-001 | Todd (via phone) | 2001-01-23 08:00 | Shawn Atherton | 760-753-5018 | City of Encinitas | 2001-01-22 17:30 | 2001-01-22 18:30 | 2500 | 500 | 2156 Manchester Avenue | Encinitas | SD | 92007 | 261-06-D127 | 0 | Roots | Large root ball | Sewer line cleaned with combination sewer cleaner (scheduled for TV) | Y | Y | Storm drain system | San Elijo Lagoon | San Elijo Lagoon | Y | Y | Y | 2
01-002 | Quarterly Report | 4/1/01 0:01 | Shawn Atherton | 760-753-5018 | City of Encinitas | 2001-03-27 19:00 | 2001-03-27 19:25 | 600 | 0 | D Street at Vulcan Avenue | Encinitas | SD | 92024 | D48-Encinitas14 | 0 | Unknown | Unknown, call came in at 7:00PM as overflowing manhole. Arrived on-site at 7:40PM and could not find blockage. Found reporting person and he said stopped spilling at 7:20PM. | Line was cleaned, no types of debris or blockage noted. Cleaning schedule has been increased. | N | Y | Storm drain system | Ocean outfall | Ocean outfall | N | N | N | N/A
1 | Voice Mail - John Philips | 1/26/2001 13:30 AM | John Pastore | 760 942-5147 | Rancho Santa Fe CSD | 2001-01-26 13:00 | 2001-01-26 15:00 | 2600 | 2340 | La Granada | Rancho Santa Fe | SD | 92067 | FM - AV1 | 0 | Line Break | A 2-inch copper line from the force main to the air-vac device ruptured and caused the pipe to leak beneath the street. | The broken segment of pipe was found and replaced with a new section of copper pipe. | Y | N | Rancho Santa Fe Golf Course | None |  | Y | Y | Y | 5 | The overflow was contained in a channel and 24,000 gallons of water was pumped back into the sewer.
000113 | CLAY CLIFTON - FAX | 01/05/01 - 11:00 a.m. | DON WASKO | 438-2722 X 7138 | CMWD | 2001-01-03 08:30 | 01/03/01 - 9:30 a.m. | 600 | 1000 | CHESTNUT AVENUE, 100 YARDS EAST OF SIERRA MORENA | CARLSBAD | SD | 92008 | MANHOLE | 1 | DEBRIS | PIECES OF BROKEN ASPHALT CAUSED BLOCKAGE OF SEWER MAIN IN EASEMENT SOUTH CHESTNUT. MANHOLE ON CHESTNUT OVERFLOWED. | WE CLEANED THOSE SECTIONS OF SEWER MAIN AND REMOVED DEBRIS. WASHED DOWN STREET AND DISINFECTED AREA, VACTORED UP FROM STORM DRAIN BOX. | Y | Y | STORM DRAIN BOX ON CHESTNUT | WE VACTORED OUT THAT BOX. | N/A | YES | N/A | NO | N/A | NONE
000114 | CLAY CLIFTON - FAX | 02/05/01 - 15:30 | DON WASKO | 438-2722 X 7138 | CMWD | 2001-02-05 13:00 | 02/05/01 - 14:00 | 100 | 300 | 2515 EL CAMINO REAL | CARLSBAD | SD | 92008 | PRIVATE SEWER CLEANOUT | 3 | GREASE & FOOD DEBRIS | HEAVY DEBRIS IN SEWER LATERAL SYPHON CAUSED BACK-UP. | THE RESTAURANT NEEDS TO ROD OR JET THIS LINE TO PREVENT DEBRIS FROM BUILDING UP. | N | N | STORM DRAIN IN PARKING LOT, WE VACTORED UP ALL OVERFLOW | NONE | THE STORM DRAIN - WE CLEANED AND SANITIZED THE PARKING LOT. | YES | N/A | NO | N/A | THIS WAS THE THIRD SPILL THERE.
000115 | CLAY CLIFTON - FAX | 02/04/01 - 10:30 a.m. | DON WASKO | 438-2722 X 7138 | CMWD | 2001-02-04 10:30 | 02/04/01 - 11:15 a.m. | 15 | 0.75 | 2715 MADISON STREET | CARLSBAD | SD | 92008 | LATERAL CLEANOUT | 1 | DEBRIS | UNKNOWN DEBRIS CAUSED STOPPAGE AT LATERAL CLEANOUT. | RODDER LINE TO MAKE FLOW GOING | N | N | NONE | NONE | RECOVERED WITH VACTOR, CLEANED AND SANITIZED THE AREA | YES | NO | NO | N/A
000116 | CLAY CLIFTON - FAX | 02/25/01 - 13:00 | DON WASKO | 438-2722 X 7138 | CMWD | 2001-02-25 13:00 | 02/25/01 - 13:30 | 30 | 30 | 2700 STATE | CARLSBAD | SD | 92008 | INSIDE STORE | 1 | ROOTS & GREASE | ROOT & GREASE BUILD UP IN MAIN CAUSED IT TO BACKUP ALL THE WAY INTO LIQUOR STORE. WATER CAME OUT TOILET AND CLEANOUT UNDER A SINK. SPILLING ONTO LIQUOR STORE FLOOR. | VACTORED OUT SEWER MAIN UP TO FLOODED MANHOLE NEXT TO LIQUOR STORE. THIS MEASURE CLEARED BLOCKAGE AND CLEARED WATER OUT OF LIQUOR STORE LATERAL. THIS IS A PRIVATE MAIN AND NEEDS TO BE CARED FOR BY RESIDENTS & BUSINESS OWNERS IN AFFECTED AREA. | N | N | NONE | NONE | VACUUMED UP AND POURED BACK DOWN TOILET LEADING TO SEWER | YES | N/A | NO | N/A | NONE
000118 | CLAY CLIFTON - FAX | 03/08/01 - 8:00 a.m. | DON WASKO | 438-2722 X 7138 | CMWD | 2001-03-06 06:00 | 03/06/01 - 10:00 a.m. | 100 | 500 | 6700 BLOCK FO MALLEE COURT (ON EASEMENT JUST WEST OF THAT LOCATION) | CARLSBAD | SD | 92009 | MANHOLE | 1 | DEBRIS CONSTRUCTION | 400 FEET OF ROPE FROM CONSTRUCTION CLOGGED 8" EASEMENT SEWER MAIN. | KEEP CONSTRUCTION DEBRIS OUT OF OUR SYSTEM. | Y | Y | STORM DRAIN GRATE NEXT TO MANHOLE | STORM DRAIN BOX 150' TO THE WEST. | WE RECAPTURED OUT OF THAT STORM DRAIN BOX BACK INTO OUR SYSTEM | YES | N/A | NO | N/A | NONE
000119 | CLAY CLIFTON - FAX | 03/15/01 - 15:20 | DON WASKO | 438-2722 X 7138 | CMWD | 2001-03-09 16:00 | 03/09/01 - 17:00 | 50 | 0 | IMPALA/PALMER | CARLSBAD | SD | 92008 | PRIVATE LIFT STATION | 1 | PUMP STATION FAILURE | PRIVATE LIFT STATION FAILED CAUSING MANHOLE TO OVERFLOW | LANDLORD (THE MULLER COMPANY) SHOULD MAINTAIN THE LIFT STATION | Y | Y | STORM DRAIN @ IMPALA/PALMER | NONE | RAVINE BELOW STORM DRAIN OUTLET. VERY THICK BRUSH. | YES | N/A | NO | N/A | NONE
000120 | CLAY CLIFTON - FAX | 03/16/01 - 14:00 | DON WASKO | 438-2722 X 7138 | CMWD | 2001-03-16 09:30 | 03/16/01 - 10:30 A.M. | 60 | 200 | 840 CARLSBAD VILLAGE DRIVE | CARLSBAD | SD | 92008 | PROPERTY LINE CLEAN OUT | 1 | ROOTS | ROOTS IN LATERAL CAUSED BACK INTO UNION BANK 840 CARLSBAD VILLAGE DRIVE | WE RODDED AND CLEANED THE LATERAL | Y | Y | STORM DRAIN BOX GRAND/JEFFERSON | NONE | WE RECAPTURED AT S.D. BOX GRAND/MADISON | YES | N/A | NO | N/A | NONE
00-1 | Voice/Fax | 01/09/2001 8:30:AM | Leo Schempp | 760-753-0155 | Leucadia County Water District | 2001-01-09 06:55 | 2001-01-09 07:23 | 28400 | >500 | La Costa Ave | Carlsbad | SD | 92009 | 4 inch air/vacuum release device | 0 | Other | Mechanical failure of air/ vacuum release device (internal disk came off closing mechanism) | LCWD staff opened and inspected all other devices on this line and checked for signs of mechanical defects | Y | Y | Batiquitos Lagoon | Ocean at South Carlsbad Beach | Ocean | Y | Y | Y | 6 days | Failure of air/vacuum release due to failure of internal mechanism that holds orifice plate
00-2 | Voice/Fax | 03/05/2001 18:00PM | Leo Schempp | 760-753-0155 | Leucadia County Water District | 2001-03-05 15:45 | 03/05/2001 16:20 PM | 300 | 250 | 1435 Encinitas Blvd. | Encinitas | SD | 92024 | 3 1/2 Lateral Cleanout | 0 | blockage | Suspect blockage due to construction on private premises | Business owner notified of his responibility to maintain on private property in proper working order | Y | Y | Encinitas Creek | Batiquitas Logoon | Ocean | Y | N | N | NA | private property overflow, private spill from cleanout.
00-3 | Voice/Fax | 03/21/2001 22:30:PM | Leo Schempp | 760-753-0155 | Leucadia County Water District | 2001-03-21 19:15 | 03/21/2001 19:50:PM | 4900 | 4000 | 1960 La Costa Ave | Carlsbad | SD | 92024 | Gravity Manhole | 0 | Pump station failure | Mechanical failure of pressure switch on wetwell level controller | Pressure switch replaced by electrical contractor and system doubled checked for proper operation | N | N | NA | NA | NA | Y | Y | NA | NA | Failure of pressure switch for pump station's level controller
001016 | Victor Vasques | 2001-01-08 11:40 | Mark Patnode | 7604355840 | Water Utilities Dept. City of Oceanside | 2001-01-08 08:05 | 2001-01-08 08:20 | 75 | 0 | 1936 Sonja Court | Oceanside | SD | 92054 | City Manhole | 1 | Roots | Tree roots on Sonja Court caused blockage in 8 inch sewer line, causing manhole on Palmer Drive to spill. | Confined Space Entry into manhole was made to remove tree roots. Line will be TV'd this week to check need for offset joint repairs. | Y | Y | Storm Drain on 2100 block of Palmer Drive. | None | Grass on Golf Course | Y | N | N | 0 | Vactor trucks had no entry to p/u spill on Golf Course grass.
001017 | Victor Vasques | 2001-01-29 13:22 | Mark Patnode | 7605350535 | Water Utilities Dept. City of Oceanside | 2001-01-29 12:10 | 2001-01-29 12:20 | 150 | 150 | 3458 Los Mochis Way | Oceanside | SD | 92056 | City Manhole | 1 | Grease | Grease & rags in City line caused manhole to overflow. | Line was Jet Rodded by City crew. Street & storm drain was cleaned by City Vactor trucks. | Y | Y | Storm drain on Los Mochis Way | Storm drain box on Tiberon. | Storm drain box on Tiberon. | Y | N | N | 0 | Vactor truck intercepted flow in storm drain box on Tiberon to prevent flow from entering Buena Vista Creek. Other Vactor broke stoppage and cleaned street. 100% recovery.
001018 | Victor Vasques | 02/27/01 1420 | Jeremy Kemp | 7604355842 | Water Utilities Dept. City of Oceanside | 2001-02-27 10:15 | 02/27/01 1030 | 300 | 0 | College Blvd./78 Freeway | Oceanside | SD | 92056 | City Manhole | 1 | Grease | Heavy grease build up in the ten (10) inch sewer line. | Area will be added to list for chlorine treatment. | Y | Y | Buena Vista Creek | Buena Vista Lagoon | N/A | Y | N | N | 0 | Quick response limited the spill amount. Recovery was not possible due to HEAVY rain runoff.
001019 | Victor Vasques | 03/20/01 1630 | Jeremy Kemp | 7604355842 | Water Utilities Dept. City of Oceanside | 2001-03-20 15:30 | 03/20/01 1545 | 200 | 75 | 3225 Roymar Road | Oceanside | SD | 92054 | City Manhole | 1 | Grease | Heavy grease in city line. | Line cleaned by vactor. Area turned in to Industrial Waste Inspector to check on Restaurants for G.I.'s. | Y | Y | Flood Control Channel | None | Soaked into Channel. | Y | N | N | 0 | City recovered 75 Gallons of spill.
001020 | Voice Mail | 03/21/01 2135 | Mike Heiser | 7604355870 | Water Utilities Dept. City of Oceanside | 2001-03-21 19:32 | 03/21/01 1935 | 60 | 0 | 2659 Via Del Prado | Oceanside | SD | 92054 | City Manhole | 1 | Vandalism | Debris thrown into manhole. Roots were also present. Found lid off the ring and upside down. | Locking Lid will be put on the manhole and line will be checked monthly. | Y | Y | Storm Drain Channel. | None | Soaked into Channel. | Y | N | N | 0 | A large wooden stake was in the manhole. Used it to pry out the debris of the stoppage. No recovery due to small amount in the storm drain channel.
010201 | FAX | 2001-02-22 08:00 | KEVIN MILLER | (760) 728-1178 | RAINBOW MWD | 2001-02-22 04:30 | 2001-02-22 05:30 | 1200 | 0 | 30516 Old River Road | BONSALL | SD | 92003 | 31D-M010 | 0 | PUMP STATION FAILURE. | LEVEL CONTROL FAILURE RESULTING IN THE PUMP TO BE AIR LOCKED. | REPLACED FAULTY LEVEL CONTROL SWITCH. ADJUSTED WET WELL LEVEL CONTROL SWITCHES. | N | N | N/A | N/A | OPEN FIELD, HEAVY BRUSH | Y | N | N | 0 | FAILURE OF A LEVEL CONTROL SWITCH CAUSED PUMPS AT THE SEWER LIFT STATION TO AIR LOCK. THE STATION WET WELL WAS THEN AT A HIGH LEVEL BUT IT WAS WORKING OFF THE REMAINING PUMP. A HIGH FLOW CAUSED THE STATION TO SPILL FOR A SHORT PERIOD OF TIME. THE STATION THEN RECOVERED AND BEGAN WORKING AGAIN. WHEN NOTIFIED OF THE SPILL, THE STATION HAD RECOVERED AND WAS NOT SPILLING WHEN CREW ARRIVED.
001-224 | Clay Clifton | 03-21-01 1400 | Ron Gunnett | 760-788-2252 | Ramona Water District | 2001-03-21 08:01 | 3-21-01 1150 | 200 | 180 | Alley behind 453 Main | Ramona Calif. | San Diego | 92065 | 6' VC | 1 | Blockage | Rags | Removed Blockage | yes | no | no | no | no | no | no | no | n/a | Rag blockage was removed
001003 | FAX | 2001-03-21 08:58 | Neil Cole | 858 720-2470 | City of Solana Beach | 2001-03-20 16:30 | 3/20/200118:45 | 675 | 0 | 600 Block of Stevens Ave. | Solana Beach | San Diego | 92075 | Manhole | 1 | Grease clogged main line | Grease clogged main line | Cleaned main line with a VACON Truck | Y | N | Stevens Creek | San Dieguito River and pacific Ocean | Pacific Ocean | Y | Y | Y |  | Signs osted and removed by City of Del Mar Lifeguards | Disk submitted was unreadable. Data was copied from hardcopy provided by City of Solana Beach.
001024 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2001-01-04 09:56 | 2001-01-04 10:30 | 170 | 170 | 719 S. Midway | Escondido | SD | 92025 | Sewer Atlas Manhole 351M4799 | 1 | Construction | A 150' rope was removed from the manhole that overflowed. More than likely the rope came from a near by construction site. | The main line segment was CCTV on 1/8/01 and revealed no structrual problems. Engineering Field Inspection was notified of the rope issue. | y | y | N/A | N/A | Recovered and returned to wastewater system | y | n | n | 0 | No samples required.
001025 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2001-01-04 10:05 | 2001-01-04 10:50 | 225 | 225 | 1006 N. Ash St. | Escondido | SD | 92025 | Sewer Atlas Manhole 308M3062 | 1 | Grease | Excessive grease build up. This main line is a blind tie. A manhole needs to be installed on the downstream side to be properly cleaned. | This main will be cleaned every three months till a sewer capital project is completed to rectify the problem. This project is currently in the design stage. | y | y | N/A | N/A | Recovered and returned to wastewater system | y | n | n | 0 | No samples required.
001026 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2001-01-15 18:30 | 2001-01-15 19:05 | 70 | 70 | 777 S. Tulip | Escondido | SD | 92025 | Private Cleanouts | 1 | Roots | Excessive root build up in private lateral. | The incident will be investigated further by our Pretreatment Inspector. | n | n | N/A | N/A | Recovered and returned to wastewater system | y | n | n | 0 | No samples required.
001027 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2001-01-17 10:25 | 2001-01-17 11:00 | 70 | 70 | 637 W. 9th | Escondido | SD | 92025 | Private Cleanout | 1 | Grease | Excessive grease build up in private lateral. | Referred to our Pretreatment Inspector. | n | n | N/A | N/A | Recovered and returned to wastewater system | y | n | n | 0 | No samples required.
001028 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2001-01-28 10:00 | 2001-01-28 18:00 | 960 | 500 | 659 S. Spruce | Escondido | SD | 92025 | Private sewer system | 1 | Roots | Excessive root build up in private sewer system. | This is a private collection system that services 8 - 10 residents. This is not a City maintained asset. | y | y | N/A | N/A | Recovered and absorption to soil. | y | y | y | 0 | No samples required.
001029 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2001-02-02 14:30 | 2001-02-02 15:00 | 60 | 60 | 1140 N. Rose | Escondido | SD | 92025 | Private Cleanout | 2 | Roots | Excessive root build up in private sewer system. | City repair crew assisted homeowner in repairing their service lateral. | n | n | N/A | N/A | Recovered and returned to wastewater system | y | n | n | 0 | No samples required.
001030 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2001-02-05 11:00 | 2001-02-05 13:40 | 480 | 360 | 649 W. Mission | Escondido | SD | 92025 | Private Cleanout | 2 | Grease | Excessive grease build up in private lateral. | Our Pretreatment Inspector issued a Notice of Correction to the property owners. A notice of Correction was also issued in Febuary of 2000 for failure to maintain their service lateral. Subsequent inspections are taking place. | y | y | Escondido Creek | San Elijo Lagoon | Pacific Ocean | y | n | n | 0 | No samples required.
001031 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2001-02-17 12:00 | 2001-02-17 13:30 | 90 | 0 | 1632 Dichoso Rd. | Escondido | SD | 92025 | Private Cleanout | 1 | Roots | Excessive root build up in private lateral. | The property owner was issued a Notice of Correction. | n | n | N/A | N/A | Soil absorption | y | n | n | 0 | No samples required.
001032 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2001-02-20 12:30 | 2001-02-20 14:10 | 100 | 80 | 200 N. Ash | Escondido | SD | 92027 | Private Cleanout | 2 | Roots | Excessive root build up in private lateral. | A Notice of Correction was issued to the property owners. | n | n | N/A | N/A | Recovered and absorption to soil. | y | n | n | 0 | No samples required.
001033 | Mark Alpert | 2001-02-27 14:35 | Darrel Hale | 760-839-6299 | City of Escondido | 2001-02-25 21:00 | 2001-02-25 23:45 | 40000 | 0 | 1521 S. Hale | Escondido | SD | 92029 | Reclained water pipe | 2 | Construction | Pipe connects reclaimed water pump station to equalization pond. Pipe has attached standpipe with blind flange. Contractor had blind flange removed. On Sunday 2/25/01, higher than average flow created by rain resulted with a high pond level which overflowed the standpipe. | Flange was replaced with seal and bolts. | y | y | Escondido Creek | San Elijo Lagoon | Pacific Ocean | y | y | y | 6 | Samples were taken.
001033 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2001-03-01 12:45 | 2001-03-01 13:45 | 120 | 120 | 950 E. Pensylvania | Escondido | SD | 92025 | Private Cleanout | 1 | Roots | Probable root build up. | The property owner will have their lateral inspected by a plumber. A Notice of Correction was issued. | n | n | N/A | N/A | Recovered and returned to wastewater system | y | n | n | 0 | No samples required.
001035 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2001-03-01 17:00 | 2001-03-01 17:40 | 60 | 60 | 749 Nancy | Escondido | SD | 92025 | Private Cleanout | 1 | Roots | Excessive root build up in private lateral. | Property owner was issued a Notice of Correction. | n | n | N/A | N/A | Recovered and returned to wastewater system | y | n | n | 0 | No samples required.
001036 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2001-03-04 20:00 | 2001-03-04 20:20 | 20 | 20 | San Pasqual and Viento Velle | Escondido | SD | 92025 | Sewer force main vacuum/air release valve. | 2 | Debris | Debris caused valve to not seal properly. | The valve was removed and rebuild. | n | n | N/A | N/A | Soil absorption | y | n | n | 0 | No samples required.
001037 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2001-03-10 13:00 | 2001-03-10 14:00 | 100 | 100 | 1204 N. Broadway | Escondido | SD | 92025 | Private Cleanout | 2 | Debris | Excessive debris with some grease and roots. Lack of maintenance. | A Notice of Correction was issued to the property owners. | y | y | N/A | N/A | Recovered and returned to wastewater system | y | n | n | 0 | No samples required.
001038 | Victor Vasquez | 2001-03-26 17:00 | Lance Lauricha | 760-839-4347 | City of Escondido | 2001-02-22 10:40 | 2001-03-24 16:20 | 1500 | 10 | 2467 Canyon Rd. | Escondido | SD | 92025 | Private Cleanout | 1 | Roots | Excessive root build up in private lateral. | The property owner was advised to repair their service lateral and remove any roots in the line. | y | y | Storm system | Kit Carson Creek / Dead Horse Creek | Lake Hodges | y | y | y | 3 | Samples were taken.
001039 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2001-03-25 17:45 | 2001-03-25 19:20 | 950 | 250 | 910 Del Dios Hwy. | Escondido | SD | 92025 | Private Cleanout | 2 | Grease | Excessive grease / rags / debris. Lack of maintenance, possible structural problems in private lateral. | City of Escondido Code Enforcement will be notified of the problem, as well as our Pretreatment Inspector. An investigation into their maintenance activities will be conducted to establish liability. This apartment comples has been counseled in the past on the importants of grease reduction and a preventive maintenance program. | y | y | Escondido Creek | San Elijo Lagoon | Pacific Ocean | y | n | y | 3 | No samples required.
001040 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2001-03-26 15:30 | 2001-03-26 15:50 | 200 | 200 | 2094 E. Grand Ave. | Escondido | SD | 92025 | Private Cleanout | 1 | Roots | Excessive grease / roots / debris. Lack of maintenance. | A Notice of Correction was issued to the apartment managers. | n | n | N/A | N/A | Recovered and returned to wastewater system | y | n | n | 0 | No samples required.
001041 | N/A | N/A | N/A | 760-839-4323 | City of Escondido | 2001-03-29 07:55 | 2001-03-29 08:10 | 600 | 500 | 14th and Kalmia St. | Escondido | SD | 92025 | Sewer Atlas Manhole 408M5628 | 1 | Grease | Excessive grease due to root intrusion from private service lateral. | The television inspection revealed heavy root intrusion from private service laterals. The property owners were notified of their responsibility to clean their laterals. This main line will also be maintained on our three month cleaning schedule. | y | y | Storm system | Dead Horse Creek | Lake Hodges | y | n | n | 0 | No samples required.
OOO129 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2001-01-04 14:30 | 2001-01-04 15:50 | 30 | 5 | 317 Sunbeam | Fallbrook | SD | 92028 | Manhole | 1 | Roots | Roots down stream 5 feet from manhole G13. | Ran rodder off flush truck 535 feet up 6" line from G22. | N | N | NA | NA | Soaked in dirt bank and evaporated on asphalt driveway. | N | N | N | NA
OOO130 | 858-571-6972 | 2001-01-08 10:55 | Patti S. Page | (760)723-5640 | Fallbrook Public Utility District | 2001-01-07 11:38 | 2001-01-07 12:10 | 100 | 100 | 818 Magarian | Fallbrook | SD | 92028 | Cleanout | 1 | Blockage | Blockage in mainline made sewer overflow in cleanout which was lowest point on street. | Flushed mainline and hit blockage at 252 feet from downstream manhole. Washed down area. Vacuumed up site and sanitized. | N | Y | * Ostrich Creek | San Luis Rey River | *Vacuumed up water in dirt dam and storm drain. | Y | N | N | NA | Storm drain was plugged with dirt. Flushed and vacuumed out all overflow plus 100 additional gallons from storm drain. No public access into storm drain area.
OOO131 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2001-01-10 09:21 | 2001-01-10 09:50 | 30 | 25 | 313 Elbrook | Fallbrook | SD | 92028 | Cleanout | 1 | Roots | Paper and roots in lateral. | Rodded line and pulled back small amount of roots. Cleaned up area and disinfected. Washed sidewalk and swept water into cleanout. | N | N | NA | NA | Sidewalk & cleanout by house. | N | N | N | NA | Private lateral - courtesy notification.
OOO132 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2001-01-13 08:45 | 2001-01-13 09:30 | 10 | 5 | 313 Elbrook | Fallbrook | SD | 92028 | Cleanout | 2 | Roots | Blockage with roots. | Rodded lateral. Cleaned up solids and toilet paper. Plan to dig up and repair root intrusion on 1-16-01. | N | N | NA | NA | Sidewalk & cleanout by house. | N | N | N | NA | Private lateral - courtesy notification.
OOO133 | 858-571-6972 | *2/23/01 12:56 | Joe Polzin/Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2001-02-18 09:00 | 2001-02-18 09:45 | 300 | 0 | 1425 S. Alturas | Fallbrook | SD | 92028 | Lift Station | 1 | Pump Station Failure | #1 pump contact wouldn't reset. After two or three times it finally reset. | Set up three pumps for backup. Also called an electrician in to check it out. | Y | Y | Fallbrook Creek | Lake O'Neil |  | Y | Y | Y | 3 | * There was an inadvertent error in reporting this overflow to the Reg. Brd. within the 24 hour reporting period. Personnel believed notification had been made. (Notification was made on 2/18/01 to County Health and OES.) Faxed notification to Reg. Brd
OOO134 | 858-571-6972 | 2001-02-22 14:00 | Patti S. Page | (760)723-5640 | Fallbrook Public Utility District | 2001-02-22 08:00 | 2001-02-22 08:30 | 200 | 20 | 1210 S. Vine | Fallbrook | SD | 92028 | Cleanout | 1 | Other | Paper towels in lateral. | Rodded lateral. Cleaned up area with wash down water. Vacuumed up. | Y | Y | *None - Unknown | NA | *Do not know where this storm drain empties. In dry weather condition, do not believe this spill entered receiving waters. | Y | N | N | NA | Private lateral - courtesy notification. Cleanout plugged with paper towels about 4 feet down. Used wash down water to clean up. All of wash down water was recovered, plus 20 gallons of overflow. Could not get access to County storm drain to recover.
OOO135 | SD County Health | 2001-03-08 12:30 | Eddie Taylor | (760)728-1125 | Fallbrook Public Utility District | 2001-03-08 11:30 | 2001-03-08 12:00 | 60 | 0 | 1125 Hillcrest | Fallbrook | SD | 92028 | Cleanout | 1 | Roots & Grease | Combination of grease and root plug in mainline. | Rodded mainline opened about 5 feet in downstream manhole. | N | N | NA | NA | Percolated into ground in yard. | Y | N | N | NA | Sewage soaked into ground. Disinfected area where possible.
OOO136 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2001-03-13 13:26 | 2001-03-13 14:00 | 60 | 0 | 1138 E. Alvarado | Fallbrook | SD | 92028 | Manhole | 1 | Roots & Grease | Roots and grease in mainline. | Rodded mainline and opened at about 160 feet. | N | N | NA | NA | Dried up in roadway. | N | N | N | NA | Sewage dried up before any could be recovered.
OOO137 | RWQCB | 2001-03-26 14:00 | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2001-03-26 06:50 | 2001-03-26 07:20 | 1250 | 1250 | 990 E. Mission | Fallbrook | SD | 92028 | Manhole | 2 | Roots & Grease | Roots and grease in mainline. | Unstopped mainline. Posted signs. Vacuumed creek & diverted/dammed area for a total of 5000 gallons vactored. Will video between manholes to determine problem. | Y | Y | Fallbrook Creek | Lake O'Neil |  | Y | Y | Y | 3 | Overflow entered concrete gutter and flowed into open dirt channel and into open 6' storm drain. Dammed up & immediately vactored 1000 gal of spill. Also dammed 1/2 mile downstream below spill plume and then vactored 4000 gal including plume. It is bel
OOO138 | Quarterly |  | Joel V. Holt | (760)723-5640 | Fallbrook Public Utility District | 2001-03-19 07:20 | 2001-03-19 08:00 | 25 | 25 | 1232 Juliette Place | Fallbrook | SD | 92028 | Cleanout | 1 | Roots & Grease | Grease and roots in mainline. | Flushed mainline and unblocked stoppage 345 feet east of manhole G129. | N | N | NA | NA | Ran about 150 feet down the road and vacuumed up. | N | N | N | NA | Contained spill with 2 dirt burms and then vacuumed up. Also vacuumed up all wash down water. Stoppage was in mainline, but came out of cleanout. Burms were 25' from cleanout and 150' down the road.
OOO139 | 858-571-6972 | 2001-03-30 07:30 | Eddie Taylor | (760)728-1125 | Fallbrook Public Utility District | 2001-03-29 20:15 | 2001-03-29 20:45 | 400 | 100 | E. Fallbrook Street & Vine Street | Fallbrook | SD | 92028 | Manhole | 1 | Roots & Grease | Combination of roots and grease in manhole. | Flushed and opened mainline about 5' in line. | Y | Y | Fallbrook Creek | Lake O'Neil | Also some overflow on blacktop and pavement. Dried up and disinfected area. | Y | N | Y | 3 | Vacuumed 1000 gal out of creek. Sand bagged and contained all wash down water. Vacuumed out in two different places in the creek at the point of entry down further along creek. Total of 1300 gal recovered. Disinfected spill area on blacktop & pavement
1001 | Quarterly Report | 8/31/2000 0835 | Rich Arrant | 760-744-0460 | V.W.D. | 2000-08-31 08:35 | 8/31/2000835 | 23200 | 0 | Camino Vida Roble | Carlsbad | S.D. | 92009 | Reclaim Water Line | 0 | Corrosion | Corrosion in bottom of pipe | Replaced corroded sections of pipe | No | Yes | San Marcos Creek | Ocean | Ocean | Yes | No | No | 0 | Reclaimed Water Line
1002 | Victor Vasquez | 4/13/01 1639 | Rich Arrant | 760-744-0460 | V.W.D. | 2001-04-13 15:00 | 4/13/01 1600 | 300 | 300 | Red Wing St. | San Marcos | S.D. | 92069 | Man Hole | 0 | Debris | Bad dip in line | Replaced sections of pipe to correct problem | No | Yes | N/A | N/A | Storm Drain | Yes | No | No | 0 | See report
1001 | Victor Vasquez | 4/3/01 1600 | Rich Arrant | 760-744-0460 | V.W.D. | 2001-04-03 12:20 | 4/3/01 1306 | 50 | 50 | Bent Ave. | San Marcos | S.D. | 92069 | 8" Gravity line | 0 | Debris | Grit and Sand caused blockage | Line was cleaned and Videoed | Yes | Yes | San Marcos Creek | N/A | N/A | Yes | No | No | 0 | Tracking numbers are out of
1003 | Voice Mail | 6/3/01 1517 | Rich Arrant | 760-744-0460 | V.W.D. | 2001-06-03 10:00 | 6/3/01 1256 | 10580 | 0 | Woodward and Vineyard Steets | San Marcos | S.D. | 92069 | Man Hole | 0 | Vandalism | Caused by rock, pipe, 5 gal buckets, a 2x6 and concrete sacks. | Cleared debri from manhole and vactored. Jetted lines that were impacted by this Vandalism. | Yes | Yes | San Marcos Creek | San Marcos Creek | N/A | Yes | Yes | Yes | 3 | Sheriffs report was filed
1004 | Casey Hunt | 6/7/01 1440 | Rich Arrant | 760-744-0460 | V.W.D. | 2001-06-07 12:01 | 6/7/01 1251 | 10 | 10 | Bennett Ave. | San Marcos | S.D. | 92069 | 8" Gravity line | 0 | Grease | Grease blockage caused problem. | Cleared blockage and added to trouble spot list. | No | Yes | N/A | N/A | Storm Drain | Yes | No | No | 0 | None
001-009 | SIRT (FAX) | 2001-04-03 12:00 | Brad Bruington | 949-425-3543 | Moulton Niguel Water | 2001-04-01 09:15 | 2001-04-01 12:38 | 900 | 200 | 18 South Peak | Laguna Niguel | OR | 92677 | 8" PVC gravity sewer line | 1 | Debris, blockage | Asphalt contractor allowed asphalt slurry to enter two or more manholes through pick holes. Normal sewer debris collected around slurry. | Cleared stoppage with jet rodder. Used root cutter equipment to break-up and remove black street slurry material. Video-inspected. Line clear, no damage. | Y | Y | Storm drain to Salt Creek | Pacific Ocean, at Salt Creek Beach | 200 gallons recovered to Vacuum truck | Y | N | Y | 3
001-010 | SIRT (FAX) | 2001-04-03 11:30 | Brad Bruington | 949-425-3543 | Moulton Niguel Water | 2001-04-01 14:00 | 2001-04-02 07:00 | 18500 | 0 | Trabuco Lift Station | Mission Viejo | OR | 92691 | Manhole on 8" gravity line | 4 | Power failure | Trabuco Lift Station lost one phase of three-phase commercial power supply from SDG&E. The circumstances caused the pump motor starters and the high level alarm to fail. The one phase lost was not enough to trigger the power-loss alarm. | Electrician was able to re-start one pump at approximately 0700. SDG&E replaced faulty equipment and restored full electrical power to station by 1500. Station is being removed from service. | Y | Y | 36" storm drain to Trabuco Creek | Pacific Ocean at Doheny Beach |  | Y | N | Y | 3
001-011 | SIRT (FAX) | 2001-04-03 12:00 | Brad Bruington | 949-425-3543 | Moulton Niguel Water | 2001-04-02 12:55 | 2001-04-02 13:15 | 700 | 200 | Las Ramblas and Puerta Real | Mission Viejo | OR | 92691 | 8" gravity sewer line |  | Rocks, debris, blockage | 1" gravel from upstream construction site collected normal sewer debris. | Line jet-rodded to remove debris. Video inspection found no other problems in line. | Y | Y | Storm drain to Oso Creek | Pacific Ocean at Doheny Beach | Recovered flow in vacuum truck | Y | N | Y | 3
001-012 | SIRT (FAX) | 2001-04-04 09:40 | Brad Bruington | 949-425-3543 | Moulton Niguel Water | 2001-04-02 16:00 | 2001-04-03 13:30 | 880 | 100 | Moulton and Luisa | Laguna Hills | OR | 92653 | 8" VCP gravity easement sewer line | 1 | Roots, blockage, line break | Partial line stoppage due to roots, which cracked sewer line. | Jet-rodded line to remove roots and return to normal flow. Sewer line will be repaired or replaced within one week. | Y | Y | Storm drain to La Paz channel, to Aliso Creek | Pacific Ocean at Aliso Creek Beach |  | Y | N | Y | 3
001-013 | SIRT (FAX) | 2001-04-11 19:15 | Brad Bruington | 949-425-3543 | Moulton Niguel Water | 2001-04-11 17:05 | 2001-04-11 17:35 | 200 | 200 | Oso and Nottingham Court | Laguna Hills | OR | 92653 | 8" gravity easement sewer line | 1 | Vandalism | 2"x 6" X 10' fence post, asphalt, and concrete found in manhole structure. Removed and jet-rodded. | Debris removed. Line cleaned and video-inspected. Manhole cover will be changed to locking style. | N | N | None | None | Overflow confined to natural wild area. Removed by vacuum truck | Y | N | N | 0
001-014 | SIRT (FAX) | 2001-04-26 16:30 | Brad Bruington | 949-425-3543 | Moulton Niguel Water | 2001-04-23 09:00 | 2001-04-26 14:30 | 200 | 0 | Chrisanta | Mission Viejo | OR | 92691 | 8" gravity easement sewer line | 1 | Roots, blockage, line break | Partial stoppage caused by roots and broken line. | Manhole and easement line jet-rodded. Video inspection found roots and broken line. Line will be repaired on 5/5/01. | N | N | None | None | Overflow ponded in natural area and soaked in. | Y | N | N | 0
001013 | Victor | 2001-04-17 18:00 | Steve Francis | (949)459-6539 | Santa Margarita Water District | 2001-04-17 17:30 | 2001-04-17 17:45 | 100 | 40 | 2nd Street | El Toro | OR | 92691 | Manhole | 1 | Construction | Investigating the cause of the overflow is still underway. A new siphon at the Aliso Creek crossing was not handling the flows and surcharged the upstream manhole and vent line which resulting in a spill. | Diverted the flows to English Canyon lift station to bypass the new siphon until the problem is resolved. | Y | Y | Storm Drain | Aliso Creek |  | Y | N | N
1021 | (858) 571-6972 (SIRT) | 2001-04-09 08:00 | MIKE DUNBAR | (949)499-4555 | SOUTH COAST WATER DISTRICT | 2001-04-07 19:15 | 2001-04-07 19:45 | 20 | 0 | 31331 HOLLY DRIVE | LAGUNA BEACH | OR | 92651 | MANHOLE | 0 | LARGE GREASE BALL BLOCKED SEWER COLLECTION LINE | LARGE GREASE BALL BLOCKED SEWER COLLECTION LINE CAUSING SPILLAGE FROM MANHOLE | BLOCKAGE CLEARED | N | Y | NONE | NONE | STORM DRAIN/SAND | Y | N | N
1022 | (858) 571-6972 (SIRT) | 2001-04-23 19:30 | MIKE DUNBAR | (949)499-4555 | SOUTH COAST WATER DISTRICT | 2001-04-23 08:00 | 2001-04-23 08:15 | 20 | 20 | CRYSTAL LANTERN/PCH | DANA POINT | OR | 92629 | PIPELINE | 0 | CONTRACTOR PUNCHED HOLE IN PIPELINE | CONTRACTOR FOR CDP PUNCHED HOLE IN PIPELINE, SEWAGE CONFINED TO PIPE TRENCH | DISTRICT CREWS VACUUMED SEWAGE. CONTRACTOR REPLACED BROKEN PIPELINE | N | N | NONE | NONE | PIPE TRENCH | Y | N | N
1023 | (858) 571-6972 (SIRT) | 2001-06-18 07:55 | MIKE DUNBAR | (949) 499-4555 | SOUTH COAST WATER DISTRICT | 2001-06-16 16:47 | 2001-06-16 17:00 | 5 | 0 | 34516 VIA ESPANDZA | CAPO BEACH | OR | 92624 | MANHOLE | 0 | ROOTS CAUSED MANHOLE TO OVERFLOW | ROOTS CAUSED MANHOLE TO OVERFLOW | LINE WAS CLEANED AND VIDEOTAPED | N | N | NONE | NONE | GRASS EASEMENT | Y | N | N
1024 | (858) 571-6972 (SIRT) | 2001-06-26 09:05 | MIKE DUNBAR | (949) 499-4555 | SOUTH COAST WATER DISTRICT | 2001-06-26 09:00 | 2001-06-26 10:00 | 20 | 0 | PCH BETWEEN CAMINEO DEL AVION & CROWN VAL | DANA POINT | OR | 92629 | PIPELINE | 0 | LINE BREAK AT LINK'S GOLF COURSE | CONTRACTOR PULLING IRRIGATION PIPE - BROKE MAIN LINE | CONTRACTOR FIXED LINE | N | N | NONE | NONE | DIVERT TO FAIRWAY | Y | N | N
000122 | CLAY CLIFTON - FAX | 04/10/01 - 16:05 | LOUIE MONTANEZ | 438-2722 X 7137 | CMWD | 2001-04-10 15:00 | 04/10/01 - 15:15 | 15000 | 0 | KALPATI CIRCLE | CARLSBAD | SD | 92008 | 18 INCH CLAY PIPE | 1 | CONSTRUCTION DEBRIS | IN THE PAST 6 MONTHS A NEW SEWER FORCE MAIN WAS INSTALLED AS THE CITY IS UPGRADING THE FOX"S LIFT STATION. THE LINE WAS CONSTRUCTED TO ENTER INTO A NEW MH & INTO THE EXISTING GRAVITY SYSTEM. ON 4/10/01 ANOTHER CONTRACTOR RESPONSIBLE FOR REPLACING EXISTING PUMPS IS REQUIRED TO SETUP A BYPASS USING THE NEW FORCE MAIN. THE CONTRACTOR WENT TO TEST HIS CONNECTION & RAN PORTABLE PUMPS FOR 15 MINUTES. THE FLOW CAME OUT OF THE MH LOCATED ON THE EAST SIDE OF I-5 WERE THE NEW FORCE MAIN ENTERS AND NEW MANHOLE WAS CONSTRUCTED. WHAT WE FOUND IS THAT THE EXISTING GRAVITY LINE WAS NEVER BROKEN OUT TO ALLOW FLOW TO ENTER FROM THE NEW FORCE MAIN. | BEFORE USING THE NEW FORCE MAIN WE ARE GOING TO HAVE A CONTRACTOR REMOVE THE TOP OF EXISTING CLAY PIPE SO THAT FLOW CAN ENTER. | Y | Y | AGUA HEDIONDA LAGOON | PACIFIC OCEAN AT TAMARACK | N/A | YES | YES | YES | 3 | NONE
001004 | fax, (858)571-6972 | 2001-04-24 08:20 | Neil Cole | (858) 720-2474 | City of Solana Beach | 2001-04-24 08:20 | 2001-04-24 09:00 | 200 | 100 | end of North Rios | Solana Beach | SD | 92075 | MANHOLE | 0 | BLOCKAGE | Pipe to pump station on access road at north end of N. Ave was clogged with silt and rags | clear pipe | N | N |  |  | percolated into soil | Y
1015 | Fax | 2001-01-12 10:37 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2001-01-11 12:45 | 2001-01-11 13:15 | 50 | 50 | 2266 Hillview Street | Laguna Beach | Orange | 92651 | Private Lateral | 1 | Roots | Tree roots in downstream manhole blocked the main line. This caused sewage to back up into the residence. Upstram manhole is higher than the lowest bathroom. | City crew jetted the 8 inch main line and removed roots. Blocked off the downstream storm drain and vacuumed all spilled water. This water was also vacuumed up. The resident was given the phone number of a clean up company to repair all the damage. | N | N | None | None |  | Y | N | N | 0 |  | Ammended by City of Laguna Beach to be a Public Overflow. Letter requesting the ammendment was received by Regional Board staff on January 23, 2002.
1016 | Fax | 2001-01-13 12:20 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2001-01-13 12:00 | 2001-01-13 13:15 | 100 | 100 | 1089 Cortez | Laguna Beach | Orange | 92651 | Sewer Manhole # Unk | 1 | Roots | Tree roots in the 8 inch main gravity line running into the easement. | Opened the stoppage with rodder. Fire Dept. had blocked off the storm drain and contained all sewage that spilled. Built a sandbag dam in the gutter next to a sewer manhole and flushed all sewer and cleanup water back into the sewer system. Sewer crew will re-clean the area on Monday Jan. 15, 2001 | N | N | None | None | Back into the City sewer system | Y | N | N | 0
1017 | Fax | 2001-01-21 13:00 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2001-01-20 13:00 | 2001-01-20 13:05 | 30 | 25 | 1299 Hillcrest Dr | Laguna Beach | Orange | 92651 | Manhole at Hillcrest/Weymouth | 1 | Roots | Private lateral roots from upstream sewer | City crews were able to fish out the roots with a fork tool at manhole #7on Hillcrest Drive | N | Y | None | None | On the street where it was diverted back into the City sewer system | Y | N | N | 0
1018 | Fax | 2001-01-21 16:30 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2001-01-21 16:00 | 2001-01-21 16:10 | 20 | 0 | 2830 Chateau Way | Laguna Beach | Orange | 92651 | Manhole at Chateau/Zell Drive | 1 | Roots | Private sewer lateral roots from an upstream area plugged our 8 inch main line in the easement, broke loose and spilled out at 2830 Chateau Way. | Cleaned our 8 inch main line with rodding equipment to remove the roots. Follow up cleaning and inspection was done on Monday January 22nd. | N | Y | Open canyon area at Old Top of the World. | None | Dirt canyon area below Old Top of the World. Soaked into the ground. | Y | N | N | 0
1019 | Fax | 2001-01-22 09:06 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2001-01-22 09:00 | 2001-01-22 09:45 | 50 | 0 | 2990 Zurich Ct. | Laguna Beach | Orange | 92651 | 8 " gravity sewer in easement | 1 | Roots | Lateral roots plugged in the 8 inch main line at the rear of the property from the upstream area. Surge flow will go to Rimrock Canyon Rd. See Report 001020 - Surge flow soaked approximately 50 gallons into the hillside. | City crews cleaned the main line with rodding equipment. Inspected up stream line for other problems. | N | N | None | None | Back into the City sewer system | Y | N | N | 0
1020 | Fax | 2001-01-22 10:30 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2001-01-22 10:30 | 2001-01-22 11:30 | 5200 | 5200 | 1800 Blk. Rimrock Canyon | Laguna Beach | Orange | 92651 | Manhole #6 | 1 | Roots | After breaking the blockage upstream at Zurich Ct.(see report 001019), the surge flow carried and broke loose additional roots which blocked the line on Rimrock. | Rodded the main line to open the blockage. Diverted the surface flow to the next downstream manhole. Built a berm at the storm drain outlet on the beach and pumped all water back into the sewer system. | N | Y | Bluebird Canyon which is a combination of storm drains and natural watercourse | None | Storm drain outlet at Bluebird Canyon Road at the beach. | Y | Y | Y | 3 | Pumped all flow back into the sewer system
1021 | Fax | 2001-01-31 10:00 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2001-01-31 10:00 | 2001-01-31 10:35 | 50 | 30 | 7 Rockledge Rd. | Laguna Beach | Orange | 92651 | City main 6 inch gravity | 2 | Roots | Tree roots in the 6 inch main at the joint 150ft from the manhole in the rear of #5 Rockledge Road. | Cleaned with hand auger from the downstream manhole to the cleanout 211 ft. Vacuumed up about 30 gallons of sewage. Estimated 20 gallons soaked into the street. | N | N | None | None | Vacuumed up with a small shop vac | Y | N | N | 0 | City easement runs along the bluff with a 6 inch VCP sewer. Overflow from the cleanout.
1022 | Fax | 2001-02-05 11:50 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2001-02-04 05:52 | 2001-02-04 07:00 | 200 | 175 | 190 High Drive | Laguna Beach | Orange | 92651 | 6 inch lateral cleanout cover | 1 | Roots | 6 inch sewer lateral plugged with tree roots causing an overflow from the cleanout | City crews used a plumbers snake to open the stoppage | N | Y | None | None | Open "V" ditch down a canyon and eventually into larger drains. | Y | N | N | 0 | Private Sewer Lateral
1023 | Fax | 2001-02-09 15:30 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2001-02-09 15:00 | 2001-02-09 16:45 | 100 | 0 | 1229 Temple Hills Dr | Laguna Beach | Orange | 92651 | Manhole at rear of 1229 Temple Hills Drive | 1 | Roots | Very large tree on each side of the manhole. Roots got in the first joing going out of the manhole | Hydro jetted the 8 inch main line from downstram manhole on Dunning Drive | N | N | None | None | soaked into the hillside area | Y | N | N | 0
1024 | Fax | 2001-02-18 15:00 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2001-02-18 10:30 | 2001-02-18 12:20 | 9000 | 6000 | 1900 Park Avenue | Laguna Beach | Orange | 92651 | Manhole #4 at Park/Hidden Valley | 1 | Roots | Roots blocked the main line. Roots retrieved appeared to be a 4 inch diameter mass from a lateral | Diverted the overflow into manhole with sandbags. Diverted the flow from the storm drain outlet into the sewer. Jetted the blocked line. | Y | Y | Cleo St. storm drain | Pacific Ocean | Cleo St. Beach/Pacific Ocean | Y | Y | Y | 3 | 200 gallons recovered in vactor;5800 gallons diverted to the sewer system.
1025 | Fax | 2001-03-09 15:00 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2001-03-08 19:30 | 2001-03-08 00:01 | 18000 | 0 | 100 Barranca Street | Laguna Beach | Orange | 92651 | Crescent Bay Pump Station | 1 | Construction | City's contractor working 200ft. Upstream dumped sand cement slurry into a sewer manhole. The slurry then filled the pump station and plugged the pumps. | Bermed beach to contain overflow. Vacuumed slurry from pump statin;cleaned pump #1 to allow pumping of waste water inflow. Removed sludge from bermed pit area. | Y | N | Pacific Ocean | Same | 2000 gallons to ocean;16,000 percolated into sand. | Y | Y | Y | 5
1026 | Fax | 2001-03-21 11:40 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2001-03-20 09:15 | 2001-03-20 10:30 | 50 | 30 | 1379 Circle Way | Laguna Beach | Orange | 92651 | 1379 Circle Way | 1 | Unknown | City crews found the leak and made the repair of the 4-inch lateral. Replaced about 8ft. Of pipe and cleaned the area of all debris. Tammie from Orange County Health also there when the leak was found. | About 200 gallons had soaked back into the sand at Crescent Bay Beach. | N | N | None | None | Sand at Crescent Bay Beach | Y | N | N | 0 | Private Sewer Lateral
1027 | Fax | 2001-03-28 11:50 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2001-03-28 11:45 | 2001-03-28 12:35 | 20 | 0 | Bluebird Canyon/Cress St. | Laguna Beach | Orange | 92651 | 8" pipe joint at the lateral | 1 | Roots | City main gravity sewer plugged with lateral roots | Cleaned main line and removed all roots and debris. Re-cleaned again with jetter truck and follow up with video inspection | N | N | None | None | All water dried on the street and soaked into the ground. | Y | N | N | 0
001-007 | SIRT (FAX) | 2001-01-15 07:45 | Brad Bruington | 949-425-3543 | Camden Development | 2001-01-14 16:40 | 2001-01-14 17:40 | 240 | 140 | La Alameda/El Regatteo | Mission Viejo | OR | 92691 | 8" gravity sewer line at manhole structure | 0 | Rocks, debris, blockage, construction | Removed approx. 1 cubic yard of gravel and plastic Gatorade bottle in sewer line of The Park at Crown Valley | Jetted and removed debris from sewer line. Video inspection of La Alameda and construction site upstream of overflow. No additional debris found. | Y | Y | Oso Creek via storm drain | Oso Creek to San Juan Creek | Pumped and vacuumed sewage into sewer | Y | N | N | 0 | Responsible party is The Park at Crown Valley, Camden Development
1017 | (858) 571-6972 (SIRT) | 1/12/01 1300 | Mike Dunbar | (949) 499-4555 | South Coast Water District | 2001-01-12 11:00 | 1/12/01 1210 | 20 | 0 | 24576 Santa Clara | Dana Point | OR | 92629 | Private Cleanout | 0 | Lateral blockage | Sewer overflowed cleanout on to sidewalk (50 ft. to storm drain that ends in harbor) | Blockage cleared | Y | Y | D.P. Harbor | Pacific Ocean | Pacific Ocean | Y | Y | N | 0
1018 | (858) 571-6972 (SIRT) | 2/5/01 1535 | Mike Dunbar | (949) 499-4555 | South Coast Water District | 2001-02-04 10:54 | 2/4/01 1210 | 400 | 400 | PCH and Vista Del Sol | Laguna Beach | OR | 92651 | Manhole | 0 | Roots and grease caused blockage | Blockage caused by roots and grease. Sewage overflowed down gutter into telephone vault. | Used jetter to unclog. Vacuumed vault and soil. | N | N | None | None | Telephone vault | Y | N | N | 0
1019 | (858) 571-6972 (SIRT) | 3/5/01 0830 | Mike Dunbar | (949) 499-4555 | South Coast Water District | 2001-03-04 08:50 | 3/4/01 0930 | 1800 | 1000 | Valido Road | Laguna Beach | OR | 92651 | Manhole | 1 | Massive root ball | Massive root ball from upper portion of collection line caused blockage and manhole to overflow. | Line was cleaned. This line is being cleaned on a monthly basis. | N | Y | None | None | Mouth of storm drain | Y | Y | N | 0 | Portion was captured with vactor truck.
1020 | (858) 571-6972 (SIRT) | 3/15/01 0820 | Mike Dunbar | (949) 499-4555 | South Coast Water District | 2001-03-14 16:00 | 3/14/01 1610 | 20 | 0 | 31561 Table Rock Drive | Laguna Beach | OR | 92651 | Drop Manhole | 0 | Roots in tunnel drop | Sewage dripping out of manhole, down to storm drain onto rocks. | Pushed roots down. | N | Y | None | None | rocks | Y | N | N | 0
01-0003 | Greg Peters (voice mail) | 2001-04-23 00:01 | Shawn Atherton | 760-753-5018 | City of Encinitas | 2001-04-21 | 2001-04-22 09:30 | 1000 | 0 | 200 Saxony Road | Encinitas | SD | 92024 | MH-F78 | 0 | Debris (paper products) | Large amount of paper was noted while cleaning line. | Line was cleaned and flushed with sewer cleaner. | Y | Y | Storm drain system | Cottonwood Creek | Ocean | Y | Y | Y | 3 | Volume based on YMCA employee information.
001042 | Victor Vasquez | 2001-04-10 16:15 | John Vaught | (760) 839-4323 | City of Escondido | 2001-04-09 | 2001-04-10 15:30 | 4320 | 100 | Morning View Dr. & Lincoln Ave. | Escondido | SD | 92026 | Sewer Manhole 5887 | 1 | Grease | The televising inspection revealed roots and grease were the major factors in this discharge. | Two abandon laterals where roots are entering the main will be removed by a contractor. This project is scheduled for the summer of 2001. | Y | Y | Reidy Creek | Escondido Creek | San Elijo Lagoon | Y | Y | Y | 3
001043 | Quarterly Report | 2001-04-19 03:45 | Jim Miller | (760) 839-4347 | City of Escondido | 2001-04-18 19:40 | 2001-04-18 22:00 | 700 | 200 | 2472 Eucalyptus | Escondido | SD | 92025 | Sewer Manhole 3727 | 1 | Pump Station Failure | No explanation given from lift station mechanic why the station failed. | A new telemetry system will be installed. | N | Y |  |  | The remainder of the spill dissipated into the soil. | Y | N | N | 0
001044 | Quarterly Report | 2001-05-22 11:30 | John Vaught | (760) 839-4323 | City of Escondido | 2001-05-22 10:15 | 2001-05-22 10:20 | 40 | 20 | 475 N. Spruce St. | Escondido | SD | 92025 | Vactor Truck #3573 | 1 | Other | Valve to the Vactor debris tank was accidentally opened which aloud the discharge. | Fleet personnel were advised not to activate the switch. A guard switch was also installed. | Y | Y | Escondido Creek | San Elijo Lagoon | Pacific Ocean | Y | N | N | 0
001045 | Victor Vasquez | 2001-06-06 13:30 | John Vaught | (760) 839-4323 | City of Escondido | 2001-06-05 | 2001-06-06 09:00 | 4800 | 2500 | 1625 E. Grand Ave. | Escondido | SD | 92025 | 6"-pipe | 1 | Grease | Private 6" service lateral was obstructed due to excessive grease. | Our Pretreatment Inspector issued a Notice of Correction to the property owners. They're instructed to clean and inspect (video) their lateral. We will then review the tape. | Y | Y | Escondido Creek | San Elijo Lagoon | Pacific Ocean | Y | Y | Y | 3 | Private spill from cleanout. This lateral serves and is owned by the Garden View Apartments at 250 S. Rose.
001046 | Quarterly Report | 2001-06-07 16:15 | Mike Schultz | (760) 839-4255 | City of Escondido | 2001-06-07 15:15 | 2001-06-07 15:20 | 20 | 5 | San Pasqual Rd. @ Viento Valle | Escondido | SD | 92025 | Forcemain air release valve | 3 | Debris | Debris caused valve not to seal properly. | The valve was removed and rebuilt. | N | N |  |  | Absorbed into soil | Y | N | N | 0
001047 | Quarterly Report | 2001-06-18 14:35 | John Vaught | (760) 839-4323 | City of Escondido | 2001-06-18 06:30 | 2001-06-18 09:30 | 900 | 150 | 309 W. Mission | Escondido | SD | 92025 | Private cleanout | 1 | Grease | Excessive grease in service lateral servicing the El Portal Restaurant. | The restaurant was inspected and a Notice of Correction was issue to have their grease trap cleaned. | Y | Y | Reidy Creek | Escondido Creek | San Elijo Lagoon | Y | N | Y | 3
001048 | Quarterly Report | 2001-06-20 13:30 | John Vaught | (760) 839-4323 | City of Escondido | 2001-06-19 11:45 | 2001-06-20 11:15 | 710 | 350 | 2500 S. Escondido Blvd. | Escondido | SD | 92029 | Private grease trap | 1 | Grease | Excessive grease in service lateral which overflowed their grease trap. | A Notice of Correction was issued to the property owners to clean, inspect, and repair portions of their collection system which in turn will be reviewed by the city's pretreatment inspector. Weekly inspections will continue until the situation is resolv | Y | Y | Storm system | small creek (no name) | Large pond on the south end of Kit Carson Park | Y | N | Y | 3 | Private spill from grease trap.
001003 | Faxed DEH | 2001-01-03 09:30 | David Vigliotti | 858/679-5419 | City of Poway | 2001-01-03 09:15 | 2001-01-03 09:45 | 75 | 0 | 12842 Indian Trail | Poway | San Diego | 92064 | 8" main | 1 | Grease, construction | While jetrodding to clear 8" main, a large piece of 8" PVC pipe was pulled down from upstream. Excessive grease was noted in the manhole upon clearing blockage. | 8" VCP sewer main was jetrodded several times to clear blockage. Overflow discharge was confined to fenced yard area of 12842 Indian Trail. Area surrounding c/o on northside of 12842 Indian Trail was cleaned up and hauled to sludge basin. | N | N | None | None | Sewage confined to rural area of property and absorbed into ground. | Y | N/A | N |  | Signs not posted due to the location and the amount of discharge. | Qtr 3/00-01
001004 | Faxed DEH | 1/23/2001 15:30 | Brad Voorhees | 858/679-5419 | City of Poway | 2001-01-23 14:10 | 2001-01-23 14:35 | 25 | 25 | 13531 Rostrata Road | Poway | San Diego | 92064 | 8" main | 1 | Roots | Roots in 8" PVC sewer main approximately 14 feet east of manhole. Roots may have come from private lateral upstream. | Cleared blockage in sewer main; jetrodded section of main affected; contained spill I asphalt burm on north side of road; disinfected area and transported to sludge basin. | N | N | None | None | Vactor truck and evaporation. | Y | N/A | N |  |  | Qtr 3/00-01
001005 | Faxed DEH, CRWQCB | 2001-02-06 15:00 | Brad Voorhees | 858/679-5419 | City of Poway | 2001-01-18 13:00 | 2001-02-06 15:00 | 578 | 0 | 13464 Poway Road | Poway | San Diego | 92064 | Coco's Restaurant, 4" sewer lateral serving 13464 Poway Rd | 1 | Line Break | 4" sewer lateral pipe cracked approximately 17 feet behind face of curb at location. 1/18/01: Odor in storm drain complaint received; 1/19/01: Storm drain system flushed to eliminate odor; 1/24/01: odor returns and 60" storm drain is video inspected and | Emergency repair on lateral 2/7/01. Built containment basin in storm drain manhole to eliminate overflow. Vactor truck used to transport overflow to sewer system. Posted warning signs on Poway Creek from Community Road to Carriage Road, approx 2,000 ft. | Y | Y | Storm drain, 13464 Poway Rd | Poway Creek |  | Y | N | Y | 5 |  | Qtr 3/00-01
001006 | Faxed DEH | 02/12/01 11:30 | Brad Voorhees | 858/679-5419 | City of Poway | 2001-02-12 09:30 | 2001-02-12 10:15 | 90 | 10 | 12721 Stone Canyon Road | Poway | San Diego | 92064 | 8" main | 1 | Roots | Roots caused partial blockage in 8" sewer main on easement road west of 12721 Stone Canyon Road. | Cleared 8" main with jetrodder truck. Cleaned and disinfected area, posted warning signs along Green Valley Creek at possible public contact points. Video inspection on this section of sewer main will be scheduled ASAP. | Y | Y | Storm drain, 12700 Stone Canyon Road | Green Valley Creek |  | Y | N | Y | 5 |  | Qtr 3/00-01
001001 | Clay Clifton | 4/20/01 19:00 hrs | Wm. Wiltse | 619-660-2007 | County of San Diego | 2001-04-19 19:00 | 04/19/01 19:45 hrs. | 500 | 0 | Jamacha Blvd. | Spring Valley | SD | 91978 | 506 010 0349E | 0 | Rocks | Rocks lodged in manhole | Accelerated maintenance, rod 3x yearly | N | Y | None | None | grassy field | Y | NA | N | 0 | Will check upstream manholes to ensure vandals do not have access.
177197 | Fax 571-6972 | 04/12/01 1500 | Johnny Peay | 6544160 | City of San Diego | 2001-04-02 11:44 | 4/2/01 - 13:00 | 2080 | N/A | 5914 Baja Way | San Diego | SD | 92115 | 6"VC | 1 | Gravity Break | Possible break on 6"VC main | 6" VC main, Machine rodded turn over to TV. | Y | N | N/A | N/A | Soaked into dirt in creek bed | Y | Y | N | N/A
177235 | Fax 571-6972 | 04/2/01 - 2253 | Jeff Wilder | 6544160 | City of San Diego | 2001-04-02 17:58 | 4/2/01 - 18:40 | 20 | 20 | 11 Hensley Street | San Diego | SD | 92101 | 14" Main | 1 | Grease | Grease build-up in main | 14" main, Vacuum puddled sewage, flush & vacuum main. Refer for P.M site | Y | N | Puddled up in gutter | N/A | Puddled up in gutter | Y | Y | N | N/A
177829 | Fax 571-6972 | 04/5/01 - 1400 | Rick Donahue | 6544160 | City of San Diego | 2001-04-04 08:29 | 4/4/01 - 22:35 | 33800 | 3800 | Fairmont & Montezuma Road | San Diego | SD | 92115 | 8"VC | 1 | Rocks | Small rocks built up in main causing stoppage, damned up concrete storm channel & captured 3,800 gallons, returned to collection system, 30,000 gallons flowed into San Diego River | Machine cleaned and televised, schedule for P.M. 8" VC | Y | Y | San Diego River | Pacific Ocean | Storm drain/San Diego River/Pacific Ocean | Y | Y | Y | Still posted | 40 or so signs posted
177680 | Fax 571-6972 | 04/4/01 - 1400 | Kent Vian | 6544160 | City of San Diego | 2001-04-04 09:34 | 4/4/01 - 10:45 | 144 | 10 | Frobisher Street and Reagan Road | San Diego | SD | 92126 | 8"VC | 1 | Grease | Stoppage caused by grease | Relieve overflow with Hydro Flusher, clean, refer to TV. Refer for P.M. 8" VC | Y | Y | Enter storm drain | N/A | Dried in storm drain | Y | Y | N | N/A
178245 | Fax 571-6972 | 4/6/01 - 20:00 | Johnny Peay | 6544160 | City of San Diego | 2001-04-06 13:57 | 4/6/01 - 16:15 | 138 | N/A | 70th and El Cajon Boulevard | San Diego | SD | 92120 | 6"VC | 1 | Gravity Break | Main break turn over to main crew to make repairs on 6"VC main | Flushed and rodded 6" main. | N | N | N/A | N/A | Sewer spill contained in contractor trench | Y | Y | N | N/A
178472 | Fax 571-6972 | 4/7/01 - 20:14 | Doug Branco | 6544160 | City of San Diego | 2001-04-07 17:15 | 4/7/01 - 18:50 | 95 | 0 | 4243 Ingraham Street | San Diego | SD | 92109 | 6"CP | 2 | Construction | Mouth of line in M/H sealed | Rodded, Vactored. 6" CP | Y | Y | Entered storm drain at 1622 Reed & dissipated in system | N/A | Dissipated in storm drain | Y | Y | N | N/A
178602 | Fax 571-6972 | 4/8/01 - 10:50 | Doug Branco | 6544160 | City of San Diego | 2001-04-08 08:23 | 4/8/01 - 9:14 | 510 | 0 | 5011 Waring Road | San Diego | SD | 92120 | 8"VC | 1 | Grease | Blockage caused by grease | Machine Rod, refer to area supervisor. 8" VC | Y | Y | Entered storm drain 150 south of 5005 Waring Road & flowed into San Diego River at Waring Road & I-8 | N/A | San Diego River | Y | Y | N | N/A
179368 | Fax 571-6972 | 4/12/01 - 10:30 | Johnny Peay | 6544160 | City of San Diego | 2001-04-12 07:39 | 4/12/01 - 8:30 | 345 | 100 | Federal Boulevard and Mallard Street | San Diego | SD | 92114 | 8"VC Main | 1 | Roots | Roots in main caused stoppage | Rodded 8" VC main, vactor, wash & deodorize. Add to cleaning site | Y | Y | N/A | N/A | Dry in storm drain at 6225 Federal | Y | Y | N | N/A
179650 | Fax 571-6972 | 4/13/01 - 17:10 | Chris Bauer | 6544160 | City of San Diego | 2001-04-13 13:45 | 4/13/01 - 15:00 | 3000 | 0 | 11570 Polaris Drive (Canyon) | San Diego | SD | 92126 | M/H 10"VC | 1 | Vandalism | Vandalism caused by kids in canyon removing strap from M/H & throwing rocks in M/H 49 | Rodded main, restrapped manhole. manhole 10" VC | N | N | Soaked into ground around M/H | N/A | Soaked into ground in canyon | Y | Y | N | N/A
179953 | Fax 571-6972 | 4/15/01 - 14:20 | Doug Branco | 6544160 | City of San Diego | 2001-04-15 10:24 | 4/15/01 - 11:59 | 180 | 0 | 540 Hollister Street | San Diego | SD | 92154 | 10"VC | 1 | Grease | Blockage was caused by heavy grease | 10" VC, flushed, refer to area supervisor. | N | N | Dried in ground along curb of Holister | N/A | Soaked into ground | Y | Y | N | N/A
180239 | Fax 571-6972 | 4/17/01 - 10:00 | Johnny Peay | 6544160 | City of San Diego | 2001-04-16 19:45 | 4/16/01 - 21:15 | 180 | 106 | Glen Vista Ct & Glen Vista Street | San Diego | SD | 92139 | 8"VC Main | 1 | Roots | Roots in main caused grease build-up | Vactor overflow, vactor grease, refer for P.M. 8" VC | Y | Y | Storm drain on Glen Vista Ct. | N/A | Dissipated in storm drain | Y | Y | N | N/A
180876 | Fax 571-6972 | 4/19/01 - 22:38 | Jeff Wilder | 6544160 | City of San Diego | 2001-04-19 18:10 | 4/19/01 - 20:19 | 12900 | 0 | Plaza Blvd & S. Woodman Street | San Diego | SD | 92139 | 10" PVC Main | 1 | Roots | Roots in main with paper debris catching on it | Rod main, refer for P.M. 10" PVC | N | N | Dry creek bed in canyon | N/A | Soaked into dry creek bed | Y | Y | N | N/A
181829 | Fax 571-6972 | 4/24/01 - 13:30 | Les Finch | 6544160 | City of San Diego | 2001-04-24 10:35 | 4/24/01 - 11:30 | 275 | 0 | 3705 Robinson Place | San Diego | SD | 92103 | 10" VC | 1 | Other | Cloth rags mixed with paper partially blocked main in M/H 593 | Clean main upstream & TV. Deodorize. 10" VC | N | N | N/A | N/A | Soaked into ground around M/H | Y | Y | N | N/A
182554 | Fax 571-6972 | 4/30/01 - 9:30 | Gary Neel | 6544160 | City of San Diego | 2001-04-27 06:52 | 4/27/01 - 7:40 | 144 | 0 | 6392 Lake Athabaska Place | San Diego | SD | 92179 | 8" VC | 1 | Roots | Blockage was caused by roots | 8" VC, Machine rodded. | Y | N | Dried in street Lake Athabraska Pl. | N/A | Dried in street | Y | Y | N | N/A
182557 | Fax 571-6972 | 4/27/01 - 12:00 | Gary Neel | 6544160 | City of San Diego | 2001-04-27 07:32 | 4/27/01 - 8:00 | 320 | 0 | 6009 Rancho Mission Road | San Diego | SD | 92108 | 10"VC | 1 | Roots | Partially stopped 10" VC main with roots | T.V. and flushed. 10" VC | Y | Y | Storm drain at 6009 Ranch Mission Rd. | San Diego River | Dried in storm drain | Y | Y | N | N/A
182839 | Fax 571-6972 | 4/29/01 - 23:05 | Doug Branco | 6544160 | City of San Diego | 2001-04-29 20:30 | 4/29/01 - 22:00 | 45 | 0 | 52nd & Haniman Drive | San Diego | SD | 92105 | 6"VC | 1 | Other | Rodded from overflowing M/H to relieve stoppage, cause unknown | 6" VC, machine Rodded, refer to area supervisor. | Y | Y | Entered storm drain at 52nd & Haniman & dissipated in system | Chollas Creek/San Diego Bay | N/A | Y | Y | N | N/A
182878 | Fax 571-6972 | 4/30/01 - 14:30 | Gary Neel | 6544160 | City of San Diego | 2001-04-30 08:50 | 4/30/01 - 9:30 | 25 | 0 | 6558 Wandermere Drive | San Diego | SD | 92120 | 8"VC | 1 | Roots | Blockage was caused by roots & overflow coming out of private clean out | 8" VC, Hand rodded. | Y | N | Soaked into yard behind 6558 Wandermere | N/A | Soaked into ground behind address | Y | Y | N | N/A
183278 | Fax 571-6972 | 5/3/01 - 9:00 | Rick Donahue | 6544160 | City of San Diego | 2001-05-01 10:21 | 5/2/01 - 14:00 | 9846 | 9346 | 3121 Boundary Street | San Diego | SD | 92104 | 10"VC | 1 | Rocks | Rocks in 10"VC main caused stoppage | 10" VC main, Machine rodded made repairs. | Y | N | N/A | N/A | Pooled into canyon, pumped back into system | Y | Y | N | N/A
184358 | Fax 571-6972 | 5/6/01 - 17:25 | Doug Branco | 6544160 | City of San Diego | 2001-05-06 13:35 | 5/6/01 - 15:30 | 50 | 0 | 2060 West California Street | San Diego | SD | 92103 | 6"CP | 1 | Construction | Contractor using pavement breaker in area renewing water lines, sewer line is broken in several places, two small sections of pipe tied to line causing intermittent overflow | 6" CP main, rodded, refer to construction. | Y | N | Dried in curb area in front of 2061 West California Street | San Diego Bay/Pacific Ocean | N/A | Y | Y | N | N/A
184341 | Fax 571-6972 | 5/6/01 - 14:30 | Doug Branco | 6544160 | City of San Diego | 2001-05-06 09:33 | 5/6/01 - 13:10 | 50 | 0 | 4431 Revillo Drive | San Diego | SD | 92115 | 6"CP | 1 | Rocks | Blockage was caused by rocks in line | 6" CP main, Flushed line, refer for scheduled maint. | Y | Y | Major portion soaked into yard/small portion flowed into storm drain at 4376 Revillo Drive & dissipated in system | Chollas Creek/San Diego Bay | N/A | Y | Y | N | N/A
184381 | Fax 571-6972 | 5/8/01 - 12:30 | Gary Neel | 6544160 | City of San Diego | 2001-05-07 07:11 | 5/7/01 - 8:30 | 395 | 0 | Tierrasanta Boulevard & Dosos Place | San Diego | SD | 92124 | 8"VC | 1 | Grease | Blockage was caused by grease | 8" VC, refer fo TV and flush. | Y | N | Soaked into canyon floor | San Diego River/Pacific Ocean | N/A | Y | Y | N | N/A
184434 | Fax 571-6972 | 5/7/01 - 14:15 | Les Finch | 6544160 | City of San Diego | 2001-05-07 10:00 | 5/7/01 - 10:15 | 25 | 0 | 2830 Boston Avenue (backyard) | San Diego | SD | 92113 | M/H seams & cracks | 1 | Other | Doing normal maintenance on a above ground main when flushing seams & crack in M/H allowed spray to leak out of M/H | Refer to Construction to repair / replace manhole. | N | N | N/A | N/A | Soaked into ground in backyard | Y | Y | N | N/A
185156 | Fax 571-6972 | 5/10/01 - 16:59 | Les Finch | 6544160 | City of San Diego | 2001-05-10 11:13 | 5/10/01 - 12:13 | 300 | 150 | 3052 Hawthorn Street | San Diego | SD | 92104 | 6"CP | 1 | Gravity Break | Partial stoppage on main caused clean out to overflow/main appears to be partially collapsed | 6" CP main, Refer to construction. | Y | Y | Storm drain at 3052 Hawthorn Street | Dried in canyon at 3000 Grape | Dried in storm drain before canyon | Y | Y | N | N/A
185357 | Fax 571-6972 | 5/11/01 - 9:27 | Denise Steele | 6544160 | City of San Diego | 2001-05-11 09:27 | 5/11/01 - 9:55 | 10 | 0 | Klauber Avenue & Scimitar Drive | San Diego | SD | 92114 | 8"VC | 1 | Gravity Break | Main break | 8" VC main, Refer to construction. | Y | N | N/A | N/A | Dried up in dirt on side of street | Y | Y | N | N/A
186279 | Fax 571-6972 | 5/16/01 - 2:23 | Jeff Wilder | 6544160 | City of San Diego | 2001-05-15 19:36 | 5/15/01 - 22:15 | 3180 | 0 | 4448 Arch Street | San Diego | SD | 92116 | 8"PVC | 1 | Other | Accumulation of rags in M/H caused stoppage | 8" PVC main, located overflow in canyon, probed MH. | N | N | N/A | N/A | Soaked into dry canyon bed | Y | Y | N | N/A
186075 | Fax 571-6972 | 5/15/01 - 13:30 | Epikopo Semo | 6544160 | City of San Diego | 2001-05-15 12:00 | 5/15/01 - 12:35 | 105 | 0 | 7687 Hillside Drive | San Diego | SD | 92037 | 8"VC | 1 | Roots | Root stop on 8"VC easement main, hand rod main to relieve stop | 8" VC main, TV easement. | N | N | Sewage soaked into ground | N/A | N/A | Y | Y | N | N/A
186038 | Fax 571-6972 | 5/16/01 - 2:15 | Jeff Wilder | 6544160 | City of San Diego | 2001-05-15 07:59 | 5/15/01 - 17:30 | 150 | 0 | 3066 Elm Street | San Diego | SD | 92102 |  | 1 | Roots | Roots in main caused stoppage | Rod main & cleaned. | N | N | N/A | N/A | Soaked into ground on hillside & canyon | Y | Y | N | N/A
186119 | Fax 571-6972 | 5/19/01 - 17:15 | Doug Branco | 6544160 | City of San Diego | 2001-05-15 16:25 | 5/19/01 - 16:00 | 50 | 0 | 1217 South 36th Street | San Diego | SD | 92113 | 6"CP | 1 | Grease | Consumer excavated backyard easement, sewer main is exposed, stoppage caused by grease & roots caused seepage from joints in pipe. Earlier investigation did not detect problem. | 6" CP main, Rod line, refer for PM. | N | N | Soaked into dirt in yard behind address | N/A | Soaked into dirt behind address | Y | Y | N | N/A
186418 | Fax 571-6972 | 5/16/01 - 22:48 | Jeff Wilder | 6544160 | City of San Diego | 2001-05-16 18:19 | 5/16/01 - 19:17 | 1134 | 504 | Dove Street & Maple Street | San Diego | SD | 92103 | 8"CP Main | 2 | Construction | Construction debris (rocks) from CIP job | 8" CP main, Maint on MH. | Y | Y | Storm drain at State Street & Maple | Lost flow in storm drain | N/A | Y | Y | N | N/A
186561 | Fax 571-6972 | 5/17/01 - 2:09 | Jeff Wilder | 6544160 | City of San Diego | 2001-05-16 16:30 | 5/16/01 - 23:28 | 2090 | 0 | 6365 Imperial Avenue | San Diego | SD | 92114 | 8"VC Main | 1 | Roots | Roots in main caused stoppage & flooding inside | 8" VC main, Flush main. | Y | Y | Storm drain by address | Dissipated in storm channel | N/A | Y | Y | N | N/A
186801 | Fax 571-6972 | 5/18/01 - 19:15 | Gary Neel | 6544160 | City of San Diego | 2001-05-18 10:30 | 5/18/01 - 12:15 | 1575 | 0 | 18100 Moon Song Court | San Diego | SD | 92127 | 8"PVC | 1 | Roots | Heavy mass of roots in M/H 237 | 8" PVC main, removed roots, rodded, refer to TV. | Y | N | Dried in creek behind address | Lake Hodges | N/A | Y | Y | N | N/A
186932 | Fax 571-6972 | 5/18/01 - 21:45 | Doug Branco | 6544160 | City of San Diego | 2001-05-18 18:52 | 5/18/01 - 20:20 | 176 | 0 | 4381 Cartagena Drive | San Diego | SD | 92115 | 8"VC | 1 | Roots | Blockage was caused by roots | 8" VC main, rod, refer for PM. | Y | Y | Entered storm drain at University & Caratagena Drive & dissipated in storm drain system | Chollas Creek/San Diego Bay | N/A | Y | Y | N | N/A
187035 | Fax 571-6972 | 5/20/01 - 13:00 | Doug Branco | 6544160 | City of San Diego | 2001-05-20 10:25 | 5/20/01 - 11:50 | 43 | 0 | 11329 Meadow Flower Place | San Diego | SD | 92127 | 8"PVC | 1 | Grease | Blockage was caused by grease, M/H was 7-32 upon arrival | 8" PVC main, flushed line, refer for PM. | Y | Y | Entered storm drain at D/E cul de sac of Meadow Flower Place & dissipated in storm drain system | Lusardi Creek/San Dieguito River | N/A | Y | Y | N | N/A
187619 | Fax 571-6972 | 5/29/01 - 10:30 | James Becker | 6544160 | City of San Diego | 2001-05-21 | 5/21/01 - | 15 | 0 | 2590 E Mission Bay Drive | San Diego | SD | 92110 | RV Dumpsite | 0 | Other | Unknown problems at waste dump site. Park & Rec. personnel called Station 38 for plumber, but no mention was made of an overflow. Metro Wastewater wasn't aware that an overflow occured until the next day when County Health contracted Metro Waste about th | Recommend Park & Rec Dept. have schld maint. | Y | Y | Mission Bay | N/A | Pacific Ocean | Y | Y | Y | Unknown | 4 signs posted
187141 | Fax 571-6972 | 5/21/01 - 20:39 | Jeff Wilder | 6544160 | City of San Diego | 2001-05-21 13:20 | 5/21/01 - 17:42 | 524 | 0 | 6518 Dwane Avenue | San Diego | SD | 92120 | 8"VC | 1 | Roots | Roots in easement main caused stoppage | 8" VC, hand rod & flush. | N | N | N/A | N/A | Soaked into ground on easement and backyard | Y | Y | N | N/A
187563 | Fax 571-6972 | 5/22/01 - 14:00 | Denise Steele | 6544160 | City of San Diego | 2001-05-22 07:35 | 5/22/01 - 9:45 | 5250 | 4950 | 4046 51st | San Diego | SD | 92105 | 15"VC | 1 | Vandalism | Vandalism caused by vandals filling M/H with rocks, concrete & debris, M/H was strapped down prior to vandalism *300 gallons dried up in dirt | 15" VC main, bypass pump. | Y | N | N/A | N/A | N/A | Y | Y | N | N/A
188400 | Fax 571-6972 | 5/25/01 - 13:30 | Denise Steele | 6544160 | City of San Diego | 2001-05-25 09:30 | 5/25/01 - 10:00 | 1500 | 0 | 6300 Alvarado Court | San Diego | SD | 92120 | 8"VC | 1 | Other | This is a 8VC line that goes into a 30VC, this restricts the flow and caused sludge to build up in line | 8" VC main, vactored, rodded, refer to TV. | Y | Y | Storm drain at spill site | Alvarado Creek/San Diego River | Pacific Ocean | Y | Y | N | N/A
188622 | Fax 571-6972 | 5/26/01 - 14:35 | David Savare | 6544160 | City of San Diego | 2001-05-26 10:11 | 5/26/01 - 10:56 | 225 | 200 | Euclid Avenue & Tiselle Way | San Diego | SD | 92105 | 8"VC | 4 | Grease | Blockage was caused by grease | 8" VC main, machine rod, refer for PM. | Y | Y | Chollas Creek | San Diego Bay | 200 gallons was recovered/25 soaked into ground | Y | Y | N | N/A
188977 | Fax 571-6972 | 5/30/01 - 10:45 | Denise Steele | 6544160 | City of San Diego | 2001-05-30 08:45 | 5/30/01 - 9:10 | 25 | 25 | Altadena & Marilou Road | San Diego | SD | 92105 | 8"VC | 1 | Vandalism | Vandalism, someone put large pieces of wood, tree parts and bricks * construction was on site when overflow started they made burn | 8" VC main, Vactor, rod, locked lid. | Y | N | N/A | N/A | Vactored up 25 gallons | Y | Y | N | N/A
188990 | Fax 571-6972 | 5/30/01 - 15:00 | Denise Steele | 6544160 | City of San Diego | 2001-05-30 10:25 | 5/30/01 - 12:28 | 123 | 0 | 3827 39th Street | San Diego | SD | 92105 | 6"VC | 1 | Vandalism | Vandalism, someone put bag with yard waste into M/H 158 | 6" VC main, rodded main, sealed MH. | Y | Y | Storm drain at spill site | N/A | Dissipated in storm drain | Y | Y | N | N/A
189287 | Fax 571-6972 | 6/1/01 - 00:05 | Jeff Wilder | 6544160 | City of San Diego | 2001-05-31 19:34 | 5/31/01 - 20:28 | 96 | 40 | Calle Chanate & Rustic Road | San Diego | SD | 92139 | 8"VC Main | 1 | Roots | Roots & grease caused stoppage | 8" VC main, Vacuum, rod, and flush. | Y | Y | Storm drain at Potomac Street & Siapan Drive | N/A | Dissipated in storm drain | Y | Y | N | N/A
190004 | Fax 571-6972 | 6/2/01 - 16:43 | Doug Branco | 6544160 | City of San Diego | 2001-06-02 06:45 | 6/2/01 - 11:00 | 510 | 0 | 3703 Albatross Street | San Diego | SD | 92103 | 6"VC | 1 | Gravity Break | Possible break in line | 6" VC, Machine/Hand Rod, refer to construction, contained by pump. | Y | N | Soaked into canyon floor behind Albatross Street | San Diego Bay/Pacific Ocean | N/A | Y | Y | N | N/A
190113 | Fax 571-6972 | 6/3/01 - 16:26 | Doug Branco | 6544160 | City of San Diego | 2001-06-03 16:25 | 6/3/01 - 17:10 | 50 | 0 | 7587 Windy Ridge Ridge | San Diego | SD | 92126 | 8"PVC | 1 | Grease | Blockage caused by heavy grease | 8" PVC, Machine Rod, refer to supervisor. | Y | Y | Entered storm drain next to M/H & dissipated into system | Penasquitos Creek/Pacific Ocean | N/A | Y | Y | N | N/A
190878 | Fax 571-6972 | 6/13/01 - 10:00 | Les Finch | 6544160 | City of San Diego | 2001-06-05 18:00 | 6/5/01 - 22:19 | 2080 | 530 | 3790 Voltaire Street | San Diego | SD | 92107 | 8"PVC | 1 | Construction | Contractor left 200' of rope with a 1 gallon plastic jug stretched out in main, caused grease to build up also new main this section has sags | 8" PVC, Cleaned, TV main. | Y | Y | Famosa slough | San Diego River to Pacific Ocean | N/A | Y | Y | Y | 5 | 15 signs posted
191893 | Fax 571-6972 | 6/9/01 - 13:40 | Doug Branco | 6544160 | City of San Diego | 2001-06-09 11:13 | 6/9/01 - 12:30 | 231 | 0 | Parkside Avenue & Parkside Court | San Diego | SD | 92139 | 8"VC | 1 | Roots | Blockage was caused by roots | 8" VC, Machine Rod, refer to area supervisor. | Y | Y | Entered storm drain at 7030 Parkside Avenue & dissipated in system | Sweetwater River/Pacific Ocean | N/A | Y | Y | N | N/A
191936 | Fax 571-6972 | 6/10/01 - 20:20 | Doug Branco | 6544160 | City of San Diego | 2001-06-10 18:37 | 6/10/01 - 19:28 | 102 | 0 | 3502 Wawona Street | San Diego | SD | 92106 | 6"CP | 2 | Roots | Blockage was caused by roots | 6" CP, Machine Rod, refer to area supervisor. | Y | Y | Entered storm drain at Clove Street & Ollphant & dissipated in storm drain | San Diego Bay/Pacific Ocean | N/A | Y | Y | N | N/A
191975 | Fax 571-6972 | 6/11/01 - 14:40 | Les Finch | 6544160 | City of San Diego | 2001-06-11 08:36 | 6/11/01 - 9:15 | 156 | 50 | Kenyon Street and Wing Street | San Diego | SD | 92110 | 8"VC | 1 | Grease | Grease caused partial stoppage on 8"VC Main | 8" VC, TV main and evaluate for maintenance site. | Y | Y | Storm drain corner of Wing & Kenyon | Dissipated before next M/H | San Diego storm station 1-10 | Y | Y | N | N/A
192533 | Fax 571-6972 | 6/13/01 - 21:29 | Jeff Wilder | 6544160 | City of San Diego | 2001-06-13 14:31 | 6/13/01 - 20:30 | 537 | 246 | 6066 Miramar Road | San Diego | SD | 92037 | Private Lateral | 1 | Construction | Contractor broke lateral during construction | Private Lateral, 11-11 area, vacuum 7-31 out. | Y | Y | Soaked into canyon side | N/A | N/A | Y | Y | N | N/A
192763 | Fax 571-6972 | 6/14/01 - 23:25 | Jeff Wilder | 6544160 | City of San Diego | 2001-06-14 18:56 | 6/14/01 - 20:18 | 4100 | 3895 | Regents Road and SR 52 (Marian Bear Park) | San Diego | SD | 92117 | 8"VC | 1 | Roots | Roots in main caused stoppage | 8" VC, Contained spill, pumped overflow, Rod main, refer for cleaning. | Y | N | Dry creek bed in San Clemente Canyon | N/A | N/A | Y | Y | N | N/A
193036 | Fax 571-6972 | 6/15/01 - 17:18 | Jose Hernandez | 6544160 | City of San Diego | 2001-06-15 10:30 | 6/15/01 - 12:00 | 30 | 0 | Pacific Highway & Hawthorn Street | San Diego | SD | 92101 | 6"CP | 1 | Gravity Break | Broken pipe in 6"CP | 6" CP, Machine Rod, refer for repairs, recommend Accelerated Gp Job. | N | N | N/A | N/A | Dried up on street | Y | Y | N | N/A
193668 | Fax 571-6972 | 6/20/01 - 00:02 | Jeff Wilder | 6544160 | City of San Diego | 2001-06-19 19:06 | 6/19/01 - 20:02 | 168 | 51 | 3953 9th Avenue | San Diego | SD | 92103 | 6" Main | 1 | Roots | Roots in main | 6" VC, Vacuum overflow, Rod main. | N | N | N/A | N/A | Soaked into hillside behind property | Y | Y | N | N/A
194891 | Fax 571-6972 | 6/27/01 - 13:00 | Gary Neel | 6544160 | City of San Diego | 2001-06-27 08:54 | 6/27/01 - 10:00 | 99 | 0 | 5310 Canterbury Drive | San Diego | SD | 92116 | 6"CP | 1 | Grease | Grease and roots caused blockage in sewer main | 6" CP, Machine rod, recommend TV. | N | N | N/A | N/A | Dried up on property at 5310 Canterbury Drive | Y | Y | N | N/A
195472 | Fax 571-6972 | 6/29/01 - 16:05 | Doug Branco | 6544160 | City of San Diego | 2001-06-29 14:06 | 6/29/01 - 14:50 | 88 | 0 | 11717 Joyas Court & Colina Dorado | San Diego | SD | 92124 | 8"PVC | 0 | Roots | Flushed line to relieve stop caused by roots & grease, removed soft drink bottle from line | 8" PVC, Flushed line, refer to area supervisor. | Y | Y | Entered storm drain at Joyas Court & Colina Dorado & dissipated in system | San Diego River/Pacific Ocean | N/A | Y | Y | N | N/A
10503 | FAX | 2001-05-03 09:00 | SERAFIN PEREZ | 619-691-5027 | City of Chula Vista | 2001-05-03 09:00 | 2001-05-03 14:30 | 660 | 420 | 1610 &1660 BROADWAY | CV | SD | 91911 | CLEAN OUT | 0 | UNKNOWN | N/A | PRIVATE LINE- CONTAINMENT ONLY | NO | YES | N/A | N/A | N/A | NO | NO | NO | N/A | PRIVATE LINE
10525 | FAX | 2001-05-25 11:00 | MARK SANCHEZ | 619-691-5027 | City of Chula Vista | 2001-05-25 11:00 | 2001-05-25 19:00 | 500 | 475 | BEHIND 681 PALOMAR ST | CV | SD | 91911 | SEWER MANHOLE | 0 | GREASE | BLOCKAGE WAS CAUSED BY GREASE | FLUSHED LINE SEVERAL TIMES AND T.V. THE LINE | NO | YES | N/A | STORM DRAIN | OPEN DRAIN CHANNEL | YES | NO | NO | N/A | STORM DRAIN WAS VACCUMED AND FLUSHED
10601 | FAX | 2001-06-01 08:00 | STEVEN GONZALES | 619-691-5027 | City of Chula Vista | 2001-06-01 08:00 | 2001-06-01 14:45 | 500 | 240 | 275 ORANGE AVE | CV | SD | 91911 | CLEAN OUT | 0 | GREASE | BLOCKAGE ALSO CONSISTED OF RAGS & MOP | PRIVATE LINE- CONTAINMENT ONLY | NO | YES | N/A | N/A | GUTTER | NO | NO | NO | N/A | PRIVATE LINE
2Q01 | 619-371-6972 | 4/8/01@ 10:00 am | Driss Elwardi | 619-667-1152 | City of La Mesa | 2001-04-08 09:00 | 2001-04-08 15:30 | 4500 | 3800 | 8855 Dallas St--La Mesita park | La Mesa | San Diego | 91942 | 8" v.c. |  | Blockage, Construction | Cal-trans has had a problem at this location for over a year. The city met with Cal-trans and their contractor last week regarding these problems. Debri entered the sewer system during construction and continues to plague the system to this date. | City crews have temporarily cleared the blockage. Cal-trans has also been notified. | Yes | Yes | Alvarado drainage channel | None | N/A | Yes | No | No | N/A
00116 | Mark McCabe, Voice Mail, Fax | 2001-04-25 10:00 | Charles Kamenides | (619) 522-7380 | City of Coronado | 2001-04-25 09:30 | 2001-04-25 10:00 | 60 | 30 | Storm drain outfall on Strand Way in front of 1710 Avenida del Mundo | Coronado | CA | 92118 | Storm drain outfall | 0 | Other | La Playa Tower: 3" pipe broken in closed loop air conditioning system. Cooling fluid (Chemsearch 777) ran into roof drain and down into storm drain and into bay. | Manager stopped leak and repaired pipe. Notified Fire Dept. who called County Environmental Health. Tests showed okay to remove chemical from storm drain using Vactor and deposit into sanitary sewer system. | Yes | Yes | San Diego Bay | N/A | N/A | Y | Y | N | N/A | Spoke with Mark McCabe, we were informed that posting was not necessary.
00117 | Fax | 2001-05-10 17:30 | Charles Kamenides | (619) 522-7380 | City of Coronado | 2001-05-10 17:30 | 2001-05-10 18:30 | 300 | 300 | 511 Marina Avenue | Coronado | CA | 92118 | Lateral/Main line | 0 | Grease/pipe failure | Stoppage in City's main line, Tenth/Alameda. Spill occurred because private lateral had a hole in it, causing sewer to spill into street | Cleared City line, cleaned up spill, located owner of lateral and directed him to repair line. | No | Yes | N/A | N/A | N/A | Y | N | N | N/A | Because we recovered all sewer water no posting or notifications needed.
001-008 | N/A | 4/19/01 1730 | Sheriff Dept | () 911 | City of Imperial Beach | 2001-04-19 17:30 | 2002-04-19 18:00 | 20 | 20 | Fern between Louden and California | Imperial Beach | CA | 92132 | M/H#434 | 0 | Grease/Small Roots | Vactor deployed to alleviate blockage. Spill cleaned using Vactor. | Jetted line/Cleaned spill | N | N | N/A | N/A | Vactor to Sewer | N | N | N | 0 | This line is a candidate for RootX treatment
001-002 | N/A | 7/25/2000 1420 | Apt Manager | Unk | City of Imperial Beach | 2000-07-25 14:15 | 2000-07-25 14:45 | 35 | 35 | 1035 Georgia St MH# 675 | Imperial Beach | CA | 92132 | MH# 675 | 1 | Grease blockage in City of San Diego Line | Grease blockage in City of San Diego Line. San Diego MH# 392 had a grease blockage 15 feet from the MH causing an overflow at Imperial Beach MH# 675 | Vactor truck used to clear line from MH# 392 to MH# 675. | N | N | N/A | N/A | Vactor to Sewer | N | N | N | 0 | Reported by Imperial Beach because we were the repairing agency. This should be recorded as a San Diego Spill.
001-009 | N/A | 5/01/2001 0900 | Bayside School Maint. Pers | Unk | City of Imperial Beach | 2001-05-01 08:55 | 2001-05-01 09:05 | 2 | 2 | 490 Emory Street | Imperial Beach | CA | 92132 | MH#221 | 1 | Grease Blockage | School Maint person called to report spill. Vactor deployed. Grease blockage between #221 & #227. Vactor cleared/cleaned/snaitised. | Vactor cleared the line and then cleaned all lines leading to P.S.#10 | N | N | N/A | N/A | Vactor to Sewer | Y | N | N | 0 | I called Clay Clifton of S.D. Dept of Health. He states that all spills must now be reported to him.
1002 | Victor Vasquez | 2001-05-02 14:00 | Doug Brown | (619) 670-2271 | Otay Water District | 2001-05-20 06:30 | 2001-05-02 07:45 | 750 | 50 | Forcemain 1/3mi.South of plant | Spring Valley | SD | 91978 | 3' X 3 1/2' concrete air vac housing | 0 | corrosion | a small hole developed in the 2" coupling suppoprting a 2" air vac assembly | A new 2" corp.,nipple and coupling were used to replace the old materials. | N | N | Sweetwater River | Sweetwater Lake | Absorption into roadway and shrubbed hillside | N | N | N | 0 | Chlorinated tertiary effluent was quickly absorbed into the ground
O00140 | 858-467-2952 | 2001-04-23 16:00 | Patti S. Page | (760) 723-5640 | Fallbrook Public Utility District | 2001-04-23 11:50 | 2001-04-23 14:10 | 4300 | 300 | 2500 Block S. Mission Rd. & 825 Winterhaven Rd. | Fallbrook | SD | 92028 | Manhole & Cleanout | 1 | Vandalism | Two big chunks of concrete were blocking downstream outlet of manhole. Vandalism. | Flushed from manhole J-3 to J-52 and moved concrete enough to get flow started. Vacuumed about 2000 gallons out of manhole J-4 and removed concrete and opened flow. Will flush and clean lines in the morning. | Y | N | Ostrich Creek | San Luis Rey River | Overflow at 825 Winterhaven out of cleanout overflowed into parking lot and into a holding pond. See comments. | Y | Y | Y | 3 | Washed down parking lot at 825 Winterhaven. Shoveled solids into buckets and vacuumed up wash down water and water in holding pond. Disinfected lot. Did not reach secondary receiving waters. Posted to "Hellers Bend" about 1 mile downstream. Moderate
O00141 | 858-571-6972 | 2001-04-26 08:00 | Patti S. Page | (760) 723-5640 | Fallbrook Public Utility District | 2001-04-25 15:10 | 04/25/01 16.15 | 240 | 20 | 148 Bamboo | Fallbrook | SD | 92028 | Cleanout and Manhole | 1 | Grease | Grease blockage in mainline. | Opened with flush truck about 259 feet. Flushed main and checked downstream manhole. | Y | Y | None. Percolated into ground. | None | Percolated into ground of dry drainage ditch. | Y | N | Y | 3 | Work order was originally given to water Dept as water running down street. Water Dept contacted Collections at about 15:50 and told us there was sewage coming out a manhole. Overflow went along curb into drainage ditch and percolated into ground. Drai
O00142 | Quarterly |  | Joel V. Holt | (760) 723-5640 | Fallbrook Public Utility District | 2001-06-11 08:00 | 2001-06-11 09:00 | 100 | 60 | 566 Ammunition Rd. | Fallbrook | SD | 92028 | Cleanout and Manhole | 1 | Grease | Mainline plugged by grease. | Flushed mainline open about 160 feet. Dammed up sewage around cleanout. Rest of sewage dried up along roadway. | N | N | NA | NA | Along paved road and damed up entry to storm drain to prevent overflow entering storm drain. | N | N | N | NA | Washed and vacuumed up wash down water along roadway and around cleanout.
O00143 | Quarterly |  | Joel V. Holt | (760) 723-5640 | Fallbrook Public Utility District | 2001-06-01 11:00 | 2001-06-01 12:00 | 30 | 10 | 427 Minnesota | Fallbrook | SD | 92028 | Cleanout | 1 | Roots | Mainline was plugged downstream about 50 feet. | Opened mainline. Upon arrival it had partially opened on its own. | N | N | NA | NA | In yard under car port. | N | N | N | NA | Vacuumed up standing sewage and washed and disinfected area.
N/A (LESS THAN 1,000 GAL.) | SCOTT WELDON | 5/20/2001 19:40:00 PM | ED BRADLEY | (760) 728-1178 | RAINBOW MWD | 2001-05-20 14:30 | 5/20/2001 16:30:00 PM | 480 | 0 | LITTLE GOPHER CANYON ROAD | VISTA | SD | 92084 | 33G-M090 | 0 | GREASE | GREASE BLOCKAGE IN SEWER MAIN CAUSED MANHOLE OVERFLOW | JET RODDED SEWER MAIN. | N | N | N/A | N/A | OPEN FIELD, HEAVY BRUSH | Y | N | N | 0 | SPILLED INTO OPEN FIELD, SEWAGE DISSIPATED. THE SPILL OCCURRED FROM MANHOLE LOCATED APPROXIMATELY 200 FT FROM INTERSECTION OF GOPHER CANYON ROAD AND LITTLE GOPHER CANYON ROAD. THOMAS GUIDE 1068 B5. NOTE: SCOTT WELDON REQUESTED COPY OF SPILL REPORT FAXED TO HIM BY THE CRWQCB.
001021 |  |  | Mike Heiser | 7604355870 | Water Utilities Dept. City of Oceanside | 2001-05-23 11:05 | 05/23/01 1130 | 75 | 75 | 3877 Bay Leaf Way | Oceanside | SD | 92054 | Private Clean Out | 1 | Roots | Roots and a few rocks were found in line and removed. | Line was jetted to next manhole, and debris removed. | N | N | N/A | N/A | Curb & Gutter | Y | N | N | N/A | Hydrant washed street. Vactor removed ALL of spill & washdown water.
001022 | Victor Vasquez | 06/12/01 1415 | Guss Pennell | 7604355804 | Water Utilities Dept. City of Oceanside | 2001-06-12 11:30 | Unknown | 300 | 300 | 1515 South Melrose | Vista | SD | 92083 | Private Clean Out | 1 | Unknown | Private sewer system at apartment complex. | Plumber has been called. | Y | Y | Vista Storm Drain | Oceanside Storm Drain | Collector @ Cannon & Melrose | Y | N | N | N/A | Oceanside crew recovered until Vista's crew took responsibility.
001023 |  |  | Paul Hojo | 7609664870 | Water Utilities Dept. City of Oceanside | 2001-06-22 18:30 | 06/22/01 1845 | 150 | 150 | 1330 South Tait Street | Oceanside | SD | 92054 | Primary Digester Transfer Box | 1 | Blockage | Blockage in Primary Transfer pipe to Secondary Digester caused sludge to overflow onto paved area between digesters. | Called out Vactor to remove sludge from storm drain manhole downstream. | Y | y | Plant Storm Drain | N/A | All recovered. | N | N | N | N/A | Street was first flushed with potable water, then sludge was recovered.
OO1028 | Fax | 2001-04-20 10:00 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2001-04-20 09:00 | 2001-04-20 10:32 | 450 | 100 | 1741 Ocean Way | Laguna Beach | OR | 92651 | 4 inch Clean-Out | 1 | Sheet Metal | A section of sheet metal lodged in the manhole just upstream of the Pearl Street Pump Station | Removed all debris from the manhole and hydro jetted the 8 inch gravity line going into the station. Recovered about 100 gallons from the containment area on the beach. Flushed the storm drain into our recovery area. | N | Y | None | None | Pumped back into the City's sewer system | Y | N | Y | 3 | None
OO1029 | Fax | 2001-04-23 08:50 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2001-04-23 08:45 | 2001-04-23 09:15 | 50 | 0 | 400 Blk. Alta Vista Way | Laguna Beach | OR | 92651 | Manhole at Alta Vista/Lomita Way | 1 | Roots | 8 inch gravity line was blocked by roots coming from private laterals | City crews jetted to open up the stoppage. We then rodded to clean out any other debris. This area will be added to our contract cleaning and TV contract. City schedule will be to clean this section every six months. | N | Y | None | None | Open canyon area. All water soaked into the ground | Y | N | N | None | None
OO1030 | Fax | 2001-04-23 09:10 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2001-04-23 09:05 | 2001-04-23 09:40 | 10500 | 10500 | 1200 Laguna Canyon Road | Laguna Beach | OR | 92651 | Manhole at intersection of Laguna Canyon Road/Milligan | 1 | Roots | Roots blocked main line | Rodded the line. Bermed channel outlet. Pumped collected waters into the sewer system for four hours after overflow stopped. | Y | Y | Laguna Canyon Channel at Milligan | None | Bermed at beach outlet and pumped into nearby sewer system | Y | Y | Y | 2 | None
OO1031 | Fax | 2001-05-15 14:29 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2001-05-23 12:00 | 2001-05-15 12:20 | 20 | 20 | 410 Broadway | Laguna Beach | OR | 92651 | 410 Broadway | 1 | Blockage | Lateral at 410 Broadway was plugged | Asked manager at 410 Broadway not to use water and they needed a plumber. Vacuumed with jetter and hosed sidewalk with water back into the jetter truck. | N | N | None | None | Ran down planter wall at 410 Broadway onto sidewalk and onto the the street. Did not reach the storm drain outlet | Y | N | N | None | Private Sewer Lateral - Courtesy Report
OO1032 | Fax | 2001-06-01 16:15 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2001-05-25 10:00 | 2001-05-25 10:45 | 10 | 10 | 1848 Catalina | Laguna Beach | OR | 92651 | Cleanout for lateral | 1 | Blockage | Plugged lateral due to roots | Contacted renter to call plumber and owner. City crews blocked off downstream outlet and flushed the drain with about 1000 gallons of water. All waters were vacuumed up and returned to the sewer system. | N | Y | None | None | Storm drain at 1856 Catalina - and final destination was the vacuum truck | Y | N | N | None | Private Sewer Lateral - Courtesy Report
OO1033 | Fax | 2001-06-04 20:50 | City of Laguna Beach | (949) 497-0765 | Laguna Beach | 2001-06-04 17:05 | 2001-06-04 18:30 | 3000 | 2850 | 211 N. Coast Hwy | Laguna Beach | OR | 92651 | 8 inch Force Main | 1 | Line Break | The cause of the flow is most likely a line break or separation. Portions of the line will have to be excavated to determine the actual cause of the break. A parallel force main is handling the flow while repairs are made. | The line will have to be repaired at the break;slip lined or replaced depending on the cause of the overflow and condition of the pipe. A parallel force main is presently handling the flow. | N | Y | None | None | Diverted back into the sewer system by 17:55. Other overflow recovered at the beach and affected sand removed or flushed. Returned tot he sewer system | Y | Y | Y | 3 | None
108 | FAX | 25 Apr 01 1130 | A J Howard | 949.366.1553 | CSC | 2001-01-25 06:30 | 25 Apr 01 0710 | 80 | 30 | La Pata @ Rick Steed Park Access Road | San Clemente | OR | 92672 | Sewer MH at Rick Steed Park | 0 | Downstream pump station failure | Suction lift pumps at La Pata Pump Station failed | Plant Operator and two Vactor Crews responded to station at 0650. Plant operator observed a flow of less than 2 GPM exiting the sewer manhole upstream of the pump station. Vactor crews set up containment at sewer manhole where flow was exiting and at catch basin where flow was entering. | N | Y | N/A | N/A | 30 Gallons captured and retruned to sanitary sewer system / 50 gallons disipated into soil on the Pacific Golf Course | Y | N | Y | N/A
109 | Victor Vasquez | 26 Jun 01 1513 | J Elston | 949.366.1553 | CSC | 2001-06-26 10:00 | 26 Jun 01 2230 | 3600 | 3200 | 100' West Ave. De Las Palmeras / Calle Ariana | San Clemente | OR | 92672 | Cypress Shores Pump Station Force Main | 0 | Force main leak | Force main cracked at 45 degree fitting | DisOp arrived at 1435 and observed moist surface on roadway, identified as raw sewage and set up containment structures. At 1445 two Vactor Teams arrived and captured all spilt contents. During excavation pipe burst allowing <400 gallons out of primary containment. Secondary containment area at RR Tracks captured this flow. Repair team completed replacement of pipe and fitting by 2230 26 Jun 01. | N | Y | N/A | N/A | Vactor / Sanitary Sewer System | Y | N | N/A | N/A | Vactor teams remained on site throughout night to bypass pump station until concrete thrust block set and cured. Force main was placed back into service at 0700 27 Jun 01. Larry Honeyborne w/OCHCA on site evening of 26 June 01 to inspect containment, capture and repair efforts. Spilled contents at secondary containment in OCTA Rail Road ROW was removed by Vactor teams and disposed of back to sanitary sewer system on 27 June 01.
1004 | Victor Vasques | 05/04/01 0900 | Anne Briggs | (909) 928-3777 | E.M.W.D. | 2001-05-04 06:30 | 05/04/01 0930 | 6300 | 5000 | First Street | Temecula | RV | 92591 | Manhole #01901 | 0 | Blockage | The manhole had a broken cement grade ring in the downstream manhole #01902. This is part of a City of Temecula bridge project that has been ongoing for several months. | Started a bypass and stopped overflow. Built a dam to help stop the flow into the river. After blockage was broke loose, recovery efforts began. 5,000 gallons were vacuumed up from both sides of the creek under the First Street bridge. Lime was spread on areas taht were not in direct flow of the creek and signs were posted on both sides of the creek and 1/2 mile down stream. | Y | Y | Murrieta Creek | Santa Margarita River |  | Y | Y | Y | 7
1005 | Charleen Robbins and Damian Meins | 05/11/01 1330 | Anne Briggs | (909) 928-3777 | E.M.W.D. | 2001-05-11 12:30 | 05/11/01 1330 | 1200 | 300 | Via Montezuma/Del Rio | Temecula | RV | 92591 | Manhole | 0 | Blockage | Contractor moved manhole cover with heavy equipment and dirt and other debris got into the manhole | Cleaned and repaired manhole. | Y | Y | Murrieta Creek |  |  | Y | Y | Y | 7
1006 | Chiara Clemente | 06/13/01 1325 | David Morycz | (909) 928-3777 | E.M.W.D. | 2001-06-13 10:44 | 06/13/01 1123 | 1950 | 20 | Via Montezuma/Commerce Circle Drive | Temecula | RV | 92590 | Manhole | 0 | Construction Debris | Contractor pushed debris into manhole | Removed debris | Y | Y | Murrieta Creek | Santa Margarita River | N | Y | Y | Y | 5
001019 | VICTOR VASQUEZ | 01/06/01 1802 | Cpl Osunabaez, R | 7607259761 | MCB, CAMP PENDLETON | 2001-01-06 10:15 | 2001-01-06 10:35 | 2500 | 0 | BLDG 51056 | CAMP PENDLETON | SD | 92055-5008 | MANHOLE 11Y106 | 3 | PUMP STATION FAILURE | PUMP CONTROL FAILURE, ELECTRICIAN COULD NOT FIND ANY APPARENT FAULT. | CORRECTIVE: PLACE PUMPS IN MANUAL TO STOP OVERFLOW-LATER RETURNED PUMPS TO AUTO AND HAD NO PROBLEMS. PREVENTATIVE: ELEC. ON SITE 1/08/01, ELEC. FOUND NOTHING WRONG WITH CONTROL SYSTEM FAULT WAS CAUSED BY A POWER SURGE WHICH DISABLED THE CONTROLS TEMPORARILY. SYSTEM IS IN AUTO AND OPERATING NORMALLY. | Y | Y | DRY SAN ONOFRE CREEK | PACIFIC OCEAN | NO FLOW TO ACTUAL SURFACE WATER | Y | Y | N | NA | SPILL TRAVELED FROM MH SOUTH 225' OVER ASPHALT TO STORM DRAIN. 1500' THROUGH SD,FLOW EXITED SD IN VEGETATED AREA & PERCOLATED INTO DRY CREEK BED.NO EXPECTED PUBLIC CONTACT
001020 | VICTOR VASQUEZ | 01/20/01 1943 | Cpl Osunabaez, R | 7607259761 | MCB, CAMP PENDLETON | 2001-01-19 18:00 | 2001-01-21 02:00 | 810 | 800 | BLDG 51918 51 AREA BEACH HOUSES | CAMP PENDLETON | SD | 92055-5008 | 6" CLAY SEWER LINE | 1 | CONSTRUCTION | A SUBCONTRACTOR DEMOLISHING A BUILDING HIT A 6" SEWAGE PIPE WHICH HE THOUGHT WAS A BLDG. LINE SCHEDULED TO BE REMOVED, BECAUSE HE WAS NOT PROPERLY BRIEFED BY THE PRIME | CORREC:500 GAL PUMPER TRUCK ARRIVES ON SITE @ 0800 JAN 20,PUMPED PIT ALL DAY TO PREVENT BUILDUP,RECOVERED SEWAGE IS DISPOSED OF @ TREATMENT PLANT , REPAIRS COMPLETED @ 0200,JAN 21 PREVENTIVE: ROICC TO BRIEF ALL CONTRACTORS ON THE LOCATION OF ALL SEWAGE LINES. | N | N | NA | NA | NO FLOW TO ACTUAL SURFACE WATER, PERC'D INTO SAND | Y | NA | Y | 1 | THE SPILL WAS CONTAINED IN A PIT, 20’ X20'. A PUMPER TRUCK WAS USED TO RECOVER 800 OUT OF THE 810 GALLONS SPILLED, REPLACED BROKEN 6" PIPE WITH 80' SECTION OF PVC PIPE. AFTER REPAIRS WERE MADE, THE PITS WERE BACKFILLED AND SIGNS REMOVED.
001021 | VICTOR VASQUEZ | 01/27/01 1943 | Cpl Osunabaez, R | 7607259761 | MCB, CAMP PENDLETON | 2001-01-27 15:00 | 2001-01-27 18:00 | 2000 | 0 | LIFT STATION 51056 | CAMP PENDLETON | SD | 92055-5008 | 2 UNNUMBERED MANHOLES | 3 | PUMP STATION FAILURE | A POWER SURGE CAUSED THE LIFT STATION CONTROL PANEL TO MALFUNCTION, WHICH KEPT LIFT STATION PUMPS FROM PUMPING | CORRECTIVE: RESET CONTROL PANEL CLEARED ALARM, LIFT STATION BACK IN NORMAL OPERATION. HOSED DOWN SPILL TO STORM DRAIN & LIMED AFFECTED AREAS PREVENTATIVE: TICKET # 1193258 WAS SUBMITTED 1/29/01 TO ELECTRONIC SHOP TO TROUBLE SHOOT CONTROL PANEL. FOUND NOTHING WRONG. | Y | Y | SAN ONOFRE CREEK | PACIFIC OCEAN | NO FLOW TO ACTUAL SURFACE WATER.SAN ONOFRE CREEK BED IS DRY | Y | Y | Y | 3 | SPILL OVERFLOWED MANHOLES & TRAVELED 100' DOWN STREET TO STORM DRAIN, 1500' THRU STORM DRAIN TO DRY SAN ONOFRE CREEK BED. CREEK MOUTH REMAINS CLOSED TO OCEAN.
001022 | VICTOR VASQUEZ | 02/01/01 1430 | Cpl Osunabaez, R | 7607259761 | MCB, CAMP PENDLETON | 2001-02-01 07:30 | 2001-02-01 09:30 | 600 | 0 | BLDG # 31611 | CAMP PENDLETON | SD | 92055-5008 | GREASE TRAP AND CLEAN OUT | 1 | DEBRIS | FOOD AND PAPER WAS ALLOWED TO GO DOWN THE DRAIN TO THE GREASE TRAP, PLUGGING UP THE SEWER LINE CAUSING GREASE TO OVERFLOW FROM GREASE TRAP AND 6" CLEAN OUT. | CORRECT: JETTED LINE THRU CLEAN OUT TO REMOVE BLOCKAGE. USE SHOVEL TO PUT GREASE BACK INTO PIT, USED HOT WATER TO WASH DOWN AREA. PREVEN: INFORMED MESS HALL PERSONNEL ABOUT THE BLOCKAGE AND WHY IT OCCURRED, ASKED THEM TO KEEP AN EYE ON FLOOR DRAINS. | Y | Y | PACIFIC OCEAN,(VIA EARTHEN DITCH) |  | NO FLOW TO ACTUAL SURFACE WATER | Y | NA | NA | NA | SPILL TRAVELED FROM GREASE TRAP COVER & CLEANOUT INTO CONCRETE DITCH, 45' THRU CONCRETE DITCH TO STORM DRAIN, 2700' THRU STORM DRAIN CULVERT TO EARTHEN DITCH WHERE IT TRAVELED 255'& PERCOLATED INTO DIRT & WEEDS. NO EXPECTED PUBLIC CONTACT.
001023 | VICTOR VASQUEZ | 02/20/01 0907 | Cpl Osunabaez, R | 7607259761 | MCB, CAMP PENDLETON | 2001-02-20 04:46 | 2001-02-20 07:30 | 5000 | 1000 | LIFT STATION 41300 | CAMP PENDLETON | SD | 92055-5008 | LS 41300, WET WELL | 1 | POWER FAILURE | ELECTRICAL PRIMARY WIRES FROM POLE TO NEW TRANSFORMER SHORTED OUT, BLOWING 2 FUSES ON THE POLE. LIFT STATION IS CURRENTLY BEING UPGRADED BY CONTRACTOR, STANDBY UP GENERATOR WAS NOT IN PLACE. | CORRECTIVE: CONNECTED PORTABLE GENERATOR, WASH DOWN ASPHALT AREA WITH FRESH WATER, WATER SERVICE TO CAMP SECURED @ 0720.VACUUM TRUCK RECOVERED 1000 GAL.FROM ASPHALT/DIRT DEPRESSION ON SITE. PUMPED UPSTREAM MANHOLE FROM WET WELL TO PREVENT ADDITIONAL SPILL.. PREVEN: REPLACED PRIMARY FEEDER WIRE (PFW) SIZE TO TRANSF.BUT DID NOT INCREASE WIRE SIZE PER A/E SPECS.AFTER ANOTHER SPILL OCCURRED ON 2/23/01, PFW SIZES WERE INCREASED FROM A # 4 TO A # 2, 15KV ON THE SAME DAY. | Y | N | UNNAMED TRIBUTARY TO PACIFIC OCEAN | PACIFIC OCEAN | NO FLOW TO ACTUAL SURFACE WATER, PERC'D INTO GROUND | Y | Y | N | NA | TRAVELED 20' FROM WET WELL (ASPHALT) TO THICK VEGETATION AREA 150'& PERCOLATED INTO GROUND. TOTAL DISTANCE TRAVELED 170'. NO EXPECTED PUBLIC CONTACT.
001024 | VICTOR VASQUEZ | 02/23/01 1104 | Cpl Osunabaez, R | 7607259761 | MCB, CAMP PENDLETON | 2001-02-23 06:15 | 2001-02-23 07:25 | 1800 | 400 | LIFT STATION 41300 | CAMP PENDLETON | SD | 92055-5008 | LS 41300,WET WELL | 2 | POWER FAILURE | ELECTRICAL PRIMARY FEED WIRES FROM POLE TO NEW TRANSFORMER SHORTED OUT. | CORRECTIVE: CONNECTED PORTABLE GENERATOR, WASH DOWN ASPHALT AREA WITH FRESH WATER, WATER SERVICE TO CAMP SECURED @0740.VACUUM TRUCK RECOVERED 400 GAL.FROM ASPHALT/DIRT DEPRESSION ON SITE. PREVENTATIVE: 2/23/01 REPLACED & INCREASED PRIMARY WIRE SIZE FROM #4 TO #2, 15 KV CABLE TO TRANSFORMER.IT'S A 4 KV SYSTEM. INSTALLED A MANUAL TRANSFER SWITCH ON KTR'S PORTABLE GENERATOR UNTIL PERMANENT GENERATOR'S INSTALLED. | Y | N | UNNAMED TRIBUTARY TO PACIFIC OCEAN | PACIFIC OCEAN | NO FLOW TO ACTUAL SURFACE WATER, PERC'D INTO GROUND | Y | Y | N | NA | TRAVELED 20' FROM WET WELL (ASPHALT) TO THICK VEGETATION AREA 150'& PERCOLATED INTO GROUND. TOTAL DISTANCE TRAVELED 170'. NO EXPECTED PUBLIC CONTACT.
001025 | VICTOR VASQUEZ | 03/01/01 0929 | Cpl Osunabaez, R | 7607259761 | MCB, CAMP PENDLETON | 2001-03-01 06:45 | 2001-03-01 07:55 | 3000 | 300 | LIFT STATION 51056 | CAMP PENDLETON | SD | 92055-5008 | 2 UNNUMBERED MANHOLES @ LS 51056 | 4 | GREASE | PUMP CONTROLS MALFUNCTION- FLOATS THAT CALL FOR THE PUMP OPERATION WERE BOUND IN GREASE INSIDE STILLING TUBE. | CORRECT: PLACED PUMPS IN MANUAL. FREE FLOATS FROM GREASE. FRESH WATER WASH DOWN OF AFFECTED AREA. PUMPER TRUCK RECOVERED 300 GALLONS. PREVENT: BASE IS INSTALLING ULTRA SONIC LEVEL CONTROLLER TO REPLACE MECHANICAL FLOAT CONTROLS. JOB STARTED 03/01/01 | Y | Y | SAN ONOFRE CREEK | PACIFIC OCEAN |  | Y | Y | Y | 5 | SPILL TRAVEL FROM MANHOLE 100' ASPHALT ALONG STREET TO STORM DRAIN 1500' THROUGH STORM DRAIN TO SAN ONOFRE CREEK HIT RUNNING WATER FLOWING TO PACIFIC OCEAN. TOTAL DISTANCE 1600' TO CREEK (6500' TO OCEAN).DEH LIFTED QUARANTINE 3/05/01.
001026 | VICTOR VASQUEZ | 03/12/01 1148 | Cpl Osunabaez, R | 7607259761 | MCB, CAMP PENDLETON | 2001-03-12 09:30 | 2001-03-12 11:00 | 700 | 0 | BLDG.53502, 2 GREASE TRAPS | CAMP PENDLETON | SD | 92055-5008 | 2 GREASE TRAPS | 1 | GREASE | GREASE & DEBRIS (PAPERS & PLASTIC WARE) MESS HALL PERSONNEL REMOVED THE SCREENS FROM THE DRAINS RESULTING IN PLUGGED DRAINS. | CORRECTIVE: SECURED DRAIN SCREENS IN GALLY, RAM JETTED LINES. HOSE DOWN AREA, NO NEED FOR DISINFECTION ALL GRAY WATER. PREVENTATIVE: ADVISE PERSONNEL NOT TO REMOVE SCREENS FROM DRAINS OR THEY WILL BE FINED. | Y | Y | NORTH FORK OF THE SAN ONOFRE CREEK | SAN ONOFRE CREEK | NO FLOW TO ACTUAL SURFACE WATER | Y | NA | NA | NA | SPILL FLOWED IN 2 PATHS; FROM GT 1 OFF LOADING DOCK TO ASPHALT 50' TO CURB/GUTTER-450' TO STM DRN 120' THRU STM DRN, TO DRY SO CK BED, & 100' INTO HEAVY VEGETATION.TOTAL DISTANCE 890' FROM GT 2 170' ACROSS PARKING LOT TO CURB/GUTTER JOINED FLOW FROM GT 1.NO EXPECTED PUBLIC CONTACT.
001027 | VICTOR VASQUEZ | 2001-05-02 10:22 | COLLEEN ECKENROAD | 7607259761 | MCB, CAMP PENDLETON | 2001-05-01 15:00 | 2001-05-02 08:53 | 18000 | 8100 | 101 A & B MARINE DR. | CAMP PENDLETON | SD | 92055-5008 | 5" CLEANOUT | 1 | ROOTS | ROOTS, TOYS AND FOREIGN DEBRIS IN SEWER MAIN CAUSED BLOCKAGE AND SPILL FROM BROKEN CLEAN OUT CAP. | COR:USED JETTER TO CLEAR BLOCKAGE-CAPTURE AND REMOVE DEBRIS AT MH.JET FROM MH 1Y187 TO 1Y188. WASH DOWN AREA-FRESH WATER,LIME AREA AROUND C/O.RECOVER 8100 GAL. WITH PUMPER TRUCK, DUMPED N NEARBY MH. PREVEN: CONTINUE WITH ALL ONGOING SEWER PM'S.REPLACE C/O CAP. TREE BY MH 1-Y-87 WILL BE REMOVED. | Y | Y | LAKE O'NEILL | SANTA MARGARITA RIVER/ PACIFIC OCEAN |  | Y | Y | Y | 6 | FROM C/O 10' ACROSS DIRT, 150' CONCRETE TO STORM DRAIN, 100' THRU STM DN TO NATURAL DRAINAGE 3800' TO LAKE O'NEILL,2900' ACROSS LK O'NEILL OVER DAM, TO EARTHEN DRAINAGE DITCH 6400' TO SMR,TOTAL DISTANCE TO SMR 13,360'. APPROX.9 MILES TO OCEAN. RESIDENCE TIME OF LAKE O'NEILL= 4680 DAYS. CURRENT OUTFLOW RATE @ 0.3 AF/D-LAKE= 1404 AF.SIGNS POSTED 3 DAYS @ C/O.
001028 | VICTOR VASQUEZ | 2001-05-13 09:36 | CPL OSUNABAEZ | 7607259761 | MCB, CAMP PENDLETON | 2001-05-12 11:15 | 2001-05-12 11:45 | 200 | 0 | BLDG 51057 | CAMP PENDLETON | SD | 92055-5008 | MANHOLE 11Y-188 | 1 | DEBRIS | MAIN LINE BLOCKAGE CAUSING OVERFLOW FROM MANHOLE. RAGS 60% AND GREASE AND DEBRIS 40% LODGED IN FORCED MAIN CAUSING PARTIAL BLOCKAGE OF LINE. | CORR. USED CAMEL TO PUMP DOWN MH WHILE USING JET TO CLEAR BLOCKAGE. PULLED 3400 GAL FROM MH TO PREVENT ADDITIONAL SPILL SHOVEL UP SOLIDS AND WASH DOWN AREA WITH FRESH WATER AND LIME AREA AROUND MH.PREVENTATIVE: CONTINUAL PM TO SEWER MAINS BASE WIDE. | Y | Y | SAN ONOFRE CREEK | PACIFIC OCEAN | NO FLOW TO ACTUAL SURFACE WATER, STAYED IN STM DRN. | Y | NA | N | NA | FROM MANHOLE 300' ACROSS ASPHALT TO STORM DRAIN APPROX 100' INTO STM DRN, FLOW DID NOT EXIT STM DRN. TOTAL DISTANCE TRAVELED 400'. NO EXPECTED PUBLIC CONTACT.
001029 | VICTOR VASQUEZ | 2001-05-15 16:49 | CPL OSUNABAEZ | 7607259761 | MCB, CAMP PENDLETON | 2001-05-14 09:30 | 2001-05-15 10:20 | 50 | 0 | BLDG 520415 | CAMP PENDLETON | SD | 92055-5008 | C/O NEXT TO NEW GYM, BLDG 520415 | 1 | CONSTRUCTION | TEST PLUG WAS LEFT IN LATERAL CAUSING PARTIAL BLOCKAGE OF LINE. | CORR. REMOVE FROM LATERAL TO CLEAR BLOCKAGE. WATER SECURED TO BLDG. ON 05/14/01 TO STOP ADDITIONAL SPILL, RESTORED ON 05/15/01 1020. WASH DOWN AREA AND RECOVER WASH DOWN WITH CAMEL. PREVENT: REPORT TO ROICC BETTER QUALTY ASSURANCE DURING CONTRUCTION . HAVE MCCS IMMEDIATELY REPORT SPILLS WHEN ASSISTANCE REQUIRED. | N | N | NA | NA | NO FLOW TO ACTUAL SURFACE WATER, EVAPORATED ON ASPHALT. | Y | NA | N | NA | FROM CLEANOUT 150' ACROSS ASPHALT. EVAPORATED OFF ASPHALT. NO EXPECTED PUBLIC CONTACT.
001030 | CHIARA CLEMENTE | 2001-05-23 07:54 | CPL OSUNABAEZ | 7607259761 | MCB, CAMP PENDLETON | 2001-05-13 08:00 | 2001-05-22 18:00 | 10 | 0 | STUART MESA BRIDGE | CAMP PENDLETON | SD | 92055-5008 | 6" C/O ON 12" FORCE MAIN BY STUART MESA BRIDGE | 2 | OTHER | 6" STAINLESS STEEL COUPLING ON C/O WEEPING POSSIBLY TOO LOOSE TO HANDLE SURGES TO C/O. | CORR. C/O COUPLING TIGHTENED 2 1/2 TURNS. FILLED IN HOLE ADJACENT TO C/O. PREVENTATIVE: C/O WILL BE REPLACE AT LATER DATE WITH PIPE SECTION. | Y | N | SANTA MARGARITA RIVER | PACIFIC OCEAN | NO FLOW TO ACTUAL SURFACE WATER, PERC'D INTO SAND. | Y | NA | N | NA | SPILL TRAVELED 2' FROM C/O AND PERCOLATED INTO SANDY AREA ADJACENT TO RIVER. NO LIKELY PUBLIC CONTACT.
001031 | CHIARA CLEMENTE | 2001-06-06 17:07 | COLLEEN ECKENROAD | 7607259761 | MCB, CAMP PENDLETON | 2001-06-06 13:00 | 2001-06-06 14:30 | 300 | 200 | DOLPHIN & NAUTILUS, DEL MAR HOUSING | CAMP PENDLETON | SD | 92055-5008 | MH 13-Y-284, 8" CLAY PIPE. | 1 | ROOTS | ROOTS (PRIMARY CAUSE) AND PAPER TOWELS LODGED IN NECK OF THE TROUGH FROM ANOTHER AREA | CORRECTIVE: CLEARED BLOCKAGE WITH RAM JET.LIMED AND WASHDOWN AREA, VACUUM UP EXCESS.RAM JETTED FROM 13-Y-285 BACK TO 13-Y-284 WHERE BLOCKAGE WAS.USED SHOVEL TO SCOOP UP ROOTS AND EXCESS WASTE. PREVENTATIVE: PM PER REGULAR PM SCHEDULE THIS YEAR. | Y | Y | OCEANSIDE HARBOR | PACIFIC OCEAN | NO FLOW TO ACTUAL SURFACE WATER, PERC'D INTO ICEPLANT | Y | NA | Y | 3 | FROM MH OVER GRASS/ASPHALT STREET TO STORM DRAIN 156', AND 144'THROUGH STORM DRAIN INTO DRAINAGE CULVERT AND PERCOLATED INTO ICEPLANT.DRAINAGE CULVERT EMPTYING INTO ICEPLANTS.TOTAL DISTANCE 300'
001032 | CHIARA CLEMENTE | 2001-06-07 08:19 | COLLEEN ECKENROAD | 7607259761 | MCB, CAMP PENDLETON | 2001-06-06 17:05 | 2001-06-06 21:00 | 48300 | 27900 | 130' WEST OF STUART MESA RD, ON MASS 3 RD. | CAMP PENDLETON | SD | 92055-5008 | OVERFLOW FROM C/O, STUART MESA FM | 1 | LINE BREAK | CLEANOUT ON FORCE MAIN FROM LS 31227 FAILED. | CORRECTIVE: C/O REMOVED FROM FM,PUMPER TRUCKS DIVERTED 22,000 GAL. OF SEWAGE FROM LS 31227,DISPOSED AT STP 13. WATER SECURED TO STUART MESA HOUSING TO MINIMIZE FLOW TO LS 31227. EARTHEN BERM CREATED SOUTH SIDE OF DIRT ROAD TO DIVERT FLOW TO LAGOON ON NORTH SIDE OF DIRT ROAD. LIME SPREAD AT SPILL SITE. PREVENTATIVE: CLEANOUT WAS REPLACED WITH A 3' SOLID SECTION OF 12" PVC PIPE. | Y | N | SANTA MARGARITA RIVER | PACIFIC OCEAN | NO FLOW TO ACTUAL SURFACE WATER, PERC'D IN GROUND | Y | Y | Y | 3 | SPILL TRAVELED 50' NORTH OFF DIRT ROAD AND ANOTHER 75' INTO DRY LAGOON. ENTRANCE TO ROAD WILL BE CLOSED TO LIMIT PUBLIC CONTACT.
001033 | CHIARA CLEMENTE | 2001-06-20 15:22 | COLLEEN ECKENROAD | 7607259761 | MCB, CAMP PENDLETON | 2001-06-20 10:00 | 2001-06-20 11:30 | 360 | 220 | EDSON RANGE MEDICAL CENTER BLDG 310514 | CAMP PENDLETON | SD | 92055-5008 | MANHOLE 14-Y-70 | 1 | GREASE | GREASE CAUSED PARTIAL BLOCKAGE IN 10" ACP LINE. | CORRECTIVE: TWO PUMPER TRUCKS WERE USED TO RECOVER 220 GALLONS.A PORTION OF THE SPILL EVAPORATED. RAM JETTED THE LINE TO CLEAR BLOCKAGE. WASHED DOWN AREA. PREVENTATIVE: 31 AREA ON SCHEDULE FOR PM | Y | N | COCKLEBURR CREEK | PACIFIC OCEAN | NO FLOW TO ACTUAL SURFACE WATER EVAPORATED & PERC'D IN DIRT | Y | NA | N | NA | NW FROM MH 40' OVER GRAVEL TO CURB AND GUTTER ON PHILLIPS ST.200' SW TO STEWART MESA RD. 50' NW ACROSS CONCRETE APRON ON PHILLIPS ST. AND PONDED. APROX 50 GAL TRAVELED PAST PONDING AREA 35' INTO VEGETATED SHALLOW EARTHEN DITCH.PERC'D INTO DIRT. TOTAL DISTANCE 325'. NO EXPECTED PUBLIC CONTACT.
001034 | CHIARA CLEMENTE | 2001-06-27 13:38 | Cpl Osunabaez | 7607259761 | MCB, CAMP PENDLETON | 2001-06-26 16:30 | 2001-06-26 19:20 | 15000 | 14000 | ADJACENT BASILONE; ALBATROSS + LONGSPUR | CAMP PENDLETON | SD | 92055-5008 | 8" PVC FORCE MAIN | 1 | LINE BREAK | MECHANICAL COUPLING FAILED. O-RINGS BLEW OUT. DUE TO UNKNOWN CAUSE. | CORR: REPLACED FAILED COUPLING 6/27/01.RECOVERED PONDED SEWAGE W/ 2 PUMP TRUCKS,SWITCHED DISCHARGE LINES@ LS 51056 TO STOP DISCHARGE TO LEAKING LINE.FRESH WATER WASH ASPHALT.LIMED EARTHEN/GRASS AREAS 6/27/01 STM DN PUMPED OUT, REMOVED 500 GAL OF SEWAGE. PREVENT: ENSURE QUALITY ASSURANCE DURING CONSTRUC. | Y | Y | SAN ONOFRE CREEK | PACIFIC OCEAN | NO FLOW TO ACTUAL SURFACE WATER, EVAPORATED & PERC'D IN SOIL | Y | Y | Y | 3 | 3 PATHS:1. FROM MAIN BREAK SPILL TRAVELED 655' S.ALBATROSS (WEST SIDE), 475' ON LONGSPUR & PONDED.2. 710' S.ALBATROSS (EAST SIDE)STM DN,100'THRU STM DN,ACROSS GRASS 50' & PONDED. 3.SAND BAGS PLACED @ SANDPIPER & ALBATROSS TO STOP FLOW THRU HOUSING DIVERTING FLOW 120' INTO EARTHEN STM DN. ALONG BASILONE ROAD. TOT DIS=2110'. 6 SIGNS POSTED NEAR HOUSING.
001035 | CHIARA CLEMENTE | 06/30/01 23:19 | COLLEEN ECKENROAD | 7607259761 | MCB, CAMP PENDLETON | 2001-06-30 18:30 | 2001-06-30 21:00 | 250 | 150 | BUILDING 52609 | CAMP PENDLETON | SD | 92055-5008 | MANHOLE 11-Y-59, 6" ACP | 1 | ROCKS | ROCKS, TRASH, PLASTIC & DEBRIS IN LINE CAUSED THE MANHOLE TO OVERFLOW. | CORRECTIVE: CLEARED STOPPAGE W/ CAMEL'S JET HOSE(RAM JET) SPILL PONDED IN LOW AREA, WHERE 150GAL. WERE RECOVERED.LIMED AFFECTED AREA W/ POTETIAL PUBLIC CONTACT.HOSED STREET. REMOVED ROCKS AND DEBRIS. PREVENTATIVE: INSPECTED AREA FOR MISSING MH COVERS, FOUND NONE MISSING. LINES WERE PM'D LAST MAY. WILL RE-CHECK AREA FOR SLOW FLOW IN THE NEXT FEW WEEKS. | Y | N | SAN ONOFRE CREEK | PACIFIC OCEAN | NO FLOW TO ACTUAL SURFACE WATER, PERC'D INTO SOIL | Y | NA | Y | 3 | FROM MH TO GUTTER 300' TO EARTHEN SWALE, EAST SIDE OF ROAD TO EARTHEN BEQ PARKING LOT. PONDED IN LOT.4 SIGNS WERE POSTED AT PARKING LOT.
Note on I372: Changed from 20 to 8030 on 12/21/01 per City of San Diego comment. The City confused volume with spill 157690.
Note on I373: Changed from 8030 to 20 on 12/21/01 per City of San Diego Comment. City confused volume with spill 157646.
Note on AC72: Remark added 12/21/01 per City of San Diego comment.