## Quarterly Summary Rpt Template
Place an "X" here if this is definitely a PRIVATE spill | Tracking No. | Regional Board Contact Notified (Name, or "VOICE MAIL", or "FAX") | Date & Time Reported | Reported By | Phone No. | Reporting Agency | Responsible Agency | Start Date & Time | End Date & Time | Estimated Overflow Flow Rate (gallons per minute) | Total Volume | Recovered Volume | Overflow Volume Released to Environment (Gallons) | SSO Location -- Street Address | SSO Location -- City | SSO Zip Code | SSO County (SD, RV, OR) | SSO Structure I.D. | No. of Overflows within 1000 ft. of this location in past 12 months | Dates of Overflows within 1000 ft. of this location in past 12 months | Cause - Short Description | SSO Cause (Detailed Description) | SSO Correction and Prevention | 72-hour period measurable precipitation? (Y or N) | Entered Storm Drain? (Y or N) | Reached surface waters other than storm drain? (Y or N) | Initial Receiving Waters | Secondary Receiving Waters | Final Sewage Destination | Local Health Services Agency Notified (Y or N) | OES Notified (Y or N) | Warning Signs Posted (Y or N) | Location of Posting | No. of Days Signs Posted | Remarks | RB staff review comments | Place an "X" here if this is definitely a private spill
X | 023001 | Clay Clifton - DEH | 8/26/02 11:15a | Shawn Atherton | 760-633-2871 | City of Encinitas | City of Encinitas | 2002-08-26 08:10 | 2002-08-26 08:30 | 15 | 300 | 0 | 300 | 200 Saxony Road | Encinitas | 92024 | SD | Sewer manhole E78, Sheet 10 | 0 | na | OTHER | Neighborhood YMCA was draining pool, pumping 165 gpm directly into sewer system. This flow was more than our sewer line could handle, causing an overflow. | Worked with staff at YMCA to develop pool draining procedures. Bill Peters (YMCA Facilities Director) has agreed and will notify us prior to future pool draining. | N | Y | N | storm drain | na | percolated into ground | Y | N | N | na | 0 | Although 300 gallons was spilled, it is our estimate that only 50 gallons was sewage. The remaining 250 gallons was pool water. |  | X
X | 020301 | Clay Clifton | 7/11/02 - 9:30 | Grant Clavier | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2002-07-10 10:00 | 2002-07-10 10:12 | 50 | 100 | 0 | 100 | 401 Chinquapin | Carlsbad | 92008 | SD | Private Lift Station | 0 | None | Pump Station Failure | During emergency drill the sewer back up-surcharging the private 2" force main. The 2" system did not have the check valve in line causing sewage to overlflow the private lift station. | When the private lift station was recently retro fitted the plumber did not re-install the 2" check valve. Withit in place, there would not have been an overflow. | N | N | Y | Augua Hedionda Lagoon | None | None | Y | N | Y | 300' each side of spill into lagoon | 3 | None |  | X
X | 020302 | Clay Clifton | 07/22/02 - 8:30 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2002-07-20 | 2002-07-21 15:00 | 0 | 100 | 300 | 0 | 3475 Roosevelt | Carlsbad | 92008 | SD | Private sewer lateral | 0 | None | Unknown | Blockage on sewer lateral caused overflow. *There is no property line cleanout exposed, only one next to the building. We used that one to clear the stoppage. | I am going to contact the property manager, they will expose the property line cleanout, we will televise from there to check the condition of the lateral. | N | N | Y | Roosevelt/Chestnut | None | Gutter along Roosevelt & Chestnut | Y | N | N | N/A | 0 | We did clean up along Roosevelt & Chestnut and disinfected the area. |  | X
| 020303 | Clay Clifton | 09/27/02 - 9:30 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2002-09-26 19:00 | 2002-09-26 19:30 | 2 | 60 | 500 | 0 | 3860 Woodvale | Carlsbad | 92008 | SD | Manhole | 0 | None | Roots | Roots growing into sewer manhole caused stoppage | Routine cleaning | N | N | N | None | None | We collected it with the vactor | Y | N | N | N/A | 0 | None
x | 023001 | Voicemail 858-637-5589 | 37442.0208 | Chris Lopez | (760)-839-4323 | City of Escondido | City of Escondido | 2002-07-03 18:00 | 2002-07-03 20:00 | 10 | 1200 | 600 | 600 | 1433 N. Broadway | Escondido | 92027 | SD | Private cleanout | 0 |  | GREASE | Grease stoppage in private lateral | A Notice of Correction was issued to the manager for discharging wastewater to the public right-of-way. | N | Y | Y | Reidy Creek | San Elijo Lagoon | San Elijo Lagoon | Y | N | N |  |  |  |  | x
x | 023002 | Fax 858-637-5589 | 2002-07-08 12:30 | Lance Lauricha | (760)-839-4347 | City of Escondido | City of Escondido | 2002-07-07 07:30 | 2002-07-08 11:30 | 1 | 960 | 200 | 760 | 527 E. Grand Ave. | Escondido | 92027 | SD | Private cleanout | 1 | 2002-06-20 | GREASE | Grease stoppage in private lateral | A Notice of Correction was issued to the manager for discharging wastewater to the public right-of-way. | N | Y | Y | Escondido Creek | San Elijo Lagoon | San Elijo Lagoon | Y | N | Y | Country Club Dr. | 3 |  |  | x
x | 023003 | Fax 858-637-5589 | 2002-07-12 15:00 | Jim Miller | (760)-839-4347 | City of Escondido | City of Escondido | 2002-07-12 09:40 | 2002-07-12 10:20 | 0.25 | 10 | 10 | 0 | 541 W. Grand Ave. | Escondido | 92025 | SD | Private cleanout | 0 |  | CONSTRUCTION | Construction debris caused service lateral to discharge. | A Notice of Correction was issued to the manager for discharging wastewater to the public right-of-way. | N | N | N | None | None | Recovered returned to system. | Y | N | N |  |  |  |  | x
| 023004 | Fax 858-637-5589 | 2002-07-26 20:20 | Ray Crouch | (760) 839-6290 | City of Escondido | City of Escondido | 2002-07-26 14:30 | 2002-07-26 16:00 | 65 | 6000 | 0 | 6000 | 3183 Lone Jack Rd. | Olivenhain | 92024 | SD | Escondido Outfall manhole 74 | 2 | 10/20/01 1/24/02 | PUMP STATION FAILURE | Incorrect instrumentation and valve setting | The pond valve was re-scaled to reflect correct open or closed percentage, training of personnel on temporary controls of valves and meters readings. | Y | N | Y | Escondido Creek | San Elijo Lagoon | San Elijo Lagoon | Y | Y | N
| 023005 | Fax 858-637-5589 | 2002-07-31 17:00 | John Burcham | (760) 839-6290 | City of Escondido | City of Escondido | 2002-07-31 10:15 | 2002-07-31 11:00 | 66 | 3000 | 3000 | 0 | 2310 Avenida Del Diablo | Escondido | 92029 | SD | San Diego Manhole#20 | 1 | 2002-06-10 | PUMP STATION FAILURE | Pump malfunction | Contractor and Engineer are currently working to replace undersized line, valving and flow meter. There are two temporary pumps on line with a standby pump and a gravity line by-pass the vault. | N | Y | N | None | None | Recovered returned to system. To soil. | Y | N | N
x | 023006 | Fax 858-637-5589 | 2002-09-19 10:15 | Lance Lauricha | (760) 839-4668 | City of Escondido | City of Escondido | 2002-09-19 09:00 | 2002-09-19 10:00 | 0.42 | 25 | 25 | 0 | 2419 Heatherwood Ct. | Escondido | 92027 | SD | Private cleanout | 0 |  | VANDALISM | Sticks pushed into private lateral | A Notice of Correction was issued to the home owner for discharging wastewater to the public right-of-way. | N | N | N | None | None | Recovered returned to system. | Y | N | N |  |  |  |  | x
x | 023007 | Fax 858-637-5589 | 2002-09-19 15:00 | Lance Lauricha | (760) 839-4668 | City of Escondido | City of Escondido | 2002-09-19 11:00 | 2002-09-19 15:00 | 0.5 | 30 | 30 | 0 | 326 E. Felicita Ave. | Escondido | 92027 | SD | Private cleanout | 0 |  | LINE BREAK | Contractor broke a private sewer lateral while excavating for fiber optic installation. | Contractor repaired the sewer lateral | N | Y | N | None | None | Recovered returned to system. | Y | N | N |  |  |  |  | x
| 023001 | Chiara Clemente | 07/01/02 09:57 | L McKnight | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2002-07-01 07:30 | 2002-07-01 08:15 | 2 | 80 | 0 | 80 | Bldg #31613 | MCB, CAMP PENDLETON | 92055-5008 | SD | Manhole 13Y32 | 0 | NA | Roots | Roots, rocks, feminine hygiene products and debris clogged line. | Correction: Remove clog by ramjetting line. Prevention: Used TV line to scan for additional clogs. Rootcutters will be used to remove roots. Root-killing foam may also be applied if necessary. | N | N | Y | Santa Margarita River | Pacific Ocean | Percolated up to 100 ft from manhole. | Y | N | Y | NA | 3 | Sewage flowed out of manhole 100 ft across earthen area and percolated into ground. Expected Public Contact: Yes
| 023002 | Brian Kelly | 07/22/02 15:35 | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2002-07-22 09:40 | 2002-07-22 09:50 | 10 | 100 | 25 | 75 | Del Mar (harbor) PS#210583 | MCB, CAMP PENDLETON | 92055-5008 | SD | Pump Station # 210583 | 0 | NA | Other | Pumps were turned off during preventative maintenance. When maintenance was completed, maintenance crew forgot to switch pumps back online. | Correction: Switched pumps back online. Prevention: Preventative Maintenance Shop will develop a checklist to verify that all switches are returned to operating position after PM is performed. | N | N | Y | Pacific Ocean | Pacific Ocean | Spill traveled a total of 40 ft where it percolated. | Y | N | Y | NA | 3 | Sewage flowed out of pump station over paved road and onto unpaved area. Spill traveled a total of 40 ft before percolating into the ground. Expected Public Contact: Yes
| 023003 | Brian Kelly | 07/24/02 15:35 | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2002-07-24 07:30 | 2002-07-24 08:00 | 15 | 450 | 400 | 50 | San Onofre (Trailer Park) | MCB, CAMP PENDLETON | 92055-5008 | SD | Lift Station#510049 | 2 | 06/15/02, 03/19/02 | Debris | One of four temporary pumps used to transfer sewage from a wetwell being worked on to an adjacent wetwell went off line due to blockage. | Correction: Switched pumps back online. Prevention: All four pumps were adjusted to the lowest known leaking level. The contractor is pursuing modifications to repair leaking wetwell seems. | N | N | N | None | None | Flowed into adjacent engineered excavation pit. | Y | N | N | NA | 0 | Sewage leaked out of the wetwell and into the surrounding excavation pit and into adjacent drywell through a core hole in the drywell base.
| 023004 | Brian Kelly | 08/02/02 11:10 | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2002-08-02 07:30 | 2002-08-02 08:15 | 11 | 500 | 400 | 100 | Stewart Mesa RD | MCB, CAMP PENDLETON | 92055-5008 | SD | Pump Station # 31220 | 2 | 02/14/02, 10/09/01 | Pump Station Failure | Float sensor failure due to rags and debris. | Correction: Replace floats with new ones. Overflow pipe to the old detention ponds was concreted in to prevent future overflows to the ponds. Prevention: Continued daily checks of lift station. | N | N | N | None | None | Flowed into detention pond. | Y | N | N | NA | 0 | Sewage flowed from lift station through overflow pipe 300' into old detention pond. Total Distance Traveled: 300' Expected Public Contact: No
| 023005 | Chiara Clemente | 08/05/02 21:48 | Michael Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2002-08-05 17:10 | 2002-08-05 17:35 | 28 | 700 | 0 | 700 | Corner of Parker and Suzuki | MCB, CAMP PENDLETON | 92055-5008 | SD | Manhole in front of housing unit 508 | 0 | NA | Pump Station Failure | Breaker for lift station was tripped. | Correction: Reset breaker to restore power to lift station. Prevention: PM shop to check electrical system and pump station for proper operation. | N | Y | Y | Cockleburr Creek | Pacific Ocean | Percolated in dry creek bed (Cockleburr Creek), northwest side of housing area | Y | N | N | NA | 0 | Sewage mixed with sprinkler runoff and washdown water, traveled 100 ft across asphalt into a storm drain, 250 ft through storm drain to open concrete ditch for 10 ft, then flowed 1300 ft through another storm drain to dry creek bed where it percolated.
| 023006 | Chiara Clemente | 08/08/02 14:10 | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2002-08-08 05:20 | 2002-08-08 11:20 | 2 | 600 | 520 | 80 | North side building #53502 | MCB, CAMP PENDLETON | 92055-5008 | SD | Grease trap | 0 | NA | Debris | A plastic bag blocked the outlet pipe at the crossover tee inside the grease trap clarifier. | Correction: Cleared blockage with Jetter. Prevention: Don Taylor will give an informative lecture to all 53 area messhall workers. 08:15 am Aug 15, 2002. | N | Y | Y | San Onofre Creek | Pacific Ocean | Entered a dry drainage ditch. | Y | N | N | NA | 0 | Spill occurred from blockage at grease trap, therefore this was a gray water spill only. Spill traveled 232 feet across asphalt parking lot, 480 feet down the street, 117 feet through storm drain before percolating into dry drainage ditch.
| 023007 | Chiara Clemente | 09/03/02 09:05 | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2002-08-30 13:00 | 2002-08-30 13:50 | 2 | 100 | 0 | 100 | Bldg.#210599 | MCB, CAMP PENDLETON | 92055-5008 | SD | Line blockage caused spill from cleanout. | 0 | NA | Blockage | Sand blockage of lateral from bathhouse building. | Correction: Cleared blockage with Jetter. Prevention: Will increase inspection frequency of sand traps at bath houses. | N | N | N | None | None | Spill percolated in sandy area around cleanout. | Y | N | Y | NA | 3 | Spill percolated in sandy area around cleanout. Total Distance Traveled: 30 ft Expected Public Contact: Yes
X | 101002 | 858-571-6972 | 10/10/2002 1030 | Rosa Gutierrez | 619-422-1972 | City of Chula Vista | City of Chula Vista | 2002-10-10 10:00 | 2002-10-10 13:45 | 15 | 3375 | 2995 | 450 | 275 Orange ave | Chula Vista | 91910 | SD | N/A | 0 | 0 | GREASE | Grease, private lateral | Drain patrol cleared lateral,city contained spill | N | N | N | None | None | Contained within the property | Y | N | N | N/A | 0 | This same location had a spill in June2001 |  | X
X | 101402 | 858-571-6972 619-397-6000 | 10/14/02 01130 | Muna Cuthbert | 619-397-6111 | City of Chula Vista | City of Chula Vista | 2002-10-14 | 2002-10-14 12:50 | Unknown | 0 | 0 | Unknown | 616 G Street | Chula Vista | 91910 | SD | N/A | 0 | 0 | UNKNOWN | Unknown | Private sewer line, stoppage was cleared at 01250, We washed down and vacuumed apprx 175 yrds of storm channel | N | Y | Y | Bay front basin | J street Marina | N/A | Y | Y | Y | J street Marina | 3 | We do not know how many days this has been running? We were told 4 or 14 days |  | X
X | 102602 | 858-571-6972 619-397-6000 | 102602 1700 | Arturo Covarubia | 619-420-3902 | City of Chula Vista | City of Chula Vista | 2002-10-26 07:00 | 2002-10-26 17:00 | 1.6 | 960 | 300 | 660 | 1408 Third Ave | Chula Vista | 91910 | SD | N/A | 0 | 0 | GREASE | Grease, private lateral | Plumber broke plug city cleaned and contained spill | N | Y | N | None | None | Main & Fresno unlined channel | N | N | N | N/A | 0 | N/A |  | X
| 113002 | 619-397-6000 | 113002 0630 | B.F Goodrich | 619-420-3902 | City of Chula Vista | City of Chula Vista | 2002-11-30 04:00 | 2002-11-30 08:00 | 20 | 4800 | 3600 | 1200 | Marina & G street | Chula Vista | 91911 | SD | G st lift station | 0 | 0 | POWER FAILURE | power failure, pump did'nt activate | Setup portable pumps recover spill from storm system | Y | Y | Y | G street marina | N/A | G street marina | Y |  | Y | Sandpiper & G street | 3 | N/A
X | 121302 | 619-338-2070 619-467-2952 | 121302 0830 | city crews | 619-397-6000 | City of Chula Vista | City of Chula Vista | 2002-12-13 07:00 | 2002-12-13 09:30 | 1 | 1000 | 100 | 900 | 1689 Main street | Chula Vista | 91911 | SD | N/A | 0 | 0 | UNKNOWN | Trailer park with one resident living in park. Resident thinks its been plugged foir 3 days | Plumber broke plug city cleaned and contained spill | N | Y | N | None | None | Parking lot and storm drain pipe | Y | Y | N | N/A | 0 | Contained in storm system followed system down stream |  | X
| 023004 | Brian Kelley Fax: (858) 571-6972 | 2002-12-23 09:20 | David Scherer | (858) 755-3294 | City of Del Mar | City of Del Mar | 2002-12-20 20:00 | 2002-12-21 11:15 | 2 to 10 gpm | 1934 | 0 | 1639 to 1934 | 302 Ocean View Ave. | Del Mar | 92014 | SD | Del Mar GIS map C12 manhole 03 | 0 | N/A | ROOTS | Roots, rags (=paper waste disposal) and a rock | Rodded sewer main from manhole B12-02 to C12-03 with a 2", 4" and with 6" auger over 100' line w/ each auger on Saturday 12/21/02, jetted line w/ water on Monday 12/23/02 as follow-up | Y | Y | Y | Beach/Ocean (Torrey Pines State Beach) | none | Same as initial | Y | Y | Y | 1/4 to 1/2 mile North and South of beach and at outfall | 3 | The spill was created by a roots, rags (=paper waste disposal) and a rock that were in the sewer main line between manholes located at Del Mar GIS map page B12 manhole #02 and Del Mar GIS map page C12 manhole #03.
| 023001 | QUARTERLY REPORT | 2002-07-30 08:50 | SUZANNE VORLICEK / TERRY HARTNETT | (858) 793-7079 (858) 755-3294 | City of Del Mar | City of Del Mar | 2002-07-30 08:45 | 2002-07-30 09:20 | 5 | 175 | 175 | 0 | 1245 Chucara near Rimini Road | Del Mar | 92014 | SD | Del Mar GIS map C8 manhole 02 | 1 | 2002-03-17 | ROOTS | Roots, paper, hygiene products | Rodded sewer main from manhole at 1245 Cuchara East with 2" auger 328' and then 256' with 6" auger | N | N | N | none | none | returned to wastewater main | Y | N | N | N/A | 0 | The spill was created by a rootball in manhole. We believe this rootball was most likely from a private lateral cleaning that found its way to our manhole. We had recently (4/23/02) cleaned our main and there were no roots within the main at that time.
| 023002 | QUARTERLY REPORT | 2002-08-01 10:40 | JAMES CHAMBERS / DOUG BLACKSTOCK | (858) 204-7680 (858) 755-3294 | City of Del Mar | City of Del Mar | 2002-08-01 10:30 | 2002-08-01 11:15 | 19 | 855 | 855 | 0 | 12th Street at Maiden Lane | Del Mar | 92014 | SD | Del Mar GIS map B8 manhole 18 | 2 | 8/19/2001, 7/30/2002 | ROOTS | Roots | Rodded twice with 2" and 6" auger over 125' from manhole #14 on 12th Street at Camino Del Mar, to manhole #18 on 12th Street at Maiden Lane | N | N | N | none | none | returned to wastewater main | Y | N | N | N/A | 0 | Wastewater was dumped back into wastewater main
| 023003 | QUARTERLY REPORT | 2002-09-12 15:30 | TERRY HARTNETT | (858) 755-3294 | City of Del Mar | City of Del Mar | 2002-09-12 15:30 | 2002-09-12 16:00 | 1.5 | 45 | 0 | 45 | 421 Serpentine | Del Mar | 92014 | SD | Del Mar Gis map B6 manhole 30 | 0 | N/A | ROOTS | Roots | Rodded 171' from the manhole on Zapo & Serpentine, on up to the manhole at 421 Serpentine | N | N | N | none | none | Spill absorbed in Canyon dirt nearby | Y | N | N | N/A | 0 | Mitigated spill
| 023001 | Faxed | 2002-07-24 16:45 | Thomas Howard | (858) 679-5450 | City of Poway | City of Poway | 2002-07-24 12:55 | 2002-07-24 14:15 | 11.78 | 1178 | 0 | 1178 | 14858 Indian Peak Land | Poway | 92064 | SD | 24-inch manhole | 0 |  | CONSTRUCTION | Discovered a 3/8-inch rope in the sewer main; the rope was approx 400 ft long. The rope was tied off at the bottom rung of the ladders between two neighboring manholes. Grease, toilet paper, and other material collected on the rope, which caused the main blockage. | Video inspected the main and Vactor jet-rodded the line for 600 feet, 300 feet in each direction. Performed an inspection of another 16 manholes to verify the integrity of the system. Crews cleaned up the area around the manhole - removed debris, raked dirt. | N | N | Y | Dry creek bed | Rattlesnake Creek |  | Y | Y | Y | Along creek bed up to Midland and Twin Peaks Roads | 5 | On 7/24/02, Preliminary report sent to: DEH faxed; OES #02-4015; OESHazMat faxed; Dept Fish/Game faxed. FINAL Report sent on 7/25/02.
| 023002 | Faxed RWQCB and DEH | 2002-09-23 17:10 | Thomas Howard | (858) 679-5450 | City of Poway | City of Poway | 2002-09-23 15:45 | 2002-09-23 16:45 | 5.33 | 320 | 0 | 320 | 15597 Paseo del Arroyo | Poway | 92064 | SD | Manhole | 0 |  | ROOTS | Roots clogged the gravity main in the manhole. | Jet-rodded and cleaned the gravity main both upstream and downstream of blockage. Visually inspected three manholes and Vactored out debris; washed down inside of manhole where blockage occurred and removed roots. Posted CONTAMINATION signs. | N | N | N | NONE |  | Open field | Y | N | Y | Along the path of sewage spill, approx 680 ft from manhole to where spill stopped. | 3 | Faxed DEH
| 023003 | Faxed RWQCB and DEH | 2002-09-25 10:10 | Thomas Howard | (858) 679-5450 | City of Poway | City of Poway | 2002-09-25 07:20 | 2002-09-25 07:32 | 10 | 120 | 50 | 70 | 13012 Avenida Granada | Poway | 92064 | SD | Access manhole | 0 |  | GREASE | Grease blockage in 8-inch VCP main. | The 8-inch main was clear (not spilling) when crew arrived. Containment barriers were set up at Green Valley Creek. The Vactor unit was utilized to remove the spill and clean up the residual waste. The main was then cleaned with the Vactor unit and a build-up of grease was documented. This line will be placed on our stepped-up Maintenance Program. | N | N | Y | Green Valley Creek | Rios Channel |  | Y | N | N |  |  | Remote public access.
| 023001 | David Hanson | 2002-10-28 09:45 | Rich Arrant | 760-744-0460 | Vallecitos Water District | Vallecitos Water District | 2002-10-26 20:20 | 2002-10-26 20:52 | 5 | 140 | 140 | 0 | Via Camella | San Marcos | 92069 | SD | Manhole | 1 | 1/00/1900 | ROOTS | Root blockage in line | Cleared root mass | N | Y | N | None | None | None | Y | N | N | None | 0 | 100 gal cleanup water
| 023002 | David Hanson | 2002-12-06 12:30 | Rich Arrant | 760-744-0461 | Vallecitos Water District | Vallecitos Water District | 2002-12-06 12:00 | 2002-12-06 13:20 | 10 | 800 | 800 | 0 | Barham Dr. | San Marcos | 92069 | SD | 8" VCP | 0 | 0 | Construction | Contrator broke line | Suggest he be more careful | N | N | N | None | None | Const. Pit | Y | N | N | None | 0 | None
| 023001 | David Hanson | 2002-07-15 14:20 | Martin Holmes | (619) 258-4706 | Padre Dam Municipal Water District | Padre Dam Municipal Water District | 2002-07-15 09:00 | 2002-07-15 09:30 | 500 | 15000 | 7500 | 7500 | 9040 Carlton Oaks Dr | Santee | 92071 | SD | 24" force main | 0 |  | CONSTRUCTION | Operational shutdown of the treatment plant and influent pump station for construction and replacement of force main caused return trunk line from the treatment plant to back up into Santee Lakes Park (owned by Padre Dam). | This incident only happened due to the construction and replacement of the force main. However, Padre Dam's Engineering Department is looking into incorporating some kind of early warning overflow system into our SCADA system to prevent this from happening again. | N | N | Y | Lakes 1 & 2 at Santee Lakes | None | NA | Y | Y | Y | Around perimeter of Lakes 1 & 2 | 3 | Number of days warning signs posted to be determined by bacteriological tests
| 0203001 | David Hanson, fax (858) 467-2952 | 2002-08-05 12:05 | Dennis McKinney | (619) 545-1108 | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2002-08-05 11:00 | 2002-08-05 11:30 | 0.5 | 25 | 0 | 25 | NAS North Island, Bldg. 446 | Coronado | 92135 | SD | 11:00 NM | 0 | N/A | Pump Station failure | Pump failed at a pump station. | Secured inlet to pump station, repaired pump station, put pump station back on line | N | N | N | N/A | N/A | N/A | Y | N/A | N | N/A | N/A | Contacted Clay Clifton at County. The 25 gallons spilled evaporated on the asphalt. Site was decontaminated as per PWC sewer spill cleanup SOP.
| 0203002 | David Hanson, fax (858) 467-2952 | 08/09/02 1530 | Hanes | (858) 577-1155 | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2002-08-09 13:00 | 2002-08-09 14:30 | 2 | 200 | 150 | 50 | MCAS Miramar, Bldg. 2240 | San Diego | 92145 | SD | Lateral from building | 1 | 2002-02-01 | Grease | Grease from building blocked the lateral coming from the building. | Hydroblasted the lateral clear. | N | N | N | N/A | N/A | N/A | Y | N/A | N | N/A | N/A | Contacted Clay Clifton at County. The 50 gallons not recovered evaporated on the ashpalt and soaked into the nearby grass. Site was decontaminated as per PWC sewer spill cleanup SOP.
| 0203003 | David Hanson, fax (858) 467-2952 | 2002-09-19 12:05 | Vince Concepcion | (619) 556-7352 | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2002-09-19 08:00 | 2002-09-19 08:50 | 4.5 | 200 | 0 | 200 | Naval Station San Diego Pier 11 | San Diego | 92136 | SD | Pier 11 sewer line | 0 | N/A | line break | broken sewer lin | ships' sewer discharge relocated | N | N | y | San Diego Bay | Pacific Ocean | San Diego Bay | Y | Y | N | N/A | N/A | Contacted Clay Clifton at County (fax) and Bob McRay (phone) at OES Control #02-5114
| 0203004 | David Hanson, fax (858) 467-2952 | 2002-10-24 14:10 | Steven Rilat | (619) 545-9150 | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2002-10-24 13:00 | 2002-10-24 13:15 | 2 | 30 | 25 | 5 | NASNI 1330 Sewer lift station | Coronado | 92132 | SD | Station 1330 | 0 | N/A | Pump Station Failure | Air release valve failed permitting sewage to pass through | Air release valve replaced | N | Y | Y | San Diego Bay | Pacific Ocean | Pacific Ocean | Y | Y | N | N/A | N/A | OES #02-5762
| 0203005 | David Hanson, fax (858) 467-2952 | 2002-11-12 09:30 | Virgil McCulligan | (619) 437-3839 | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2002-11-12 04:00 | 2002-11-12 08:00 | 125 | 40000 | 0 | 40000 | NAB Sewer Lift station A | Coronado | 92135 | SD | Lift Station A | 0 | N/A | Line Break | Collapsed sewerline on the discharge side of a pump station. | Sewer line repaired | Y | Y | N | San Diego Bay | Pacific Ocean | Pacific Ocean | Y | Y | N | N/A | N/A | OES #02-6170
| 301373 | Fax (858) 571-6972 (RWQCB) | 2002-07-03 15:45 | MIKE ROSENBERG | (858) 614-5742 | City of San Diego | City of San Diego | 2002-07-03 09:36 | 2002-07-03 11:55 | 3 | 417 | 300 | 117 | 1575 TORREY PINES RD | San Diego | 92037 | SD | 8' VC MAIN | 0 |  | ROOTS | HEAVY ROOTS | REFER TO HAVE MAIN TELEVISED BY CCTV | N | Y | N | None | None | Dissipated into storm drain | N | Y | N |  | 0 | WILL REFER TO AREA SUPERVISER FOR CORRECTIVE ACTION
| 301669 | Fax (858) 571-6972 (RWQCB) | 2002-07-05 15:45 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-07-05 12:45 | 2002-07-05 13:40 | 5 | 275 | 0 | 275 | 6193 STETSON PL | San Diego | 92122 | SD | 8"VC | 0 | 0 | GREASE | BLOCKAGE WAS CAUSED BY GREASE. | FLUSHED LINE TO RELIEVE STOP. REFER TO AREA SUPERVISOR FOR EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORMDRAIN SYSTEM. | Y | Y | N
| 302053 | Fax (858) 571-6972 (RWQCB) | 2002-07-07 20:20 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-07-07 16:54 | 2002-07-07 18:05 | 15 | 1065 | 0 | 1065 | 4880 COLLEGE AVE (IN CANYON) | San Diego | 92115 | SD | 6"CP | 0 | 0 | ROOTS | 7-31 OUT OF GROUND IN CANYON CAUSED BY ROOT BLOCKAGE. | VACTOR CONTAINED OVERFLOW AT 18:05; RODDING TRUCK RELIEVED STOPPAGE AT 19:35; REFERRED TO AREA SUPERVISOR FOR EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORMDRAIN SYSTEM | N | Y | N
| 302312 | Fax (858) 571-6972 (RWQCB) | 2002-07-09 17:00 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2002-07-08 16:03 | 2002-07-08 17:30 | 0.25 | 21.75 | 5 | 16.75 | 3717 INDIA ST. | San Diego | 92101 | SD | LATERAL | 0 | N/A | FLOOD DAMAGE | LATERAL NOT CONNECTED TO RENEWED MAIN. | CONSTRUCTION CREW CALLED OUT TO MAKE REPAIR. | N | Y | N | None | None | DRIED IN STORM BOX AT INDIA ST AND WINDERS ST. | Y | Y | N |  |  | NO OVERFLOWING MANHOLE.
| 302192 | Fax (858) 571-6972 (RWQCB) | 2002-07-08 14:19 | Eric Swanson | (858) 654-4152 | City of San Diego | City of San Diego | 2002-07-08 01:37 | 2002-07-08 03:30 | 1 | 100 | 0 | 100 | 2646 Simi Ct | San Diego | 92139 | SD | 8"pvc | 0 | 0 | LINE BREAK | Unknow cause. Evidence of 7-33 and stoppage in section between mh#162 & 157. Stoppage relieved itself at unknown time. | Clean mains and TV for inspection | N | y | n | None | None | storm drain and dissipated | y | Y | N
| 303636 | Fax (858) 571-6972 (RWQCB) | 2002-07-16 14:00 | MIKE ROSENBERG | (858) 614-5742 | City of San Diego | City of San Diego | 2002-07-16 08:10 | 2002-07-16 11:00 | 15 | 2550 | 2550 | 0 | 4850 WARING RD | San Diego | 92120 | SD | 10" VC PIPE | 0 | 0 | ROCKS | ROCKS IN 10" VC SEWER MAIN. | REFERED TO CONSTUCTION SECTION FOR REPAIRS VIA STATION 38. | N | N | N | None | None | PUMPED BACKED INTO SEWER SYSTEM | Y | Y | N |  | 0 | ROCKS WERE IN NEW PIPE AND MANHOLE NOT YET IN CITY MAPPING SYSTEM CONTRACTOR IS ON SITE BUILDING A NEW WATER PUMP STATION.
| 303632 | Fax (858) 571-6972 (RWQCB) | 2002-07-16 07:30 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2002-07-16 07:30 | 2002-07-16 13:40 | 0.06 | 22.2 | 0 | 22.2 | 4795 Cereza Street | San Diego | 92113 | SD | 8" VC | 0 | 0 | ROOTS | HEAVY ROOTS IN MAIN. | ROD MAIN AND LATERAL TO REMOVE ROOTS . LEFT LATERAL POLICY WITH CUSTOMER | N | N | N | None | None | DISSIPATED IN STREET GUTTER | N | Y | N |  | 0 | Very cooperative tenant.
| 304506 | Fax (858) 571-6972 (RWQCB) | 2002-07-20 17:30 | D.A. BRANCO. | (858) 614-5770 | City of San Diego | City of San Diego | 2002-07-20 12:30 | 2002-07-20 14:25 | 30 | 3450 | 0 | 3450 | MENLO & REDWOOD (IN CANYON) | San Diego | 92105 | SD | 8"VC | 0 | 0 | ROOTS | Blockage caused by roots & grease. | Handrodded line to relieve stoppage; refer to canyon supervisor for scheduled maintenance. | N | Y | N | None | None | soaked into canyon floor & dissipated in system. | Y | Y | N
| 304509 | Fax (858) 571-6972 (RWQCB) | 2002-07-20 21:15 | D.A.BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-07-20 18:42 | 2002-07-20 20:30 | 0.25 | 27 | 0 | 27 | 4606 C ST | San Diego | 92105 | SD | 8"VC | 1 | 01-17-2002 | GREASE | BLOCKAGE WAS CAUSED BY GREASE. | FLUSHED LINE TO RELIEVE STOP; REFER TO AREA SUPERVISOR FOR EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORMDRAIN SYSTEM. | N | Y | N
| 304558 | Fax (858) 571-6972 (RWQCB) | 2002-07-21 11:45 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-07-21 09:49 | 2002-07-21 10:25 | 0.5 | 18 | 0 | 18 | 2094 LAURINDA PL | San Diego | 92105 | SD | 8" VC | 2 | 10/02/01 & 04/23/02 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS. | MACHINE RODDED TO RELIEVE STOP. FLUSH STORM DRAIN TO CLEAN UP OVERFLOW; REFER TO AREA SUPERVISOR FOR EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN. | N | Y | N
| 304736 | Fax (858) 571-6972 (RWQCB) | 2002-07-22 22:00 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2002-07-22 16:56 | 2002-07-22 18:30 | 2 | 188 | 0 | 188 | 5955 LAURETTA ST. | San Diego | 92110 | SD | 8"VC | 0 |  | ROOTS | ROOT BLOCKAGE ON EASEMENT MAIN. | RODDED MAIN TO RELIEVE ROOT STOP. CLEANED WITH FULL SIZE BLADE. REFER TO HAVE MAIN TELEVISED. | N | N | N | None | None | SOAKED INTO EASEMENT 80' SOUTH OF OVERFLOWING MH. | Y | Y | N
| 304844 | Fax (858) 571-6972 (RWQCB) | 2002-07-23 16:00 | Mike Rosenberg | (858) 614-5719 | City of San Diego | City of San Diego | 2002-07-23 07:16 | 2002-07-23 14:01 | 12 | 4536 | 4000 | 536 | 3683 Albatross Street | San Diego | 92103 | SD | 6" VC. | 2 | 09/12/2001 - 04/09/2002 | ROOTS | Heavy roots and toilet paper | Hand rod to releive stoppage, refer to area supervisor for further action, also to tv section for inspection. | N | Y | N | None | None | dissipated in storm drain conveyance system also soak in ground | N | Y | N |  |  | Spill was contained at 9:50
| 305355 | Fax (858) 571-6972 (RWQCB) | 2002-07-25 20:00 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2002-07-25 15:59 | 2002-07-25 17:03 | 15 | 930 | 105 | 825 | 5325 LEA ST. | San Diego | 92105 | SD | 8" VC | 0 |  | GREASE | HEAVY GREASE IN SEWER MAIN. | FLUSHED AND VACTORED TWO SECTION UPSTREAM AND TWO SECTIONS DOWNSTREAM. REFERRED MAIN TO BE TELEVISED. | N | Y | Y | CHOLLAS CREEK | None | DRIED IN CREEK NEAR CHOLLAS PL.XCHOLLAS PKWY. | Y | Y | N
| 305485 | Fax (858) 571-6972 (RWQCB) | 2002-07-26 13:30 | Rick Donahue | (858) 654-4155 | City of San Diego | City of San Diego | 2002-07-26 05:37 | 2002-07-26 06:30 | 1 | 45 | 0 | 45 | W. Grape & Kettner Blvd. | San Diego | 92101 | SD | 8" PVC | 0 |  | CONSTRUCTION | Debris (sludge) in 8" PVC main | Machine rodded to relieve stoppage, followed with hydro cleaning to remove sludge and debris. | N | N | Y | None | None | Dried in street | Y | Y | N |  | 0
| 305746 | Fax (858) 571-6972 (RWQCB) | 2002-07-27 20:40 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-07-27 16:00 | 2002-07-27 18:50 | 0.5 | 85 | 0 | 85 | 4243 INGRAHAM ST | San Diego | 92109 | SD | 6"CP | 0 | 0 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS. | MACHINE RODDED TO RELIEVE STOP; VACTORED AND CLEANED AREA; REFERRED TO AREA SUPERVISOR FOR EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | N | Y | N
| 306918 | Fax (858) 571-6972 (RWQCB) | 2002-08-01 23:00 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2002-08-01 18:09 | 2002-08-01 19:20 | 15 | 990 | 70 | 920 | 2324 VANCOUVER AVE. | San Diego | 92104 | SD | 8" VC | 0 |  | ROOTS | HEAVY ROOT BLOCKAGE ON EASEMENT MAIN. | RODDED THREE SECTIONS OF EASEMENT MAIN WITH FULL SIZE BLADE. REFERRED FSN 39377 TO BE TELEVISED. | N | Y | N | None | None | DRIED IN STORM DRAIN PIPE AND SOAKED INTO DIRT IN EASEMENT. | Y | Y | N |  |  | 2 GPM FROM FSN 106248 IN STREET. SECONDARY SPILL FROM EASEMENT FSN 106315 CAUSED WHILE CLEARING HEAVY ROOT BLOCKAGE ON STEEP EASEMENT MAIN.
| 307103 | Fax (858) 571-6972 (RWQCB) | 2002-08-02 16:00 | Mike Rosenberg | (858) 614-5742 | City of San Diego | City of San Diego | 2002-08-02 11:41 | 2002-08-02 14:00 | 5 | 695 | 300 | 395 | Countryclub rd and Pepita wy | San Diego | 92037 | SD | 6" cp main | 0 | 0 | OTHER | Found suction hose screen in manhle #281 blocking downsteam pipe. | Will refer to rose cyn section superviser for corrective action including but not limited to possibly changing frame and cover to lockdown type. | N | Y | N | None | None | Dried up in storm drain. | Y | Y | N |  |  | Will give findings to area superviser a.s.a.p.
| 307511 | Fax (858) 571-6972 (RWQCB) | 2002-08-04 18:00 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-08-04 16:22 | 2002-08-04 17:20 | 0.5 | 29 | 0 | 29 | HEMINGWAY DR & WILDFLOWER WAY | San Diego | 92120 | SD | 8"VC | 0 | 0 | GREASE | Blockage relieved itself upon arrival; cause was grease | Flushed line for grease; cleaned area; refer to area supervisor for evaluation. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | N | Y | N
| 307373 | Fax (858) 571-6972 (RWQCB) | 2002-08-03 15:00 | Revised by Jeff Wilder | (858) 614-5770 | City of San Diego | City of San Diego | 2002-08-03 11:58 | 2002-08-03 13:02 | 2 | 128 | 0 | 128 | HOLLISTER & PALM AVE | San Diego | 92154 | SD | 8"VC | 0 | 0 | GREASE | BVLOCKAGE WAS CAUSED BY GREASE. | MACHINE ROD TO RELIEVE STOP; CALL FOR FLUSHER TO FLUSH LINE FOR HEAVY GREASE; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | N | N | None | None | DRIED IN DIRT AREA ALONG SIDE OF HOLLISTER RD. | Y | Y | N
| 307980 | Fax (858) 571-6972 (RWQCB) | 2002-08-06 17:30 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2002-08-06 12:36 | 2002-08-06 14:02 | 18 | 1548 | 1400 | 148 | Menlo Av. & Orange Av. | San Diego | 92105 | SD | 6" V.C. | 0 | 0 | GREASE | Heavy grease in main | Rodded main to releive heavy grease blockage between manhole numbers 118 and 312 on polk Av. Refered to area supervisor to add on a routine maintenance. Vactor overflow & runoff, desinfected area. | N | Y | N | None | None | Dissipated in storm drain conveyance system | N | Y | N |  | 0 | Full containment with vactor at 13:30 very heavy grease found blocking main, clean up area.
| 308868 | Fax (858) 571-6972 (RWQCB) | 2002-08-09 23:25 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-08-09 19:32 | 2002-08-09 22:01 | 120 | 15480 | 13500 | 1980 | BLACK MTN RD & MAYA LINDA RD | San Diego | 92126 | SD | 15"VC | 0 | 0 | GREASE | BLOCKAGE WAS CAUSED BY GREASE. | HYLINED HOSE AND FLUSHED LINE TO RELIEVE GREASE BLOCKAGE.TWO VACTORS MAINTAINED OVERFLOW WHILE DETERMINING PLAN OF ACTION; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | PRIVATE POND AT VULCAN CEMENT YARD. | N | Y | N
| 308998 | Fax (858) 571-6972 (RWQCB) | 2002-08-11 19:10 | D.A.BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-08-11 17:24 | 2002-08-11 17:40 | 5 | 80 | 0 | 80 | 6157 CAMINITO PAN | San Diego | 92120 | SD | 8"VC | 1 | 1-13-2002 | ROOTS | Blockage was caused by roots. | Cleaned roots from m/h 122 & flushed line to relieve stop. Refer to area supervisor for further evaluation. | N | Y | N | None | None | DRIED IN STREET AND STORM DRAIN SYSTEM. | Y | Y | N
| 309523 | Fax (858) 571-6972 (RWQCB) | 2002-08-14 14:15 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2002-08-14 08:46 | 2002-08-14 10:37 | 15 | 1665 | 1200 | 465 | 3rd Avenue and Maple. | San Diego | 92101 | SD | 6" VC. | 1 | 12/28/2001 | ROOTS | Roots and Rags cause stoppage. | Vactor overflow and runoff. Rodded main to releive stoppage between MH# 216 and MH# 200. Refered to area supervisor to add on a routine maintenance and to TV section. | N | Y | N | None | None | Sewege was absorbed in to the ground in canyon area. | N | Y | N |  | 0 | NOT MANHOLE OVERFLOW. LATERAL FSN. # 243498 WAS OVERFLOWING.
| 310663 | Fax (858) 571-6972 (RWQCB) | 2002-08-21 16:00 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2002-08-20 23:57 | 2002-08-21 01:07 | 5 | 350 | 0 | 350 | 6104 CASTEJON DR. | San Diego | 92037 | SD | 8" VC | 0 |  | ROOTS | HEAVY ROOTS GROWING IN EASEMENT MAIN. | RODDED TO RELIEVE ROOT BLOCKAGE. CLEANED WITH FULL SIZE CUTTING BLADE. WILL TELEVISE MAIN. | N | N | N | None | None | DRIED IN DIRT NEAR OVERFLOWING MH ON EASEMENT. | Y | Y | N |  |  | FLOODED GUESTHOUSE NEAR OVERFLOWING MH.
| 311147 | Fax (858) 571-6972 (RWQCB) | 2002-08-23 17:30 | Mike Rosenberg | (858) 614-5742 | City of San Diego | City of San Diego | 2002-08-23 13:28 | 2002-08-23 16:00 | 1 | 152 | 152 | 0 | 715 Torrance st | San Diego | 92103 | SD | 6" cp pipe | 1 | 10/16/2001 | ROOTS | Heavy roots in cp sewer main. | Will refer to have 6" main televised a.s.a.p | N | N | N | None | None | Captured sewage with vactor. | Y | Y | N |  |  | Will give area superviser copy of report for further investigation a.s.a.p.
| 311612 | Fax (858) 571-6972 (RWQCB) | 2002-08-27 11:30 | Eric Swanson | (858) 654-4152 | City of San Diego | City of San Diego | 2002-08-27 01:27 | 2002-08-27 02:30 | 1 | 63 | 0 | 63 | 7224 Zest st | San Diego | 92139 | SD | 8" pvc sewer main | 0 |  | GREASE | Grease stop in main ,sewer was not spilling opon arrival but there was evidence of overflow. | Rodded main to relieve stop will refer to area superviser for follow up action. | N | Y | N | None | None | DRIED IN STORM DRAIN | Y | Y | N |  |  | Will give copy of report to area supervisor a.s.a.p.
| 311657 | Fax (858) 571-6972 (RWQCB) | 2002-08-27 17:00 | Mike Rosenberg | (858) 614-5742 | City of San Diego | City of San Diego | 2002-08-27 12:10 | 2002-08-27 14:00 | 10 | 1100 | 1000 | 100 | 3634 07th ave | San Diego | 92103 | SD | 8" vc pipe | 0 |  | ROOTS | ROOTS IN M/H # 481 | Will refer to area supervisor for corrective action. | N | N | N | None | None | Captured by vactor at bottom of hill. | Y | Y | N |  |  | Main will be referred to cctv section for further investigation.
| 311802 | Fax (858) 571-6972 (RWQCB) | 2002-08-28 13:30 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-08-28 10:19 | 2002-08-28 10:45 | 4 | 104 | 0 | 104 | 5220 GAINES ST | San Diego | 92110 | SD | 15" VC | 0 | 0 | GREASE | Grease assumed due to heavy grease in line. | No overflow upon arrival; stop relieved itself. Street was wet; possible partial overflow; estimate 100 gal. | N | Y | N | None | None | DISSIPATED IN STREET & STORM DRAIN CHANNEL. | Y | Y | N
| 312027 | Fax (858) 571-6972 (RWQCB) | 2002-08-29 16:00 | Mike Rosenberg | (858) 614-5742 | City of San Diego | City of San Diego | 2002-08-29 11:05 | 2002-08-29 13:20 | 5 | 675 | 0 | 675 | Hunter st & Jackdaw st | San Diego | 92103 | SD | 6" CP PIPE | 0 |  | ROOTS | Roots in manhole # 132 | Will refer to cctv to inspect main. | N | N | N | None | None | Soaked into soil around manhole. | Y | Y | N |  |  | Will give copy of report to area supervisor for further investigation a.s.a.p.
| 312176 | Fax (858) 571-6972 (RWQCB) | 2002-08-30 14:00 | Mike Rosenberg | (858) 614-5742 | City of San Diego | City of San Diego | 2002-08-30 09:46 | 2002-08-30 11:00 | 2 | 148 | 148 | 0 | 1630 Kearsage rd | San Diego | 92037 | SD | 8" vc | 0 |  | ROOTS | Roots in 8" vc sewer main. | Will refer to have cctv inspect main a.s.a.p. | N | N | N | None | None | Vactored up from curb and gutter. | N | Y | N |  |  | Will give copy to area supervisor for further investigation.
| 312350 | Fax (858) 571-6972 (RWQCB) | 2002-08-31 21:40 | D.A.BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-08-31 18:32 | 2002-08-31 20:50 | 0.25 | 34.5 | 0 | 34.5 | 4954 63RD ST | San Diego | 92115 | SD | 6"VC | 2 | 11/06/01 & 11/08/01 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS. | Contacted crew to remove asphalt covering m/h; Flushed line to relieve root stop; refer to area supervisor for evaluation. | N | N | N | None | None | SOAKED INTO GROUND AROUND EASEMENT M/H. | Y | Y | N
| 313358 | Fax (858) 571-6972 (RWQCB) | 2002-09-07 17:10 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-09-07 13:01 | 2002-09-07 13:33 | 5 | 160 | 0 | 160 | 2317 54TH ST | San Diego | 92105 | SD | 6"VC | 0 | 0 | LINE BREAK | AEROSOL CANS TAPED TOGETHER & THROWN INTO SEWER CAUSED LINE TO STOP | MACHINE RODDED & REMOVED CANS FROM LINE; CONTACTED SD POLICE; REFERED TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | N | Y | N
| 312691 | Fax (858) 571-6972 (RWQCB) | 2002-09-04 14:15 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-09-04 11:19 | 2002-09-04 12:56 | 5 | 485 | 0 | 485 | 4927 CRESITA DR | San Diego | 92115 | SD | 6"CP | 2 | 11-06-01; 11-08-01; | ROOTS | Blockage caused by roots. | Machine rodded from street & turned screw in canyon to relieve stop; Refer to area supevisor for further evaluation. | N | N | N | None | None | SOAKED INTO EASEMENT HILLSIDE & FLOOR. | Y | Y | N
| 314302 | Fax (858) 571-6972 (RWQCB) | 2002-09-12 23:45 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2002-09-12 18:38 | 2002-09-12 19:50 | 1 | 72 | 35 | 37 | 3502 WAWONA DR. | San Diego | 92133 | SD | 6" CP | 0 |  | ROOTS | ROOTS GROWING IN EASEMENT MAIN. | VACTOR OVERFLOW TO CONTAIN. ROD MAIN TO RELIEVE ROOT BLOCKAGE. CLEAN MAIN WITH FULL SIZE CUTTING BLADE THOROUGHLY. REFER TO BE TELEVISED. | N | Y | N | None | None | DRIED IN STORM PIPE AT NEWELL ST X NIMITZ BL. | Y | Y | N
| 314752 | Fax (858) 571-6972 (RWQCB) | 2002-09-15 12:25 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-09-15 10:23 | 2002-09-15 11:08 | 3 | 120 | 0 | 120 | 9777 Camto Munoz | San Diego | 92131 | SD | 8"pvc | 0 | 0 | ROOTS | blockage was caused by roots | Flushed line to relieve root stop; clean area and refer to area supervisor for evaluation. | N | Y | N | None | None | dissipated in storm drain system. | N | Y | N
| 314794 | Fax (858) 571-6972 (RWQCB) | 2002-09-16 14:30 | Mike Rosenberg | (858) 614-5742 | City of San Diego | City of San Diego | 2002-09-16 07:20 | 2002-09-16 08:30 | 3 | 210 | 210 | 0 | Pomerado rd & Scripps Ranch blvd | San Diego | 92131 | SD | 15" vc Main | 1 | 6/10/02 | CONSTRUCTION | RAGS & CARPET | Will refer to cctv for inspection of 15" main. | N | N | N | None | None | Puddled up in front of storm drain and captured by vactor. | N | Y | N |  |  | Will give copy of sso report to area supervisor for futher investigation.
| 314791 | Fax (858) 571-6972 (RWQCB) | 2002-09-16 14:30 | Marcelino Oregel | (619) 614-5719 | City of San Diego | City of San Diego | 2002-09-16 06:35 | 2002-09-16 10:15 | 0.5 | 110 | 0 | 110 | 1904 Edgemont St. | San Diego | 92102 | SD | 6" CP | 0 | 0 | ROOTS | Roots and rags in concrete pipe caused blockage. | Rodded main to releive stoppage at 342' between MH# 277 and MH# 278. Will refer area supervisor for further action. | N | N | N | None | None | dissipated in canyon grounds. | N | Y | N |  | 0 | MAIN BLOCKAGE SPILLING IN SEWER CONNECTION, NOT MANHOLE OVERFLOWING
| 314864 | Fax (858) 571-6972 (RWQCB) | 2002-09-16 16:00 | Melody Shaw | (858) 614-5772 | City of San Diego | City of San Diego | 2002-09-16 11:15 | 2002-09-16 12:45 | 50 | 4500 | 0 | 4500 | 5375 Auburn .Dr | San Diego | 92105 | SD | 15"main | 0 | 0 | ROCKS | unit 744 was sailing the main when rocks got caught in the main and caused the 733. | Rod/crew responded to assist unit 744 and relieved the stop. Flusher crew conducted the clean up.Bucket crew will go back and bucket the main to remove additional rocks if any are still in the main to prevent another overflow. | N | Y | y | Chollas Creek | None | The spill soaked into Chollas Creek bed, the area is fenced in no public access. | y | Y | N |  | 0 | The manhole that was over flowing was manhole # 225. Problem has been resolved at this time.
| 314917 | Fax (858) 571-6972 (RWQCB) | 2002-09-16 18:46 | Matt Hauer | (858) 654-4130 | City of San Diego | City of San Diego | 2002-09-16 18:46 | 2002-09-16 21:30 | 0.5 | 82 | 0 | 82 | 3545 Island Ave. | San Diego | 92105 | SD | 8" VC | 0 |  | GREASE | Grease blockage on city sewer main | Flushed main to relieve blockage and cleaned pipe. Main refered to be televised. | N | Y | N | None | None | DRIED IN STORM DRAIN PIPE SOUTH OF 36TH & TOMPKINS ST | Y | Y | N
| 314877 | Fax (858) 571-6972 (RWQCB) | 2002-09-16 13:23 | MATT HAUER | (858) 654-4130 | City of San Diego | City of San Diego | 2002-09-16 13:23 | 2002-09-16 22:30 | 0.2 | 127.4 | 0 | 127.4 | 1040 W UPAS St. | San Diego | 92103 | SD | 6" CP | 1 | 10/16/2001 | FLOOD DAMAGE | BREAK ON 6" CP EASEMENT MAIN | RODDED MAIN TO RESTORE FLOW. BROKEN CP PIPE WILL BE REPAIRED ASAP IN THE AM. | N | N | N | None | None | SOAKED INTO GROUND 20' WEST OF MH# 351 IN EASEMENT | N | Y | N |  |  | OVERFLOW COMING UP THROUGH GROUND ON EASEMENT
| 313164 | Fax (858) 571-6972 (RWQCB) | 2002-09-17 07:30 | Jeff Wilder | (858) 614-5770 | City of San Diego | City of San Diego | 2002-09-06 11:36 | 2002-09-06 19:32 | 0.25 | 25.25 | 0 | 25.25 | Alenxandria Dr & Hill st | San Diego | 92107 | SD | 6"cp | 0 |  | FLOOD DAMAGE | BLOCKAGE WAS CAUSED BY ROOTS and BREAK IN MAIN | upon arrival, constrution crew contained spill to mh 130; rodder unit relieved stop (roots) from mh114: refer to area supervisor for evaluation. | N | N | N | None | None | SOAKED INTO GROUND IN THE ALLEY | Y | Y | N |  |  | Construction crew found a broken main upon excavating the area
| 315275 | Fax (858) 571-6972 (RWQCB) | 2002-09-18 16:30 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2002-09-18 13:13 | 2002-09-18 14:13 | 3 | 180 | 90 | 90 | 4110 Orange | San Diego | 92105 | SD | 6" VC | 0 | 0 | GREASE | Very Heavy Grease in main cause blockage. | Roodded main to releive heavy grease blockage at 57" from d/s MH# 82 and overflowing u/s MH# 80. Refered to area supervisor to add in a routine maintenance. Vactor overflow & runoff, desinfected area. | N | N | N | None | None | Dissipated on the street gutter | N | Y | N |  | 0 | Will be refered to area supervisor for further investigation.
| 313353 | Fax (858) 571-6972 (RWQCB) | 2002-09-07 16:10 | JEFF WILDER | (858) 614-5770 | City of San Diego | City of San Diego | 2002-09-07 11:17 | 2002-09-07 13:15 | 50 | 5900 | 0 | 5900 | BALBOA & GENESEE (IN TECOLOTE CANYON) | San Diego | 92117 | SD | 8"VC | 0 | 0 | FLOOD DAMAGE | OAK TREE SELF DESTRUCTED UNDER ITS OWN WEIGHT AND FELL ON EXPOSED SEWER LINE CROSSING CREEK. | Investigate; locate break; set up containment on overflow; notify construction; contain overflow until construction repaired pipe. Refer to area supervisor for follow-up. | Y | N | Y | Tecolote Creek | Mission Bay |  | Y | Y | Y | Bay/Lagoon/Beach | 11
| 315553 | Fax (858) 571-6972 (RWQCB) | 2002-09-19 21:45 | MATT HAUER | (858) 654-4130 | City of San Diego | City of San Diego | 2002-09-19 17:25 | 2002-09-19 18:50 | 5 | 425 | 200 | 225 | 606 MERLIN DR. | San Diego | 92114 | SD | 8" VC MAIN | 0 |  | ROOTS | ROOTS AND ROCKS CAUSED STOPPAGE ON 8"VC MAIN | VACTORED OVERFLOW, MACHINE RODDED MAIN TO RELIEVE STOP. REFERED MAIN TO BE BUCKETED | N | N | N | None | None | ABSORBED INTO GROUND OF EASEMENT | Y | Y | N |  |  | WILL REFER MAIN TO BE BUCKETED ASAP
| 315893 | Fax (858) 571-6972 (RWQCB) | 2002-09-21 16:05 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-09-21 11:56 | 2002-09-21 12:55 | 3 | 177 | 0 | 177 | 2920 CLAREMONT DR | San Diego | 92117 | SD | 8"VC | 0 | 0 | ROOTS | Blockage was caused by roots. | Overflowing c/o; contained at 12:40 & relieved at 15:10. Recovered/prevented additional 450 gallons from spilling. Stop was relieved by rodding machine. Station 38 notified consumer using own clean-up com; Refer to area supervisor for further evaluation. | N | N | N | None | None | soaked into side of canyon. | Y | Y | N
| 315986 | Fax (858) 571-6972 (RWQCB) | 2002-09-22 14:20 | D.A.BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-09-22 13:16 | 2002-09-22 14:20 | 3 | 177 | 0 | 177 | 2355 Calle Del Oro | San Diego | 92037 | SD | 8:VC | 1 | 12-02-01 | ROOTS | Blockage caused by roots | Contained at 14:20 by 719. Unit 718 relieved stop at 14:35. Recovered/prevented additional 45 gal from entering storm drain. Refer to area supervisor for further evaluation. | N | Y | N | None | None | DV 5 LOW FLOW DRAINAGE DIVERSION VALVE. | Y | Y | N
| 315992 | Fax (858) 571-6972 (RWQCB) | 2002-09-22 18:50 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-09-22 16:56 | 2002-09-22 17:55 | 0.5 | 17 | 0 | 17 | 1872 ALTA VIEW DR | San Diego | 92139 | SD | 8" VC | 0 | 0 | GREASE | BLOCKAGE WAS CAUSED BY GREASE. | FLUSHED LINE TO RELIEVE BLOCKAGE; REFER TO AREA SUPERVISOR FOR EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | N | Y | N
| 315680 | Fax (858) 571-6972 (RWQCB) | 2002-09-20 13:15 | Marcelino Oregel | (858) 514-5719 | City of San Diego | City of San Diego | 2002-09-19 17:10 | 2002-09-20 11:10 | 0.05 | 180 | 0 | 180 | Edgemont & Elm Streets | San Diego | 92102 | SD | 6" CP | 1 | 09/16/2002 | ROOTS | Roots & Debris caused the s;ill | Set up bypass pumping. Spill contained at 18:30, 09/19/2002. | N | N | N | None | None | Dried in canyon grounds | N | Y | N |  | 0 | Manhole was overflowing intermitently. Estimated gallon spill of 180 gallons total.
| 316089 | Fax (858) 571-6972 (RWQCB) | 2002-09-23 17:30 | LES FINCH | (858) 654-4132 | City of San Diego | City of San Diego | 2002-09-23 13:20 | 2002-09-23 15:15 | 1.5 | 172.5 | 0 | 172.5 | 4316 RANDOLPH ST--CANYON BEHIND | San Diego | 92103 | SD | 6CP-LINED | 0 |  | ROOTS | roots and heavy paper products | handrod main and submit for possible root inhibitor treatment | N | N | N | None | None | soaked into ground at manhole | N | Y | N |  | 0
| 314769 | Fax (858) 571-6972 (RWQCB) | 2002-09-15 23:50 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-09-15 19:02 | 2002-09-15 22:00 | 25 | 4450 | 0 | 4450 | 6300 Alvarado Rd | San Diego | 92182 | SD | 8"VC | 0 | 0 | LINE BREAK | Crew had to backflush to relieve stop; possible root stop but actual cause unknown. | Flushed line from parking lot into canyon to relieve stop. Refer to area supervisor for further evaluation. | N | N | Y | Alvarado Creek | San Diego River |  | Y | Y | N
| 314889 | Fax (858) 571-6972 (RWQCB) | 2002-09-17 07:30 | Mike Rosenberg | (858) 614-5742 | City of San Diego | City of San Diego | 2002-09-15 19:02 | 2002-09-16 22:00 | 2 | 3176 | 540 | 2636 | 5859 Adobe Falls | San Diego | 92182 | SD | Abandoned 8" pipe in MH 123 | 1 | 09/15/2002 | LINE BREAK | Sewage leaking from m/h # 123 into abandoned pipe dumping into creek | Will have confined space crew seal off abandoned pipe with concrete. | N | Y | Y | Alvarado Creek | San Diego River |  | Y | Y | N |  |  | Got containment at 19:30 by sand bagging down stream and pumping sewage back into system capturing 312000 gals of creek water including overflow. Will refer to area supervisor and cyn section for clean up and further investigation.
| 316453 | Fax (858) 571-6972 (RWQCB) | 2002-09-25 11:40 | D.A.BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-09-25 07:24 | 2002-09-25 08:10 | 20 | 920 | 0 | 920 | 6401 Bell Bluff St | San Diego | 92120 | SD | 8"vc | 0 | 0 | ROOTS | Blockage caused by root blockage in m/h55. | Two vactor flushers called to contain overflow; plugged stormdrain & contained overflow. Stop was relieved with a fork in M/h 55. Crews cleaned area & flushed lines. Refer to area supervisor for further evaluation. | N | Y | Y | None | None | Soaked into beginning of canyon floor off Jackson. | N | Y | N
| 316222 | Fax (858) 571-6972 (RWQCB) | 2002-09-25 15:00 | MATT HAUER | (858) 654-4130 | City of San Diego | City of San Diego | 2002-09-23 21:50 | 2002-09-23 23:15 | 5 | 425 | 0 | 425 | 1603 ROWAN ST. | San Diego | 92105 | SD | 8"VC MAIN | 0 |  | ROOTS | ROOT BLOCKAGE, 78' UP FROM MH# 131, CAUSING STOP ON 8"VC MAIN. | RODDED MAIN W/6" SCREW TO RELIEVE BLOCKAGE. THEN RODDED MAIN WITH A 8" BLADE. | N | Y | N | NONE | NONE | DRIED UP IN CONCRETE BROW DITCH ON SIDE OF SOUTH 15 | Y | Y | N |  |  | 7-33 HAD CEASED UPON FIRST UNITS ARRIVAL (23:15). STOP RELIEVED AT 23:50 HRS. 3RD PARTY ESTIMATE BELIEVED TO BE ACCURATE. EXTENSIVE FLOODING INTO RESIDENCE.
| 317180 | Fax (858) 571-6972 (RWQCB) | 2002-09-28 18:35 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-09-28 09:10 | 2002-09-28 14:30 | 0.25 | 80 | 0 | 80 | Whitman & Witherby St | San Diego | 92103 | SD | 6" CP | 1 | 5/30/02 | FLOOD DAMAGE | Break in pipe. | Machine rodded to determine main break. Notified Standby construction; Crew arrived and contained. Refer to area supervisor for further evaluation. | N | N | N | None | None | SOAKED INTO CANYON FLOOR. | N | Y | N
| 317249 | Fax (858) 571-6972 (RWQCB) | 2002-09-29 17:45 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-09-29 15:17 | 2002-09-29 16:15 | 20 | 1160 | 100 | 1060 | 5848 Streamview Dr | San Diego | 92105 | SD | 8"vc | 0 | 0 | GREASE | BLOCKAGE CAUSED BY GREASE & ROOTS. | FLUSHED LINE TO RELIEVE STOP; VACTORED PUDDLES; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | Y | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
| 317245 | Fax (858) 571-6972 (RWQCB) | 2002-09-29 18:35 | D.A. BRANCO | (858) 654-4142 | City of San Diego | City of San Diego | 2002-09-29 12:14 | 2002-09-29 12:55 | 5 | 205 | 0 | 205 | 3526 Ticonderoga St | San Diego | 92117 | SD | 8"VC | 0 | 0 | ROOTS | Blockage Was caused by roots. | Handrod main in canyon to relieve stop; Vactor began capturing spill at 12:55; stop was relieved at 16:25. Refer to area supervisor for further evaluation. | Y | Y | N | None | None | CAPTURED BY DV-6 VALVE. | Y | Y | N
| 317567 | Fax (858) 571-6972 (RWQCB) | 2002-10-01 15:30 | Johnny Peay | (858) 654-4133 | City of San Diego | City of San Diego | 2002-10-01 11:00 | 2002-10-01 12:00 | 1 | 60 | 0 | 60 | 5606 San Onofre TR. | San Diego | 92113 | SD | 6" C.P. | 0 | 0 | ROOTS | Roots caused the overflow. | Hand rodded to releive sotoppage. Will put in a hand rod cleaning site. | N | N | N | None | None | Soak in dirt. | N | Y | N |  | 0 | Will refer to CCTV for further investigation.
| 317754 | Fax (858) 571-6972 (RWQCB) | 2002-10-02 17:00 | Mike Rosenberg | (858) 614-5742 | City of San Diego | City of San Diego | 2002-10-02 10:53 | 2002-10-02 12:38 | 10 | 910 | 760 | 150 | Golfcrest dr & Navajo rd | San Diego | 92119 | SD | 8 " vc | 0 |  | OTHER | Rags & papertowels in 8" vc sewer main | Area supervisor will refer to cctv for further investigation | N | Y | Y | None | None |  | N | Y | N |  |  | Captured 760 gals at drain brow ditch with vactor
| 318531 | Fax (858) 571-6972 (RWQCB) | 2002-10-05 08:00 | Mike Bedard | (858) 654-4154 | City of San Diego | City of San Diego | 2002-10-04 22:53 | 2002-10-05 00:30 | 3 | 111 | 0 | 111 | 1271 Prospect St | San Diego | 92037 | SD | 10" PVC | 0 | 0 | GREASE | GREASE | Flushed and removed grease blockage. Schedule to televise for condition assestment. Referral to FEWD | N | Y | Y | None | Pacific Ocean | Pacific Ocean | Y | Y | Y | Bay/Lagoon/Beach | 1 | Signs removed by DEH on 10/06/02
| 318708 | Fax (858) 571-6972 (RWQCB) | 2002-10-07 15:00 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2002-10-07 09:44 | 2002-10-07 12:10 | 5 | 730 | 500 | 230 | * 5367 Auburn Drive | San Diego | 92105 | SD | 8" V.C. | 4 | 02/14/02 - 03/01/02 - 04/09/02 and 09/16/02 | ROOTS | Roots stoppage cause exfiltration from pipe. | Vactor to catch overflow at down stream storm drain manhole. Rod to releive blockage. Will refer to T.V.and Canyon Access sections for further investigation. | N | Y | N | None | None | Soak in dry canyon grounds | N | Y | N |  | 0 | * Location is 3203 Isla Vista Drive in canyon. Spill was contained at 11:10
| 319179 | Fax (858) 571-6972 (RWQCB) | 2002-10-09 18:30 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2002-10-09 14:06 | 2002-10-09 16:07 | 3 | 363 | 225 | 138 | 2251 Barney Street | San Diego | 92139 | SD | 8" V.C. | 0 | 0 | ROOTS | Heavy roots caused exfiltration from clean out. | Vactor to recover spill. Rod to releive blockage at 200' from u/s MH# 29 to d/s MH# 30. Will refer to CCTV and to area supervisor for further action, also submit for possible root inhibitor treatment. | N | Y | N | None | None | Dissipated in storm drain conveyance system. | N | Y | N |  | 0 | By the time overflow ends 4 full plastic containers of roots were filled up, Spill was contained at 15:30
| 319752 | Fax (858) 571-6972 (RWQCB) | 2002-10-13 16:45 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-10-13 12:32 | 2002-10-13 13:45 | 0.5 | 36.5 | 0 | 36.5 | 4595 CONTOUR BL | San Diego | 92115 | SD | 6"CP | 0 | 0 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS. Sewage was seeping from cracks in street. | FLUSHED LINE TO RELIEVE STOP. REFER TO AREA SUPERVISOR FOR EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | N | Y | N
| 319778 | Fax (858) 571-6972 (RWQCB) | 2002-11-04 14:15 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2002-10-14 07:28 | 2002-10-14 08:45 | 15 | 1155 | 565 | 590 | 730 Cornish Drive | San Diego | 92107 | SD | 6" C.P. | 1 | 08/30/2002 | ROOTS | Heavy roots caused exfiltration from C.P main | Vactor to recover spill. Rodded to releive blockage at 60' from u/s MH# 301 to d/s MH# 302. Will refer to CCTV and to area supervisor for further action. Also submit for possible root inhibitor tratment. OVERFLOWING MH. IS 301 | N | Y | Y | Pacific Ocean | None |  | N | Y | Y | Bay/Lagoon/Beach | 1 | Spill was contained at 8:20. Revision was done to correct arrival date, from what it was from 7/14/02 to 10/14/02.
| 320552 | Fax (858) 571-6972 (RWQCB) | 2002-10-17 04:00 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2002-10-16 23:01 | 2002-10-17 00:45 | 5 | 520 | 300 | 220 | 4000 40TH ST | San Diego | 92105 | SD | 6" VC | 0 |  | GREASE | GREASE AND PAPER BLOCKAGE ON 6" VC SEWER MAIN. | RODDED MAIN TO RELIEVE BLOCKAGE. REFER TO HAVE MAIN FLUSHED AND TELEVISED. | N | Y | Y | None | None | SOAKED INTO DIRT STORM CHANNEL SO. OF I-805 I-15 SPLIT. | Y | Y | N |  |  | OVERFLOW CAME OUT OF ABANDONED LATERAL IN VACANT LOT EAST OF SEWER MAIN.
| 320673 | Fax (858) 571-6972 (RWQCB) | 2002-10-18 07:30 | Jeff Wilder for Carl Mickelson | (858) 614-5770 | City of San Diego | City of San Diego | 2002-10-17 16:28 | 2002-10-17 17:07 | 2 | 78 | 40 | 38 | Kurtz St. x Smith St. | San Diego | 92110 | SD | 4" CI | 0 | 0 | CONSTRUCTION | Debris blocked 4" CI main | Vacuumed overflow, flushed to relieve blockage, rodded to clean main, refer to be TV'd | N | Y | N | None | None | Dissapated in stormdrain | Y | Y | N
| 321082 | Fax (858) 571-6972 (RWQCB) | 2002-10-19 14:40 | D.A.BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-10-19 10:23 | 2002-10-19 11:35 | 3 | 216 | 0 | 216 | 3212 31ST ST | San Diego | 92104 | SD | 8"VC | 0 | 0 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS. | HANDRODDED LINE TO RELIEVE ROOT STOPPAGE; REFER TO AREA SUPERVISOR FOR EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
| 321098 | Fax (858) 571-6972 (RWQCB) | 2002-10-19 16:40 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-10-19 14:48 | 2002-10-19 15:25 | 0.25 | 9.25 | 0 | 9.25 | 4205 60TH ST | San Diego | 92115 | SD | 6"VC | 0 | 0 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS. | M/H 7-32 upon arrival; vactored m/h; Rodder set up & relieved root blockage; refer to area supervisor for further evaluation. Amount of overflow estimated. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
| 321140 | Fax (858) 571-6972 (RWQCB) | 2002-10-22 08:10 | Mike Bedard | (858) 654-4154 | City of San Diego | City of San Diego | 2002-10-19 23:23 | 2002-10-21 19:10 | 2 | 1654 | 0 | 1654 | 5430 REGENTS RD | San Diego | 92117 | SD | 8"VC | 0 | 0 | OTHER | Stby unable to locate at night in canyon and access due to Poision Oak, gained access on 10/20/02. set up bypass pumps at 1910 hours. Relieved stoppage at 1300hours on 10/21/02 | relieved debri stoppage vactored ponded sewage and returned to system in addition to containment comment on line item#16. Schedule to televise for condition of structure | N | N | N | None | None | SOAKED INTO CANYON. | Y | Y | N |  |  | This spillage was intermittent throughout low flow periods due to partail flow in the sewer main. Estimate of spillage volume reflects this adjustment.
| 321093 | Fax (858) 571-6972 (RWQCB) | 2002-10-19 16:05 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-10-19 11:49 | 2002-10-19 12:40 | 3 | 153 | 153 | 0 | 5323 Soledad Mtn Rd | San Diego | 92037 | SD | 8"vc | 0 | 0 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS. | FLUSHED LINE TO RELIEVE ROOT STOPPAGE; REFER TO AREA SUPERVISOR FOR EVALUATION. | N | Y | N | None | None | IPS 8 | Y | Y | N
| 321165 | Fax (858) 571-6972 (RWQCB) | 2002-10-20 18:05 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-10-20 16:28 | 2002-10-20 17:15 | 0.5 | 23.5 | 0 | 23.5 | 4717 University Ave | San Diego | 92105 | SD | 6"VC | 0 | 0 | GREASE | BLOCKAGE CAUSED BY GREASE & RAGS | FLUSHED LINE TO RELIEVE STOP; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
| 321168 | Fax (858) 571-6972 (RWQCB) | 2002-10-20 19:50 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-10-20 17:15 | 2002-10-20 18:55 | 8 | 800 | 800 | 0 | 950 VAN NUYS ST | San Diego | 92109 | SD | 8"VC | 1 | 04/04/2002 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS. | FLUSHED LINE IN CANYON TO RELIEVE ROOT STOP; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION | N | Y | N | None | None | DV-1 | Y | Y | N
| 321160 | Fax (858) 571-6972 (RWQCB) | 2002-10-20 17:30 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-10-20 13:25 | 2002-10-20 15:25 | 1 | 120 | 0 | 120 | 8551 LAJOLLA SHORES DR | San Diego | 92037 | SD | 8"VC | 1 | 1/02/2002 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS; ALSO FOUND PLASTIC JUG | MACHINE RODDED TO RELIEVE ROOT STOP; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | N | N | None | None | SOAKED INTO HEAVY BRUSH AREA ON PRIVATE PROPERTY. | Y | Y | N
| 321156 | Fax (858) 571-6972 (RWQCB) | 2002-10-20 21:25 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-10-20 11:28 | 2002-10-20 13:10 | 0.5 | 51 | 0 | 51 | 2159 54TH ST | San Diego | 92105 | SD | 6"VC | 2 | 1/13/02; 9/7/02 | ROOTS | 7-31 C/O CAUSED BY ROOTS IN MAIN | FLUSHED D/E LINE TO RELIEVE ROOT STOP; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
| 322718 | Fax (858) 571-6972 (RWQCB) | 2002-11-01 10:30 | Mike Rosenberg | (858) 614-5742 | City of San Diego | City of San Diego | 2002-10-28 10:45 | 2002-10-28 12:00 | 50 | 3750 | 2250 | 1500 | 14085 Mango Dr | San Diego | 92130 | SD | 8" vc sewer main | 0 |  | CONSTRUCTION | Paper towels and other debris in 8" vc sewer main | Contacted cctv to have 8" main televised a.s.a.p. | Y | Y | Y | Penasquitos lagoon | Pacific Ocean |  | Y | Y | N |  | 3 | Will refer to area supervisor for further investigation. Will close out report when county heath calls us back to pick up signs. Signs were picked up 10/31/2002 after call from county heath.
| 323433 | Fax (858) 571-6972 (RWQCB) | 2002-10-31 12:30 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2002-10-31 06:40 | 2002-10-31 07:20 | 7 | 280 | 80 | 200 | 5550 Blueridge Street | San Diego | 92139 | SD | 8" V.C. | 0 | 0 | ROOTS | Root Blockage at 88' from u/s MH# 47, causing stop on 8" V.C. pipe. | Rodded main with 6" screw ti relieve sotppage. Then rodded main with a 8" blade. | N | Y | N | None | None | Dissipated in storm drain conveyance system | N | Y | N |  | 0 | Spill ceased upon emergency response unit arrived at 7:20 A.M. Spill dissipated in storm drain system before hitting canyon ground.
| 325038 | Fax (858) 571-6972 (RWQCB) | 2002-11-10 15:00 | Rick Donahue | (858) 654-4155 | City of San Diego | City of San Diego | 2002-11-10 10:30 | 2002-11-10 12:30 | 5 | 600 | 0 | 600 | Jackson Dr & Mission Gorge Road | San Diego | 92124 | SD | 10"vc | 0 | 0 | ROOTS | ROOTS IN 10" vc MAIN CASUED STOPPAGE. | FLUSHED TO RELIEVE ROOT STOPPAGE, CLEARED ACCESS TO M/H, TELEVISE TO DETERMINE ROOT ENTRY POINT AND REVISE MAINTENANCE SCHEDULE | Y | N | Y | Tributary to San Diego River | San Diego River |  | Y | Y | N |  | 0 | SSO WAS DISCOVERED BY PARK RANGER AND AERIAL SUPPORT PROVIDED PIN POINT LOCATION. Revised to reflect correct service request.
| 325072 | Fax (858) 571-6972 (RWQCB) | 2002-11-11 16:30 | RICK DONAHUE | (858) 654-4155 | City of San Diego | City of San Diego | 2002-11-11 08:20 | 2002-11-11 09:15 | 10 | 550 | 550 | 0 | 2314 AMITY ST. | San Diego | 92109 | SD | 8" POLY LINED | 0 |  | ROOTS | ROOTS IN DOWNSTREAM SIDE OF MANHOLE | FLUSHED TO RELIEVE STOOPAGE, CLEANED MANHOLE, TELEVISE AND REVISE SCHEDULED MAINTENANCE | Y | Y | N | None | None | STORM DRAIN TO IPS #9, RETURNED TO SYSTEM | Y | Y | N |  |  | ALL SEWAGE WAS CAPTURED AT LOW FLOW INTERCEPTOR PUMP STATION #9 AND RETURNED TO COLLECTION SYSTEM.
| 325068 | Fax (858) 571-6972 (RWQCB) | 2002-11-11 16:00 | RICK DONAHUE | (858) 654-4155 | City of San Diego | City of San Diego | 2002-11-11 07:40 | 2002-11-11 08:30 | 1 | 50 | 0 | 50 | HERMAN & LANDIS | San Diego | 92105 | SD | 8" VC | 1 | 12/18/2001 | GREASE | GREASE AND PAPER PRODUCTS CAUSE PARTIAL STOPPAGE ON MAIN | FLUSHED TO RELIEVE STOPPAGE, TELEVISE AND REVISE SCHEDULED MAINTENANCE. | N | N | N | None | None | DRIED IN ALLEY | Y | Y | N
| 325773 | Fax (858) 571-6972 (RWQCB) | 2002-11-14 19:00 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2002-11-14 13:42 | 2002-11-14 15:50 | 10 | 1280 | 1100 | 180 | SR-163 SB & University Av. | San Diego | 92103 | SD | 8" VC | 1 | 01/02/2002 | ROOTS | Heavy roots in pipe caused stoppage | Vactor to recover spill. Handrod main to releive blockage. Will refer to area supervisor for further investigation. | N | Y | N | None | None | Storm pump station "E" under Hwy. 163 | N | Y | N |  | 0 | Spill was contained at 14:10. Submit for possible root inhibitor treatment.
| 325925 | Fax (858) 571-6972 (RWQCB) | 2002-11-15 12:30 | Mike Rosenberg | (858) 614-5742 | City of San Diego | City of San Diego | 2002-11-15 08:20 | 2002-11-15 11:15 | 50 | 8750 | 6600 | 2150 | Linda Vista rd & Ulric st | San Diego | 92110 | SD | 8" vc pipe | 0 |  | GREASE | Heavy grease in 8" vc pipe | Will refer to cctv for tv inspection of 8" vc pipe a.s.a.p. | N | Y | N | None | None | Soaked in to ground around storm drain outlet. | Y | Y | N |  |  | Will refer to area supervisor for further investigation.
| 326200 | Fax (858) 571-6972 (RWQCB) | 2002-11-17 11:20 | Carlos E. Gomez Tagle | (858) 614-5770 | City of San Diego | City of San Diego | 2002-11-17 07:41 | 2002-11-17 09:30 | 1 | 109 | 0 | 109 | 1040 W UPAS St | San Diego | 92101 | SD | 6" CP | 6 | 12/20, 23/01, 1/6/02, 1/15/02, 2/5/02, 9/16/02 | ROOTS | Sewage leaking from underground behind residence. | Units responding contained spill at 0930 hrs and cleared stop from dwon stream MH35, on easment. | N | N | N | None | None | Dissipated on property ground. | Y | Y | N |  |  | Stand by Supervisor was advised over possible break main, however units reponding cleared stop. Will refer to area supervisorfor futher investigation. REVISION COMENTS: Confirmation time and volumen was change.
| 326254 | Fax (858) 571-6972 (RWQCB) | 2002-11-18 12:45 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2002-11-18 08:28 | 2002-11-18 10:28 | 0.25 | 30 | 0 | 30 | 1847 Bancroft Street | San Diego | 92102 | SD | 6" VC | 3 | 3/7/02 - 9/16/02 - 9/19/02 | ROOTS | Heavy roots in pipe cause blockage | Walked in canyon to locate manholes, rod to releive stoppage, will refer to area supervisor to add on a routine maintenance. | N | N | N | None | None | Soak in canyon ground | N | Y | N |  | 0 | Manhole was overflowing intermintently. Estimated gallons spil of 30 gallons total.
| 327537 | Fax (858) 571-6972 (RWQCB) | 2002-11-23 20:00 | K. Gensler | (858) 614-5770 | City of San Diego | City of San Diego | 2002-11-23 12:00 | 2002-11-23 13:03 | 5 | 315 | 0 | 315 | Donax Av x Georgia St | San Diego | 92154 | SD | 12"vc | 0 |  | CONSTRUCTION | Heavy sludge on a 30" main just upstream of contractors bypass pump. | Units responding contained spill from stormdrain outlet, advised standby supervisor to respond to pump station problem. Setup bypass pumps and clean spill on private property. | N | Y | Y | Otay River | San Diego Bay |  | Y | Y | N |  |  | Setup bypass pumps until 30" main can be clean.
| 327526 | Fax (858) 571-6972 (RWQCB) | 2002-11-23 19:30 | Carlos E. Gomez Tagle | (858) 614-5770 | City of San Diego | City of San Diego | 2002-11-23 09:34 | 2002-11-23 11:30 | 2 | 236 | 150 | 86 | 5210 Joan Ct | San Diego | 92115 | SD | 8"vc | 1 | 05/27/2002 | ROOTS | Sewage leaking from MH47 caused by roots | Units responding contained & relieved stop from down stream MH(20), stand by supervisor advised to respond on sewage puddle down on easment. | N | Y | N | None | None | sewage puddle on the bottom of the easment | Y | Y | N |  |  | Stand-by crew went and recovered 150 gal of sewage by pumping sewage back to system. That change amount of overflow released to enviorment. Added MHMap Id #47
| 327583 | Fax (858) 571-6972 (RWQCB) | 2002-11-24 14:45 | Carlos E. Gomez Tagle | (858) 614-5770 | City of San Diego | City of San Diego | 2002-11-24 10:56 | 2002-11-24 14:10 | 2 | 388 | 333 | 55 | 3646 Albert St | San Diego | 92103 | SD | 8"vc | 1 | 12/10/01 | ROOTS | sewage leaking from MH570 caused by roots and grease. | Units responding contained & relieved stop from down stream MH(353), advised stand via supervisor and referred to section supervisor for futher investigation. | N | Y | N | None | None | contained and vaccumed back to the system, rest dryed in canyon | Y | Y | N
| 329109 | Fax (858) 571-6972 (RWQCB) | 2002-12-03 14:00 | Mike Rosenberg | (858) 614-5742 | City of San Diego | City of San Diego | 2002-12-03 09:05 | 2002-12-03 10:30 | 10 | 850 | 850 | 0 | Bluffside ave & Mission Bay dr | San Diego | 92109 | SD | 8" vc pipe | 0 |  | GREASE | Heavy grease & roots in 8" vc pipe. | Clean two section up & down from overflowing manhole. | N | Y | N | Rose creek | None | IPS 1 Mission bay sewer interceptor | N | Y | N |  |  | Will refer to cctv a.s.a.p. and give copy of sso report to area supervisor.
| 329320 | Fax (858) 571-6972 (RWQCB) | 2002-12-03 23:30 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2002-12-03 20:00 | 2002-12-03 21:40 | 0.5 | 50 | 50 | 0 | 813 ALLERTON CT. | San Diego | 92109 | SD | 8" PVC | 0 |  | GREASE | GREASE AND RAG BLOCKAGE 20' UPSTREAM OF MH24 ON CITY SEWER MAIN. | FLUSHED TO RELIEVE BLOCKAGE AND CLEAN MAIN. VACTORED OVERFLOW, RECOVERING ALL SEWAGE. REFER TO HAVE MAIN TELEVISED. | N | N | N | None | None | PUDDLED UP IN LOW AREA IN ALLEY. | Y | Y | N
| 329557 | Fax (858) 571-6972 (RWQCB) | 2002-12-05 12:00 | Paul Anderson | (858) 614-5719 | City of San Diego | City of San Diego | 2002-12-05 08:10 | 2002-12-05 10:20 | 0.5 | 65 | 30 | 35 | 3323 Dwight St. | San Diego | 92105 | SD | 6" cp pipe | 3 | 12-18-2001, 2-3-2002, 11-11-2002 | ROOTS | Heavy roots in 6" cp pipe | Cleaned roots out of 6" cp pipe with rodding truck. | N | N | N | None | None | Disipated into dirt alley. | Y | Y | N |  |  | Will give area superviser copy of report and recommend they refer that section of main to be televised by cctv.
| 329796 | Fax (858) 571-6972 (RWQCB) | 2002-12-05 22:00 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2002-12-05 18:56 | 2002-12-05 19:10 | 1 | 30 | 15 | 15 | 2912 INGELOW ST. | San Diego | 92106 | SD | 8" CP | 0 |  | GREASE | HEAVY GREASE IN SEWER MAIN BETWEEN MH 313 AND MH 296. | FLUSHED MAIN TO RELIEVE GREASE BLOCKAGE AND CLEAN. VACTORED TO RECOVER 15 GALS. DEODORIZED AREA. REFER TO BE TELEVISED AND FOR FEWD INVESTIGATION. | N | N | N | None | None | PUDDLED IN LOW SPOTS IN GUTTER AND SWALE AT SCOTT ST. | Y | Y | N |  |  | MH 313 WAS NOT OVERFLOWING UPON ARRIVAL.
| 329898 | Fax (858) 571-6972 (RWQCB) | 2002-12-06 18:00 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-12-06 13:48 | 2002-12-06 15:30 | 3 | 306 | 0 | 306 | ASTER & RANDALL ST | San Diego | 92109 | SD | 8"VC | 0 | 0 | ROOTS | Blockage was caused by roots and grease. | Flushed line to relieve stop; refer to area supervisor for further evaluation. Call originally came in as a water problem SR 329881. | N | Y | N | None | None | I 9 interceptor. | N | Y | N
| 330201 | Fax (858) 571-6972 (RWQCB) | 2002-12-08 21:55 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-12-08 18:53 | 2002-12-08 19:35 | 1 | 42 | 0 | 42 | 3972 JACKDAW ST | San Diego | 92103 | SD | 8"PVC | 0 | 0 | ROOTS | BLOCKAGE WAS CAUSED BY GREASE AND ROOTS. | VACTORED M/H TO STOP OVERFLOW; INSERTED ROD IN 7-32 M/H & RODDED TO RELIEVE STOP. REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | N | N | None | None | SOAKED INTO CANYON. | Y | Y | N
| 331003 | Fax (858) 571-6972 (RWQCB) | 2002-12-12 18:00 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2002-12-12 14:34 | 2002-12-12 16:34 | 0.25 | 30 | 25 | 5 | Campanile Drive & Lindo Paseo | San Diego | 92115 | SD | 6" V.C. | 0 | 0 | ROCKS | Big rocks, debris and sludge cause spill | Rodded main to rellieve blockage at 403' will refer to area supervisor for further investigation. | N | N | N | None | None | Vactored to catch overflow at street level or dissipated on gutter. | N | Y | N |  | 0 | Manhole was overflowing intermitently. Vactored inside manhole to contained spill at 15:38.
| 331658 | Fax (858) 571-6972 (RWQCB) | 2002-12-16 13:30 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2002-12-16 08:35 | 2002-12-16 09:20 | 18 | 810 | 0 | 810 | Valencia & Latimer | San Diego | 92113 | SD | 8" V.C. | 1 | 01/06/2002 | ROCKS | Big rock in main caused blockage | Hand rod to relleive stoppage. Will refer to supervisor to add on a routine maintenance | N | Y | N | None | None | Soak in Cayon grounds, in channel sands before reach 47th St. | N | Y | N |  | 0 | Manhole was overflowing intermitently, it is an aproximatly volume of gallons spilled.
| 332000 | Fax (858) 571-6972 (RWQCB) | 2002-12-17 14:15 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2002-12-17 09:05 | 2002-12-17 11:10 | 0.8 | 100 | 60 | 40 | 4544 Valencia Drive | San Diego | 92115 | SD | 6" C.P. | 1 | 05/16/2002 | ROOTS | Heavy roots in main caused sotoppage | Flushed main to releive blockage, vactored to catch overflow at surface level. | Y | N | N | None | None | Dissipated on street gutter. | N | Y | N |  | 0 | Will give area supervisor copy of report recomending to add on a routine maintenance
| 332795 | Fax (858) 571-6972 (RWQCB) | 2002-12-20 20:40 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-12-20 17:10 | 2002-12-20 18:00 | 5 | 250 | 0 | 250 | 3050 K ST | San Diego | 92102 | SD | 6"VC | 2 | 2-04-2002 & 5-04-2002 | GREASE | BLOCKAGE WAS CAUSED BY GREASE. | FLUSH LINE TO RELIEVE STOP; WASH DOWN ALLEY; RODDING MACHINE CLEANED TWO LINES UP AND DOWN FROM STOP: REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | Y | Y | N | None | None | STORM DRAIN NOT RUNNING; DISSIPATED IN SYSTEM. | Y | Y | N
| 332859 | Fax (858) 571-6972 (RWQCB) | 2002-12-21 12:55 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-12-21 08:14 | 2002-12-21 10:15 | 0.5 | 60.5 | 0 | 60.5 | 4962 SAN JOAQUIN DR | San Diego | 92109 | SD | 8"VC | 1 | 12-06-2002 | ROOTS | 7-31 C/O; BLOCKAGE WAS CAUSED BY ROOTS; | FLUSHED LINE TO RELIEVE BLOCKAGE; CLEAN AREA; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | Y | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
| 332941 | Fax (858) 571-6972 (RWQCB) | 2002-12-22 15:40 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-12-22 12:57 | 2002-12-22 13:45 | 5 | 240 | 50 | 190 | 4545 ALTADENA AVE | San Diego | 92115 | SD | 6" CP | 1 | 10-13-2002 | GREASE | BKLOCKAGE WAS CAUSED BY GREASE. | FLUSHED LINE TO RELIEVE STOP; CLEAN SPILL AREA; RECOVER 50 GALLONS; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
| 333164 | Fax (858) 571-6972 (RWQCB) | 2002-12-24 15:00 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2002-12-24 11:20 | 2002-12-24 12:12 | 1.75 | 91 | 60 | 31 | 3403 Little Flower Street. | San Diego | 92104 | SD | 6" C.P. | 1 | 03/29/2002 | ROCKS | Rocks and gravel caused stoppage in 6" concrete pipe. | Rodded and hit stoppage at 75' from d/s MH# 370. Area supervisor will refer to T.V. section, for further investigation.l | N | Y | N | None | None | Dissipatted in storm drain conveyance system. | Y | Y | N |  | 0 | Vactored to recover spill at groun level. Will give a copy of report and recommend to add in maintenace program
| 333284 | Fax (858) 571-6972 (RWQCB) | 2002-12-25 20:00 | RICK DONAHUE | (858) 654-4155 | City of San Diego | City of San Diego | 2002-12-25 10:00 | 2002-12-25 17:10 | 3 | 1290 | 100 | 1190 | 2156 NATIONAL AVE | San Diego | 92101 | SD | 6"VC | 0 |  | FLOOD DAMAGE | BREAK ON 6' GRAVITY MAIN | MACHINE RODDED TO CLEAR STOP, FOLOW UP FLUSHING, REFER FOR REPAIRS | N | Y | Y | None | None | DRIES IN GUTTER AND STORM CONVEYANCE SYSTEM | N | Y | N
| 333329 | Fax (858) 571-6972 (RWQCB) | 2003-01-02 14:00 | Rick Donahue | (858) 654-4155 | City of San Diego | City of San Diego | 2002-12-26 10:31 | 2002-12-26 12:13 | 88.17 | 130756.1 | 4500 | 126256.1 | 2636 GRAND AVE | San Diego | 92109 | SD | 10"VC | 0 | 0 | GREASE | BLOCKAGE WAS CAUSED BY GREASE. SEWAGE BACKFLOWED UP DV76A AND INTO STORM DRAIN | MACHINE RODDED TO RELIEVE STOP; VACTORED 2 & A QUARTER LOADS FROM STORMDRAIN WHILE WORKING ON STOP; FLUSH LINES IN AREA; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | Y | ROSE CREEK INLET | MISSION BAY |  | Y | Y | Y | Bay/Lagoon/Beach | 7 | 202 signs were posted for 5 days, 5 signs were posted for 7 days. Due to high bacteriological levels on 12-25-02 this report reflects spill could have started on 12-25-02, no visual confirmation until 12-26-02 at 10:30.
| 333581 | Fax (858) 571-6972 (RWQCB) | 2002-12-28 00:30 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2002-12-27 19:48 | 2002-12-27 21:00 | 5 | 360 | 0 | 360 | 5001 PIROTTE DR | San Diego | 92105 | SD | 8"VC | 0 | 0 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS. | MACHINE RODDED TO RELIEVE BLOCKAGE; DOWNSTREAM M/H PLUGGED; CLEANED ROOTS FROM M/H; FLUSHER CALLED TO FLUSH DEEP M/H; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | N | Y | N
| 023001 | FAX 338-2386 | 2002-07-26 | C. Kamenides | (619) 522-7387 | City of Coronado | City of Coronado | 2002-07-25 16:30 | 2002-07-25 17:00 | 1.67 | 50 | 50 | 0 | 1600 blk Miguel Avenue | Coronado | 92118 | SD | Sewer main line | 0 |  | ROOTS | Roots in line trapped non-dissolved paper products, causing blockage | Cleared blockage, scheduled additional rodder maintenance to prevent future occurrence | N | N | N | None | None | Vactor tank | Y | N | N
X | 023002 | Quarterly Report | 2002-10-31 11:05 | K. LeMoine | (619) 522-7380 | City of Coronado | City of Coronado | 2002-10-31 11:05 | 2002-10-31 11:25 | 1 | 20 | 20 | 0 | 860 Olive Avenue | Coronado | 92118 | SD | Private lateral | 0 |  | PRIVATE PROPERTY | Resident removed cap to sewer lateral cleanout | Replaced cap, informed resident that cap must be properly installed and maintained | N | N | N | None | None | Vactor | N | N | N |  |  |  |  | X
| 2001 | Victor Vasquez | 2002-12-10 15:30 | John Pastore | 760 942-5147 | Rancho Santa Fe Community Services District | Rancho Santa Fe Community Services District | 2002-12-10 06:30 | 2002-12-10 08:30 |  | 4800 | 4000 | 800 | Rancho Santa Fe Golf Course | Rancho Santa Fe | 92067 | SD | 26624139-350B | 0 |  | Debris | Accumulation of paper debris in manhole. | Sewer blockage was jet rodded and cleared. This sewer line is cleaned semi-annually. There was no roots or grease observed. | N | N | N | Golf Course Swale | None | On-site runoff collect system. | Y | Y | N |  |  | A full recovery of the sewage was made less the amount that soaked into the ground.
X | 023008 | Fax (858)-571-6972 | 2002-10-07 15:45 | John Vaught | (760) 839-4323 | City of Escondido | City of Escondido | 2002-10-07 11:00 | 2002-10-07 11:30 | 1 | 30 | 30 | 0 | 101 S. Spruce St. | Escondido | 92025 | SD | Private cleanout | 2 | 12/22/01 2/16/02 | PRIVATE PROPERTY | Unknown - Private property | The apartment management was issued a Notice of Correction. Investigation continuing. | N | Y | N | none | none | Vacuumed and returned to sanitary sewer. | Y | N | N |  |  |  |  | X
X | 023009 | Fax (858)-571-6972 | 2002-10-10 14:30 | John Vaught | (760) 839-4323 | City of Escondido | City of Escondido | 2002-10-10 10:45 | 2002-10-10 11:15 | 7 | 210 | 125 | 85 | 939 S. Andreasen Dr. | Escondido | 92025 | SD | Private cleanout | 0 |  | PRIVATE PROPERTY | Unknown - Private property | A Notice of Correction was issued to the property owner. | N | Y | Y | Escondido Creek | San Elijo Lagoon |  | Y | N | N |  |  |  |  | X
X | 023010 | Fax (858)-571-6972 | 2002-10-23 09:30 | Jim Miller | (760) 839-4668 | City of Escondido | City of Escondido | 2002-10-23 07:00 | 2002-10-23 09:00 | 1.66 | 200 | 200 | 0 | 1135 Goldenrod St. | Escondido | 92027 | SD | Private cleanout | 0 |  | PRIVATE PROPERTY | Unknown - Private property | A Notice of Correction was issued to the property owner. | N | N | N | none | none | Vacuumed and returned to sanitary sewer. | Y | N | N |  |  |  |  | X
X | 023011 | Fax (858)-571-6972 | 2002-11-07 15:00 | John Vaught | (760) 839-4323 | City of Escondido | City of Escondido | 2002-11-07 06:40 | 2002-11-07 13:00 | 5 | 1900 | 300 | 1600 | 774 E. Mission Ave. | Escondido | 92025 | SD | Private cleanout | 1 | 2001-11-28 | PRIVATE PROPERTY | Unknown - Private property | A Notice of Correction was issued to the property owner. | N | Y | N | none | none | The volume that was not recovered absorbed to soil. | Y | Y | N |  |  |  |  | X
X | 023012 | Fax (858)-571-6972 | 2002-11-13 15:00 | John Vaught | (760) 839-4323 | City of Escondido | City of Escondido | 2002-11-12 19:00 | 2002-11-13 10:00 | 7 | 6300 | 800 | 5500 | 1240 N. Broadway | Escondido | 92025 | SD | Private cleanout | 0 |  | PRIVATE PROPERTY | Unknown - Private property | The apartment management was issued a Notice of Correction. | N | Y | Y | Escondido Creek | San Elijo Lagoon |  | Y | Y | Y | Public access points along Esc. Creek | 3 |  |  | X
X | 023013 | Fax (858)-571-6972 | 2002-12-03 10:30 | John Vaught | (760) 839-4323 | City of Escondido | City of Escondido | 2002-12-02 14:30 | 2002-12-02 16:00 | 0.25 | 22 | 22 | 0 | 613 E. Lincoln Ave. | Escondido | 92025 | SD | Private cleanout | 0 |  | PRIVATE PROPERTY | Possible broken service lateral | Contractor made necessary repairs. | N | N | N | none | none | Vacuumed and returned to sanitary sewer. | Y | N | N |  |  |  |  | X
| 023014 | Fax (858)-571-6972 | 12/19/02 14:00 | John Vaught | (760) 839-4323 | City of Escondido | City of Escondido | 2002-12-19 06:40 | 2002-12-19 07:05 | 170 | 4260 | 1200 | 3060 | 353 Highland Place | Escondido | 92025 | SD | Escondido Sewer Manhole 5476 | 0 |  | GREASE | Grease and debris collected at low point in main line. | Scheduled cleanings will occur three times annually. | Y | Y | Y | Escondido Creek | San Elijo Lagoon |  | Y | Y | Y | Public access points along Esc. Creek | 3
X | 023015 | Fax (858)-571-6972 | 2002-12-31 15:35 | Lance Lauricha | (760) 839-4668 | City of Escondido | City of Escondido | 2002-12-17 | 2002-12-31 13:00 | 0.024 | 500 | 50 | 450 | 1905 Conway Dr. | Escondido | 92027 | SD | Private cleanout | 0 |  | BLOCKAGE | Reverse fall in private lateral caused a partial stoppage. | A Notice of Correction was issued to the property owner. | N | Y | Y | Reidy Creek | Escondido Creek |  | Y | N | N |  |  |  |  | X
| 022002 | Brian Kelly | 2002-10-08 16:00 | John Walter | 858-451-7837 | Olivenhain Municipal Water District | Olivenhain Municipal Water District | 2002-10-07 20:00 | 2002-10-08 09:35 | 62 | 3100 | 3100 | 3100 | 17034 Camino San Bernardo | San Diego | 92198 | SD | Manhole | 0 | 0 | ROOTS | Roots disturbed manhole rings and blocked sewage flow. | Repair manhole and eliminate nearby active tree stump. Continue to establish listing of hot spots. | N | Y | N | Artifician Riparian Habitat | San Dieguito River | None | Y | N | N | None | 0 | See Attached letter
| 032002 | Bryan Ott | 2002-10-16 16:00 | John Walter | 858-451-7837 | Olivenhain Municipal Water District | Olivenhain Municipal Water District | 2002-10-14 18:00 | 2002-10-15 01:00 | 3 | 1260 | 0 | 1260 | Calle Ambiente | San Diego | 92067 | SD | Manhole | 0 | 0 | DEBRIS | Construction debris collected at base of slope and plugged sewer line | County of San Diego crews responded to the overflow and cleared the blockage. | N | Y | N | Natural wetlands | San Dieguito River | None | Y | N | N | None | 0
X | 020304 | Clay Clifton | 10/10/02 - 8:00 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2002-10-01 17:30 | 2002-10-01 17:30 |  | 50 | 50 | 0 | 2285 Hosp Wy | Carlsbad | 92008 | SD | Private cleanout in apartment complex | 0 | None | Private Property | Sewer line in apartment complex has low spot causing debris to block up | Repair low spot in their line or rod it regularly. *I gave property manager instructions on how to clean up the area. | N | N | N | parking lot of complex | None | same as #26 | Y | N | N | N/A | 0 | Private spill |  | X
| 020305 | Clay Clifton | 10/11/02 - 8:30 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2002-10-10 19:30 | 2002-10-10 21:00 | 1 | 90 | 300 | 0 | 382 Hemlock Ave | Carlsbad | 92008 | SD | Property line cleanout | 0 | None | Roots | Blockage in main caused backup into laterals which overflowd | Clear stoppage, continue with more aggressive cleaning program. * Clean up and washdown was done, the area was sanitized | N | N | N | Gutter in front of complex | Gutter in front of complex | Storm drain inlet was blocked, no sewage made it any farther | Y | N | N | N/A | 0 | None
X | 020306 | Clay Clifton | 1/17/02, 8:30 am | Mario Remillard | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2002-11-17 08:30 | 2002-01-17 08:45 |  | 5 | 5 | 1 | 2335 Via Francisca | Carlsbad | 92008 | SD | 4" cleanout, private lateral | 0 | None | Blockage | Private lateral stoppage in apartment complex | Instructed property management rep to clean their system as well as do proper cleanup | N | Y | N | None | None | Storm drain, property management company recaptured out of storm drain | Y | N | N | N/A | 0 | None |  | X
X | 020307 | Clay Clifton | 11/20/02 - 1:54 pm | Mario Remillard | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2002-11-20 13:54 | 2002-11-20 14:00 |  | 20 | 20 | 0 | 2700 State St | Carlsbad | 92008 | SD | 3" Private cleanotu | 0 | None | Blockage | Grease | Jet vac sewer main to clear blockage | N | N | N | None | None | N/A | Y | N | N | N/A | 0 | None |  | X
X | 020308 | Clay Clifton | 11/25/03 - 8:00 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2002-11-24 09:00 | 2002-11-24 09:05 | 1 | 5 | 5 | 0 | 1261 Oak Ave | Carlsbad | 92008 | SD | Property line cleanout, toilet | 0 | None | Unknown | Blockage in main caused back up | Routine preventative maintenance sewer main cleaning program | N | N | N | Bathroom of 1261 Oak Ave | None | Bathroom of 1261 Oak Ave | Y | N | N | N/A | 0 | None |  | X
| 020309 | Clay Clifton | 11/27/02 - 8:00 | Martin Flores | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2002-11-26 17:30 | 2002-11-26 17:45 | 1 | 15 | 75 | 0 | 2669 Madison St | Carlsbad | 92008 | SD | Property line cleanout | 0 | None | Unknown | Blockage in main caused proeprty line clean out to overflow | Routine sewer main cleaning | N | N | N | None | None | In parking lot, recaptured everythign | Y | N | N | N/A | 0 | Washed down parking lot, recaptured everything
| 120311 | Clay Clifton | 2002-12-30 16:00 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2002-12-30 09:30 | 2002-12-30 12:30 | 40 | 7200 | 200 | 7000 | 2300 blk Hosp | Carlsbad | 92008 | SD | Cleanout | 0 | None | Roots | Roots caused blockage | 1) Televise the main to check for pipe abnormalities. 2) Accelerate regular cleaning schedule | Y | Y | Y | Buena Vista Creek | Buena Vista Lagoon | N/A | Y | Y | Y | Along north shore of Buena Vista Lagoon and at beach where Buena Vista Creek meets | 2 | Samples taken | issued NOV No. R9-2003-0015
| 120312 | Clay Clifton | 1/3/03 - 11;00 | Pam James-Adams | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2002-12-31 | 2002-12-31 06:00 |  |  | 0 |  | Aviara Golf Course | Carlsbad | 92008 | SD |  | 0 | None | Line Break | Irrigation main line break (6") on private water system belonging to Aviara Golf Course | Break repaired | Y | Y | Y | Agua Hedionda Lagoon | None | N/A | N | N | N | N/A | 0 | Meter reading does nto show abnormal usage for this time of year. Line break was post meter on customers private water system
| 023002 | Quarterly Report | 2003-01-21 | Shawn Atherton | 760-633-2871 | City of Encinitas | City of Encinitas | 2002-12-04 07:30 | 2002-12-04 08:15 | 10 | 450 | 400 | 50 | 1230 Windsor Road | Encinitas | 92007 | SD | Cleanout located at 1230 Windsor | 0 | N/A | ROOTS | Appears that plumber pushed roots from lateral into our main line. | Flushed main and removed roots. | N | N | N | none | none | Gutter located at intersection of Windsor and Munevar | N | N | N | N/A | 0 | We responded to the blockage within 15 minutes, found water pooling in the intersection of Windsor Road and Munevar. Sandbags were used to create a berm and the water was sucked up with the Vac-Con.
| 020301 | Victor Vasquez | 2003-01-16 09:00 | Gary Masters | (858) 720-2400 | City of Solana Beach | City of Solana Beach | 2003-01-15 20:10 | 2003-01-15 20:40 | 1000 | 30000 | 30000 | 0 | 1000 N. Rios | Encinitas | 92024 | SD | Spill Basin | 0 | NA | Pump Station Failure | Pressure switch on air compressor failed, bubbler could not monitor wetwell level, pumps would not start due to loss of compressor air. | Replaced air compressor. Submersible pump set in spill basin to pump sewage to manhole at station. | N | N | N | None | None | Spill Basin | Y | N | N | N/A |  | Sewage spilled into basin pumped out by 1/16/03 | NOV No. R9-2003-0087 issued for this overflow
| 023001 | yes | 2/20/03 0900 | Earl Colia | 760-789-1330 | Ramona Municipal Water District | Ramona Municipal Water District | 2003-02-19 11:00 | 2003-02-19 12:00 |  | 50 | 0 | 50 | 23443 Barona Mesa Road | Ramona | 92065 | SD | B M #2 Pump Station | 0 | none | PUMP STATION FAILURE | Impeller spun off | Repaired pump damage | N | Y | N | none | none | Street | Y | N | N | N/A | 0
| 023003 | bryan off | 2/23/03 0800 | Earl Colia | 760-789-1330 | Ramona Municipal Water District | Ramona Municipal Water District | 2003-02-21 | 2/21/03/ 09:00 | 8.3 | 500 | 0 | 500 | 23443 Barona Mesa Road | Ramona | 92065 | SD | B M #2 Pump Station | 1 | 2003-02-19 | PUMP STATION FAILURE | Float Failure | Replace Float | Y | Y | N | none | none | Creek | Y | N | N | N/A | 0 |  | RMWD 5-day report states overflow occurred on 2/23/03 NOT 2/21/03
| 03-0677 | OES - Keven & RWQCB - Bryan Ott | 2003-02-05 12:14 | Gary @ Morgan Run Resort | (858) 759-2155 | Whispering Palms Community Services District | Whispering Palms Community Services District | 2003-02-05 12:00 | 2003-02-05 12:50 | 15 | 750 | 250 | 500 | 5690 Cancha De Golf | Rancho Santa Fe | 92091 | SD | 302-121-17L | 0 |  | Grease | Excessive grease build-up in 10" sewer line coming from the Morgan Run Country Club | Increase maintenance from bi-annual cleaning to quarterly cleaning. Re-investigate grease trap maintenance at Morgan Run Country Club food prep area | N | N | N | None | None | Unrecovered sewage saturated into Golf Course prior to reaching San Dieguito River | Y | Y | ** N |  |  | Saturated area cleaned and washed of all solid material. * On 2/6/03 we received a call from the DEH that they had received a report of the spill approx. one hour earlier than the District. This info. Conflicts with the time reported by the Golf Course Manager. ** We have been notified that the DEH has posted the mouth of the San Dieguito River as a precautionary measure.
| 023001 | FAX 858-571-6972 | 2002-07-01 08:15 | Mike Dunbar | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2002-07-01 08:15 | 2002-07-01 08:33 | 3 | 50 | 50 | 0 | 31526 Valida | Laguna Beach | 92651 | OC | manhole | 0 | none | roots | overflow due to roots | Crew inspected with tv camera. Line had been cleaned on 6/18/02 and at that time used root cutter. Line is cleaned every 4 months. | N | Y | N | None | None | about 1 gallon flowed into catch basin | Y | N | N
| 023002 | FAX 858-571-6972 | 2002-08-13 11:45 | Mike Dunbar | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2002-08-13 11:15 | 2002-08-13 11:50 | 10 | 350 | 50 | 300 | LS11 at Dana Point Harbor | Dana Point | 92629 | OC | manhole | 0 | none | PUMP STATION FAILURE | pump station malfunctioned | manufacturer repaired pump station | N | N | Y | Dana Point Harbor | Pacific Ocean | NA | Y | N | Y | shipyard; boat launch; L, M, O docks | 4 | shipyard was reopened on 8/15 at 4:00 pm, other locations were reopened on 8/17 at 4:00 pm
| 023003 | FAX 858-571-6972 | 2002-09-06 19:00 | Mike Dunbar | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2002-09-06 15:25 | 2002-09-06 15:40 | 4 | 100 | 100 | 0 | 35032 Camino Capistrano | Dana Point | 92629 | OC | storm drain | 0 | none | roots | Roots from District main collection pipeline caused backup into customer's residence. Wastewater entered storm drain to catch basin. | Crews cleared backup and recovered wastewater. | N | Y | N | None | None | catch basin | Y | N | N
| 023001 | Fax | 2002-07-06 01:30 | Carl Hubber | (949) 497-3668 | City of Laguna Beach | City of Laguna Beach | 2002-07-05 23:00 | 2002-07-06 03:10 | 2 | 500 | 100 | 400 | 520 Cliff Drive | Laguna Beach | 92651 | OR | Parking Garage, Lower Level Bathroom | 0 | N/A | Debris | The City's 8-inch main line easement starting at the 100 blk. Of Myrtle Street was plugged with paper towels about 300ft. Downstream. This easement is 470ft. In length located in the rear of the condo units on the 400 blk. Cliff Drive. | City crews cleaned the main to remove the blockage with the rodder truck. Then they re-cleaned with the jetter and continued downstream for two more sections. This line is an 8 inch VCP. In the year 2000 it was lined from Myrtle to Cliff Drive. 100 gallons was recovered with the vacuum truck. The crew built a sand dam to stop any other water from reaching the ocean. City crews cleaned up the beach and posted the area with signs. The Orange County Health Care Agency closed Divers Cove and Picnic Beach at 03:00 on July 6th. At 10:50 they reopened Divers Cove. On July 8 at 15:30 they re-opened Picnic Beach and all signs were removed. | N | Y | Y | Storm Drain | Pacific Ocean | Pacific Ocean | Y | N | Y | Picnic Beach to Divers Cove | 3
| 023002 | Fax | 2002-07-07 09:45 | Laguna Beach Police Department | (949) 497-0701 | City of Laguna Beach | City of Laguna Beach | 2002-07-07 | 2002-07-07 09:45 | Unk | 500 | 1 | 499 | 1400 Blk. Hillcrest/Dartmoor | Laguna Beach | 92651 | OR | Manhole #14 | 0 | N/A | Roots | Roots from upstream house lateral plugged in manhole #14 on Hillcrest Drive. | Crew jetted the 8-inch main line. Cleaned the streets and vacuumed up all of the water used to wash down the spill area. | N | Y | N | Storm Drain | N/A | Sand at Crescent Bay Beach | Y | N | N | North End of the beach | N/A | Soaked into the sand at Crescent Bay Beach due to a sand dam at the outlet. Warning signs only were placed as a precaution at the storm drain outlet at the north end of the beach. It is not known when the overflow started. However, based on the amount of flow on the street and the sand, the overflow amount is estimated to be less than 500 gallons. It appears that the overflow was intermittent and at a very low flow rate. | "Y" reported under "Warning Signs Posted?" changed to "N" per phone conversation with John Pietig and Dave Shissler of City of Laguna Beach 06/12/03. The sand at the beach was posted but not the ocean water.
| 023003 | Fax | 2002-07-08 22:45 | Laguna Beach Police Department | (949) 497-0701 | City of Laguna Beach | City of Laguna Beach | 2002-07-08 22:40 | 2002-07-09 00:30 | 5 | 500 | 499 | 1 | 520 Cliff Drive | Laguna Beach | 92651 | OR | Lower Level Bathroom | 1 | 2002-07-06 | Debris | A large amount of paper towels discharged into the City's 8-inch main. This section has a very low flow rate. Unable to move this large amount into the downstream trunk sewer. | This line was recleaned with high pressure jetter. City crews are making daily inspections of this sewer line for the next week. They also made personal contact with all apartments and hotels. | N | N | N | N/A | N/A | Pumped back into the City's Sewer System | Y | N | N | N/A | N/A | Ongoing problem. Sent out flyer to all owners within this area and informed the Police Department of our ongoing efforts.
x | 023004 | Fax | 2002-07-25 | City of Laguna Beach | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2002-07-25 10:45 | 2002-07-25 12:10 | 0.8 | 70 | 69 | 1 | 180 N. Coast Hwy | Laguna Beach | 92651 | OR | Grease Trap | N/A | N/A | Grease/Line Break | During a routine walkthrough inspection of Diederich Coffee House, the County of Orange Health Inspector Janis McBride noticed a sewer spill occurring from their grease trap. Ms. McBride called the City and a crew was dispatched. A plumber was also called (Minuteman Plumbing Service) who found that the 4-inch line was broken between the grease trap and the City's main line. | During the cleanup process of the sewer spill, the plumber did not take adequate measures to contain the spill and therefore was cited under the City's ordinance for illegal discharge. City crews vacuumed up all water at the storm drain box before it entered into the storm drain line that connects to the flood control dam at Main Beach. Repairs are in the process of being made and are being coordinated with the City's Building Division | N | Y | N | N/A | N/A | Back into the Vacuum Truck | Y | N | N | N/A | N/A | Private Sewer Lateral - Courtesy Report |  | x
x | 023005 | Fax | 2002-08-02 14:00 | City of Laguna Beach | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2002-07-26 16:55 | 2002-07-26 17:00 | 0.005 | 1 | 0.75 | 0.25 | 355 Broadway | Laguna Beach | 92651 | OR | Cleanout | N/A | N/A | Debris | I responded to a report of a possible sewer spill at 303 Broadway. I arrived on scene at 5:30 p.m. and noticed sewage leaking from a lateral cleanout cap onto the driveway for this location. I approached one of the businesses to obtain a telephone number for the property management company (Richard Cox at (949) 640-9881). I called Mr. Cox who stated that he would call a plumber to alleviate the problem. | I then put some dirt over the water and swept it up into a bucket. I then closed the restrooms to this location. When City crews followed up the next day we were informed that the lateral actually belonged to Second Chance Thrift shop at 355 Broadway which is located next to 303 Broadway. The plumber was on scene and making repairs. City crews inspected the work and no other spill or damage occurred. The Orange County Health Care Agency was informed of the sewer spill on Friday July 26, 2002 at 6:20 p.m. | N | N | N | N/A | N/A | Sewage went into the driveway and onto the street. Swept up into bucket. | Y | N | N | N/A | N/A | Private Sewer Lateral - Courtesy Report |  | x
x | 023006 | Fax | 2002-07-29 14:44 | City of Laguna Beach | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2002-07-29 14:00 | 2002-07-29 14:44 | 0.4 | 100 | 99 | 1 | 190 High Drive | Laguna Beach | 92651 | OR | Cleanout | N/A | N/A | Debris | Anthony Condon from the Parks Division called the Sewer Division to report sewage overflowing from 190 High Drive. Upon arriving on scene we found that the lateral was running over from the building. | City crews set up the vacuum truck at the end of the street and jetted the City's main line which was open. We vacuumed up all water and the Parks Division snaked the lateral to the building. Public Works Dispatch called the sewer system owner (Tom Olives- Girl Scouts of America) and advised them of the problem. They stated that they would send out maintenance personnel to repair the problem. In the meantime, City crews shut off all water to the building and called the Orange County Health Care Agency to report the spill. At 3:30 p.m. the City received a call for assistance from the Girl Scouts maintenance personnel at the site and we informed them that a toilet in the restroom had been the problem and that a valve had stuck. | N | N | N | N/A | N/A | Vacuumed up into the Vector Truck from the street | Y | N | N | N/A | N/A | Private Sewer Lateral - Courtesy Report |  | x
| 023007 | Phone | 2002-08-19 12:55 | City of Laguna Beach | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2002-08-19 09:00 | 2002-08-19 11:30 | 1 | 150 | 0 | 150 | 1649 Sunset Ridge Dr | Laguna Beach | 92651 | OR | Manhole #27 | 1 | 2002-07-07 | Roots | Public Works Dispatch received a call from a resident (Mr. Jim Sullivan at (949) 497-3111) who stated that there was sewer overflowing on Sunset Ridge Drive. City crews responded and upon inspection of the City's 8-inch main line they noticed that it was plugged with tree roots at approximately 250ft. upstream of manhole #26. | City crews opened up the main line with a high pressure jetter and cleaned upstream from manhole #26 to manhole #27. | Y | Y | Y | Storm Drain | Open Canyon Area | Soaked into the ground | Y | N | N | N/A | N/A | This line has approximately 30 homes connected and was last cleaned during December 2001. It is scheduled to be cleaned again in November 2002. It is also scheduled to be lined by June 2003. The discharge point of the storm drain goes into open canyon area where the discharge soaked into the ground.
| 023008 | Phone | 2002-09-05 12:10 | City of Laguna Beach | (949) 497-0342 | City of Laguna Beach | City of Laguna Beach | 2002-09-02 09:00 | 2002-09-05 11:19 | 0.05 | 480 | 0 | 480 | 624 Mystic View | Laguna Beach | 92651 | OR | Manhole #97 | 0 | N/A | Roots | The City's Sewer Division received a voice mail from the resident (Mr. Bob McCord (949) 497-7450) at 11:00 a.m. this morning of a possible sewer spill in the easement at the back of the property. Sewer crews responded and upon arriving on scene confirmed that the manhole was in fact trickling over. | City crews opened up the main line with a high pressure jetter and cleaned upstream from manhole #10 to manhole #9 | N | N | Y | Dry Open Canyon Area | N/A | Soaked into the ground. | Y | N | N | N/A | N/A | Mr. Bob McCord noticed a sewer smell on Monday September 2, 2002 and upon inspection on September 5, 2002 he noticed the manhole overflowing.
x | 023009 | Fax | 2002-09-18 | City of Laguna Beach | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2002-09-16 15:30 | 2002-09-16 16:00 | 0.78 | 25 | 0 | 25 | 2906 Alta Laguna Blvd. | Laguna Beach | 92651 | OR | Private Lateral Cleanout | N/A | N/A | Roots | The City's Sewer Division received a call from Andrus Plumbing that the lateral at this location was blocked and had overflowed onto the driveway of the residence. We responded and found that the spill had stopped prior to our arrival and Andrus Plumbing had snaked the lateral. The cause was found to be roots from the trees on the property. | As a precaution, we jetted our 8 inch main line which was not blocked. We washed the driveway and the gutter going south to the storm drain box. We vacuumed up all standing water in the box and all of the water that was used to clean up the street. Andrus Plumbing are going to make all the necessary repairs to the lateral. | N | N | Y | Alta Laguna Blvd. in the gutter line | N/A | Alta Laguna Blvd. at Tree Top Lane in the gutter line | Y | N | N | N/A | N/A | Private Sewer Lateral - Courtesy Report |  | x
x | 023001 | Adam Laputz | 2002-08-06 | Bill Wiltse | 619-660-2007 | County of San Diego | County of San Diego | 2002-08-06 11:30 | 2002-08-06 12:00 | 5 | 800 | 200 | 600 | 9119 Birch ST | Spring Valley | 91978 | SD | 578-240-220A | 0 | n/a | Grease | Contractor dumped grease trap oil into system | SD City Industrial Waste investigating. Clean-out was capped at property. | N | N | N | None | None | On Private Property | Y | Y | N | n/a | 0 | Illegal lateral use. |  | x
| 023002 | Adam Laputz | 08-28-02 1000a | Bill Wiltse | 619-660-2007 | County of San Diego | County of San Diego | 2002-08-28 10:00 | 2002-08-28 10:40 | 30 | 1200 | 0 | 1200 | Whitestone Canyon | Spring Valley | 91978 | SD | 505-220-0224C | 0 | n/a | ROOTS | Roots combined with debris | Contractor to repair pipe segment | N | N | N | None | None | Sandy Area | Y | Y | N | n/a | 0 | Contactor to repair pipe
| 023003 | Adam Laputz | 9/3/2002 1000a | Bill Wiltse | 619-660-2007 | County of San Diego | County of San Diego | 2002-08-30 10:00 | 2002-08-30 11:45 | 20 | 2000 | 0 | 2000 | Whitestone Canyon | Spring Valley | 91978 | SD | 505-220-307F | 1 | 2002-08-28 | Line Break | Pipe Callasped | Contractor to repair pipe segment | N | N | N | None | None | Sandy Area | Y | Y | N | n/a | 0 | Arrieta Contractor to repair all line segments ASAP
| 012019 | FAX, (858) 571-6972 | 2002-08-19 14:30 | Dave Seymour | (949) 459-6540 | Santa Margarita Water District | Santa Margarita Water District | 2002-08-19 06:50 | 2002-08-19 07:32 | 20 | 840 | 600 | 640 | Capricio | Mission Viejo | 92691 | OC | Manhole G26585 | 0 | 0 | OTHER | A root ball apparently cut from the customer's lateral lodged in the 8-inch easement line and caused an overflow | Crews arrived on site and Vactored up sewage while second truck cleared blockage from the downstream manhole. | N | Y | Y | Oso Creek | San Juan Creek | 200 gallons to Vactor. 640 gallons to San Juan Creek | Y | Y | N | N/A | 0 | The "estimated overflow volume recovered," 600 gallons, included wash water.
| 023001 | Voice Mail | 07/04/02 1825 | Michael Heiser | 7604355870 | City of Oceanside | City of Oceanside | 2002-07-04 15:50 | 2002-07-04 16:11 | 30 | 630 | 0 | 630 | 4706 Cannon Road | Oceanside | 92056 | SD | Lift Station | 0 |  | PUMP STATION FAILURE | Bubbler line plugged and caused all 3 pumps to air lock. | Station is monitored by SCADA and manually visited daily. | N | Y | Y | Aqua Hedionda Creek | Hedionda Lagoon |  | Y | N | N |  |  | Area has no access from mainstreet, and limited access from "off road" areas.
| 023002 | Voice Mail | 07/15/02 0805 | Jeremy Kemp | (760)435-5842 | City of Oceanside | City of Oceanside | 2002-07-14 16:15 | 2002-07-14 18:00 | 10 | 1050 | 0 | 1050 | 800 Blk. Of Capistrano Drive | Oceanside | 92054 | SD | Manhole | 0 |  | Debris | Heavy Grit, Sticks and Rags. | Easements are checked & maintained on a weekly basis. | N | N | N |  |  | Soaked into sandy soil. | Y | Y | N |  |  | Spill duration was excessive because Vactor got stuck in the easement.
| 023003 | Voice Mail | 07/19/02 0805 | Michael Heiser | 7604355870 | City of Oceanside | City of Oceanside | 2002-07-18 21:05 | 2002-07-18 22:45 | 10 | 1050 | 0 | 1050 | 3605 North Way | Oceanside | 92056 | SD | Manhole | 0 |  | DEBRIS | Grease on debris caused overflow. | Line was rodded & jetted. Manhole will be raised to be more visible in the future. | N | Y | N |  |  | Soaked into ground at end of culdesac on south side of Route #78. | Y | Y | N |  |  | No stream/creeks were affected.No access for public as protected by barbed wire.
| 023004 | Brian Kelley | 08/14/02 1605 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 2002-08-14 11:30 | 2002-08-14 11:35 | 10 | 50 | 0 | 50 | 287 Capistrano Drive | Oceanside | 92054 | SD | Manhole | 1 | 2002-07-14 | DEBRIS | Rags and debris blocking city main. | Checking city easements weekly. Need access road along SLR River. | N | Y | Y | San Luis Rey River | Pacific Ocean |  | Y | N | N |  |  | Spill was aprox. 1 mile upstream of Ocean. Mouth of River was HUGE dilution factor.
| 023005 | Voice Mail | 08/17/02 0955 | Michael Heiser | 7604355870 | City of Oceanside | City of Oceanside | 2002-08-16 10:20 | 2002-08-16 10:25 | 15 | 75 | 30 | 45 | 1777 Ivy Road | Oceanside | 92054 | SD | Cleanout | 0 |  | UNKNOWN | Unknown cause of stoppage in City Line. | Line jetted on 20Jun02 with no problems. Line will be TV'd ASAP. | N | N | N |  |  | Soaked into resident's backyard. | Y | N | N |  |  | Crew responded from minutes away. Crew asked to spread dirt over spill in backyard.
| 023006 | Voice Mail | 09/09/02 0809 | Mark Patnone | 7604355840 | City of Oceanside | City of Oceanside | 2002-09-08 18:00 | 2002-09-08 18:15 | 15 | 225 | 100 | 125 | 3755 Vista Campana | Oceanside | 92054 | SD | Manhole | 1 | 2001-11-05 | ROOTS | Roots & grease caused the main to backup and heavy grit was found in channel, also. | Line will be scheduled to be TV'd and possibly "slip lining" the main. | Y | Y | N |  |  | Spill traveled into a valley with dence undergrowth and no access. | Y | N | N
| 023007 | Voice Mail | 09/13/02 1045 | Michael Heiser | 7604355870 | City of Oceanside | City of Oceanside | 2002-09-13 09:58 | 2002-09-13 10:41 | 3 | 129 | 129 | 0 | 1617 Mission Avenue | Oceanside | 92054 | SD | Manhole | 0 |  | DEBRIS | Grease & debris caused a partial blockage in city main. | 07/07/02 chlorine (100#) was dumped in line. Line has now been jetted and rodded. | N | Y | N |  |  | Total recovery was made by crew. | Y | N | N |  |  | Good mapping of the Storm Drain System made it easy for us to make the recovery.
x | 023008 | Voice Mail | 09/30/02 1912 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 2002-09-30 12:35 | 2002-09-30 12:50 | 1 | 15 | 0 | 15 | 1325 Harbor Drive North | Oceanside | 92054 | SD | Private Grease Trap | 0 |  | PRIVATE PROPERTY | Grease Trap backed up and overflowed. | Code Enforcement cited Restaurant for Stormwater Violations, etc. | Y | Y | Y | Oceanside Harbor | Pacific Ocean |  | Y | N | N |  |  | NOV sent to Corporate Hdqtrs. |  | x
| 012008 | Mark McCabe | 2002-08-21 09:00 | Bob Millan | (760) 726-6328 | Buena Sanitary District | Buena Sanitary District | 2002-08-05 12:30 | 2002-08-05 12:40 | 5 | 50 | 20 | 30 | Green Oaks at Sycamore Avenue | Vista | 92083 | SD | B02.31 | 0 | NA | Blockage/Vandalism | Vandalism; 2-3' Rock/debris piled into manhole channel. | Vacuum sewage to exposed rock; performed confined space entry to remove rocks/debris; used high pressure nozzle to break blockage; washed down and capture surface sewage; contaminated soils was removed and replaced; line was TV'D inspected to verify that there were no problems downstream the line; an access gate was installed, and locking mechanism were installed to both manholes; creek side was flushed to remove sewage and contaminated material (up to about 100' downstream); all materail was captured by the use of vaccum system. | N | N | Y | Agua Hedionda | None | N/A | Y | N/A | Y | 200' upstream of spill site to El Camino Real. | 5 | Signs were removed after downstream area tested, and contamination levels reached an acceptable level. Signs were removed at the direction of Mark McCabe.
| 023001 | FAX 858-571-6972 | 07/24/2002 08:50 | Patti S. Page | (760) 723-5640 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2002-07-23 20:50 | 2002-07-23 21:20 | 1 | 30 | 0 | 30 | 509 Teran | Fallbrook | 92028- | SD | Cleanout | 0 |  | ROOTS | Roots and grease in mainline caused this to come out of the 4" house cleanout. | Rodded lateral and flushed mainline. | N | Y | N | None | None | Dissipated in storm drain. Did not reach Fallbrook Creek. | Y | N | N |  | 0 | Washed down street and vacuumed up wash down water. |  |  | 1
| 023002 | FAX 858-571-6972 | 08/14/2002 14:35 | Patti S. Page | (760) 723-5640 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2002-08-14 07:10 | 2002-08-14 07:40 | 5 | 150 | 60 | 90 | 532 E. Fallbrook Street | Fallbrook | 92028- | SD | Manhole | 0 |  | ROOTS | Loose roots in manhole. | Flushed mainline and opened at about 132 feet. | N | Y | N | None. | None. | Ran along private driveway and into dry drainage ditch and dried up. | Y | N | Y | Ditch Area | 3 | Removed dirt and debris out of ditch and disinfected the area. |  |  | 1
| 023003 | FAX (858) 571-6972 | 08/26/2002 11:15 | Patti S. Page | (760) 723-5640 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2002-08-25 21:35 | 2002-08-25 22:00 | 2 | 50 | 5 | 45 | 1285 S. Mission Road | Fallbrook | 92028- | SD | Cleanout | 0 |  | UNKNOWN | Unknown. Nothing on hose or nozzle to indicate what the problem was. | Flushed mainline, opened stoppage at 416'. Flushed area, recovered wash down water, disinfected area, and cleaned out storm drain. | N | Y | N | None. | None. | Storm drain and vactored up. | Y | N | N |  | 0 | Removed grate from storm drain box and vacuumed out contents. Flushed 100 gallons of fresh water into storm drain box. Do not know where strom drain system goes for sure. |  |  | 1
x | 023004 | QUARTERLY REPORT |  | Joel V. Holt | (760) 723-6026 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2002-08-29 11:08 | 2002-08-29 11:30 | 2 | 44 | 44 | 0 | 325 Potter Street | Fallbrook | 92028- | SD | Cleanout | 0 |  | PRIVATE PROPERTY | There were a few roots but believe the cause was cloth like towels. Pulled back about 20-30 towels. Gave some to manager of property to show his people what was causing most of the problem. | Rodded the lateral and unplugged. Rodded the second time all the way to the mainline. | N | N | N | None. | None. | Ran down sidewalk for about 100' and then puddled up at blacktop driveway. | Y | N | N |  | 0 | COURTESY NOTIFICATION. Picked up all the soaked leaves and paper trash along the sidewalk. Vacuumed up all overflow with combination unit. Sanitized sidewalk and all around where water puddled up. All overflow and wash down was recovered. |  | x | 0
| 023005 | QUARTERLY REPORT |  | Joel V. Holt | (760) 723-6026 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2002-09-08 11:00 | 2002-09-08 11:45 | 10 | 450 | 300 | 150 | 706 N. Orange | Fallbrook | 92028- | SD | Cleanout | 0 |  | GREASE | Grease in mainline. | Flushed mainline. Opened line, had lots of grease. Cleaned up & disinfected area. | Y | N | N | None. | None. | Soaked into ground. | Y | N | N |  | 0 | None. |  |  | 0
| 023006 | QUARTERLY REPORT |  | Joel V. Holt | (760) 723-6026 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2002-09-26 13:00 | 2002-09-26 14:00 | 0.67 | 40 | 40 | 0 | 1800 Block Chapulin Lane | Fallbrook | 92028- | SD | Manhole | 0 | NA | ROOTS | Roots in mainline. | Flushed mainline, washed down area, disinfected area, and recovered wash down water. | N | N | N | None. | None. | Ran down side of roadway, was dammed up and recovered. | Y | N | N |  | 0 | None. |  |  | 0
x | Private | Fax | 7/25/02 10:45am | Jay Elston | (949) 366-1553 | City of San Clemente | City of San Clemente | 2002-07-24 17:08 | 2002-07-24 18:25 |  | 77 | 57 | 20 | 401 S. El Camino Real | San Clemente | 92672 | OR | Private Lateral | 0 |  | Grease | Grease Blockage | Private System |  | Y | N | N/A | N/A | Inside Drain Pipe / Vactor | Y | N | N |  | N/A |  | Data submitted in old template form. Copied data to appropriate fields. | x
x | Private | Fax | 8/9/02 12:00pm | Jay Elston | (949) 366-1553 | City of San Clemente | City of San Clemente | 2002-08-08 23:00 | 2002-08-09 02:45 |  | 10 | 8 | 2 | 217 Del Mar | San Clemente | 92672 | OR | Private Lateral | 0 |  | Unknown | Unknown | Private System |  | N | N | N/A | N/A | Vactor | Y | N | N |  | N/A |  | Data submitted in old template form. Copied data to appropriate fields. | x
x | Private | Fax | 9/5/02 9:00am | Jay Elston | (949) 366-1553 | City of San Clemente | City of San Clemente | 2002-09-04 17:40 | 2002-09-04 18:00 |  | 2000 | 0 | 2000 | 3000 Calle Nuevo | San Clemente | 92672 | OR | Private Lateral | 0 |  | Unknown | Unknown | Private System |  | Y | Y | MO1 Storm Drain | Pacific Ocean | Pacific Ocean | Y | Y | Y |  | 5 |  | Data submitted in old template form. Copied data to appropriate fields. | x
| 023001 | faxed | 2002-11-07 13:10 | Jim Guzman | (760) 726-1340, X1665 | Buena Sanitary District | Buena Sanitary District | 2002-11-06 08:00 | 2002-11-07 08:10 | 10 | 14400 | 4000 | 10400 | 1441 York Drive | Vista | 92084 | SD | B13.49 | 0 | None | Roots | Broken sewer main with heavy root intrusion | Two vactors were sent to the site; the first vactor was sent to the downstream manhole and jetted upstream (approx. 481') to hit the blockage; the second vactor was sent to send to the site, approx. 150' downstream the manhole; a sandbag dam area was constructed to capture sewage; downstream manhole lid was removed to allow sewage flow directly into the manhole; much of the spill saturated into the ground; Lime was pour after area was washed down. | N | N | N | None | None | Ground saturation; vacuum and/or flowed back into sewer system manhole. | Y | Y | Y | 100' North of the site (1441 York Dr.) to 200' south of spill (1505 York Dr.) |  | Nothing to sample due to dry creek and ground saturation. | Reporting Agecny was incorrectly entered as "City of Vista"; it was changed to Buena Sanitation District.
x | 023002 | City of Vista Storm Water Pollution Office | 2002-12-05 15:20 | David Brookbank | (760) 726-1340, X1663 | City of Vista | City of Vista | 2002-12-05 15:10 | 2002-12-05 16:56 | 0.5 | 50 | 50 | 0 | 128 Camino Corto | Vista | 92083 | SD | V08.044 (PRIVATE) | None | None | Roots | Roots in private lateral | City notified owner to call a plumber; also, crew call storm water technician (Mike Broyles) to respond. | N | N | N | None | None | None | N | N | N | N/A | 0 | Sewer spill was reported by resident at 128 Camino Corto; city responded with two vactor trucks; crew found a sewer lateral overflowing. | Reporting Agecny was incorrectly entered as "Private"; it was changed to City of Vista. | x
| 023004 | Adam Laputz | 10/03/2002 - 1515 | Bob Braun | 619-660-2007 | County of San Diego | County of San Diego | 2002-10-03 16:15 | 2002-10-03 14:15 | 66 | 12108 | 1108 | 11000 | Arnold Way | Alpine | na | SD | 503-100-6304A | 0 | 0 | CONSTRUCTION | Boring contractor punctured line | Line repaired - Pot Holeing procedures revised | N | N | N | None | None | Puetz Valley Road | Y | Y | Y | Puetz V>R - Arnold Way | 5
| 023005 | Adam Laputz | 2002-12-23 | Bill Wiltse | 619-660-2007 | County of San Diego | County of San Diego | 2002-12-21 18:15 | 2002-12-21 19:15 | 2 | 120 | 0 | 120 | 4208 Lovette Lane | Spring Valley | 91978 | SD | 501-100-0175E | 0 | 0 | Roots | Roots protruding from several laterals | Excellerated Maintenance and homeowners will be notified to clean laterals | N | Y | N | None | None | Open channel in field | Y | N | N | n/a | 0
| 023006 | Adam Laputz | 2002-12-10 | Bill Wiltse | 619-660-2007 | County of San Diego | County of San Diego | 2003-12-10 11:45 | 2003-12-10 12:00 | 66 | 1000 | 200 | 800 | 888 Lamar St | Spring Valley | 91978 | SD | 503-271-5901A | 0 | 0 | Grease | Excessive grease build up | Line will be cleaned every 60 days | N | N | N | None | None | Front Yard | Y | Y | N | n/a | 0
| 023007 | QUARTERLY REPORT |  | Joel V. Holt | (760) 723-6026 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2002-10-29 13:15 | 2002-10-29 13:45 | 2 | 60 | 20 | 40 | 2857 S. Mission Road | Fallbrook | 92028- | SD | Pump Seal Hose | 0 |  | PUMP STATION FAILURE | Seal hose on wastewater pump burst and sprayed on ground around lift station. Seal hose is plastic with push connection stainless steel elbows. | Shut down pumps and made repairs. Cleaned up area. Plan to change out hoses every six months to prevent weather damage. | N | N | N | None. | None. | Soaked into ground around lift station pumps. | Y | N | N |  | 0 | Removed standing water and soil on ground. Total of 20 gallons recovered. |  |  | 1
| 023008 | QUARTERLY REPORT |  | Joel V. Holt | (760) 723-6026 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2002-10-30 09:45 | 2002-10-30 10:35 | 4 | 200 | 150 | 50 | 2857 S. Mission Road | Fallbrook | 92028- | SD | Pump Seal Hose Elbow | 1 | 10-29-02 | PUMP STATION FAILURE | 90 degree elbow on mechanical seal hose connection broke. The elbow was a swivel push connection and it came apart in the swivel joint. | Replaced plastic hose and stainless steel swivel elbows with brass fittings and steel braided hose with screw on connectors. Used combination truck to vacuum up standing water. Removed contaminated soil and replaced with clean soil. Placed bad soil in | N | N | N | None. | None. | Soaked into ground around lift station pump. | Y | N | N |  | 0 |  |  |  | 1
x | 023009 | QUARTERLY REPORT |  | Joel V. Holt | (760) 728-6026 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2002-11-06 13:00 | 2002-11-06 14:00 | 1 | 60 | 40 | 20 | 319 W. Alvarado | Fallbrook | 92028- | SD | Cleanout | 0 |  | ROOTS | Roots in lateral about 30 feet. | Rodded lateral and removed roots and grease. | N | N | N | None. | None. | Along roadway, puddled up. Vacuumed standing water. | Y | N | N |  | 0 | COURTESY NOTIFICATION. Rodded lateral, removed grease and roots, washed down roadway and disinfected spill. |  | x | 0
| 023010 | QUARTERLY REPORT |  | Joel V. Holt | (760) 723-0626 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2002-11-14 10:04 | 2002-11-14 11:04 | 0.5 | 30 | 5 | 25 | 2104 Reineman Road | Fallbrook | 92028- | SD | Manhole | 1 | 03-18-02 | GREASE | Grease in mainline. | Rodded mainline from manhole J96 to J97. Hit stoppage about 30' out. Ran 6" cutter through mainline after clearing stoppage. Picked up about 5 gallon bucket of paper film. Will flush with vactor truck asap. | N | N | N | None. | None. | Seeped into ground by manhole. | Y | N | N |  | 0 |  |  |  | 0
| 023011 | QUARTERLY REPORT |  | Joel V. Holt | (760) 723-6026 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2002-11-16 14:30 | 2002-11-16 15:30 | 10 | 600 | 550 | 50 | 1127 E. Mission Road | Fallbrook | 92028- | SD | Manhole | 0 |  | GREASE | Grease build-up caused stoppage. | Cleaned mainline. Hit stoppage at about 80 feet. Spill was on asphalt. Vacuumed up and recovered 550 gallons. The rest soaked into the ground. Washed down & disinfected area. Recovered wash down water. | N | N | N | None. | None. | Asphalt parking lot. | Y | N | N |  | 0 |  |  |  | 0
| 023012 | QUARTERLY REPORT |  | Joel V. Holt | (760) 723-6026 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2002-11-20 11:20 | 2002-11-20 11:45 | 1 | 25 | 7 | 18 | 248 E. Fig Street | Fallbrook | 92028- | SD | Manhole | 1 | 03-26-02 | ROOTS | Roots & grease in mainline. | Flushed mainline with flail nozzle. Cleaned up spill and sanitized area. | N | N | N | None. | None. | Customer's driveway (dried up). | Y | N | N |  | 0 |  |  |  | 0
| 023013 | FAX 858-571-6972 | 12/03/2002 12:20 | Patti S. Page | (760) 723-5640 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2002-11-29 10:00 | 2002-11-29 10:50 | 1 | 50 | 25 | 25 | 1225 Juliette Place | Fallbrook | 92028- | SD | Cleanout | 0 |  | GREASE | Found to be grease in the mainline. | Flushed mainline with relief of stoppage at about 245 feet. | Y | Y | N | None. | None. | Storm drain was full of debris & plugged up with dirt. Flushed and vacuumed out storm drain. Did not reach surface waters. | Y | N | N |  | 0 | Flushed storm drain. Vacuumed and used disinfectant. |  |  | 1
| 023014 | FAX 858-571-6972 | 12/03/2002 12:20 | Patti S. Page | (760) 723-5640 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2002-12-02 13:56 | 2002-12-02 14:45 | 1 | 50 | 25 | 25 | 1635 S. Mission Road | Fallbrook | 92028- | SD | Cleanout | 0 |  | GREASE | Grease in mainline. | Flushed mainline, opened at about 131 feet. | Y | Y | N | None. | None. | Along the side of roadway & storm drain. Vactored up. Did not reach surface waters. | Y | N | N |  | 0 | Flushed and vacuumed standing water along roadway. Vacuumed out storm drain. Disinfected the area. |  |  | 1
x | 023015 | QUARTERLY REPORT |  | Joel V. Holt | (760) 723-6026 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2002-12-04 09:45 | 2002-12-04 10:30 | 2 | 90 | 0 | 90 | 1252 E. Fallbrook Street | Fallbrook | 92028- | SD | Cleanout | 0 |  | PRIVATE PROPERTY | Noticed lateral from customer's house was leaking. Lateral spans small ravine. ABS pipe has sections that have bad repairs. Supports have fallen. Needs repair. | Located cleanout and raised to grade. Rodded lateral. TV'd lateral. | N | Y | N | None. | None. | Soaked into ground around customer's cleanout & across ravine. | Y | N | N |  | 0 | COURTESY NOTIFICATION. Removed debris out of line. Cleaned and found only dirt. Customer needs to replace sewer lateral plastic pipe. Exposed and in bad repair. Supports needed. |  | x | 0
x | 023016 | QUARTERLY REPORT |  | Joel V. Holt | (760) 723-6026 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2002-12-04 12:15 | 2002-12-04 13:00 | 0.33 | 15 | 10 | 5 | 1272 S. Vine Street | Fallbrook | 92028- | SD | Cleanout | 0 |  | PRIVATE PROPERTY | Roots in cleanout. | Rodded lateral and removed roots out of cleanout. | N | N | N | None. | None. | Around cleanout. | Y | N | N |  | 0 | COURTESY NOTIFICATION. Roots in lateral. Cleaned up toilet paper and disinfected area. |  | x | 0
| 023017 | QUARTERLY REPORT |  | Joel V. Holt | (760) 723-6026 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2002-12-06 16:21 | 2002-12-06 16:51 | 2 | 60 | 0 | 60 | 205 Alvarado (x Hawthorne) | Fallbrook | 92028- | SD | Manole | 0 |  | GREASE | Grease in mainline. | Flushed mainline, hit stoppage at 176 feet. Flushed a total of 206 feet to make sure line was clear. Washed down street and vactored up wash down water and disinfected area. | N | N | N | None. | None. | Was spread on roadway by traffic and dried up. | Y | N | N |  | 0 |  |  |  | 0
| 23001 | Ouarterly Report | N\A | John von Borstel | (760) 749-5212 | Valley Center Municipal Water District | Valley Center Municipal Water District | 2002-11-04 12:00 | 2002-11-04 14:30 | 0.5 | 100 | 0 | 100 | 29244 Meadow Glen Way West | Escondido | 92082 | SD | 1 1/4" PVC preessure system lateral | 0 | N/A | Construction | Contractor drove heavy equipment over valve can breaking pressure lateral stub on undeveloped lot | Contractors working on similar lots in area advised of location of valve cans and ofthe necessity of avoiding them | N | N |  | N/A | N/A | overflow was absorbed in ground at leak location | N | N | N | N/A | 0 | Spill was from a Rimrock STEP system 1 1/4" PVC house lateral stub on an undeveloped lot. Lateral terminated with valve located in valve can at edge of lot. Contractor drove over valve can breaking off the valve. Lateral connected to sewer line that is
| 23002 | Ouarterly Report | N\A | John von Borstel | (760) 749-5212 | Valley Center Municipal Water District | Valley Center Municipal Water District | 2002-11-29 10:20 | 2002-11-29 10:40 | 0.2 | 20 | 0 | 20 | 28109 Par View | Escondido | 92082 | SD | Manhole located behind residence | 0 | N/A | Roots | Roots in 8 "line and manhole downstream caused partial blockage and backup in manhole | Roots removed from downstream manhole, line jet rodded for root removal. Lines TV'd, additional lines in area cleaned, will be inspected semiannually | N | N | N | N/A | N/A | overflow was absorbed in ground at leak location | n | N | N | N/A | 0 | Homeowner reported wastewater seeping out of manhole. Upon arrival no overflow was noted however concrete around manhole was damp. Manehole located at edge of golf course, no sign of sewage in grass.
| 23003 | Ouarterly Report | N\A | John von Borstel | (760) 749-5212 | Valley Center Municipal Water District | Valley Center Municipal Water District | 2002-12-12 08:30 | 12/12/02 10:30 | 0.1 | 12 | 0 | 12 | Meadow Glen Way W & Crystal Ridge Dr | Escondido | 92082 | SD | 4" PVC pipe | 1 | 37564 | Line Break | Small crack in PVC tee at junction of 2" and 4" pressure sewer lines. Possibly caused by ground movement due to heavy construction equipment activity in area. | Turned off pumps feeding sewer line, excavated, PVC tee replaced, backfilled, compacted and asphalt patched. | N | N | N | N/A | N/A | overflow was absorbed in ground under road ar leak location or evaporated | N | N | N | N/A | 0 | Homeowner reported wet spots at small cracks in asphalt, tiny trickle at asphalt/curb concrete interface, along with sewage smell. Appeared to be long term slow leak from 1 inch crack in PVC tee in pressure sewer line. Line is under periodic pressure whe
x | 023004 | FAX 858-571-6972 | 2002-10-04 16:30 | Mike Dunbar | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2002-10-03 11:10 | 2002-10-03 11:50 | 4 | 50 | 25 | 25 | 33811 Robles Dr | Dana Point | 92629 | OC | cleanout structure on sewer lateral | 0 | none | roots | Blockage in sewer lateral. | District crews cleaned sewer lateral from cleanout to District main line. | N | Y | Y | Dana Point Harbor | Pacific Ocean |  | Y | N | N |  |  | Private System Overflow |  | x
| 023005 | FAX 858-571-6972 | 2002-10-21 15:45 | Mike Dunbar | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2002-10-21 11:00 | 2002-10-21 11:15 | 4 | 50 | 50 | 0 | LS5 at Breakers Isle | Dana Point | 92629 | OC | manhole | 0 | none | PUMP STATION FAILURE | Power outage | relocate generators | N | N | N | None | None | overflowed into street and contained at storm drain | Y | N | N
| 023006 | FAX 858-571-6972 | 2002-11-12 15:30 | Mike Dunbar | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2002-11-12 13:30 | 2002-11-12 13:45 | 2 | 30 | 20 | 10 | Via Valez & Calle Almanza | Capistrano Beach | 92624 | OC | manhole | 0 | none | roots | loose roots from plumber | Ran root cutter thru this line on 10/29/02. District crews cleaned line and put on hot spot list. | N | Y | N | None | None | catch basin | Y | N | N |  |  | 10 gallons went into stormdrain. Contained in catch basin at Pacific Coast Highway.
| 023009 | Voice Mail | 10/06/02 1132 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 2002-10-06 07:20 | 2002-10-06 07:50 |  | 400 | 250 | 150 | 900 Blk of North Cleveland | Oceanside | 92054 | SD | Sewer Air Valve | 0 |  | OTHER | Sewer Air Valve in easement along railroad tracks was stuck open. Flow sprayed out of 1 inch bleeder valve. | All air valves are checked weekly. Valve will be repaired or repdlaced. | N | N | N |  |  | Soaked into sandy soil of railroad easement. | Y | N | N |  |  | Overflowed only when pumps were running.
| 023010 | Quarterly Report |  | Mike Heiser | 7604355870 | City of Oceanside | City of Oceanside | 2002-11-15 11:00 | 2002-11-15 11:20 | 3 | 60 | 60 | 0 | 4070 Mira Verde | Oceanside | 92056 | SD | Manhole | 0 |  | ROOTS | Roots caused stoppage in main line. | Line was rodded, and will be televised. | N | N | N |  |  | Full recovery. | Y | N | N |  |  | Street & curb were washed and recovered.
| 023011 | Quarterly Report |  | Armond Badillo | 7604355870 | City of Oceanside | City of Oceanside | 2002-11-23 10:30 | 2002-11-23 10:45 | 2.5 | 25 | 25 | 0 | 3725 Ropsemary Drive | Oceanside | 92054 | SD | Manhole | 0 |  | ROOTS | Roots caused stoppage in main line. | Line was rodded, and will be televised. | N | N | N |  |  | Full recovery. | Y | N | N |  |  | Street & curb were washed and recovered.
| 023012 | Voice Mail | 12/17/02 2025 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 2002-12-17 16:04 | 2002-12-17 16:18 | 100 | 1400 | 300 | 1100 | 4706 Cannon Drive | Oceanside | 92056 | SD | Lift station "wet-pit". | 1 | 2002-07-04 | PUMP STATION FAILURE | Moisture inside electrical panel tripped SCADA System. Override floats connected to SCADA failed, resulting in station overflow. | Override system is being rewired to individual power source. | Y | Y | Y | Aqua Hedionda Creek. | Aqua Hedionda Lagoon. |  | Y | Y | Y | Aqua Hedionda Lagoon, YMCA, Snug Harbor, 200 ft. North & South of Tamarack Jeyys. | 3 | No access to chase spill down Creek. Heavy rains carried spill off.
| 023013 | Voice Mail | 12/22/02 0925 | Mike Heiser | 7604355870 | City of Oceanside | City of Oceanside | 2002-12-21 21:00 | 2002-12-21 22:00 | 2 | 120 | 80 | 40 | 2004 Greenbrier Drive | Oceanside | 92056 | SD | Manhole | 0 |  | ROOTS | Roots and Grease caused stoppage in the City Main Line. | Line was jetted and will be televised to view extent of root infiltration. | Y | Y | Y | Loma Alta Creek | Loma Alta Lagoon |  | Y | N | N |  |  | Temp. dam was constructed to contain spill in drainage channel. Channel "daylights" to open area and then to another channel, then to Creek.
| 023010 | Phone | 2002-10-07 11:40 | City of Laguna Beach | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2002-10-07 | 2002-10-07 09:30 | 5 | 50 | 0 | 50 | Capistrano/Oro | Laguna Beach | 92651 | OR | 8" Gravity Pipeline | 0 | N/A | Line Break | This 8inch VCP sewer line is located in open canyon area across a dry creek. A bell joint at the top of the pipe was broken due to a small sag in the pipe. This break only leaks during high flow. The creek had washed the soil from under the pipe causing it to sag. Over time this sag caused the bell joint to crack | City crews made a temporary repair to stop the pipe from leaking and cleaned the line to remove any other debris. The City contractor, Kisling Construction during repairs, removed and replaced 20ft of pipe. | N | N | Y | Open Canyon Area | N/A | Soaked into the ground. | Y | N | N | N/A | N/A | The damaged portion of the sewer line has been replaced and will be further protected by encasing it in concrete by the end of October 2002. As part of our Sewer Lining Project, this pipe will be lined by June 2003.
x | 023011 | Fax | 2002-10-28 | City of Laguna Beach | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2002-10-22 | 2002-10-24 09:45 | Unk | 300 | 0 | 300 | 697 Mystic Way | Laguna Beach | 92651 | OR | Private Lateral | 0 | N/A | Line Break | We received a call from Public Works Dispatch that there was a sewer lateral running over at 554 Mystic Way. We arrived on scene and found that the lateral had separated releasing sewage onto the street below at 554 Vista Lane. We later found out from the reporting party that the sewer lateral had been running for approximately two days prior to the Sewer Division being called. | Sewer crews made a temporary repair to the lateral by reconnecting the lateral pipe. The homeowner was not at home. We left a notice informing them not to use any water and to call a plumber to make the necessary repairs. | N | Y | N | Storm Drain | N/A | The flow was diverted to the sewer system | Y | N | N | N/A | N/A | Private Sewer Lateral - Courtesy Report |  | x
| 023012 | Fax | 2002-10-27 16:30 | City of Laguna Beach | (949) 497-0754 | City of Laguna Beach | City of Laguna Beach | 2002-10-27 09:35 | 2002-10-27 10:40 | 0.76 | 50 | 0 | 50 | 142 Sunset Terrace | Laguna Beach | 92651 | OR | Private Cleanout | 0 | N/A | Roots | Sewer Crews received a call from LBPD of a possible sewer spill on private property at 138 Sunset Terrace. Upon arriving, we found that the overflow point was at 142 Sunset Terrace at the cleanout to the rear of the property. The resident (Mark Custer) directed us to his neighbors backyard at 138 Sunset Terrace where the owner had been making repairs to his lateral for approximately one week and had dug a large trench over his lateral. They checked the City's mainline and found a blockage 200ft. downstream from the manhole | City crews jetted the main line from manhole #54 up to manhole #120. Crews produced roots from the main line. Crews determined that these roots had likely been pushed from the lateral at 138 Sunset Terrace into the City's main line during the repairs at this location. | N | N | N | Private Property | N/A | Private Property | Y | N | N | N/A | N/A | As a precaution, City crews checked all storm drains and catch basins in the area and determined that the overflow remained on site at 142 Sunset Terrace. They then swept up and raked the overflow area. A further check of the City's main line on October 28, 2002 revealed that the line was operating normally.
x | 023013 | Fax | 2002-10-30 | City of Laguna Beach | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2002-10-29 | 2002-10-30 20:00 | 0.01 | 50 | 1 | 49 | 2442 S. Coast Hwy | Laguna Beach | 92651 | OR | Private Lateral | 0 | N/A | Roots | Private lateral was plugged with tree roots that caused the sewage to overflow. The overflow cap was off next to the building about 20ft from the curb. Over 95 percent of the spill was contained on the property and soaked into the ground due to heavy brush and trees. The remaining 5 percent was cleaned up by sewer crews. | The City received the call at 4:15 p.m. on October 30, 2002. We arrived on scene at $;20 and found the plugged lateral. We made contact with all of the apartments and advised them not to use any water. We called the property manager, Earnest Holiday (626) 644-7316 and First Team Realty at (949) 494-8110. At 8:00 p.m. the plumber was able to open the blockage. City crews returned on the morning of October 31 to do a follow-up and clean any residue that may have been left on the property. | N | N | N | Private Property | N/A | Soaked into the ground next to the apartments. | Y | N | N | N/A | N/A | Private Sewer Lateral - Courtesy Report |  | x
x | 020314 | Fax | 2002-11-14 09:46 | City of Laguna Beach | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2002-11-11 11:20 | 2002-11-11 12:20 | 0.83 | 50 | 0 | 20-50 | 2880 S. Coast Hwy | Laguna Beach | 92651 | OR | Private Lateral | 1 | 2001-12-12 | Roots | City crews received a call from Laguna Beach Police Department of a possible sewer spill at 2880 S. Coast Hwy. LBFD and LBPD were on scene when our crews arrived and they found sewer to be overflowing from a private lateral onto the driveway at this location. Crews checked the building and found a toilet to be overflowing. | Crews then checked the main line from downstream manhole to the upstream manhole and found it to be open and running. Crews advised the homeowner to stop using all water and to call a plumber. The plumber arrived on scene at 2:15 p.m. and snaked the lateral. The Health Department was notified of the spill and because it had reached a storm drain and there was high tide, they advised crews to close the beach 100ft. north and south of Dumond at Victoria Beach as a precaution. Any debris that was left on the driveway was swept up by the plumber. | Y | Y | Y | Storm Drain | Pacific Ocean | Pacific Ocean | Y | N | Y | Victoria Beach 100ft. North and Sound of Dumond | 3 | Private Sewer Lateral - Courtesy Report |  | x
| 023015 | Fax | 2002-11-20 09:00 | City of Laguna Beach | (949) 497-0754 | City of Laguna Beach | City of Laguna Beach | 2002-11-15 11:40 | 2002-11-15 12:00 | 2.5 | 50 | 0 | 50 | 2191 Ocean Way | Laguna Beach | 92651 | OR | Private Lateral | 0 | N/A | Roots/Debris/Baby Wipes | At 11:40 a.m. Sewer Crews received a call from Mr. Jack Reynolds who resides at #7 Rockledge. He stated that there was sewage overflowing at 2191 Ocean Way. Sewer crews arrived on scene at 11:50 a.m. and found sewage to be overflowing from the lateral going down the stairs and trickling onto the sand at Moss Street Beach. Crews immediately made a small dam at the bottom of the stairs and checked the City's main line which was found to be blocked with roots and a large amount of rags. | Sewer crews jetted the main line from the downstream manhole #62 to the upstream manhole #61 and this cleared the line. Crews then shoveled up the small amount of sewage that had collected in the sand which was approximately 10 gallons into a bucket. | N | N | N | N/A | N/A | Approximately 10 gallons soaked onto the beach on the sand. See remarks column for more information. | Y | N | N | N/A | N/A | The swage leaked form the private lateral which is located to the side of the house and down the stone stairways leading to the beach. Approximately 10 gallons reached the bottom of the stairs. The remainder of the spill evaporated and soaked into the ground. A large amount of baby wipes and roots were removed from the blockage. The Health Dept. was notified and they advised that no posting was necessary. | Total volume and volume released to the environment were reported as 40-50; these were changed to 50 in order to facilitate use of this databse.
x | 023016 | Fax | 2002-12-09 11:00 | City of Laguna Beach | (949) 497-0754 | City of Laguna Beach | City of Laguna Beach | 2002-12-05 07:30 | 2002-12-05 08:00 | 6.66 | 200 | 0 | 200 | 350 Y Place | Laguna Beach | 92651 | OR | Private Lateral | 0 | N/A | Roots/Debris | Public Works Dispatch received a call from a resident who stated that at 7:30 a.m. she had noticed that the private lateral at 350 Y Place had been running over and had gone into the street. Sewer crews were dispatched and arrived on scene at 11:37 a.m. They noticed that sewage was not flowing but that there was evidence of a spill that had occurred sometime during the morning and had gone into the street. Crews believe that this overflow occurred intermittently during peak flows that morning. | City crews checked the upstream storm drain which was found to contain debris. The downstream manhole on Second Street was also checked and was found to be dry. As a precaution, the City's main line was checked and found to be open and operating normally. They advised the property owner to call a plumber as soon as possible. The Health Dept. was notified of the spill at 11:45 a.m. All debris was contained and vacuumed up by City crews. At 3:30 p.m. City crews checked the property again and found that a plumber was on scene and snaking the lateral. | N | Y | N | Storm Drain | N/A | Storm Drain | Y | N | N | N/A | N/A | Private Sewer Lateral - Courtesy Report |  | x
| 023017 | Fax | 2002-12-14 | City of Laguna Beach | (949) 497-0754 | City of Laguna Beach | City of Laguna Beach | 2002-12-12 10:05 | 2002-12-14 10:17 | 0.8 | 50 | 0 | 50 | 1 Rockledge | Laguna Beach | 92651 | OR | Lift Station #3 | 0 | N/A | Pump Station Failure | The level controller air tube was believed to be temporarily blocked with debris, causing the wet well to overflow into the floor of the lift station. By the time the crew arrived, the blockage was cleared; however, some sewage spilled out of the station. | Drain lines from the lift station will be plugged and a sump pump installed to pump any liquid on the floor of the station into the wet well. All alarm points were checked and the wet well was cleaned as a precautionary measure. | N | N | Y | Pacific Ocean | Same | Pacific Ocean | Y | N | N | N/A | N/A | No signs were posted per direction of the Orange County Health Agency since there is no public access to a beach near this rock cliff.
| 023018 | Fax | 2002-12-23 16:00 | City of Laguna Beach | (949) 497-0754 | City of Laguna Beach | City of Laguna Beach | 2002-12-21 16:30 | 2002-12-21 17:30 | 0.33 | 20 | 0 | 20 | 3029 Cresta Way | Laguna Beach | 92651 | OR | Private Cleanout | 0 | N/A | Manhole | Sewer crews responded to a call from Laguna Beach Police Dispatch that a plumber was on scene at 3029 Cresta Way. The plumber had been called by the resident when she had noticed sewage leaking out of her private cleanout. Upon inspection of the City's main line, he noticed that the manhole was half full. | We jetted the City's main line to remove the stoppage. We found toilet paper and roots. We then raked up and swept the private walkway. A follow-up was completed the next day and the line was found to be clear. | Y | N | N | Private Property | N/A | Soaked into ground on private property | Y | N | N | N/A | N/A
| 023001 | Voice Mail | 2002-10-04 13:50 | Jay Elston | (949) 366-1553 | City of San Clemente | City of San Clemente | 2002-10-04 12:10 | 2002-10-04 13:10 | 4 | 240 | 0 | 240 | 700 Ave Pico | San Clemente | 92672 | OC | 8" Gravity Sewer | 0 | 0 | DEBRIS | Broken Sewer Tile cause blockage | Incorporated into the quarterly cleaning schedule and video inspection of the line | N | Y | Y | MO2 Storm drainage Channel | None | Pacific Ocean | Y | N | Y | North Beach in San Clemente | 3
| 023002 | Fax | 2002-10-16 14:00 | A. Howard | (949) 366-1553 | City of San Clemente | City of San Clemente | 2002-10-15 21:30 | 2002-10-15 22:00 | 40 | 2500 | 2500 | 0 | Ave. Junipero | San Clemente | 92672 | OC | 8" Gravity Sewer | 0 | 0 | ROOTS | Crews found cut roots and and abandoned plumbers root rodder in the line | Added to the quarterly root rooutine | N | Y | N | Junipero canyon storm drain | None | Sewer System | Y | N | N | N/A | 0 | Canyon drains enters a low flow diversion that enters the sewer
| 023003 | Voice Mail | 2002-11-18 10:00 | A. Howard | (949) 366-1553 | City of San Clemente | City of San Clemente | 2002-11-18 08:00 | 2002-11-18 08:45 | 3 | 420 | 200 | 240 | 100 Block Ave. Calafia | San Clemente | 92672 | OC | 8" Gravity Sewer | 0 | 0 | ROOTS | Small amount of roots caused sewer to exit from an abandoned lateral | Added to the quarterly root rooutine | N | N | Y |  | None | Sand at the Calafia Beach | Y | N | Y | Calafia Beach San Clemente | 2
x |  | Voice Mail | 2002-12-22 | A. Howard | (949) 366-1553 | City of San Clemente | City of San Clemente | 2002-12-22 | 2002-12-22 | 4 | 150 | 75 | 75 | 2812 Cam. Capistrano | San Clemente | 92670 | OC | Private System | 0 | 0 | UNKNOWN | Unknown, Private Lateral | Notified HOA to set up routine maintenance | N | Y | Y | MO1 Storm Drain | None | Pacific Ocean | Y | N | Y | Poche Beach San Clemente | 8 |  |  | x
| 023002 | David Hanson | 2002-11-04 17:00 | Kevin Wright | (619) 441-1658 | City of El Cajon | City of El Cajon | 2002-11-01 17:18 | 2002-11-01 18:30 | 1 | 75 | 0 | 75 | 610 Second St. | El Cajon | 92021 | SD | MH# 25-155 | 0 | N/A | GREASE | Accumulation of grease in line | Line (MH# 25-156 to MH #25-157 will be added to quarterly trouble spot list | N | N | N | None | None | Roadway Evaporation | Y | N | N | N/A | 0
| 012001 | Fax 858-571-6972 | 2001-07-27 07:00 | Kevin Wright | (619) 441-1658 | City of El Cajon | City of El Cajon | 2001-07-26 12:30 | 2001-07-26 12:40 | 3 | 30 | 0 | 30 | 793 Greenfield Dr. | El Cajon | 92020 | SD | MH 08-036 | 0 | N/A | MANHOLE FAILURE | Broken Drop in Manhole | Manhole submitted to Eng. for repair | N | Y | N | None | None | Dry Dirt Drainage Ditch | N | N | N | N/A
| 023001 | N/A | 2002-09-10 20:00 | I.B. Fire Dept | (619)429 8225 | City of Imperial Beach | City of Imperial Beach | 2002-09-10 20:00 | 2002-09-10 20:30 | 1 | 30 | 20 | 10 | 859 Florida St. | Imperial Beach | 91932 | SD | Lateral Cleanout | 0 | N/A | UNKNOWN | Main line blockage between m/h#285 and 299. Effluent came out lateral to street. F/D built a dam around S/D for recovery. Apx 10 gals soaked into soil and was unrecoverable. | Jetted line clear and used Vactor to collect spill. | N | N | N | None | None | Vactor to Sewer | N | N | N | N/A | 0 | The cleanout is on private property and the main runs through a "non-alley" easment. We cannot control what property owners do , but we recommended they install a backflow preventer.
X | 023002 | N/A | 2002-10-29 10:00 | Steve Kerr | (619)628 1371 | City of Imperial Beach | City of Imperial Beach | 2002-10-29 09:55 | 2002-10-29 10:10 | 1 | 5 | 5 | 0 | 825 Imerial Beach Blvd | Imperial Beach | 91932 | SD | Lateral Cleanout | 0 | N/A | ROOTS | The lateral was spilling intermitantly. Reported as 1GPM this report because this form does not allow for intermitant flows. Lateral had roots. | Hand rods were used to clear the root blockage and the vactor truck was used to collect and clean. | N | Y | N | None | None | Vactor to Sewer | N | N | N | N/A | 0 | None |  | X
X | 023003 | N/A | 2002-11-21 13:00 | Manuel Casas | (619)628 1372 | City of Imperial Beach | City of Imperial Beach | 2002-11-21 13:00 | 2002-11-21 13:15 | 1 | 2 | 2 | 0 | 825 Imerial Beach Blvd | Imperial Beach | 91932 | SD | Lateral Cleanout | 1 | 2002-10-29 | UNKNOWN | The lateral was spilling intermitantly. Reported as 1GPM. | Hand rods were used to clear the blockage and the vactor truck was used to collect and clean. Blockage unknown. The TV cew did a video of the lateral and found nothing out of the ordinary. Since roots were present, RootX was applied 24Dec02. | N | Y | N | None | None | Vactor to Sewer | N | N | N | N/A | 0 | None |  | X
X | 023004 | N/A | 12/02/02 0730 | A. Franco | (619)628 1372 | City of Imperial Beach | City of Imperial Beach | 2002-12-02 07:30 | 2002-12-02 07:50 | 5 | 5 | 5 | 0 | 1590 Seacoast Drive | Imperial Beach | 91932 | SD | Lateral Cleanout | 0 | N/A | UNKNOWN | Private lateral spill from private residance. | A plumber was called to correct the problem. The Vator truck came to vacuum up the spill. | N | N | N | None | None | Vactor to Sewer | N | N | N | N/A | 0 | The clean out for this property is close to the estuary, so the vactor was dispatched as soon as the spill was identified to protect adjeacent waters. |  | X
X | 023005 | N/A | 2002-12-18 10:00 | Manuel Casas | (619)628-1372 | City of Imperial Beach | City of Imperial Beach | 2002-12-18 10:00 | 2002-12-18 10:05 | 0.5 | 2.5 | 2.5 | 0 | 773 8th Street | Imperial Beach | 91932 | SD | Lateral Cleanout | 0 | N/A | UNKNOWN | Private lateral spill from private residance. | A plumber was called to correct the problem. H/O discontinued use of water. | Y | N | N | None | None | Plumber Cleaned | N | N | N | N/A | 0 | Code Enforcement notified for future referance. |  | X
X | 023006 | N/A | 12/20/02 0800 | Manuel Casas | (619)628-1372 | City of Imperial Beach | City of Imperial Beach | 2002-12-20 08:00 | 2002-12-20 08:00 | 0 | 0 | 0 | 0 | 1690 Seacoast | Imperial Beach | 91932 | SD | Lateral Cleanout | 0 | N/A | UNKNOWN | Private lateral spill from private residance. | Residents were notified not to use water. John Kitnella prperty management notified. John stated he would get the plumber out immediately. | Y | N | N | None | None | Plumber Cleaned | N | N | N | N/A | 0 | There was no water visable. Manuel Casas saw rtesidual toilet paper around the cleanout and called it in. |  | X
| 023007 | N/A | !2/30/02 12:00 | Sheriff Dept | (858)565-5200 | City of Imperial Beach | City of Imperial Beach | 2002-12-30 12:00 | 2002-12-30 12:20 | 0.5 | 10 | 10 | 0 | M/H#197 | Imperial Beach | 91932 | SD | M/H#197 | 0 | N/A | BLOCKAGE | There is a belly in the line between M/H#208 and #219 that had a partial blockage. This is a small area of single family dwellings. | Aj used the Vactor truck to clear the partial blockage between M/H#208 and #219. Once the blockage was cleared, Aj visited the spill site to clean the catch basin and clean the underground pipe. | Y | Y | N | None | None | Vactor to Sewer | N | N | N | N/A | 0 | The line with the partial blockage is apx 19 feet deep. Any blockage here should create enough hydraulic pressure to self relive.
| 023008 | David Hanson Voicemail | 2003-01-08 18:15 | Cal-Am | (619) 575-1106 | City of Imperial Beach | City of Imperial Beach | 2003-01-08 18:15 | 2003-01-08 19:45 | 1 | 90 | 60 | 30 | M/H#197 | Imperial Beach | 91932 | SD | M/H#197 | 1 | 2002-12-30 | BLOCKAGE | There was a small spill at this location a week prior. As part of the follow up, Aj, the sewer supervisor sent the vactor crew out to clean the section of line that had the blockage. As a result of only cleaning the one section, a partial blockage was created further down the line causing this spill. | The duty man had alleviated the blockage and done the cleanup. . The catch basin was cleaned and the storm drain line cleaned to the distance of ninety feet. The following day, the line was fully cleaned from the start of the line to the pump station | N | Y | Y | South Bay Wildlife Refuge | San Diego Bay | 60gal Vactor/30gal San Diego Bay | Y | N | N | N/A | 0 | This spill was a direct result of re-cleaning a line that had a partial blockage. The Vactor crew was scheduled to clean this entire section of town with in the next two weeks, so the incorrect decision was made to only shoot the one line until the crew came into the area. Lesson learned for the supervisor.
| 023009 | David Hanson Voicemail | 01/13/03 0715 | Bayside Maintenance | (619) 628-2500 | City of Imperial Beach | City of Imperial Beach | 2003-01-10 22:30 | 2003-01-13 08:15 | 2 | 1800 | 1800 | 800 | 490 Emory | Imperial Beach | 91932 | SD | M/H#211 | 0 | N/A | GREASE | The overflow was in a school parking lot. The last person at the school was at 2230 on 10Jan03. The reporting agency has no way to narrow down the time any closer, so calculations are based on the spill starting at that time. There was a blockage in the city main line between M/H#227 and #211 causing M/H#211 to overflow into the school district drainage system that is then connected to the city storm drain system just prior to the outfall. | The Vactor was immediately dispatched to alleviate the blockage and the storm drain recovery vehicle was dispatched to begin the recovery process. The Vactor cleared the blockage and cleaned additional downstream lines to ensure there was no additional blockages created. There were two spill sites cleaned by city crews as well as the school personnel cleaning the kitchen that also experienced a sewerage back up. The outfall where the spill discharged is within the tidal zone and is subject to tidal flows causing a flushing action with each tide cycle. The Vactor was than sent to the outfall where it recovered three thousand gallons from the outfall, which included the tidal waters and sewer overflow waste. The school drain inlets were then flushed with apx five hundred gallons of clean water while the Vactor truck vacuumed from the outfall another thousand gallons of tidal flows and sewerage mix. As an additional follow up, the sewer supervisor sent the Vactor crew out to clean the section of line that had the blockage from the blocked manhole to the pump station. | N | Y | Y | Otay River | San Diego Bay | Vactor truck recovered apx 4000 gallons of fluid from the outfall and placed it in the sewer | Y | N | N | N/A | 0 | This spill was a line that had a partial blockage. The start time in non verifiable, so the worst-case scenario is calculated and reported.
X | 023010 | N/A | 2003-01-08 10:00 | Manuel Casas | (619)628-1372 | City of Imperial Beach | City of Imperial Beach | 2003-01-08 10:00 | 2003-01-08 10:05 | 0.5 | 2.5 | 2.5 | 0 | 773 8th Street | Imperial Beach | 91932 | SD | Lateral Cleanout | 1 | N/A | UNKNOWN | Private lateral spill from private residance. | A plumber was called to correct the problem. H/O discontinued use of water. | Y | N | N | None | None | Plumber Cleaned | N | N | N | N/A | 0 | Code Enforcement notified. H/O given a notice to repair. This is a known problem residence for root intrusion. |  | X
| 002005 | fax | 08/14/02 16:30 | Leo Schempp | 760-753-0156 | Leucadia County Water District | Leucadia County Water District | 2002-08-14 15:00 | 2002-08-14 15:45 | 20 | 900 | 550 | 250 | Costa del Mar Rd | Carlsbad | 92009 | SD | manhole # 11-0760 | 0 | na | roots | roots | thorough cleaning w/ followup CCTV inspection | N | N | N | na | na | contained/percolated in ground | Y | N | N | NA | NA | Faxed spill report erroneously numbered 002004
| 002006 | fax | 09/02/02 10:00 | Leo Schempp | 760-753-0156 | Leucadia County Water District | Leucadia County Water District | 2002-09-02 08:43 | 2002-09-02 09:17 | < 20 | 600 | 0 | 600 | Corintia @ Alga | Carlsbad | 92009 | SD | manhole # 10-6065 | 0 | na | construction | line blocked with concrete slag | through cleaning, qtrly cleaning next 4 qtrs | N | Y | Y | San Marcos Creek | Batiquitos Lagoon | Pacific Ocean | Y | N | Y | San Marcos Creek | 3 | Faxed spill report erroneously numbered 002005 Street washed down, creek posted at La Costa Golf Course
| 101502 | 858-565-5255 | 10/15/02 @ 8:30 pm | Grant Mitchell | 619-667-1478 | City of La Mesa | City of La Mesa | 2002-10-15 18:30 | 2002-10-15 19:30 | 5 | 300 | 0 | 300 | 4750 Date St | La Mesa | 91941 | SD | 8" Clay Pot | 0 | None | Grease | Grease in main line | Rodded main line | N | Y | N | None | None | Storm Drain Pipe | N |  | N | N/A | 0
| 111402 | 858-571-6972 | 11/14/02 @ 8:00 pm | Police Dept | 619-667-1400 | City of La Mesa | City of La Mesa | 2002-11-14 19:30 | 2002-11-14 20:45 | 5 | 180 | 0 | 0 | 3861 Capitol | La Mesa | 91941 | SD | 6" VC Pipe | 0 | None | Roots | Roots in main line | Rod main line to open | N | N | Y | None | None | Street | N | N | N | N/A | 0
| 101402 | 619-338-2174 | 10/15/02 @ 7:00 am | Grant Mitchell | 619-667-1478 | City of La Mesa | City of La Mesa | 2002-10-14 17:00 | 2002-10-14 17:30 | 2.5 | 90 | 0 | 90 | West Point | La Mesa | 91941 | SD | 6" Concrete | 0 | None | Roots | Roots | Rodded main line | N | Y | N | None | None | Storm Drain Pipe | N | N | N | N/A | 0
| 23009 | Quarterly Report | 10/02/02 08:00 | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2002-10-01 09:00 | 2002-10-01 10:30 | 1 | 90 | 80 | 10 | WIRE MT RD, NEAR SAN JACINTO | MCB, CAMP PENDLETON | 92055-5008 | SD | 10 INCH CONCRETE GRAVITY MAIN | 0 | NA | Construction | Contractor installed a guard rail post through a 10" concrete sewer main. Soil caused a partial blockage downstream, which caused the sewer line to backup and spill around the post. | CORRECTIVE: Ram jet sewer line from downstream manhole. Repair line. Hose down street, recover cleanup water with vacuum truck. PREVENTATIVE: Inform contractor rep of procedures to locate underground untilities before construction begins. | Y | N | N | NA | NA | Overflow did not reach actual receiving waters but: Spill ran onto asphalt at Wire Mountain Road. | Y | N | N | NA | 0 | Spill traveled across earthen area 2 feet from post, to asphalt street (Wire Mtn. Road) and traveled 700 feet southwest and stopped. 702 ft. total distance traveled. No public contact expected.
| 23010 | Chiara Clemente | 11/02/02 21:30 | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2002-11-02 18:00 | 2002-11-02 18:50 | 16 | 800 | 750 | 50 | LIFT STATION 510049 | MCB, CAMP PENDLETON | 92055-5008 | SD | Lift Station #510049 | 3 | 07/24/02, 06/15/02, 03/19/02 | Unknown | Found pumps unplugged from electical outlet. | CORRECTIVE: Plugged in pumps to restore power. Spill was contained in the contractors containment pit. PREVENTATIVE: Pump station will be inspected daily by contractor. | N | N | N | None | None | Overflow did not reach actual receiving waters but: Engineered containment pit. | Y | N | N | NA | 0 | Spill flowed into engineered containment pit. No public contact expected.
| 23011 | Chiara Clemente | 11/18/02 10:40 | L McKnight | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2002-11-17 17:30 | 2002-11-18 10:30 | 30 | 30600 | 0 | 30600 | Building 210440 | MCB, CAMP PENDLETON | 92055-5008 | SD | Manhole 13Y278 | 0 | NA | Blockage | Manhole overflow due to debris including soap, grease, clay pipe fragments in gravity sewer line. | CORRECTIVE: Pumper trucks cleared blockage in sewer line between MH 13Y330 and MH 13Y277. Cleaned line by jetting. Area was limed. PREVENTATIVE: Lines in the spill area are scheduled for preventative maintenance. | N | Y | Y | Oceanside Harbor | Pacific Ocean | NA | Y | Y | Y | 90 signs were posted around the edge of North Oceanside Harbor. | 4 | OES Control # 02-6296. Notified Harbor Master (852-7550). Spill flowed 130' from manhole over earthen area to storm sewer, 127' through storm sewer into Oceanside Harbor. 257' total distance traveled. Public contact expected.
| 23012 | Chiara Clemente (Voice Mail) | 11/27/02 15:05 | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2002-11-27 06:30 | 2002-11-27 12:10 | 4 | 1360 | 0 | 1360 | Building 53502 | MCB, CAMP PENDLETON | 92055-5008 | SD | Grease Trap | 1 | 08/08/02 (Seq Tracking #023006) | Grease | Appears to have had an excessive amount of fryer grease dumped into the grease trap, which passed through the tee connection and caused a blockage. | CORRECTIVE: Use pumper truck to pump down grease trap. Jet line to clear blockage. Wash area w/ fresh water and recover w/ pumper truck. Clean grease trap Wed., Nov. 27, 2002. PREVENTATIVE: Discuss proper grease disposal w mess hall mgmt. | N | Y | Y | San Onofre Creek | Pacific Ocean | Overflow did not reach actual receiving waters but: Dry drainage ditch. | Y | Y | N | NA | 0 | Flowed from trap 600 ft across asphalt to storm drain; 100 ft through storm drain to natural drainage ditch; 125 ft through ditch and percolated into ground. 825 ft total distance traveled. No public contact expected.
| 23013 | Chiara Clemente | 12/09/02 07:00 | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2002-12-04 14:20 | 2002-12-04 14:35 | 12 | 185 | 185 | 0 | Building 2394 | MCB, CAMP PENDLETON | 92055-5008 | SD | Manhole-SW side of bldg 2394 in asphalt car park | 0 | NA | Pump Station Failure | Pumps at lift station tripped overloads and failed to come on. | CORRECTIVE: Reset pumps at lift station.Pumped down sewer line at clean out.Storm drain protected w sandbags. Asphalt washed w fresh water; pumper truck recovered wash water from asphalt and storm drain. PREVENTATIVE:None | N | Y | Y | Santa Margarita River | Pacific Ocean | Overflow did not reach actual receiving waters but: Asphalt road and storm drain manhole. | Y | N | N | NA | 0 | Flowed from manhole 250 ft on asphalt to storm drain inlet. Sewage ponded because of sandbags at inlet. Approx 50 gal entered storm drain but was recovered at manhole 100 ft away. 350' total distance traveled. Public contact not expected.
| 23014 | Chiara Clemente | 12/12/02 09:35 | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2002-12-11 10:30 | 2002-12-11 10:35 | 12 | 60 | 0 | 60 | Bldg. 31335A, MCTSSA | MCB, CAMP PENDLETON | 92055-5008 | SD | Lift Station # 31334 - 6" steel line | 0 | NA | Construction | Contractor removing pump station effluent piping for repair. Effluent spilled from disassembled flanged opening and when new flexible coupling installed below header tee failed after priming pump. | CORRECTIVE: Shut down pumps. Contain spill w sandbags and brooms. Redirect flow to wet well. Lime area. PREVENTATIVE: Contractors attended extra training on fitting disassembly/reassembly procedures. Extra spill containment provided. | N | N | N | None | None | Overflow did not reach actual receiving waters but: Asphalt parking lot. | Y | N | N | NA | 0 | Spill split along 2 paths: W 100ft by S side of Bldg. 31335A on asphalt parking lot; 100ft N along E side of Bldg. 31335A on asphalt. Traveled 100ft total from lift station. Public contact not expected.
| 23015 | Quarterly Report | 12/31/02 14:50 | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2002-12-31 13:00 | 2002-12-31 13:40 | 10 | 400 | 250 | 150 | West of building 31603 | MCB, CAMP PENDLETON | 92055-5008 | SD | Manhole # 13-Y-88 6" PVC Line | 0 | NA | Blockage | Partial line blockage by paper towels and debris. | CORRECTIVE: Pumper trucks stopped spill and recovered ponded water. Lines jetted to clear blockage. Spill area washed w fresh water; wash recovered by pumper trucks. PREVENTATIVE:Preventative maintenance done in early Dec and scheduled for Jan 2003. | N | N | N | None | None | Overflow did not reach actual receiving waters but: Earthen area. | Y | N | N | NA | 0 | Spill traveled 80 feet from manhole across earthen area where it ponded. Public contact not expected.
| 23016 | Chiara Clemente | 01/27/03 11:45 | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2003-01-27 06:40 | 2003-01-27 08:20 | 75 | 7500 | 7500 | 1500 | Building 620591, Area 62 | MCB, CAMP PENDLETON | 92055-5008 | SD | Overflow from cleanout, north side of bldg #620591 | 1 | 2002-03-13 | Blockage | Rags causing partial blockage of main line. | CORRECTIVE: Responded with 4 pumper trucks to pump down manhole to stop spill and jetted line to clear blockage. PREVENTATIVE: Continued preventative maintenance and tenant education. | N | Y | N | None | None | Overflow did not reach actual receiving waters but: Spill ponded on dirt road. | Y | Y | N |  |  | Recovery volume is higher than the amount spilled due to fresh water mixing with the sewage in the storm drain following hydrant flushing on January 24, 2003. An estimated 1500 gallons of raw sewage percolated into the ground.
| 23017 | Chiara Clemente | 01/28/03 13:09 | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2003-01-28 13:00 | 2003-01-28 13:01 | 20 | 20 | 0 | 20 | Del Mar Beach, PS# 210583 | MCB, CAMP PENDLETON | 92055-5008 | SD | Pump station discharge line | 1 | 2002-07-22 | Construction | Contractor broke his own bypass line with backhoe during contruction project at pump station #210583. | CORRECTIVE: Stopped bypass pumps and repaired the broken pipe. PREVENTATIVE: Discussed with contractor construction methods and general awareness when working around sewer lines. | N | N | N | None | None | Overflow did not reach actual receiving waters but: Spill percolated in contractors excavation trench. | N | N | N |  |  | The flow to the pipe was turned off before the bipass pipe was broken. The volume spilled was the remainder left in the pipe after the pipeline was shut off.
| 23018 | Chiara Clemente | 02/04/03 08:00 | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2003-02-03 20:10 | 2003-02-03 21:10 | 10 | 600 | 100 | 500 | Building 52609 | MCB, CAMP PENDLETON | 92055-5008 | SD | Manhole 11-Y-59 Line Type: VCP Line Size: 6 Inch | 0 |  | Other | Overflow due to excessive flow after potable water was restored to area. Flushometers stuck open and overloaded the sewage collection system. | CORRECTIVE: Secured potable water to buildings to stop flow to the sewer. PREVENTATIVE: During future potable water outages, water will be secured at each building, and restored as the flushometers are inspected. | N | N | N | None | None | Overflow did not reach actual receiving waters but: Ponded on dirt road | Y | N | N |  |  | Overflow was caused by flushometers sticking open after potable water was restored in area.
| 23019 | Chiara Clemente | 02/25/03 07:40 | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2003-02-25 06:30 | 2003-02-25 12:30 | 300 | 108000 | 0 | 108000 | Vandegrift Blvd, 22 Area | MCB, CAMP PENDLETON | 92055-5008 | SD | Manholes 3-Y-76, 3-Y-2, 3-Y-3 and 3-Y-4 | 1 | 2002-09-01 | Infiltration | Manholes 3-Y-76, 3-Y-002, 3-Y-003 and 3-Y-004 overflowed outside of STP#3 due to inflow of heavy rain into the collection system. | CORRECTIVE: Heavy equipment used to clear the debris blocking the storm water pump station barscreen. PREVENTATIVE: Regularly scheduled preventive maintenance on upstream storm water culverts to keep storm drains flowing properly and free of debris. | Y | Y | Y | Santa Margarita River | Pacific Ocean | Pacific Ocean | Y | Y | Y | Del Mar Beach | 3 | 1.63 inches of rainfall was reported from the air station at Camp Pendleton this day. The sewage/stormwater mixture overflowed from the manholes to the storm water conveyance system, which empties into the Santa Margarita River.
| 010205 | n/a | 2002-11-14 | Anne Briggs | 909-928-3777 | Eastern Municipal Water District | Eastern Municipal Water District | 2002-11-14 | 2002-11-14 |  | 200 | 100 | 100 | Members Drive/Branwin Court | Murrieta | 92562 | RV | Manhole | 0 | 0 | BLOCKAGE | Sandbag and rock debris from new construction | Unstopped blockage | N | Y | N | n/a | n/a | ground | Y | N | N | n/a | 0
| 010206 | n/a | 2002-12-30 | Anne Briggs | 909-928-3777 | Eastern Municipal Water District | Eastern Municipal Water District | 2002-12-30 | 2002-12-30 |  | 100 | 100 | 0 | Quintana/Taos | Murrieta | 92562 | RV | Manhole | 0 | 0 | BLOCKAGE | Contractor's screw plug left in line | Unstopped blockage | N | N | N | n/a | n/a | n/a | N | N | N | n/a | 0
| 010207 | Chiara Clemente | 2003-03-04 08:45 | Roger Turner | 909-928-3777 | Eastern Municipal Water District | Eastern Municipal Water District | 2003-03-03 19:55 | 2003-03-04 03:25 |  | 34750 | 18500 | 16250 | Via Lobo/Deer Meadow Road | Temecula | 92563 | RV | Manhole | 0 | 0 | CONSTRUCTION | Contractor excavation caused debris in manhole (cover had been removed from manhole) | Possible fines against contractor | Y | Y | Y | Santa Gertrudis Creek | Murrieta Creek | n/a | Y | Y | Y | Along spill route and near creek | 5
| 023003 | Bryan Ott | 2003-02-02 11:45 | Shawn Atherton | 760-633-2871 | City of Encinitas | City of Encinitas | 2003-02-02 08:30 | 2003-02-02 10:00 | 75 | 6750 | 0 | 6750 | 2695 Manchester Avenue | Cardiff | 92007 | SD | Olivenhain Pump Station Force Main | 0 | N/A | LINE BREAK | 14-inch cast iron force main failure. The force main developed a crack, causing sewage to spill when the lift station's pumps were activated | Contractor called in to make emergency repairs. A stainless steel full-circle clamp was used to repair the pipe. | N | N | N | none | none | Percolated into ground. | Y | Y | N | N/A | 0 | Atlas Pumping called in to assist with water recovery while repairs were made to the force main.
| 023004 | Bryan Ott | 2003-02-25 14:30 | Shawn Atherton | 760-633-2871 | City of Encinitas | City of Encinitas | 2003-02-25 08:00 | 2003-02-25 11:15 | 400 | 48000 | 40800 | 7200 | Corner of 3rd and B Streets | Encinitas | 92024 | SD | Moonlight Beach Pump Station | 1 | 2002-05-17 | INFILTRATION | Flows coming into station were more than pumps could handle. | At this time, we do not know where extra inflow is coming from. All major sewer lines going to pump station investigated and did not find any unusual or high flows. This investigation will continue until source of inflow is found. | Y | N | Y | Cottonwood Creek | Ocean | Ocean | Y | Y | Y | 150 yards south and north of entry point | 3 | This type of spill not common to our system. Have not had spills caused by infiltration in past ten years. Investigation will continue until source of infiltration is found.
| 023005 | Bryan Ott | 2003-03-15 19:45 | Shawn Atherton | 760-633-2871 | City of Encinitas | City of Encinitas | 2003-03-15 17:05 | 2003-03-15 19:30 | 215 | 29000 | 16400 | 12600 | Corner of 3rd and B Streets | Encinitas | 92024 | SD | Moonlight Beach Pump Station | 2 | 5/17/02, 2/25/03 | INFILTRATION | Flows coming into station were more than pumps could handle. | At this time, we do not know where extra inflow is coming from. All major sewer lines going to pump station investigated and did not find any unusual or high flows. This investigation will continue until source of inflow is found. | Y | Y | Y | Cottonwood Creek | Ocean | Ocean | Y | Y | Y | 150 yards south and north of entry point | 3 | Again, this type of spill not common to our system. We will continue to investigate source of infiltration until found.
| 023006 | Victor Vasquez | 2003-03-17 14:00 | Shawn Atherton | 760-633-2871 | City of Encinitas | City of Encinitas | 2003-03-17 06:40 | 2003-03-17 07:15 | 25 | 875 | 0 | 875 | 3243 Lone Jack Road | Encinitas | 92024 | SD | Manhole #R19 | 0 | N/A | ROOTS | Found roots in line while cleaning. | Sewer line cleaned of roots and added to trouble spot list. | Y | Y | Y | Escondido Creek | Ocean | Ocean | Y | Y | N | N/A | 0 | This line will be placed on trouble spot list and will be cleaned every 3 months.
| 023001 | Voice Mail | 2003-02-22 18:15 | Ron Hightower | (949) 837-7050 | El Toro Water District | El Toro Water District | 2003-02-22 18:15 | 2003-02-22 19:20 | 10 | 850 | 250 | 600 | 24535 Dardanin St. | Mission Viejo | 92691 | OC | ETWD Atlas page MC- 504, MH #6 | 0 | N-A | GREASE | Grease blockage downstream of manhole | Set up traffic control and containment area with sand bags and sand tubes. Used Vactor/Hydro cleaner truck to break blockage and vacuum contained spill. Cleaned, washed down, and vacuumed wash down water. TV Video inspection showed line to be in good conditions | N | Y | Y | Storm drain | Aliso Creek | Aliso Creek | Y | Y | N | NA |  | Notified all Regulatory agencies, City of MV and emailed report. This line was last cleaned January 2002
| 023019 | Mike Golena | 2003-01-17 09:20 | Lloy Thompson | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2003-01-17 08:00 | 2003-01-17 08:10 | 50 | 500 | 450 | 50 | 2200 Blk. Temple Hills Drive | Laguna Beach | 92651 | OR | Manhole #69 | 0 |  | Roots | Roots from upstream of manhole #69 and a sharp turn in the pipe caused it to surcharge and spill over. The spill had cleared by the time that sewer crews had arrived on scene but as a precaution they checked all downstream manholes. Upon checking the downstream manholes we found theline plugged at 1102 Temple Hills Drive. The line was cleared before any sewage spilled. | Crews jetted the line and the flow returned to normal. Parks Division crews blocked off the storm drain outlet at Bluebird Canyon Beach and the pumps were turned back on so that all Stormwater went back into the sewer system. | 0 | Y | Maybe | Storm Drain | Pacific Ocean(Poss) | Most, if not all of the sewage was pumped back into the City's sewer system | Y | Y | Y | 150 ft. north and south of Bluebird Beach Outlet | 3 | The beach was closed by Orange County Health Care Agency as a precaution only due to the high tide. The storm drain will remain plugged for several days until the next rain storm. During this time all nuisance water will be pumped back into the City's sewer system
| 023020 | Victor Vasquez | 2003-01-23 09:55 | Lloy Thompson | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2003-01-23 08:15 | 2003-01-23 08:55 | 25 | 1000 | 999 | 1 | 669 Canyon View Drive | Laguna Beach | 92651 | OR | Manhole #34 | 0 |  | Roots | I received a page from Police Dispatch who notified me that there was a possible sewer spill at 648 Canyon View Drive. Upon arriving at the location I noticed that sewage was coming from manhole #34 at 669 Canyon View. An unknown lateral had been cleaned and dislodged roots into the main sewer system. | City crews jetted the main line with a full cutting blade to remove all of the roots which cleared the line. A follow-up video of this line will be completed by January 30, 2003. | 0 | Y | N | Storm Drain | N/A | Diverted back into the sewer system at Cleo Street Beach through the CDS Unit | Y | Y | N |  |  | Police and Fire also responded to the scene. OES #03-0447
| 023021 | Voice Mail | 2003-01-26 10:15 | John Pietig | (949) 497-0754 | City of Laguna Beach | City of Laguna Beach | 2003-01-26 08:30 | 2003-01-26 09:18 | 83 | 4000 | 3800 | 200 | 1460 Temple Terrace | Laguna Beach | 92651 | OR | Manhole #4 | 0 |  | Roots | Roots created a blockage in a City sewer line which overflowed at manhole #4 in an easement which runs parallel to 1460 Temple Terrace. The sewage subsequently flowed into Bluebird Park which is adjacent to the property. The blockage was cleared by City crews at 9:18 a.m. | The blockage was cleared with the jetting tool. Cleanup continued until 1:50 p.m. The park will remain closed until all contaminated soil and sand in the park is removed and replaced. The line will be TV'd this week and was last cleaned in December 2002 | 0 | N | N | N/A | N/A | The sewage was vacuumed up by the vactor truck and pumped back into the City's sewer system. All contaminated soil and sand was removed from the park. | Y | Y | Y | Bluebird Park | 3 | It is estimated that about 5% of the spill soaked into private property and/or dissipated into the air. Closure signs were placed on all gates of the park and police caution tape placed all around the playground area. We anticipate that signs will be removed by Wednesday.
| 023022 | Voice Mail | 2003-02-01 20:00 | Doug Hellman | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2003-02-01 18:15 | 2003-02-01 19:05 | 0.2 | 10 | 0 | 10 | 1045 Wykoff Way | Laguna Beach | 92651 | OR | Private Lateral | 0 |  | Construction | Crews were called out by Laguna Beach Police Department in reference to a private lateral that was running over. When we arrived on scene we set up the rodder at manhole #45 at 1306 Bluebird Canyon Drive. We pulled back broken clay pipe and approximately 50ft. of rope. The City contractor had failed to remove the tag line at the end of the day and this allowed the rope to plug the easement main line. | City crews cleared the stoppage and removed the rope. A follow-up was done the next day and the line was jetted. | 0 | N | N | N/A | N/A | Soaked into the ground next to the home. | Y | N | N
| 023023 | Voice Mail | 2003-02-02 09:13 | John Pietig | (949) 497-0754 | City of Laguna Beach | City of Laguna Beach | 2003-02-02 07:30 | 2003-02-02 08:15 | 10 | 450 | 20 | 430 | 680 S. Coast Hwy & 686 S. Coast Hwy | Laguna Beach | 92651 | OR | Manhole #28 | 1 | 2002-03-05 | Rocks | Sewer crews were dispatched by Parks personnel who stated that there was a manhole running over at the 600 blk. S. Coast Hwy. We responded with the jetter truck and pump truck. Upon arriving at the scene we immediately sandbagged around the manhole and pulled the jetter truck around and started jetting the line between manhole #79 and manhole #20. Rocks and debris in the City main line caused the blockage. | The flow was restored to the main line. Additional measures will be taken to protect manholes during street rehabilitation, although no direct connection to paving activities could be made. | 0 | Y | Y | Storm Drain | Pacific Ocean | 20 gallons was vacuumed up in the vactor truck | Y | N | Y | 500ft. Up coast and downcast of Sleepy Hollow Storm Drain | 3 | Per the Health Dept, the beach was closed 500ft. Up coast and down coast of Sleepy Hollow storm drain and at the beach entrances. This line was last cleaned on December 6, 2002.
| 023024 | Voice Mail | 2003-03-01 15:55 | John Greybeck | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2003-03-01 08:00 | 2003-03-01 13:58 | 1.4 | 500 | 40 | 460 | 2898 Chillon Way | Laguna Beach | 92651 | OR | Manhole in easement | 0 |  | Roots | Gardener noticed sewage leaking from manhole to the rear of the property at 8:00. Called the property owner to report it to the Sewer Division. Police Dispatch were notified by property owner at 13:18 who dispatched crews at that time. Crews noticed that the manhole at the rear of the property was surcharged and trickling over with sewage. Crews proceeded to the downstream manhole and forked the line. The line broke free and the fork came back with roots and grease. | At the same time, the Fire Dept. placed sandbags around the storm drain and the CDS was switched on at Bluebird Beach. Jetted the line and vacuumed up at the dam around the storm drain. | Y | Y | Y | Storm Drain | Open Canyon Area | Diverted back into the City Sewer System | Y | N | Y | Next to the creek and on the fence. |  | Signs posted as a precaution only. Since the overflow was at a very slow rate, most of the sewage soaked into the ground in the back yard. The crews recovered what they could through washing down and vacuuming.
x | 023025 | Fax | 2003-03-19 16:57 | City of Laguna Beach | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2003-03-18 17:00 | 2003-03-18 17:55 | 0.9 | 50 | 50 | 0 | 1365 Catalina Street | Laguna Beach | 92651 | OR | Private Cleanout | 0 |  | Debris | Mr. Sanderson upon arriving home from work noticed that his cleanout had run over and was plugged with an unknown type of debris. | Sewer crews noticed that the spill had reached the storm drain box on Mountain/Glenneyre but noted that it had not gone into the pipe. The storm drain was checked at Mountain Street Beach and the area was also dry. Crews washed down the alley into the City vacuum truck and recovered all of the spill at the storm drain box at Catalina/Glenneyre | 0 | Y | N | Storm Drain | N/A | Storm drain box at Mountain/Glenneyre. All sewer water was recovered into the City's vacuum truck | Y | N | N |  |  | Courtesy Report - Private Sewer Spill |  | x
| 023026 | Brian Kelly | 2003-03-24 09:13 | Lloy Thompson | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2003-03-24 07:50 | 2003-03-24 08:40 | 50 | 2500 | 2499 | 1 | 1600 Blk. Hillcrest Drive | Laguna Beach | 92651 | OR | Manhole #15 | 1 | 2002-08-19 | Roots | I received a call from Public Works Dispatch at 8:05 a.m. that the Water District was on scene at the 1600 Blk. Of Hillcrest Drive and that sewage was overflowing from the manhole at this location. Sewer crews arrived on scene and proceeded upstream of manhole #15. We jetted the main line and pulled a root out that was 4' long x 4" in diameter. This blockage caused the lower manhole on Hillcrest Drive to run over. We believe that these roots were private lateral roots and had been pushed down into the City's main line. | We continued to jet the line and removed all roots and debris. We televised the line from manhole #10 to manhole #12 where the blockage had occurred. All sewage that had spilled went into a storm drain system that is connected to the sewer main in Emerald Bay. | N | Y | N | Storm Drain | N/A | All sewage was recovered back into Emerald Bay's sewer system | Y | Y | N |  |  | This section of sewer main was lined and televised on March 4, 2003. No sewage made it to the beach. OES Report #03-1587.
| 023003 | Voice | 2-24-03 1:35pm | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2003-02-23 10:00 | 2003-02-24 | 1.5 | 850 | 0 | 850 | 721 Ave. Columbo | San Clemente | 92672 | OC | Pump Station | 0 | 0 | PUMP STATION FAILURE | Control Panel Failure | Install Secondary Alarm Feature | N | Y | N | None | None | Canyon Storm Drain | Y | N | N | N/A
| 023004 | Fax | 3-31-03 11:00am | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2003-03-30 14:15 | 2003-03-30 14:30 | 1 | 30 | 25 | 5 | 200 Blk La Pata | San Clemente | 92672 | OC | Pump Station | 1 | 0 | PUMP STATION FAILURE | Control Panel Failure | Install Secondary Alarm Feature | N | Y | N | None | None | Canyon Storm Drain | Y | N | N | N/A
X |  | Voice / Fax | 2-4-03 1:20pm | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2003-02-04 09:35 | 2003-02-04 10:00 | 5 | 125 | 125 | 0 | 100 Blk Los Arboles | San Clemente | 92673 | OC | 8" Gravity | 0 | 0 | BLOCKAGE | Contractors Test Plug | Private Sewer System | N | Y | N | None | None | 100% Captured | Y | N | N | N/A |  | Private System |  | X
X |  | Voice | 2-4-03 3:55pm | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2003-02-04 13:40 | 2003-02-04 14:00 | 5 | 100 | 50 | 50 | 700 S. El Camino Real | San Clemente | 92672 | OC | Private Lateral | 0 | 0 | GREASE | Private Lateral | Private Sewer System | N | Y | N | None | None | Canyon Storm Drain | Y | N | N | N/A |  | Private System |  | X
X |  | Fax | 3-5-03 1:30pm | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2003-03-05 10:15 | 2003-03-05 10:30 | 10 | 150 | 148 | 2 | 256 A. Victoria | San Clemente | 92672 | OC | Private Lateral | 0 | 0 | BLOCKAGE | Private Lateral | Private Sewer System | N | Y | N | None | None | Storm Drain Pipe | Y | N | N | N/A |  | Private System |  | X
X |  | Fax | 3-12-03 3:00pm | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2003-03-12 12:15 | 2003-03-12 12:25 | 3 | 30 | 20 | 10 | 951 C. Negocio | San Clemente | 92672 | OC | Private Lateral | 0 | 0 | BLOCKAGE | Private Lateral | Private Sewer System | N | Y | N | None | None | Canyon Storm Drain | Y | N | N | N/A |  | Private System |  | X
| 023007 | Victor Vasquez | 1/6/2003 0715 | B. Wiltse | 619-660-2007 | County of San Diego | County of San Diego | 2003-01-03 09:00 | 2003-01-03 09:20 | 6.75 | 135 | 100 | 35 | 3263 Fairway Dr. | Spring Valley | 91978 | SD | 503-17-350-A | 0 | 0 | Grease | Accumulated grease build up in 8-inch line | Line televised, placed on accellerated quarterly cleaning schedule | N | Y | N | NA | NA | Central Ave./Fairway Channel | Y | N | N | NA | 0
| 023008 | Victor Vasquez | 1/6/2003 1130 | B. Wiltse | 619-660-2007 | County of San Diego | County of San Diego | 2003-01-04 | 1/4/2003 1130 | 0 | 50 | 0 | 50 | 10441 Madrid Dr. | Spring Valley | 91978 | SD | 501-27-291D | 0 | 0 | UNKNOWN | UNKNOWN | Line televised, placed on quarterly cleaning schedule | N | Y | N | NA | NA | Dry open channel | Y | N | N | NA | 0
| 023009 | Victor Vasquez | 1/14/2003 1000 | B. Wiltse | 619-660-2007 | County of San Diego | County of San Diego | 2003-01-14 08:45 | 2003-01-14 09:45 | 0 | 50 | 0 | 50 | 14065 Old Hwy 80 | El Cajon | 92040 | SD | 398-321-60K | 0 | 0 | BLOCKAGE | Contractor left mechanical plug in line | Installed locking lid on manhole | N | Y | N | NA | NA | Dry open channel | Y | N | N | NA | 0
| 023010 | Victor Vasquez | 2/23/2003 0930 | B. Braun | 619-660-2007 | County of San Diego | County of San Diego | 2003-02-23 09:30 | 2003-02-23 10:30 | 5 | 300 | 275 | 25 | 415 Ramona Ave. | Spring Valley | 91977 | SD | 584-50-364D | 0 | 0 | ROOTS | VCP line craced roots growing through crack | Line cleared of roots, televised and placed on quarterly cleaning schedule. | N | Y | N | NA | NA | Dry open channel | Y | N | N | NA | 0
| 023011 | Adam Laputz | 3/18/2003 0900 | B. Wiltse | 619-660-2007 | County of San Diego | County of San Diego | 2003-03-16 09:00 | 2003-03-16 10:00 | 13 | 800 | 0 | 800 | 9734 Campo Rd. | Spring Valley | 91978 | SD | 500-192-0412A | 0 | 0 | ROOTS | Roots in manhole | Line cleaned, televised, place on quarterly cleaning schedule | Y | Y | N | NA | NA | Kenwood creek | Y | N | N | NA | 0
| 012020 | Quarterly Report | 2003-03-01 14:00 | Dave Seymour | (949) 459-6540 | Santa Margarita Water District | Santa Margarita Water District | 2003-03-20 13:45 | 2003-03-20 13:55 | 1 | 10 | 10 | 0 | Christianitos Road | Rancho Mission Viejo | 92688 | OC | Air Vac on Ortega Force Main | 0 | N/A | Other | Broken float stem in air vac prevented proper seating | Replaced the air vac control. | N | N | N | None | None | Sewage removed by Vactor truck | Y | N | N
| 023007 | FAX 858-571-6972 | 2003-01-14 12:00 | Mike Dunbar | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2003-01-14 07:40 | 2003-01-14 08:30 | 20 | 1000 | 440 | 560 | 31104 PCH (LS #2) | Laguna Beach | 92651 | OC | lift station no. 2 | 0 | none | PUMP STATION FAILURE | The main controller failed due to an electrical surge. This palced the main controller in standby mode. The backup controller did not operate due to a low air pressure problem. The third backup (float system) was connected to the main controller which was in standby mode and not operational. | Manufacturer reviewed the main controller operation. Backup battery and battery charger were replaced. Air system was adjusted with greater air pressure. | N | Y | Y | Aliso Creek | Pacific Ocean | NA | Y | Y | Y | 100 ft north/south of Aliso Creek | 3 | Planned preventative measures: replace bubbler system with entrapped air system, install backup float system separate from main controller, require sanitary personnel to monitor station until primary control system and backup system are fully operational, and motor starter would be installed that would be less susceptable to power surge.
| 023008 | FAX 858-571-6972 | 2003-01-29 12:10 | Mike Dunbar | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2003-01-29 09:00 | 2003-01-29 09:30 | 9 | 300 | 300 | 0 | 34146 PCH | Dana Point | 92629 | OC | manhole | 0 | none | Grease | Grease build-up from restaurant at location of overflow | Jet main line with high pressure and also use hydraulic cutter to cut grease then use CCTV unit. District will discuss grease control practices with restaurant. | N | Y | N | None | None | Storm drain catch basin at Dana Point Harbor Drive | Y | N | N | NA | 0 | Spill was contained behind sand bags and energy decipitator. Wastewater was vacuumed up by District vac con truck.
X | 023009 | FAX 858-571-6972 | 2003-02-09 07:40 | Mike Dunbar | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2003-02-08 08:00 | 2003-02-08 11:00 | 15 | 2700 | 0 | 2700 | 24097 Vista Corona | Dana Point | 92629 | OC | manhole | 0 | none | DEBRIS | Rags, silt and debris plugged a private sewer pipeline. Raw wastewater flowed out of a manhole. | District crews responded and unplugged the pipeline using the jetter truck. The pipeline was jetted and cleaned of the rags and debris. | N | Y | Y | Salt Creek | Pacific Ocean | NA | Y | Y | Y | 1/2 mile upcoast and 1/2 mile downcoast of the Salt Creek Ocean interface at Monarch Beach | 4 | Private system overflow |  | X
| 023010 | FAX 858-571-6972 | 2003-03-10 12:30 | Mike Dunbar | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2003-03-10 06:45 | 2003-03-10 07:20 | 25 | 875 | 250 | 625 | 31526 Paseo Valido | Laguna Beach | 92651 | OC | Manhole | 1 | 2002-07-01 | Roots | Overflow was caused from roots coming from the service lateral at 31526 Paseo Valido | Ball jetter with root cutter hit root obstruction from service lateral. | N | Y | N | None | None | Sewage ponded and absorbed into sand at bottom of storm drain. | Y | N | N | NA | 0 | History of location evidences private laterals with roots exiting into main system. Main line was lined on 3/22/00 with 125 milimeters of SanCon 100 polyurethane. District will notify private property owners of conditions of laterals and request cooperation.
X | 023011 | FAX 858-571-6972 | 2003-03-03 18:00 | Mike Dunbar | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2003-02-28 16:30 | 2003-03-02 18:00 | 3.25 | 14000 | 0 | 14000 | DP Marine Mobile Home Park | Dana Point | 92629 | OC | Cleanout | 0 | none | Roots | Roots/debris clogged a sewer collection pipeline. The wastewater backed up and out one of the cleanouts. | Contact management company for District to provide sewer cleaning services | N | Y | N | None | None | Treatment Plant | Y | Y | N | NA | 0 | Private system overflow. Wastewater flowed through the storm drain system to a pumping station. The pumping station pumped the wastewater to the treatment plant. It appears that the blockage cleared itself |  | X
x | 023018 | QUARTERLY REPORT |  | Joel V. Holt | (760) 723-6026 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2003-01-02 14:30 | 2003-01-02 14:45 | 1 | 15 | 0 | 15 | 911 Salt Air Lane | Fallbrook | 92028- | SD | Cleanout | 0 |  | PRIVATE PROPERTY | Build up of toilet paper, hair, and some roots. | Ran rodder and cleaned out stoppage. | N | N | N | None. | None. | Stopped and dried up on asphalt road. | Y | N | N |  | 0 | COURTESY NOTIFICATION. Rodded lateral and cleared stoppage at about 25 feet. |  | x | 0
| 023019 | 858-571-6972 | 01/08/2003 15:15 | Patti S. Page | (760) 723-5640 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2003-01-08 11:45 | 2003-01-08 12:15 | 10 | 300 | 250 | 50 | 1148 S. Main Street | Fallbrook | 92028- | SD | Cleanout | 0 |  | GREASE | Mainline plugged with combination of roots and grease. | Flushed mainline to relieve sewage. Flushed and vacuumed storm drains. | Y | Y | N | None. | None. | Tracked in the storm drain and found a dry storm drain and vacuumed out there. | Y | N | N |  | 0 | Flushed mainline and vacuumed up standing sewage. |  |  | 1
| 023020 | QUARTERLY REPORT |  | Joel V. Holt | (760) 723-6026 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2003-01-29 18:30 | 2003-01-29 19:30 | 0.5 | 30 | 5 | 25 | 1285 Aves Lane | Fallbrook | 92028- | SD | Cleanout | 0 |  | ROOTS | Mainline stoppage due to roots causing backup out of private cleanout. | Plumber rodded lateral into mainline and cleared stoppage on 1-29-03. District TV'd lateral, flushed mainline, and picked up debris around cleanout on 1-30-03. | N | N | N | None. | None. | Soaked into ground around cleanout. | Y | N | N |  | 0 | Renter called landlord and he called plumber. The District wasn't notified about the problem until the following morning. Informed all to call the District any time there is a sewage problem. |  |  | 0
| 023021 | FAX 858-571-6972 | 02/27/2003 08:30 | Patti S. Page | (760) 723-5640 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2003-02-26 12:30 | 2003-02-26 13:15 | 10 | 450 | 300 | 150 | 500 block Ammunition Road | Fallbrook | 92028- | SD | Manhole | 0 |  | GREASE | Grease blockage in mainline. | Dammed up gutter to stop flow to storm drain. Flushed mainline to open stoppage. Ran mainline several times. Vacummed up dammed water and dirt. Went 1/4 mile downstream in creek and vacuumed 3000 gallons of creek water. Flushed out storm drain. Wash | Y | Y | Y | Fallbrook Creek | Lake O'Neill, Santa Margarita River, Pacific Ocean | NA | Y | N | Y | Fallbrook Creek from Ammunition to NWS | 3 | Vactored a total of 3000 gallons from creek in attempt to recover as much of overflow as possible. |  |  | 1
| 023022 | FAX 858-571-6972 | 03/17/2003 13:30 | Patti S. Page | (760) 723-5640 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2003-03-16 18:00 | 2003-03-16 19:20 | 2 | 240 | 180 | 60 | Elder & Vine | Fallbrook | 92028- | SD | Manhole | 1 | 11-20-02 | ROOTS | Stoppage caused by roots 65 feet upstream of manhole B53. | Ran vactor hose 65 feet and cleared stoppage. Run CCTV to try to identify any other problems. | Y | N | N | None | None | Asphalt road and was vacuumed up. | Y | N | N |  | 0 | Per Collections Supervisor on 3-28-03, the 60 gallons not recovered had evaporated and dried up on the road by the time the crew arrived on site. (psp notation 3-28-03) |  |  | 1
| 023014 | Voice Mail | 01/02/03 1425 | Mark Anderson | 7604355957 | City of Oceanside | City of Oceanside | 2003-01-02 00:20 | 2003-01-02 00:40 | 100 | 2000 | 2000 | 0 | 3950 North River Road | Oceanside | 92057 | SD | WWTP Selector Box | 0 |  | OTHER | Selector Box was hydraulically ov erloaded due to unexpected high flows. | High Level Sensor and Level Indicator are being installed. | N | N | N |  |  | Returned to WWTP Process. | Y | Y | N
| 023015 | Voice Mail | 01/05/03 1241 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 2003-01-05 11:25 | 2003-01-05 11:48 | 8 | 184 | 0 | 184 | Esplanade & Alto Streets | Oceanside | 92056 | SD | Manhole & Cleanout | 0 |  | DEBRIS | City main backed uup with rags and other debris. | Area is being cleaned on a routine schedule this quarter. | N | Y | N |  |  | Asphalt Street. | Y | N | N |  |  | Spill was calc'd. @ 5GPM for manhole & 3GPM for cleanout. Most evaporated in the warm weather, before reaching curb/gutters.
| 023016 | Voice Mail | 01/08/03 1010 | Mike Heiser | 7604355870 | City of Oceanside | City of Oceanside | 2003-01-08 08:40 | 2003-01-08 09:05 | 2 | 50 | 50 | 0 | 100 Block of Breakwater | Oceanside | 92054 | SD | Manhole | 0 |  | UNKNOWN | Stoppage removed itself after crews on scene. | Line was rodded and will be televised. | N | N | N |  |  | Totally recovered. | Y | N | N |  |  | Street & curb were washed and vactored.
| 023017 | Voice Mail | 01/20/03 1220 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 2003-01-20 08:30 | 2003-01-20 09:30 | 5 | 300 | 0 | 300 | 3685 Vista Campana | Oceanside | 92054 | SD | Manhole | 2 | 09/08/02 and 10/10/02 | ROOTS | Small line with tight 90 degree turn backed up with roots and grease. | Area is being cleaned on quarterly basis. Dropped chlorine to help with grease. | Y | Y | N |  |  | Spill pooled in remote flood control channels with limited access. | Y | N | N
| 023018 | Voice Mail | 01/20/03 1220 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 2003-01-20 10:11 | 2003-01-20 10:38 | 15 | 405 | 75 | 330 | 1650 Loretta Street | Oceanside | 92054 | SD | Manhole | 0 |  | GREASE | Stoppage caused by heavy in city main | Area is known for grease problems, cleaned regularly and reveives routine chlorine drops. | N | Y | N |  |  | Storm drains lead into canyon where flows are absorbed. | Y | N | N |  |  | Broke stoppage first, then recovered as much as possible.
| 023019 | Voice Mail | 01/26/03 1311 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 2003-01-26 10:30 | 2003-01-26 10:42 | 35 | 420 | 0 | 420 | College & Marvin Street | Oceanside | 92054 | SD | Manhole | 0 |  | GREASE | Heavy grease in city main | Line is on chlorine "drop" list and bleach trucks "burn" line occasionally. | N | Y | N |  |  | Storm drain leads to El Camino Golf Course, where it is adsorbed and evaporated. | Y | N | N |  |  | Recovery was not possible by the time work was completed.After breaking stippage, crew made manhole entry to recover large grease "logs" to prevent downstream blockage.
| 023021 | Voice Mail | 02/11/03 1502 | Ed Calhoun | 7604355870 | City of Oceanside | City of Oceanside | 2003-02-11 13:15 | 2003-02-11 13:30 | 10 | 150 | 0 | 150 | 4217 Thomas Street | Oceanside | 92056 | SD | Manhole | 0 |  | ROOTS | Roots & Rags were blocking city main | Area is jetted/rodded on a routine basis. | Y | Y | Y | Buena Vista Creek | Buena Vista Lagoon |  | Y | N | N |  |  | No recovery poossible. Storm drain 20 ft. from manhole and rains carried spill off with storm runnoff.
| 023022 | Voice Mail | 03/16/03 2210 | Mark Anderson | 7604355957 | City of Oceanside | City of Oceanside | 2003-03-16 20:00 | 2002-03-16 21:45 | 90 | 9400 | 9400 | 0 | 3950 North River Road | Oceanside | 92057 | SD | WWTP Load Equal. Tanks | 1 | 2003-01-02 | LINE BREAK | High influent flow raised 6 inch pipe attached to LET to break allowing sewage to spill. Some spilled into Windmill Creek drainage area. | 6000 gals was contained in construction trench. 2650 gals were contained behind dirt berms. 750 gals reached drainage area, but was contained. All was pumped back to plant process. Pipe being repaired. | Y | N | N |  |  | Total spill returned to plant process. | Y | Y | N
| 023023 | Quarterly Report |  | Mike Heiser | 7604355870 | City of Oceanside | City of Oceanside | 2003-03-19 08:05 | 2003-03-19 08:45 | 5 | 200 | 200 | 0 | 3202 Vista Way | Oceanside | 92054 | SD | Manhole | 0 |  | GREASE | Residential Grease blocked City Main. | Rodded Main. Chlorine will be added. | N | N | N |  |  | Collected in depression next to Green #3. | Y | N | N |  |  | Extra water might be irrigation runoff or leaking irrigation pipe. Full recovery effected.
| 023003 | faxed | 2003-01-05 13:22 | Carlos Mariscal | (760) 726-6328 | City of Vista | City of Vista | 2003-01-05 10:20 | 2002-01-05 10:40 | 5 | 100 | 100 | 0 | 723 Maryland Avenue | Vista | 92083 | SD | V06.93 | 0 | None | Manhole Failure | Manhole channnel failed -- broken concrete piece plugged pipe causing the sewage blockage. This manhole was recently rehabilitated during the capital improvement project. | Crew washed spilled area, and vacuumed out of the storm drains -- all sewage captured. | N | N | N | None | None | Storm drains | Y | Y | N | N/A | N/A | NONE
| 023004 | faxed | 2003-02-06 16:01 | Brenda (VID) for Jeanette Rusnak | 760.758-9544 | City of Vista | City of Vista | 2003-02-06 16:10 | 2003-02-06 16:21 | 2 | 22 | 11 | 11 | 326 N. Citrus Ave. | Vista | 92084 | SD | V12.106 | 0 | None | Roots and Grease | Roots and grease within a six-inch main. | Main was cleaned using a hydro-jetter; followed with a power rooter w/ 3 blades root cutter; followed by treating roots with ROOT-X; followed by video inspection of the main. | N | Y | N | None | None | Underground Storm drains | Y | N/A | N | N/A | N/A | Cleared blockage with vactor truck; setup recovery vacuum system with vactor and washed down spill area with water truck; followed spill down the storm drain to recover all of the spill.
X | 023005 | faxed | 2003-02-19 14:50 | George Solano | 760.726-1340, X1661 | City of Vista | City of Vista | 2003-02-18 09:00 | 2003-02-18 10:15 | 1 | 60 | 60 | UNKNOWN | 1279 Calle Jules | Vista | 92084 | SD | PRIVATE LATERAL | 0 | 0 | Grease | Plumber indicated there was grease in PRIVATE LATERAL. | Private plumber cleaned the sewer lateral -- city called the plumber because no one was home to handle the private spill. | N | N | Y | Drainage along Taylor Ave. | None | Drainage along Taylor Ave., which terminates at Guajome Lake Creek. | Y | N/A | Y | Along creek site (between Calle Jules and Taylor st.) | Still posted | Sewage is present along the creek -- based on sample testing results |  | X
| 023006 | faxed | 2003-03-29 07:30 | Jim Guzman | (760) 726-6328 | City of Vista | City of Vista | 2003-03-29 07:30 | 2003-03-29 08:15 | 1 | 50 | 40 | 10 | 321 Morningside Terrace | Vista | 92083 | SD | V22.89 | 0 | None | Roots | Roots in sewer main. | Jetted and rodded the main three times. | N | N | N | On private driveway next to shrubs. | None | Sewage was vacuum & wash down area. | Y | N/A | N | N/A | 0 | NONE
X | 023007 | faxed | 2003-04-01 07:00 | Jim Guzman | (760) 726-6328 | City of Vista | City of Vista | 2003-03-29 17:00 | 2003-03-29 21:30 | 1 | 50 | 50 | 0 | 210 Camino Corto | Vista | 92083 | SD | PRIVATE LATERAL | 0 | None | Damage lateral & cleanout | PRIVATE LATERAL' ran over by a car, and damage the lateral. | Sewer main was checked and cleared. Site spill was cleaned/washed, and vacuumed. City crew notified the property owner to call plumber. | N | N | N | None | None | N/A | Y | N/A | N | N/A | 0 | NONE |  | X
| 023001 | FAX (858) 571-6972 | 2002-07-26 11:53 | D Catone | (619) 582-1413 | City of Lemon Grove | City of Lemon Grove | 2002-07-25 08:15 | 2002-07-26 01:30 | 1.33 | 240 | 50 | 190 | Alford St/Dayton St | Lemon Grove | 91945 | SD | 479-16 NH 01-03 | 0 | none | GREASE | Heavy roots from service lateral 55 ft from MH | Main line jetted & rootcut. TV on 7/26 to check cleaning. | N | N | N | none | none | Dirt Alley | Y | N | N | none | 0 | Phone conversation w/ Environ Health No signs needed.
| 023002 | FAX (858) 571-6972 | 2002-08-19 17:27 | D Catone | (619) 582-1413 | City of Lemon Grove | City of Lemon Grove | 2002-08-19 08:30 | 8-19-02 11 ;00 | 10 | 1500 | 400 | 1100 | Shea Lane | Lemon Grove | 91945 | SD | 576-15 MH 02 | 0 | none | VANDALISM | MH cover stolen. Rocks, debris dropped into system | contained & pumped to downstream mh. Contractor removed rocks from mainline, rejetted, video, City crew lugged manhole lid w/cement | N | Y | N | none | none | Dirt ditch.No sign of flow at city limits | Y | N | N | none | 0 | Photo's of containment site available
x | 023016 | Fax (858) 571-6972 | 2003-01-04 17:20 | Romero Gonzalez | (760) 807-1135 | City of Escondido | City of Escondido | 2003-01-04 10:30 | 2003-01-04 14:30 | 2 | 480 | 480 | 0 | 1670 El Norte Pkwy. | Escondido | 92025 | SD | Private sewer lateral | 0 |  | PRIVATE PROPERTY | Unknown | Property owner was issued a Notice of Correction for violation of city code. | N | Y | N | none | none | Recovered and returned to system. | Y | N | N |  |  |  |  | x
x | 023017 | Fax (858) 571-6972 | 2003-01-13 09:30 | Chris Lopez | (760) 839-4323 | City of Escondido | City of Escondido | 2003-01-11 13:30 | 2003-01-11 15:30 | 0.25 | 30 | 30 | 0 | 619 S. Escondido Blvd. | Escondido | 92025 | SD | Private sewer lateral | 1 | 2002-01-16 | PRIVATE PROPERTY | Unknown | Property owner was issued a Notice of Correction for violation of city code. | N | N | N | none | none | Recovered and returned to system. | Y | N | N |  |  |  |  | x
| 023018 | Fax (858) 571-6972 | 2003-02-26 09:15 | John Vaught | (760) 839-4323 | City of Escondido | City of Escondido | 2003-02-25 16:00 | 2003-02-25 17:15 | 6 | 450 | 0 | 450 | 2080 Encino Dr. | Escondido | 92025 | SD | City manhole 2115 | 0 |  | ROCKS | During a heavy rain event, rock entered the manhole through a 8" stub and caused the main line to discharge. | The 8" stub was mechanically plugged to prevent further infiltration. | Y | Y | Y | Dead Horse Creek | Lake Hodges |  | Y | N | N
| 023019 | Fax (858) 571-6972 | 2003-02-28 11:00 | John Vaught | (760) 839-4323 | City of Escondido | City of Escondido | 2003-02-27 17:00 | 2003-02-27 19:30 | 5 | 750 | 0 | 750 | 558 Bear Valley Pkwy. | Escondido | 92025 | SD | Private sewer lateral due to main line stoppage. | 1 | 2003-02-25 | ROCKS | Rock and debris which entered the system on 2/25/03 continued to caused the main to drain slow and discharge. | City mains were cleaned, vacuumed, and inspected. The rock infiltration was sealed on 2/26/03. | Y | Y | Y | Dead Horse Creek | Lake Hodges |  | Y | N | Y | At public contact points near and through Kit Carson Park. | 3
| 023020 | Quarterly Report | 2003-03-18 11:15 | Lance Lauricha | (760) 839-4668 | City of Escondido | City of Escondido | 2003-03-18 06:58 | 2003-03-18 10:00 | 1 | 182 | 182 | 0 | 530 Chestnut St. | Escondido | 92027 | SD | City manhole 6372 | 0 |  | ROOTS | Damaged pipe with roots. | The main was inspected and will be repaired on 4/1/03. | Y | N | N | none | none | Overflow was contained and returned to system. | Y | N | N
| 023004 | Faxed RWQCB and DEH | 2003-01-13 09:40 | Thomas Howard | (858) 679-5450 | City of Poway | City of Poway | 2003-01-12 11:00 | 2003-01-12 16:00 | 2.1 | 630 | 0 | 630 | Old Coach Lift Station, TB F7 | Poway | 92064 | SD | Manhole | 0 |  | DEBRIS | Asphalt grindings obstructed the gravity main, causing debris to backup sewer main. | Blockage was cleared with Vactor unit at manhole spill site. Sewer spill trail area was washed down with potable water on dirt easement road. Recovered debris was put back into manhole/sewer main. | N | N | N | NONE | NONE | Spill disbursed into an oak tree grove. | Y | N | N |  |  | Remote public access.
| 023005 | Faxed RWQCB and DEH | 2003-04-01 15:10 | Thomas Howard | (858) 679-5450 | City of Poway | City of Poway | 2003-04-01 12:55 | 2003-04-01 13:15 | 35 | 700 | 300 | 400 | Pomerado Road and Treadwell St | Poway | 92064 | SD | Sewer Manhole | 0 |  | GREASE | Grease blockage in 8" diameter sewer main. | Will perform grease trap inspection in strip mall; put this section of main on quarterly maintenance program and video inspect for defects. | N | Y | Y | Beeler Creek | Poway Creek |  | Y | N | N
| 334335 | Fax (858) 571-6972 (RWQCB) | 2003-01-02 23:30 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2003-01-02 16:53 | 2003-01-02 17:20 | 1 | 27 | 0 | 27 | SARATOGA AV. X BACON ST. | San Diego | 92107 | SD | 6" CP | 0 |  | CONSTRUCTION | GROUP JOB IN PROGRESS. LATERALS NOT CONNECTED AND MAIN BREAK UNDER TRENCH PLATES. | VACTORING AND BYPASS PUMPING UNTIL REPAIRS CAN BE MADE. | N | N | N | None | None | DRIED IN STREET AND GUTTER. | Y | Y | N |  |  | NEED TO FOLLOW UP WITH CONTRACTOR. POSSIBLY USING POOR CONSTRUCTION PRATICES.
| 334644 | Fax (858) 571-6972 (RWQCB) | 2003-01-04 16:25 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-01-04 12:02 | 2003-01-04 13:01 | 2 | 118 | 0 | 118 | 2550 K ST | San Diego | 92102 | SD | 6" CP | 0 | 0 | GREASE | BLOCKAGE WAS CAUSED BY GREASE | No sewer seepage from cracks in street upon arrival; street dry but evidence of overflow; rodded and flushed line for city protection; heavy grease in line. Refer to area supervisor for further evaluation. | N | Y | N | None | None | DRIED IN STREET AND STORM DRAIN. | Y | Y | N
| 334665 | Fax (858) 571-6972 (RWQCB) | 2003-01-04 20:25 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-01-04 18:41 | 2003-01-04 19:15 | 1 | 34 | 0 | 34 | 4274 03RD AVE | San Diego | 92103 | SD | 8"PVC | 3 | 9/12/02; 11/14/02; 11/21/02 | LINE BREAK | UNKNOWN; STOP RELIEVED UPON ARRIVAL. | FLUSHED LINE FOR CITY PROTECTION; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
| 334697 | Fax (858) 571-6972 (RWQCB) | 2003-01-05 16:35 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-01-05 11:39 | 2003-01-05 14:00 | 100 | 14100 | 13900 | 200 | 2323 EUCLID AVE | San Diego | 92105 | SD | 8" VC | 1 | 2002-12-27 | OTHER | BLOCKAGE WAS CAUSED BY RAGS & LIGHT ROOTS | Two vactors sent to contain overflow & clean up after line was cleared by unit handrodding line.. Refer to area supervisor for further evaluation. | N | Y | N | None | None | DISSIPATED AND SOAKED INTO CANYON AREA. | Y | Y | N
| 334720 | Fax (858) 571-6972 (RWQCB) | 2003-01-05 21:20 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-01-05 19:46 | 2003-01-05 20:45 | 2 | 118 | 0 | 118 | 5029 70TH ST | San Diego | 92115 | SD | 6"VC | 1 | 2002-04-30 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS. | FLUSHED LINE TO RELIEVE BLOCKAGE; REFERRED TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
| 334931 | Fax (858) 571-6972 (RWQCB) | 2003-01-07 14:45 | Paul Anderson( OCA W.U.S.) | (858) 614-5719 | City of San Diego | City of San Diego | 2003-01-07 08:21 | 2003-01-07 09:19 | 5 | 290 | 140 | 150 | 3791 Boundary St. | San Diego | 92104 | SD | 8" vc sewer main | 0 | 0 | ROOTS | Section of main was bloked by roots and toilet paper ,Rodding truck cleared stop at 9:19 | Set up vactor to collect overflow and rodding truck cleared stop to relieve main.. | N | Y | N | None | None | Disapated in the storm drain.(Chollas Creek) | N | Y | N |  |  | Will give copy of report to area supervisor for further investigation.
| 335159 | Fax (858) 571-6972 (RWQCB) | 2003-01-08 14:35 | Paul Anderson(OCA W.U.S.) | (858) 614-5719 | City of San Diego | City of San Diego | 2003-01-08 08:15 | 2003-01-08 11:40 | 0.5 | 102.5 | 0 | 102.5 | 825 9th St. X Johnson Ave. | San Diego | 92103 | SD | 6" vc sewer main | 1 | 2002-03-04 | ROOTS | Section of main was blocked by roots and tiolet paper,Hand rodded to relieve stop at 11:40 | Overflow disapated into dirt and set up hand rod's also refer to area supervisor. | N | N | N | None | None | Disapated into dirt area around main hole. | N | Y | N |  |  | Will give copy of report to area supervisor for further investigation.
| 336541 | Fax (858) 571-6972 (RWQCB) | 2003-01-17 16:00 | Mike Rosenberg | (858) 614-5742 | City of San Diego | City of San Diego | 2003-01-15 12:05 | 2003-01-15 13:45 | 5 | 500 | 0 | 500 | La Jolla Blvd & Playa Del Sur St | San Diego | 92037 | SD | 6" CP | 0 |  | GREASE | Grease in 6" cp sewer main | Releaved grease stop with rodder and contacted cctv to televise 6" main asap. | N | Y | Y | Pacific Ocean | None | Pacific Ocean | Y | Y | Y | Bay/Lagoon/Beach | 2 | When rodder releaved grease stop it cause a surcharge from a private lateral resulting in 500 gals of sewage entering the storm drain at Neptune Pl & Gravilla St which dumps into the Pacific Ocean.Signs picked up 01/17/03
| 336697 | Fax (858) 571-6972 (RWQCB) | 2003-04-02 15:00 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2003-01-16 07:59 | 2003-01-16 12:10 | 10.5 | 2635.5 | 2500 | 135.5 | Fairmount Avenue & Home Avenue | San Diego | 92105 | SD | 8" V. C. | 0 | 0 | GREASE | Heavy grease and roots cause blockage | Rod from upand down stream manholes to clear stoppage. Vactor at surface level ro recover spill. Called contruction crews to clean heavy roots inside manhole # 397 and to strap it. | N | Y | N | None | None | Dissipated in storm drain conoveyance system | N | Y | N |  | 0 | Will be refered to area supervisor to add in a maintenance and root inhibitor program
| 336692 | Fax (858) 571-6972 (RWQCB) | 2003-01-16 12:25 | Kevin Gensler | (858) 614-4577 | City of San Diego | City of San Diego | 2003-01-16 06:55 | 2003-01-16 09:44 | 25 | 4225 | 4000 | 225 | Rue Chantemar and Rue Vincennes | San Diego | 92131 | SD | 8" PVC | 0 | 0 | PUMP STATION FAILURE | electrical failure at sps 60 | recovered 4000 galons of spill and replaced electrical relay | N | y | n | None | None | dried in canyon | y | Y | N
| 336743 | Fax (858) 571-6972 (RWQCB) | 2003-01-16 16:00 | Mike Rosenberg | (858) 614-5742 | City of San Diego | City of San Diego | 2003-01-16 11:15 | 2003-01-16 13:25 | 2 | 260 | 200 | 60 | Capricorn Wy & Westview Pwy | San Diego | 92131 | SD | 10" pvc | 0 |  | ROCKS | Rocks in 10' pvc sewer main | Relieved blockage with rodder will refer to east const to retrieve broken screw asap. | N | Y | N | None | None | Dried up in storm drain. | N | Y | N |  |  | Will give copy of sso report to area supervisor for further investigation.
| 337026 | Fax (858) 571-6972 (RWQCB) | 2003-01-17 13:00 | Mike Rosenberg | (858) 614-5742 | City of San Diego | City of San Diego | 2003-01-17 07:20 | 2003-01-17 07:45 | 5 | 125 | 0 | 125 | Andorra Wy & Del Diablo Wy | San Diego | 92128 | SD | 8" vc | 0 |  | GREASE | Grease & Roots in 8" vc pipe | Flush & vactor grease and roots from 8" vc pipe | N | Y | N | None | None | Dried up in storm drain | Y | Y | N |  |  | Will give area supervisor a copy of sso report for further investigation.
| 337290 | Fax (858) 571-6972 (RWQCB) | 2003-01-19 14:35 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-01-19 10:14 | 2003-01-19 10:50 | 5 | 180 | 0 | 180 | 1699 BLAINE AVE | San Diego | 92103 | SD | 6" VC | 0 | 0 | ROOTS | BLOCKAGE CAUSED BY ROOTS & GREASE. | FLUSHED LINE TO RELIEVE STOP; CLEANED AREA; REFERRED TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
| 337295 | Fax (858) 571-6972 (RWQCB) | 2003-01-19 15:05 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-01-19 11:48 | 2003-01-19 12:15 | 5 | 135 | 135 | 0 | 4100 35TH ST | San Diego | 92116 | SD | 6" CP | 1 | 2002-05-21 | GREASE | BLOCKAGE WAS CAUSED BY GREASE.L | FLUSHED LINE TO RELIEVE GREASE STOP; ; VACUUMED AREA & RECOVERED PUDDLED SEWAGE; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | N | N | None | None | PUDDLED IN ALLEYWAYS; VACUUMED PUDDLES. | Y | Y | N
| 337755 | Fax (858) 571-6972 (RWQCB) | 2003-01-22 03:30 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2003-01-21 23:54 | 2003-01-22 01:15 | 0.3 | 24.3 | 0 | 24.3 | 4243 INGRAHAM ST. | San Diego | 92109 | SD | 6" CP | 1 | 07 27 2002 | CONSTRUCTION | DEBRIS CATCHING ON TRANSITION FROM MAIN REPAIR AND OLD CEMENT PIPE. | TELEVISE PVC PIPE TO CONNECTION POINT WITH OLD CEMENT PIPE. MAIN SCHEDULED FOR RENEWAL. | N | N | N | None | None | DRIED AT SAND BAGS AT STORM DRAIN ON REED ST. | Y | Y | N
| 338566 | Fax (858) 571-6972 (RWQCB) | 2003-01-26 22:50 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-01-26 20:12 | 2003-01-26 21:00 | 1 | 48 | 48 | 0 | 5940 UNIVERSITY AVE | San Diego | 92115 | SD | 6"VC | 1 | 2002-10-19 | GREASE | BLOCKAGE WAS CAUSED BY GREASE | FLUSHED LINE TO RELIEVE STOP;VACTORED & RECOVERED TOTAL SPILL; CLEANED AREA; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM | Y | Y | N
| 338706 | Fax (858) 571-6972 (RWQCB) | 2003-01-27 18:00 | Matt Hauer | (858) 654-4155 | City of San Diego | City of San Diego | 2003-01-27 14:00 | 2003-01-27 15:00 | 1 | 60 | 0 | 60 | 12101 Lake Dr. | San Diego | 92025 | SD | 20" DI | 0 |  | OTHER | Leak on valve inside station | Repair valve | N | N | N | None | None | soaked into ground outside station | Y | Y | N
| 338854 | Fax (858) 571-6972 (RWQCB) | 2003-01-27 21:00 | MATT HAUER | (858) 654-4130 | City of San Diego | City of San Diego | 2003-01-27 14:30 | 2003-01-27 14:30 | 500 | 500 | 500 | 0 | 9150 TOPAZ WAY | San Diego | 92123 | SD | VACTOR | 0 |  | OTHER | OPERATOR ERROR OF VACTOR TRUCK CAUSING REAR DOOR TO OPEN | 100% OF SPILL RECOVERED. CLEANED AREA BY FLUSHING DOWN WITH WATER. | N | N | N | None | None | CONTAINED BY VACTOR IN GUTTER | Y | Y | N
| 340215 | Fax (858) 571-6972 (RWQCB) | 2003-02-01 13:30 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-02-01 08:34 | 2003-02-01 09:25 | 1 | 51 | 30 | 21 | FIR & GRANADA | San Diego | 92102 | SD | 8" UNK | 1 | 2002-03-27 | OTHER | HEAVY SAND. | FLUSHED LINE TO RELIEVE STOP BY HEAVY SAND; POSSIBLE BREAK; REFER TO STBY TO TV LINE. VACUUMD AND CLEANED AREA. | N | N | N | None | None | RECOVER 30 GAL;REMAINDER SOAKED INTO DIRT. | Y | Y | N
| 340416 | Fax (858) 571-6972 (RWQCB) | 2003-02-04 17:15 | Jeff Wilder | (858) 614-5770 | City of San Diego | City of San Diego | 2003-02-03 12:30 | 2003-02-03 19:00 | 2 | 780 | 600 | 180 | 3645 Brant St. | San Diego | 92103 | SD | 6" cp | 2 | 07/23/2002, 04/09/2002 | OTHER | Boken screw in main caused stoppage | unit 715 handrod main to remove broken screw and relieved stop. Will refer to clean main further. | N | y | n | None | None | dissapated in storn drain | y | Y | N
| 341584 | Fax (858) 571-6972 (RWQCB) | 2003-02-09 18:50 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-02-09 14:03 | 2003-02-09 14:35 | 10 | 320 | 0 | 320 | S 13TH ST & COMMERCIAL ST | San Diego | 92101 | SD | 8'VC | 1 | 2002-04-09 | CONSTRUCTION | Blockage caused by rags in line; | Flusher set up containment upon arrival; Rodder relieved stop caused by rags; Refer to area supervisor for further evaluation. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | N | Y | N
| 341739 | Fax (858) 571-6972 (RWQCB) | 2003-02-10 21:30 | MATT HAUER | (858) 654-4130 | City of San Diego | City of San Diego | 2003-02-10 17:39 | 2003-02-10 18:45 | 15 | 990 | 600 | 390 | 1743 MIDVALE DRIVE | San Diego | 92105 | SD | 8" VC MAIN | 1 | 2002-09-23 | ROOTS | ROOT BLOCKAGE IN MAIN 115' DOWNSTREAM OF MH 202. | FLUSHED MAIN TO RELIEVE ROOT STOP. FLUSHED TWO SECTIONS UP AND DOWN FROM STOPPAGE SECTION. | N | Y | N | None | None | DRIED UP IN STORM CHANNEL | Y | Y | N
| 342035 | Fax (858) 571-6972 (RWQCB) | 2003-02-12 16:00 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2003-02-12 13:20 | 2003-02-12 14:52 | 1.2 | 110.4 | 0 | 110.4 | 4424 Kansas Street | San Diego | 92104 | SD | 8" V.C. | 0 | 0 | GREASE | Heavy grease caused Manhole # 168 spill | Flushed main to releive stoppage, will be referred to area supervisor and to FEWD for further investigation. | Y | Y | N | None | None | Diluted in storm drain with heavy rain | Y | Y | N |  | 0 | Manhole was overflowing intermitently, and rain was very heavy at the time of spill.
| 342003 | Fax (858) 571-6972 (RWQCB) | 2003-02-12 11:45 | Mike Rosenberg | (858) 614-5742 | City of San Diego | City of San Diego | 2003-02-12 08:15 | 2003-02-12 09:00 | 5 | 225 | 0 | 225 | 6425 Lake Shore Dr | San Diego | 92119 | SD | 8" vc pipe | 0 |  | ROOTS | Heavy roots in 8" vc pipe | Machine rodded roots out of 8" vc pipe two sections up & down. | Y | Y | Y | None | None | Dissipated in V trench around Lake Murray | Y | Y | N |  |  | Per County Heath not a 7-35, did not reach public waters. Will give copy of report to area supervisor for futher investigation
| 342154 | Fax (858) 571-6972 (RWQCB) | 2003-02-13 12:30 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2003-02-13 09:30 | 2003-02-13 10:15 | 9 | 405 | 300 | 105 | South 16th Street & Newton Avenue | San Diego | 92101 | SD | 8" Lined | 2 | April 09, 2002 - May 15, 2002 | CONSTRUCTION | Sanitary toilet paper caused stoppage | Vactored to recover spill. Rodded to releive blockage. Will refer to area supervisor to add on a three months routine maintenance. | Y | Y | N | None | None | Dissipated in storm drain conveyance system | N | Y | N |  | 0 | Spill was running intermitently from 8 to 9 GPM. This sewer lines are in a CIP job program. Resident Engineer is Dick Giron.
| 342587 | Fax (858) 571-6972 (RWQCB) | 2003-02-16 21:40 | D.BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-02-16 19:34 | 2003-02-16 20:20 | 1 | 31 | 0 | 31 | 1420 GOLDEN GATE DR | San Diego | 92116 | SD | 6"PVC | 0 | 0 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS& HEAVY PAPER. | MACHINE RODDED TO RELIEVE STOP; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
| 342650 | Fax (858) 571-6972 (RWQCB) | 2003-02-26 15:00 | Mike Rosenberg | (858) 614-5742 | City of San Diego | City of San Diego | 2003-02-18 06:17 | 2003-02-18 11:30 | 150 | 46950 | 46950 | 0 | Atoll St & Frakes St | San Diego | 92111 | SD | 10" VC | 0 |  | ROCKS | Rocks in 10" vc main | Machine rodded rocks out of 10" main to relieve stop and captured 15750 gals of sewage with vactor. IP3 captured the remaining sewage. | N | Y | Y | Tecolote Creek | none | IP 3 storm water interceptor. | Y | Y | Y | Bay/Lagoon/Beach, creek | 5 | Mission bay was posted as a precaution until test results are returned. Test results indicate that no sewage reached the bay.SR# 345645 is the same 7/33 Will give copy of sso report to area supervisor for further investigation.
| 343221 | Fax (858) 571-6972 (RWQCB) | 2003-02-20 12:30 | Mike Rosenberg | (858) 614-5742 | City of San Diego | City of San Diego | 2003-02-20 08:46 | 2003-02-20 09:19 | 3 | 99 | 0 | 99 | Mt Alifan Dr.& Mt Bernard Ave. | San Diego | 92111 | SD | 8" vc pipe | 0 |  | OTHER | Old 8" screw in 8" vc main. | Machine rodded main to retrieve screw from main will also flush two sections up & down. | N | Y | N | None | None | Dissapated in the storm drain. | Y | Y | N |  |  | Will give copy of report to area supervisor for further investigation.
| 344037 | Fax (858) 571-6972 (RWQCB) | 2003-02-26 15:30 | Mike Rosenberg | (858) 614-5742 | City of San Diego | City of San Diego | 2003-02-25 08:37 | 2003-02-25 09:30 | 2 | 106 | 106 | 0 | Bayside Ln.& San Fernando Pl. | San Diego | 92109 | SD | 21" V.C. | 0 |  | ROOTS | Infiltration of rain water caused the sewer main to surcharge resulting in an overflow. It is believed that citizens have opened manholes and otherwise interoduced stormwater flows upstream of PS 11." | Vactored sewage from around manhole and MWWD staff is now investigating methods to bolt down select m/hs with pentabolts upstream of PS 11." | Y | N | N | None | None | Captured by Vactor. | Y | Y | N |  |  | Working with pump crews we were able to get the sewage back into the system, will give copy of report to area supervisor for further investigation.
| 344758 | Fax (858) 571-6972 (RWQCB) | 2003-03-01 16:00 | D. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-03-01 09:43 | 2003-03-01 10:35 | 5 | 260 | 0 | 260 | MISSION CENTER RD. & SEVAN CT. | San Diego | 92123 | SD | 8" PVC | 0 | 0 | LINE BREAK | REMOVED SOME ROOTS; UNABLE TO DETERMINE ACTUAL CAUSE; POSSIBLE MAIN BREAK | CONTAINED OVERFLOW WITH VACTOR; MACHINE RODDED TO RELIEVE STOP; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | Y | Y | N | None | None | DISSIPATED IN SYSTEM. | Y | Y | N
| 344782 | Fax (858) 571-6972 (RWQCB) | 2003-03-01 20:00 | G. SIAUMAU | (858) 614-5770 | City of San Diego | City of San Diego | 2003-03-01 15:44 | 2003-03-01 16:30 | 0.25 | 11.5 | 0 | 11.5 | 7533 MIRAMAR AV. | San Diego | 92037 | SD | 8"VC | 1 | 2002-08-02 | ROOTS | BLOCKAGE CAUSED BY ROOTS | FLUSHED/ MACHINE ROD TO RELIEVE STOPPAGE. REFERED TO AREA SUPERVISOR FOR FURTHER EVALUATION.. | Y | N | N | None | None | DRIED AROUND MANHOLE. | Y | Y | N
| 344823 | Fax (858) 571-6972 (RWQCB) | 2003-03-02 12:20 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-03-02 08:30 | 2003-03-02 10:15 | 2 | 210 | 0 | 210 | 1315 47TH ST | San Diego | 92113 | SD | 6"VC | 0 | 0 | OTHER | BLOCKAGE CAUSED BY ROOTS & RAGS. | CREW LOCATED UPON ARRIVAL TO MAINTENANCE LINE ; HANDRODDED TO RELIEVE STOP; REFERRED TO AREA SUPERVISOR FOR FURTHER EVALUATION. | Y | N | N | None | None | SOAKED INTO GROUND AROUND EASEMENT M/H. | Y | Y | N
| 345055 | Fax (858) 571-6972 (RWQCB) | 2003-03-04 02:00 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2003-03-03 21:47 | 2003-03-03 22:15 | 150 | 150 | 50 | 100 | 4815 VOLTAIRE ST. | San Diego | 92107 | SD | 6" CP | 0 |  | FLOOD DAMAGE | MAIN BREAK ON 6" CP PIPE. | VACTORED TO CONTAIN OVERFLOW. RODDED MAIN TO RESTORE PARTIAL FLOW. CALLED FOR CONSTRUCTION CREW TO REPAIR MAIN. CLEANED ALLEY. | N | N | N | None | None | DRIED IN GUTTER AT NE CORNER MUIR ST. X BACON ST. | Y | Y | N
| 345139 | Fax (858) 571-6972 (RWQCB) | 2003-03-04 23:00 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2003-03-04 16:04 | 2003-03-04 16:28 | 1 | 36 | 10 | 26 | S. 16TH ST. X NEWTON AVE. | San Diego | 92113 | SD | 6" VC | 2 | 04/09/2002, 02/09/2003 | CONSTRUCTION | CONTRACTOR BYPASS SYSTEM PARTIALLY FAILED CAUSING BLOCKAGE. | VACTORED CONTRACTORS TRENCH. CONTRACTOR CLEANED BYPASS PIPES TO RESTORE FLOW. VACTORED OVERFLOW TO CONTAIN. RODDED MAIN. | N | Y | N | None | None | 1/2 GAL. WENT INTO DRY STORM BOX. THE REST DRIED IN STREET. | Y | Y | N |  |  | CONTRACTOR IS BRH-GARVER, INC.
| 346183 | Fax (858) 571-6972 (RWQCB) | 2003-03-11 15:15 | Paul Anderson(OCA WUS) | (858) 614-5719 | City of San Diego | City of San Diego | 2003-03-11 10:00 | 2003-03-11 11:30 | 2 | 180 | 150 | 30 | 39th and Juniper | San Diego | 92105 | SD | 8" vc pipe | 2 | 10/19/2002 , 01/26/2003 | FLOOD DAMAGE | Main break on 8" vc pipe | Set up vactor to contain spill and flushed main to relieve stop, then called construction crew to repair break. | N | n | n | None | None | Sewer water dissipated into dirt. | N | Y | N |  |  | Overflow was coming out of broken pipe between M/H #89 to M/H #91.
| 346577 | Fax (858) 571-6972 (RWQCB) | 2003-03-13 14:00 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2003-03-13 10:07 | 2003-03-13 12:15 | 0.4 | 51.2 | 0 | 51.2 | 4336 Goldfinch Street | San Diego | 92103 | SD | 6" C.P. | 1 | 2002-08-29 | ROOTS | Stoppage was caused by heavy roots in 6" C.P. Main | Hand rod from d/s manhole in canyon to releive stoppage. Will refer to area supervisor to add on a routine maintenance. | N | N | N | None | None | Sewer water dissipated into canyon grounds. | Y | Y | N |  | 0 | Spill was coming from u/s manhole into canyon intermitently.
| 346980 | Fax (858) 571-6972 (RWQCB) | 2003-03-15 10:15 | G. SIAUMAU | (858) 614-5770 | City of San Diego | City of San Diego | 2003-03-15 07:21 | 2003-03-15 07:55 | 1 | 34 | 0 | 34 | 1511 REGULUS STREET | San Diego | 92111 | SD | 8"VC | 0 | 0 | ROOTS | ROOTS IN MAIN | MACHINE RODDED TO RELIEVE STOP. CLEANED AREA. REFERRED TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN | Y | Y | N
| 347065 | Fax (858) 571-6972 (RWQCB) | 2003-03-16 20:00 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-03-16 18:24 | 2003-03-16 18:55 | 1 | 31 | 0 | 31 | 3707 COLUMBIA ST | San Diego | 92103 | SD | 6" UNK | 2 | 6-6-2002 7-8-2002 | LINE BREAK | UNKNOWN; STOP RELIEVED ITSELF UPON ARRIVAL. | RODDED MAIN FOR CITY PROTECTION; CLEANED AREA; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | Y | Y | N | None | None | DISSIPATED IN STORM DRAIN. | N | Y | N
| 347706 | Fax (858) 571-6972 (RWQCB) | 2003-03-19 21:45 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2003-03-19 17:45 | 2003-03-19 18:10 | 2 | 50 | 0 | 50 | WIGHTMAN ST. X ALTADENA AVE. | San Diego | 92105 | SD | 8" VC | 0 |  | ROOTS | ROOTS GROWING IN CITY SEWER MAIN. | FLUSHED TO RELIEVE BLOCKAGE. CLEANED 2 SECTIONS UPSTREAM AND 2 SECTIONS DOWNSTREAM. REFER MAIN TO BE TELEVISED. | N | Y | N | None | None | DRIED IN DIRT STORM CHANNEL JUST BEYOND STORM BOX. | Y | Y | N |  |  | MAIN BLOCKAGE RELIEVED ITSELF BEFORE CREWS ARRIVED.
| 347846 | Fax (858) 571-6972 (RWQCB) | 2003-03-20 11:20 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2003-03-20 06:36 | 2003-03-20 08:05 | 1.5 | 133.5 | 0 | 133.5 | 4461 Alamo Drive. | San Diego | 92115 | SD | 6" C. P. | 2 | 05/16/2002 - 12/17/2002 | ROOTS | Heavy roots. Rags and sanitary debris caused blockage. | Hand rod main from d/s manhole to releive stoppage. Will refer to area supervisor to add on a routine maintenance. | N | N | N | None | None | Sewer water dissipated into ground | N | Y | N |  | 0 | Sewer dissipated in back yard grounds of 4461 Alamo Drive.
| 348099 | Fax (858) 571-6972 (RWQCB) | 2003-03-21 19:30 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-03-21 18:19 | 2003-03-21 18:55 | 1.5 | 54 | 0 | 54 | PENDLETON ST & ROMNEY | San Diego | 92109 | SD | 8"VC | 0 | 0 | ROOTS | Blockage caused by heavy roots | Flushed line to relieve stop; cleaned area; refer to area supervisor for further evaluation. | N | Y | N | None | None | Interceptor I- 9 | N | Y | N
| 348294 | Fax (858) 571-6972 (RWQCB) | 2003-03-24 14:30 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2003-03-24 09:25 | 2003-03-24 11:30 | 2 | 250 | 0 | 250 | 5987 Baja Drive and Campanille | San Diego | 92115 | SD | 8" V.C. | 4 | 04/08/2002 - 07/07/2002 - 07/17/2002 - 09/04/2002. | ROOTS | Heavy Roots and Rags caused spill | Machine rod to relieve spill. Will refer to area supervisor to add on a routine mintenance program | N | N | N | None | None | Dissipated in canyon grounds | Y | Y | N |  | 0 | Spill was going to canyon grounds. Machine rod to clear stoppage from u/s manhole # 527 thru MH# 285 to manhole # 270
| 348657 | Fax (858) 571-6972 (RWQCB) | 2003-03-25 15:00 | Stanley Harvey | (858) 614-5742 | City of San Diego | City of San Diego | 2003-03-25 09:45 | 2003-03-25 10:25 | 5 | 175 | 175 | 0 | 2204 Torrey Pines Rd | San Diego | 92037 | SD | 8" VC | 1 | 2002-06-18 | ROCKS | rocks,dirts and rags caused the problemin manhole. | Roded and flush main clean. | N | N | N | None | None |  | N | Y | N |  | 0 | Clean 2 section up and down
| 348751 | Fax (858) 571-6972 (RWQCB) | 2003-03-25 20:30 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2003-03-25 16:23 | 2003-03-25 18:00 | 1 | 97 | 97 | 0 | 3627 44TH ST. | San Diego | 92105 | SD | 8" VC | 0 |  | GREASE | HEAVY GREASE IN MAIN. | VACTORED AND FLUSHED MAIN. CLEAN 2 SECTIONS UPSTREAM AND TWO SECTIONS DOWNSTREAM. TELEVISE MAIN. | N | N | N | None | None | PUDDLED IN ALLEY 300' DOWN FROM MH 9. | Y | Y | N |  |  | MH 9 OVERFLOWED WHEN RODDING TRUCK BROKE A HEAVY GREASE BLOCKAGE. ALL SEWAGE RECOVERED.
| 348978 | Fax (858) 571-6972 (RWQCB) | 2003-03-26 19:30 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2003-03-26 16:19 | 2003-03-26 16:50 | 75 | 75 | 0 | 75 | CAM BERDECIO X CAM DEGRAZIA | San Diego | 92111 | SD | 18" CI | 0 |  | CONSTRUCTION | CONTRACTORS BYPASS PUMP DID NOT KEEP UP WITH THE VOLUME OF FLOW ON THE MAIN. | CONTRACTOR INCREASED THE RPMs ON BYPASS PUMP. | N | Y | N | None | None | DRIED IN STORM PIPE AT FRIARS RD | Y | Y | N |  |  | ESTIMATE OF SPILL VOLUME IS BY CITY RESIDENT ENGINEER ISIDRO ALLENDE, ON THE JOB SITE.
| 349117 | Fax (858) 571-6972 (RWQCB) | 2003-03-26 23:45 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2003-03-26 21:43 | 2003-03-26 22:45 | 2 | 124 | 60 | 64 | JUAN ST X MASON ST | San Diego | 92104 | SD | 6" CP | 0 |  | OTHER | RAGS AND GREASE BLOCKAGE ON SEWER MAIN. | VACTORED OVERFLOW. RODDED DE MAIN TO RELEIVE BLOCKAGE. WILL REFER TO HAVE 2 DOWN STREAM SECTIONS CLEANED. REFER TO HAVE MAIN TELEVISED. | N | Y | N | None | None | DRIED IN STORM DRAIN ON CONGRESS ST. | Y | Y | N
| 349121 | Fax (858) 571-6972 (RWQCB) | 2003-03-27 05:00 | RICK DONAHUE | (858) 654-4155 | City of San Diego | City of San Diego | 2003-03-27 02:30 | 2003-03-27 02:40 | 100 | 100 | 0 | 100 | 3259 LA JOLLA VILLAGE DR. | San Diego | 92122 | SD | 18" VC | 0 | N/A | CONSTRUCTION | CONTRACTOR SEWER BYPASS PLUG STUCK IN MAIN. | REMOVED PLUG, RESTORED SEWER PUMP STATION TO FULL OPERATION. CLEANED AREA. | N | Y | N | None | None | DISSPATED IN STORM DRAIN SYSTEM | Y | Y | N
| 349439 | Fax (858) 571-6972 (RWQCB) | 2003-03-28 15:00 | Stanley Harvey | (858) 614-5742 | City of San Diego | City of San Diego | 2003-03-28 08:06 | 2003-03-28 11:15 | 15 | 2400 | 2400 | 0 | Mira Lago | San Diego | 92131 | SD | 8" PVC | 0 |  | GREASE | GREASE IN MAIN AND ROOTS IN MANHOLE | Flush main and call confine space to remove roots from manhole #03 and FSN114686 | N | Y | N | None | None | Dry up in storm drain | N | Y | N |  | 0
| 349621 | Fax (858) 571-6972 (RWQCB) | 2003-04-01 20:00 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2003-03-29 08:37 | 2003-03-29 10:15 | 100 | 9800 | 4500 | 5300 | BLACK MOUNTAIN RD./ BABAUTA RD. | San Diego | 92129 | SD | 10"VC | 0 | 0 | LINE BREAK | Blockage caused by rocks thrown into manhole. Blockage caused by rocks thrown into manhole. | 719- Flusher set up containment, 718- Flusher, High Lined hose and relieved stop caused by rocks thrown into manhole, Due to vandalism. Confined space entry to remove rocks. Locked down manhole cover.8791 and Standby units posted signs,Also filed police | N | Y | Y | Penasquitos Creek | Penasquitos Lagoon |  | Y | Y | Y | Bay/Lagoon/Beach |  | Posted signs from Black Mountain Rd. along Penasquitos creek, to Penasquitos lagoon, and Torrey Pines State Beach. REMOVED 3 SIGNS AT PENASQUITOS CREEK AND 7 AT PENASQUITOS LAGOON AND TORREY PINES BEACH ON 4-1-2003.
| 349736 | Fax (858) 571-6972 (RWQCB) | 2003-04-01 07:45 | Terrell D Powell | (858) 654-4133 | City of San Diego | City of San Diego | 2003-03-31 10:15 | 2003-03-31 11:05 | 2 | 100 | 0 | 100 | 5838 Agee St. | San Diego | 92122 | SD | 8"VC | 0 |  | ROOTS | Roots in 8" VC sewer main. | Rodded 8" VC sewer main, removed heavy roots. | N | N | N | None | None | Dissapated in property. | N | Y | N |  |  | Will give copy of report to area supervisor for further investigation, claims will clean pool and other area's on property.
| 349780 | Fax (858) 571-6972 (RWQCB) | 2003-04-01 09:00 | Terrell D Powell | (858) 654-4133 | City of San Diego | City of San Diego | 2003-03-31 19:30 | 2003-03-31 20:30 | 25 | 1500 | 450 | 1050 | 1856 Manzana | San Diego | 92139 | SD | 8"PVC | 0 | 0 | GREASE | Heavy Grease in 8" PVC sewer main. | Flushed 2 sections up and 2 sections down to clear stoppage. | N | N | N | None | None | Captured by Vactor in Right of way area. | Y | Y | N |  |  | Will give copy to area supervisor for further investigation.
| 350044 | Fax (858) 571-6972 (RWQCB) | 2003-04-02 11:50 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2003-04-02 08:12 | 2003-04-02 09:41 | 5 | 440 | 400 | 40 | 1826 Bancroft Street | San Diego | 92102 | SD | 8" C.P. | 3 | 09/16/2002 - 09/19/2002 - 11/18/2002. | ROOTS | Very heavy roots caused stoppage. | Machine rodded to relieve stoppage at 240' from D/S manhole number 81. Vactored spill next to storm drain preventing it to get into channel. Will refer to area supervisor for more frequent maintanence and cleaning untill replacement starts. | N | Y | N | None | None | Dissipated in storm drain conveyance system. | N | Y | N |  | 0 | Spill was contained at 8:41 before entering storm drain.
| 350531 | Fax (858) 571-6972 (RWQCB) | 2003-04-04 12:40 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2003-04-04 08:48 | 2003-04-04 10:05 | 0.5 | 38.5 | 10 | 28.5 | 2281 Whitman Street | San Diego | 92103 | SD | 8" C.P. | 1 | 2002-05-30 | ROOTS | Heavy roots in main caused spill. | Vactored at surface level to recover spill. Machine rod to clear stoppage. Will refer to area supervisor to add on a routine maintenance program, also to be televised. | N | Y | N | None | None | Dissipated in storm drain conveyance system. | Y | Y | N |  | 0 | Walked down to locate D/S Manhole # 306 in canyon and did the cleaning inside this manhole.
| 350600 | Fax (858) 571-6972 (RWQCB) | 2003-04-05 12:45 | D. A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-04-04 16:46 | 2003-04-04 20:45 | 1 | 239 | 0 | 239 | 1052 LINCOLN AVE | San Diego | 92103 | SD | 6"VC | 1 | 2003-01-08 | ROCKS | STOP CAUSED BY ROCKS AND ROOTS. | DIVERTED FLOW OF SEWAGE INTO DOWNSTREAM M/H IN CANYON; RETURNED IN AM; HAD CALTRANS SHUT DOWN RAMP TO TRAFFIC; SET UP FLUSHER & HY-LINED HOSE TO RELIEVE ROCK& MINOR ROOT STOP. REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN SYSTEM. | Y | Y | N
| 350705 | Fax (858) 571-6972 (RWQCB) | 2003-04-05 17:25 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-04-05 12:25 | 2003-04-05 14:05 | 5 | 500 | 0 | 500 | 3606 08TH AVE | San Diego | 92103 | SD | 6"VC | 1 | 2003-08-27 | ROOTS | BLOCKAGE CAUSED BY ROOTS. | HANDROD LINE IN CANYON TO RELIEVE ROOT STOP. REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | N | N | None | None | SOAKED INTO CANYON. | Y | Y | N |  |  | M/H OVERFLOWING IS NOT SHOWN IN GATEBOOK OR ON COMPUTER. IT IS LOCATED BTWN M/H 481 & 482.
| 350711 | Fax (858) 571-6972 (RWQCB) | 2003-04-05 17:50 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-04-05 13:21 | 2003-04-05 15:45 | 0.5 | 72 | 0 | 72 | 4445 LOGAN ST | San Diego | 92113 | SD | 6" VC | 1 | 2002-06-08 | ROCKS | BLOCKAGE WAS CAUSED BY ROCKS & RAGS. | HY-LINED HOSE TO FLUSH EASEMENT LINE & RELIEVE STOP. CONTACT CLAIMS PER CONSUMER FOR SEWAGE IN BACKYARD; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | N | N | None | None | PUDDLED AROUND M/H IN BACKYARD | N | Y | N
| 350758 | Fax (858) 571-6972 (RWQCB) | 2003-04-06 16:05 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-04-06 11:55 | 2003-04-06 13:10 | 3 | 210 | 0 | 210 | CALLE CRISTOBAL & CAM SANTA FE (TOP OF CYN) | San Diego | 92126 | SD | 8"PVC | 0 | 0 | LINE BREAK | vandalism; rocks; chunks of cement & debris. | Vactored m/h down & relieved stop with fork & bar; cleaned rocks & chunks of cement from m/h; refer to area supervisor for further evaluation. | N | N | N | None | None | SOAKED INTO SIDE OF CANYON. | Y | Y | N
| 350859 | Fax (858) 571-6972 (RWQCB) | 2003-04-08 10:30 | Mike Rosenberg | (858) 614-5742 | City of San Diego | City of San Diego | 2003-04-07 13:25 | 2003-04-07 14:45 | 1 | 80 | 80 | 0 | 5021 Maynard St. | San Diego | 92117 | SD | 8"PVC | 2 | 10/19/02 01/26/03 | ROOTS | Heavy roots in 8"pvc pipe. | Machine rodded heavy roots out of 8"pvc pipe and vactored 80 gal of sewage out of storm drain. | N | Y | N | None | None | Vactored up sewage from storm drain | N | Y | N |  |  | Will give copy of report to area supervisor for futher investigation.
| 351445 | Fax (858) 571-6972 (RWQCB) | 2003-04-16 14:15 | Jeff Wilder | (858) 614-5770 | City of San Diego | City of San Diego | 2003-04-10 09:00 | 2003-04-10 10:45 | 6 | 270 | 270 | 0 | 2580 Via Barletta | San Diego | 92037 | SD | 8"VC | 0 |  | ROOTS | Roots in manhole | Rod main to clear problem | N | N | N | None | None | Vactored to capture all overflow from gutter | N | Y | N |  | 0 | Original report was under SR#351469. Corrections made to data base on 4-16-03.
| 351450 | Fax (858) 571-6972 (RWQCB) | 2003-04-29 14:20 | Mike Rosenberg | (858) 614-5742 | City of San Diego | City of San Diego | 2003-04-10 09:40 | 2003-04-10 11:50 | 15 | 1950 | 1950 | 0 | Genesee Ave. & 52 Fwy | San Diego | 92117 | SD | 10"vc pipe | 2 | 10/19/2002 & 01/26/2003 | ROOTS | Heavy roots in m/h # 183. | Highlined flusher hose to manhole # 183 to relieve stop in manhole. | N | N | Y | San Clemente Creek | None | Sewage was captured by IPS 1 | Y | Y | Y | Canyon | 3 | Canyon Access will clear and expose around manhole # 183 and west construction will remove concrete cap from manhole # 230 so we can clean and televise 10" main. Per County Health will post signs for 72 hrs.
| 351667 | Fax (858) 571-6972 (RWQCB) | 2003-04-29 14:00 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-04-11 15:44 | 2003-04-11 19:30 | 30 | 6780 | 6780 | 0 | GENESEE AVE & SR 52 EB | San Diego | 92122 | SD | 10"VC | 1 | 2003-04-07 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS | OVERFLOW CONTAINED; CREWS PUMPING OVERFLOW BACK INTO MANHOLE; WORK CONTINUES ON THE LINE. OVERFLOW AMOUNT INTO CREEK PRIOR TO CONTAINMENT WILL EVENTUALLY REACH INTERCEPTOR 1 AND RE-ENTER THE SEWER SYSTEM AT THAT POINT. | N | Y | Y | SAN CLEMENTE CANYON CREEK | ROSE CREEK | MISSION BAY SEWER INTERCEPTOR I-1 | Y | Y | Y |  | 3
| 351945 | Fax (858) 571-6972 (RWQCB) | 2003-04-13 12:15 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-04-12 15:36 | 2003-04-13 10:05 | 0.05 | 55.45 | 0 | 55.45 | 758 CORDOVA ST | San Diego | 92107 | SD | 6"CP | 1 | 2002-10-14 | ROCKS | BLOCKAGE CAUSED ROCKS & SAND; POSSIBLE BREAK. | Investigate; previous EO1 experienced an error in judgement; Unit 724 noted no 7-33; 7-31 out of ground and surfacing at m/h332 causing appearance of 7-33; sewage was surfacing at and re-entering m/h with minor seepage excaping; unit machine rodded. | Y | N | N | None | None | DRIED IN STREET. | Y | Y | N |  |  | Unit noticed sinking area in alley; possible break on line; tv crew was called to televise& inspect line.
| 352374 | Fax (858) 571-6972 (RWQCB) | 2003-04-16 11:40 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-04-16 08:06 | 2003-04-16 08:42 | 0.5 | 18 | 0 | 18 | 1534 MONMOUTH DR | San Diego | 92109 | SD | 6"CP | 0 | 0 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS. | M/H NOT OVERFLOWING UPON ARRIVAL; HANDRODDED TO RELIEVE STOP CAUSED BY ROOTS; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | N | N | None | None | DRIED UP ON PRIVATE PROPERTY. | Y | Y | N
| 352891 | Fax (858) 571-6972 (RWQCB) | 2003-04-20 12:10 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-04-20 10:43 | 2003-04-20 11:12 | 5 | 145 | 145 | 0 | 4331 42ND ST | San Diego | 92105 | SD | 6"VC | 2 | 4-23-02 & 9-18-02 | GREASE | BLOCKAGE CAUSED BY GREASE. | RELIEVED STOP WITH FLUSHER; RECOVERED ALL SPILLED SEWAGE AND CLEANED ALLEY THAT CONTAINED IT; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | N | N | None | None | CONTAINED IN ALLEY; VACTOR RECOVERED TOTAL AMOUNT. | Y | Y | N
| 319506 | Fax (858) 571-6972 (RWQCB) | 2003-04-30 10:20 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-04-29 13:30 | 2003-04-29 14:30 | 5 | 300 | 0 | 300 | BOUNTY ST & SPEARS ST (IN CANYON) | San Diego | 92120 | SD | 8"VC | 0 | 0 | CONSTRUCTION | TRENCH FAILURE DURING REPAIR CAUSED M/H TO OVERFLOW. | UNIT 602 REPAIRED PIPE AND REVERTED FLOW BACK INTO SYSTEM. | N | N | N | None | None | SOAKED INTO DIRT AROUND M/H AREA. | Y | Y | N
| 354877 | Fax (858) 571-6972 (RWQCB) | 2003-05-03 12:45 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-05-03 11:05 | 2003-05-03 11:45 | 5 | 200 | 0 | 200 | 3796 WARD RD | San Diego | 92116 | SD | 8"CP | 0 | 0 | GREASE | BLOCKAGE WAS CAUSED BY GREASE. | FLUSHED LINE TO RELIEVE GREASE STOP. REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | Y | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
| 354929 | Fax (858) 571-6972 (RWQCB) | 2003-05-04 20:45 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-05-04 18:14 | 2003-05-04 18:50 | 2 | 72 | 0 | 72 | 4318 5TH AVE | San Diego | 92103 | SD | 8"VC | 0 | 0 | LINE BREAK | RELIEVED BLOCKAGE WITH FORK; UNABLE TO DETERMINE CAUSE OF STOP | RELIEVED STOP WITH FORK; UNABLE TO DETERMINE WHAT CAUSED THE M/H STOP; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | Y | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
| 355271 | Fax (858) 571-6972 (RWQCB) | 2003-05-13 10:00 | Stanley Harvey | (858) 614-5742 | City of San Diego | City of San Diego | 2003-05-07 07:00 | 2003-05-07 09:15 | 150 | 9150 | 2000 | 7150 | 2656 Bayside Walk | San Diego | 92109 | SD | 12"PVC | 2 | 10/17/2002 1/26/2003 | FLOOD DAMAGE | Forced main clean out cap blew off. Revised amount of spill due to engineer calculations. | Repair cap. | N | N | Y | Mission bay | None |  | N | Y | Y | Bay/Lagoon/Beach | 5 | Per County Health, Clay Clifton, picked up signs on 05/12/2003.
| 355634 | Fax (858) 571-6972 (RWQCB) | 2003-05-09 15:00 | Marcelino Oregel | (858) 614-5716 | City of San Diego | City of San Diego | 2003-05-09 10:30 | 2003-05-09 10:50 | 12.5 | 250 | 130 | 120 | Montezuma Rd. & Yerba Santa Drive | San Diego | 92115 | SD | 8" V.C. | 2 | 05/27/2002 - 11/23/2002 | ROOTS | Very heavy roots caused main brake. | Vactor at surface level to contained spill. Construction crews made pipe repairs. Called street sweeper to clean debris and dirt on street. Clean up and desinfected area. | N | Y | N | None | None | Dissipated in storm drain convance system. | Y | Y | N |  | 0 | Construction crews did confined space entry to remove roots and broken rod inside manhole.
| 356965 | Fax (858) 571-6972 (RWQCB) | 2003-05-19 14:00 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2003-05-19 11:40 | 2003-05-19 12:45 | 1.5 | 97.5 | 0 | 97.5 | Intersection Boundary & Haller Streets | San Diego | 92105 | SD | 10" V.C. | 2 | 08/01/2002 - 03/11/2003 | GREASE | Heavy grease, debris and rocks caused spill. | Flushed main to relieve heavy grease blockage. Will refer to area supervisor to add in a routine maintenance program and also to televise section of main under HWY 1-15. | N | N | N | None | None | Dissipated in creek grounds | Y | Y | N |  | 0 | Sewer was running intermitently. Clean up area.
| 357190 | Fax (858) 571-6972 (RWQCB) | 2003-05-21 00:20 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2003-05-20 18:49 | 2003-05-20 20:15 | 4 | 344 | 344 | 0 | 731 BRIGHTON CT. | San Diego | 92109 | SD | 10" VC | 2 | 05/29/2002 12/03/2002 | GREASE | HEAVY GREASE IN SEWER MAIN. | RODDED MAIN TO RELIEVE GREASE BLOCKAGE. REFER TO HAVE MAIN CLEANED 2 SECTIONS UP AND 2 SECTIONS DOWN, AND TELEVISED. | N | Y | N | None | None | CAPTURED BY DV 30, RETURNED TO SEWER SYSTEM. | N | Y | N
| 357248 | Fax (858) 571-6972 (RWQCB) | 2003-05-24 17:00 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-05-21 01:38 | 2003-05-24 14:18 | 1 | 52 | 0 | 52 | KURTZ & SMITH ST | San Diego | 92110 | SD | 4"UNK | 1 | 2002-10-17 | FLOOD DAMAGE | BREAK IN LINE | RODDED LINE TO RESTORE FLOW; HEAVY SAND IN M/H DUE TO BREAK IN LINE; REFERRED TP STBY TO HAVE TELEVISED. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
| 357510 | Fax (858) 571-6972 (RWQCB) | 2003-05-28 16:00 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2003-05-22 19:45 | 2003-05-22 20:00 | 25 | 375 | 225 | 150 | 10300 ROSELLE ST | San Diego | 92130 | SD | 15" PVC | 0 |  | CONSTRUCTION | HEAVY SLUDGE AND ROCKS IN ROCK TRAP MANHOLE 19. SPILL OCCURRED WHILE CREWS WERE CLEANING MANHOLE. | MANHOLE VACTORED, CLEANING COMPLETE. REASSESS DESIGN OF SYSTEM. | N | N | N | None | None | DRIED IN DIRT AREA EAST OF DUMP SITE. | Y | Y | N
| 357901 | Fax (858) 571-6972 (RWQCB) | 2003-05-24 13:30 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-05-23 10:30 | 2003-05-23 11:26 | 1 | 56 | 0 | 56 | 4478 47TH ST | San Diego | 92115 | SD | 6"VC | 0 | 0 | GREASE | BLOCKAGE CAUSED BY GREASE. | CREW LOCATED OVERFLOW WHILE WORKING IN AREA; MACHINE RODDED TO RELIEVE STOP; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
| 358038 | Fax (858) 571-6972 (RWQCB) | 2003-05-29 17:00 | Jeff Wilder | (858) 614-5770 | City of San Diego | City of San Diego | 2003-05-23 17:30 | 2003-05-28 08:00 | 0.00225 | 18.1575 | 0 | 18.1575 | Pico St. and Garnet Ave | San Diego | 92109 | SD | Air valve | 0 |  | OTHER | Air valve leaking | Air valve to be repaired. | N | N | N | None | None | Drying up in dirt below leak. | Y | Y | N |  |  | west construction temporarily plugged hole in air valve to stop overflow.
| 357969 | Fax (858) 571-6972 (RWQCB) | 2003-05-25 21:25 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-05-25 18:19 | 2003-05-25 19:25 | 1 | 66 | 0 | 66 | 3993 PARK BLVD | San Diego | 92103 | SD | 6"VC | 1 | 2003-01-19 | OTHER | BLOCKAGE CAUSED BY HEAVY SLUDGE | RODDED LINE & THEN FLUSHED TO RELIEVE STOP CAUSED BY HEAVY SLUDGE. REFERRED TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
| 358353 | Fax (858) 571-6972 (RWQCB) | 2003-05-29 12:35 | Stanley Harvey | (858) 614-5742 | City of San Diego | City of San Diego | 2003-05-29 09:08 | 2003-05-29 09:35 | 10 | 170 | 100 | 70 | 5861 Collage Ave & Lambada | San Diego | 92120 | SD | 8" VC | 1 | 2002-09-19 | ROOTS | Blockage in main do to roots. | Main will be clean 2 section up and 2 section down and referrded to area supervisor. | N | Y | N | None | None | Dry up in stom drain. | Y | Y | N
| 358462 | Fax (858) 571-6972 (RWQCB) | 2003-05-29 22:00 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2003-05-29 18:50 | 2003-05-29 19:05 | 30 | 450 | 0 | 450 | 1105 MADERA ST. | San Diego | 92114 | SD | 8" VC | 0 |  | ROOTS | HEAVY ROOTS BLOCKED TRAP IN MH AS MAIN WAS BEING CLEANED. UNABLE TO REMOVE TRAP DO TO HEAD PRESSURE. | CLEANED MAIN WITH FULL SIZE CUTTING BLADE. REFER TO BE TELEVISED. | N | Y | N | None | None | DRIED IN STORM CHANNEL AT ATKINS AV. X 64TH ST. | Y | Y | N
| 358373 | Fax (858) 571-6972 (RWQCB) | 2003-06-02 16:00 | Thang Hoang | (858) 654-4173 | City of San Diego | City of San Diego | 2003-05-29 10:38 | 2003-05-29 12:06 | 0.5 | 44 | 44 | 0 | 1000 ft South of PS 65 / 12112 Sorrento Valley Rd. | San Diego | 92125 | SD | Charcoal Canister | 0 |  | CONSTRUCTION | Valve at canister was clogged up with debris | Bi-weekly PM and valve inspection | N | N | N | None | None | on surface street 15 feet from charcoal canister | N | Y | N |  |  | Initial inspection was mistaken spill for process water since PS 65 was having problem with the process water at the time, later the spill was determined as sewage which resulted in delay of reporting.
| 358603 | Fax (858) 571-6972 (RWQCB) | 2003-05-31 07:30 | Leonard Williams | (858) 614-4059 | City of San Diego | City of San Diego | 2003-05-30 21:40 | 2003-05-31 02:40 | 3 | 900 | 0 | 900 | 6206 Oakridge Rd | San Diego | 92119 | SD | 8" vc | 0 | n/a | ROOTS | Heavy roots found in the main | Rodded main to clear roots | N | n | n | None | None | Dried in dirt in easement | y | Y | N
| 360055 | Fax (858) 571-6972 (RWQCB) | 2003-06-11 22:40 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2003-06-11 16:16 | 2003-06-11 18:35 | 0.25 | 34.75 | 34.75 | 0 | 1700 CRESPO DR | San Diego | 92037 | SD | 6" VC | 1 | 2002-08-30 | ROOTS | HEAVY ROOTS GROWING IN MAIN. | RODDED WITH FULL SIZE BLADE. VACTORED AND CLEANED AREA. REFERRED UPSTREAM AND DOWN STREAM MAINS TO BE CLEANED, AND STOPPAGE SECTION TO BE TELEVISED. | N | N | N | None | None | 350' N OF MH 53, VACTORED ALL. | Y | Y | N
| 360218 | Fax (858) 5716972 (RWQCB) | 2003-06-12 22:00 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2003-06-12 16:19 | 2003-06-12 18:20 | 60 | 7260 | 1800 | 5460 | 3294 LOGAN AVE. | San Diego | 92113 | SD | 8" CI | 1 | 2002-06-16 | LINE BREAK | VANDALIZED MANHOLE. | VACTORED OVERFLOW. RODDED TO RELIEVE BLOCKAGE. CLEANED 4 UPSTREAM SECTIONS OF MAIN. REFER TO HAVE MANHOLE COVER BOLTED DOWN AND MAIN TO BE TELEVISED. Police case # 03038769. Per officer Keller badge # 5588 . | N | Y | Y | CHOLLAS CREEK | SAN DIEGO BAY |  | Y | Y | N
| 360437 | Fax (858) 571-6972 (RWQCB) | 2003-06-13 20:55 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-06-13 18:00 | 2003-06-13 19:53 | 5 | 565 | 0 | 565 | 1261 RHODA DR | San Diego | 92037 | SD | 8"VC | 1 | 2003-03-01 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS. | HANDRODDED LINE TO RELIEVE STOP CAUSED BY ROOTS. VACTOR STANDBY TO CAPTURE SPILL IF REACHED STREET; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | N | N | None | None | SOAKED INTO EASEMENT AREA AROUND M/H. | Y | Y | N
| 360431 | Fax (858) 571-6972 (RWQCB) | 2003-06-13 19:10 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-06-13 15:59 | 2003-06-13 17:00 | 1 | 61 | 0 | 61 | 6356 MESITA DR | San Diego | 92115 | SD | 8" VC | 1 | 2002-08-31 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS. | VACTOR CONTAINED OVERFLOW WHILE RODDER RELIEVED STOP CAUSED BY ROOTS. REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
| 360507 | Fax (858) 571-6972 (RWQCB) | 2003-06-14 22:55 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-06-14 18:12 | 2003-06-14 19:00 | 1 | 48 | 0 | 48 | PAN AMERICAN PLAZA & PRESIDENTS WAY/CANYON | San Diego | 92101 | SD | 8"VC | 1 | 2002-06-17 | ROOTS | blockage caused by roots | Unable to locate ds m/h; handrod from wet m/h & hi-lined hose into canyon to relieve stop at 22:45. Refer to area supervisor to have line tv'd & downstream m/h located. | N | Y | N | None | None | SOAKED INTO GROUND IN AREA & SOME ENTERED & DISSIPATED IN STORM DRAIN. | Y | Y | N
| 360560 | Fax (858) 571-6972 (RWQCB) | 2003-06-16 01:30 | Rick Donahue | (858) 654-4155 | City of San Diego | City of San Diego | 2003-06-15 20:24 | 2003-06-15 23:00 | 200 | 200 | 0 | 200 | 2550 BIOLA Ave | San Diego | 92154 | SD | 4" By Pass | 0 |  | CONSTRUCTION | Leak on 4" PVC union on contractors by pass pump discharge pipe. | Contractor switched to back up by pass line and rerpaired primary line. | N | N | N | None | None | Soaked into ground around M/H #186 in backyard | N | Y | N
| 361081 | Fax (858) 571-6972 (RWQCB) | 2003-06-19 18:00 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2003-06-19 09:27 | 2003-06-19 16:32 | 10 | 4250 | 4100 | 150 | South Bound Hwy. 163 @ East Bound Washington St. | San Diego | 92103 | SD | 8" V.C. | 1 | 2002-11-14 | ROOTS | Heavy Roots in a 30' deep manhole caused stoppage. | Spill was contained at 10:25 A.M. Vactor to recover overflow untill dry at spill site. Machine and hand rod to relieve stoppage. Will refer to area supervisor to add in a routine maintenance program, also to televise main. | N | Y | N | None | None | Dissipated in storm drain conveyance system | Y | Y | N |  | 0 | All E.R. units were call to respond to this emergency situation.
| 361139 | Fax (858) 571-6972 (RWQCB) | 2003-06-19 20:00 | C. MICKELSON | (858) 654-4132 | City of San Diego | City of San Diego | 2003-06-19 15:35 | 2003-06-19 18:15 | 1 | 160 | 115 | 45 | 1543 MINDEN DR. | San Diego | 92111 | SD | 8" VC | 0 |  | ROOTS | ROOTS GROWING IN SEWER MAIN. | HAND RODDED TO RELIEVE BLOCKAGE. FLUSHED 5 SECTIONS OF MAIN TO CLEAN. REFER TO BE TELEVISED. | N | Y | N | None | None | DRIED IN DIRT AT STORM OUTLET, ULRIC ST.X NB ON RAMP SR 163 | Y | Y | N |  |  | SPILL FINDER DOWN.
| 361345 | Fax (858) 571-6972 (RWQCB) | 2003-06-21 09:40 | Carlos E. Gomez Tagle | (858) 614-5770 | City of San Diego | City of San Diego | 2003-06-20 15:58 | 2003-06-20 18:00 | 1 | 122 | 0 | 122 | 2261 WHITMAN ST | San Diego | 92103 | SD | 8" VC | 1 | 2003-04-04 | ROOTS | BLOCAGE WAS CAUSED BY ROOTS | HANDRODDED LINE FROM C/O (FSN-280182) TO RELIEVE STOP, THEN ROOD MAIN FROM MH334 (FSN-87324) TO MH337 (FSN-87327) W/SCREW AND RETRIEVED W/BLAD, REMOVING HEAVY ROOTS, REFER TO AREA SUPERVISOR FOR FUTHER EVALUATION. | N | N | N | None | None | SOAKED INTO EASMENT AREA AROUND M/H | Y | Y | N
| 361746 | Fax (858) 571-6972 (RWQCB) | 2003-06-24 19:10 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2003-06-24 15:01 | 2003-06-24 17:00 | 1 | 119 | 0 | 119 | 3972 JACKDAW ST. | San Diego | 92103 | SD | 8" PVC | 0 |  | ROOTS | HEAVY ROOTS GROWING IN SEWER MAIN. | VACTORED DOWN OVERFLOWING MANHOLE. RODDED MAIN TO RELIEVE ROOT BLOCKAGE. CLEANED MAIN WITH FULL SIZE BLADE. REFER MAIN TO BE TELEVISED. | N | N | N | None | None | DRIED IN DIRT AREA 40 FT. EAST OF OVERFLOWING MANHOLE. | Y | Y | N |  |  | SPILL FINDER PROGRAM DOWN.
| 362215 | Fax (858) 571-6972 (RWQCB) | 2003-06-27 11:45 | D.A. BRANCO | (858) 614-5770 | City of San Diego | City of San Diego | 2003-06-27 18:58 | 2003-06-27 20:00 | 20 | 1240 | 0 | 1240 | 7435 SAN VICENTE ST | San Diego | 92114 | SD | 8"VC | 0 | 0 | GREASE | BLOCKAGE WAS CAUSED BY GREASE. | UNIT 718 CONTAINED OVERFLOW AT 20:00 WHILE UNIT 724 RODDED LINE TO RELIEVE STOP AT 22:49. REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | SOAKED INTO DRAINAGE DITCH IN VACANT LOT | Y | Y | N
| 362448 | Fax (858) 571-6972 (RWQCB) | 2003-06-30 21:00 | C, MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2003-06-30 18:49 | 2003-06-30 19:45 | 2.5 | 140 | 140 | 0 | 4545 ALTADENA AVE. | San Diego | 92115 | SD | 6" CP | 0 |  | GREASE | GREASE BUILD UP IN CITY SEWER MAIN. | FLUSHED TO RELIEVE GREASE BLOCKAGE. VACTORED AND CLEANED ALLEY AND STREET, RECOVERING TOTAL VOLUME OF SPILL. DEODORIZED AREA. WILL DO FOLLOW UP CLEANING IN AM WITH RODDING TRUCK. REFER TO BE TELEVISED. | N | N | N | None | None | DRIED AT NW CORNER OF ALTADENA AVE. X MONROE AVE. | Y | Y | N |  |  | SPILL FINDER PROGRAM DOWN.
| 023013 | N/A | 5/13/03 0830 | Jim Barber | (619) 429-8311 | City of Imperial Beach | City of Imperial Beach | 2003-05-13 08:20 | 2003-05-13 08:45 | 5 | 125 | 125 | 0 | 221 Donax | Imperial Beach | 91932 | SD | M/H 3 53 | 0 | N/A | ROOTS | Roots and Grease found in line. 221 Donax has an underground garage that is the low spot in the line.Gargage sump pump sent sewerage to street. Spill ran to catch basin @ Palm and Seacoast leading to the storm drain wet-well. Storm drain wet-well was pumped to sewer. | Vactor truck jetted from M/H#52 to M/H#53 to alleviate blockage. Vactor then sent to Palm and Seacoast catch basin to recover. Gutters cleaned by fresh water wash-and broom down from Graffiti removal truck from spill site to Vactor. | N | Y | N | None | None | Sewer | N | N | N | N/A | 0 | Sewerage from this part of town will never reach surface waters. Storm drain wet-well will collect and then be pumped to the sewer
X | 023014 | N/A | 5/27/03 1000 | Robert Ghiloni | (619) 628-1357 | City of Imperial Beach | City of Imperial Beach | 2003-05-27 09:00 | 2003-05-27 10:00 | 3 | 5 | 5 | 0 | 940 Calla Ave | Imperial Beach | 91932 | SD | Lateral Cleanout | 0 | N/A | UNKNOWN | Private lateral spill from private residence. Plumber onscene when city found. | City building official was at property to sign final inspection report and found a plumber working on clearing a cleanout. Building official call sewer sup for reording purposes. Plumber cleaned and sanitized 20 yards on concrete alley after work was preformed. Plumber stated that there was effluent seeping from clean out due to missing cap. | N | N | N | None | None | Plumber Cleaned | N | N | N | N/A | 0 | The plumber was onscene when city official became aware. This was strictly a private lateral problem and is recorded because effluent contacted city right of way. |  | X
| 023011 | N/A | 3/7/03 0800 | Cal Am | (619) 575-1106 | City of Imperial Beach | City of Imperial Beach | 2003-03-07 07:45 | 2003-03-07 08:20 | 1 | 40 | 40 | 0 | Donax and Elm | Imperial Beach | 91932 | SD | M/H#680 | 0 | N/A | GREASE | There was a main line blockage that caused the overflow from the manhole. | The vactor was immediately dispatched to alleviate the blockage and the storm drain recovery vehicle was dispatched to begin the recovery process. The Vactor cleared the blockage and then proceeded to the spill site where the below ground storm drain was cleaned. The downstream lines were cleaned by the regular vactor crew the following week. | N | Y | N | None | None | Vactor truck recovered apx 40 gallons of fluid from the storm drain and placed it in the sewer | N | N | N | N/A | 0 | This spill was a line that had a partial blockage. The report from Cal Am was that it was his belief that the spill had just started based on the flow amount. Upstream of the spilling manhole is a dead end.
X | 023012 | N/A | 3/10/03 1215 | PWD Hank Levien | (619) 628-1369 | City of Imperial Beach | City of Imperial Beach | 2003-03-10 12:10 | 2003-03-10 13:15 | 3 | 195 | 195 | 0 | 600 Block of Palm | Imperial Beach | 91932 | SD | Lateral Cleanout | 0 | N/A | GREASE | There was a blockage in the lateral that services the Silver Strand Plaza. City personnel responded to assist in the clean up effort. Upon arrival by city personnel, it was noted that the plumber was already working and a representative of the shopping center was working to contain the spill. The storm drain recovery vehicle was stationed at the storm drain and the vactor truck cleaned the main line adjacent to the shopping center to ensure it was not a city problem. After the line was shot, the vactor took over at the storm drain and cleaned the storm drain while the storm drain recovery vehicle cleaned the 150 yards to the shopping center. | The vactor truck was immediately dispatched to clean the city main line while the storm drain recovery vehicle protected the storm drain. | N | Y | N | None | None | The vactor and storm drain recovery vehicle recovered all the spill and place it in the sewer. | N | N | N | N/A | 0 | This was a wonderful effort using two vehicles to ensure the spill did not reach surface waters. |  | X
|  | Non-Reportable |  | Martin Holmes | (619) 258-4706 | Padre Dam Municipal Water District | Padre Dam Municipal Water District | 2003-06-26 11:00 | 2003-06-26 11:50 | 1 | 50 | 50 | 50 | 9225 Carlton Hills Blvd | Santee | 92071 | SD | Manhole #1858 | 0 |  | GREASE | 8" PVC sewer main clogged with grease, causing manhole #1858 to overflow, pooling in low section of parking lot. | 8" PVC sewer main placed on 60 day sewer cleaning schedule. Grease trap program administrator checked on restuarants in shopping center, all in compliance. | N | N | N | None | None | Sewage pooled in low area of parking lot | N | N | N | NA
|  | Non-Reportable |  | Martin Holmes | (619) 258-4706 | Padre Dam Municipal Water District | Padre Dam Municipal Water District | 2003-06-27 22:30 | 2003-06-27 23:10 | 2 | 80 | 80 | 80 | 9925 Conejo Rd | Santee | 92071 | SD | Manhole #1500 | 0 | 0 | ROOTS | 8" VCP Sewer main clogged with roots causing overflow from manhole #1500. Sewage pooled at end of street. | 8" VCP sewer main cleaned using Hydro Root cutting saw. CCTV's entire main and in process of spot repairing area with root intrusion. | N | N | N | None | None | Sewage pooled at the end of Conejo & Teresa Rd | N | N | N | NA
| 023004 | David Hanson | 2003-03-13 | Patrick Jackson | (619) 441-1658 | City of El Cajon | City of El Cajon | 2003-03-13 10:25 | 2003-03-13 10:40 | 2 | 25 | 0 | 25 | Avocado Blvd. | El Cajon | 92020 | SD | 16-014 | 0 | NA | ROOTS | Roots in line | Added this segment of sewer line to six month rodding schedule | N | Y | N | None | None | Dry creek bed | Y | N | N | N | 0
| 023001 | David Hanson | 2002-07-15 15:45 | Patrick Jackson | (619) 441-1658 | City of El Cajon | City of El Cajon | 2002-07-15 14:20 | 2002-07-15 14:50 | 10 | 300 | 0 | 300 | 112 S. Pierce | El Cajon | 92021 | SD | MH# 08-187 | 0 | N/A | ROOTS | Roots from Eucalyptus trees on Interstate 8 freeway on ramp intruded into City Main Line | Line will be added to Six month Rodding schedule | N | Y | Y | County Ditch | None | NA | Y | N | N | N/A | 0 | County Ditch is completely fenced in, No public access
| 023003 | David Hanson | 3/11/03 945 | Rich Arrant | 760-744 0460 | Vallecitos Water District | Vallecitos Water District | 2003-01-24 09:30 | 2003-01-12 11:00 | 0.16 | 15 | 15 | 0 | Calle Venado | San Marcos | 92069 | SD | 8" VCP | 0 | 0 | Construction | Contractor broke line | Suggest he be more careful | N | N | N | None | None | Const. Pit | Y | N | N | None | 0 | None
| 023004 | David Hanson | 4/28/03 1307 | Rich Arrant | 760-744-0460 | Vallecitos Water District | Vallecitos Water District | 2003-04-28 11:15 | 2003-04-28 12:15 | 50 | 3000 | 2200 | 800 | San Marcos Blvd | San Marcos | 92069 | SD | 8" VCP | 0 | 0 | GREASE | Grease Blockage | Cleared Grease Blockage | N | Y | Y | Drainage Ditch | San Marcos Creek | San Marcos Creek | Y | Y | Y | San Marcos Creek | 3 | None
| 023005 | David Hanson | 5/15/03 1557 | Rich Arrant | 760-744-0460 | Vallecitos Water District | Vallecitos Water District | 2003-05-15 10:55 | 2003-05-15 11:30 | 10 | 200 | 200 | 0 | R S F | San Marcos | 92069 | SD | Manhole | 1 | 2003-01-12 | CONSTRUCTION | Rocks,Roots,Grease | Is being replaced | N | N | N | Spill berm | None | None | Y | N | N | None | 0 | None
| 003001 | fax | 02/07/03 10:30 | Leo Schempp | 760-753-0156 | Leucadia County Water District | Leucadia County Water District | 2003-02-07 09:37 | 2003-02-07 10:03 | < 5 | 50 | 30 | 20 | 418 Hillcrest Drive | Encinitas | 92024 | SD | manhole # 03 - 0560 | 0 | na | roots | roots coming from lateral of 361 Hillcrest Drive | root sawed & CCTV sewer, notified resident | N | Y | Y | Batiquitos Lagoon | Pacific Ocean | Pacific Ocean | Y | N | N | NA | NA | Resident brought in plumber
| 003002 | fax | 02/12/03 18:05 | Leo Schempp | 760-753-0156 | Leucadia County Water District | Leucadia County Water District | 2003-02-12 16:45 | 2003-02-12 17:15 | 300 | 10000 | 0 | 10000 | 2017 N Coast Highway | Carlsbad | 92009 | SD | Batiquitos Pump Station | 0 | na | pump station failure | utility voltage surge caused extensive eqmt damage | installing additional electrical protection devices | Y | Y | Y | Batiquitos Lagoon | Pacific Ocean | Pacific Ocean | Y | Y | Y | S. Carlsbad Beach | 5 | All beach samples were below County Health Standards for closure.
| '003003 | fax | 03/19/03 09:30 | Leo Schempp | 760-753-0156 | Leucadia County Water District | Leucadia County Water District | 2003-03-19 06:57 | 2003-03-19 07:50 | 50 | 2500 | 1600 | 900 | 7504 Gibraltar St | Carlsbad | 92009 | SD | manhole # 10-1910 | 1 | 37437 | roots | roots & rocks | line on trouble spot list - cleaned, CCTV inspected | Y | Y | Y | San Marcos Creek | Batiquitos Lagoon | Pacific Ocean | Y | Y | Y | S. Carlsbad Beach | 1 | All beach samples were below County Health Standards for closure.
| 003004 | fax | 5/28/03 10:00 | Leo Schempp | 760-753-0156 | Leucadia County Water District | Leucadia County Water District | 2003-05-28 08:30 | 2003-05-28 09:11 | 5 | 810 | 600 | 210 | Saxony Rd (S of La Costa Ave) | Encinitas | 92024 | SD | manhole # 04-0670 | 0 | na | roots | roots & possible debris | line on trouble spot list - cleaned, CCTV inspected | N | Y | Y | Dry Creek Bed | None | Dry Creek Bed | Y | N | Y | Desilting Basin | 5 | No water reached Batiquitos Lagoon; Pumped additional water out of Desilting Basin. Further Investigation showed this location in Encinitas, not Carlsbad.
X | 023008 | Quarterly Report | 2003-04-13 16:25 | Terrance Hartnett | (858) 755-3294 | City of Del Mar | City of Del Mar | 2003-04-13 16:20 | 2003-04-13 18:20 | 2 | 240 | 240 | 0 | 2719 Camino Del Mar | Del Mar | 92014 | SD | Private lateral spill at 2719 Camino Del Mar Costa Del Rey Apts., Del Mar GIS map A4 | 0 | N/A | PRIVATE PROPERTY | Plugged Private Lateral | Private residential lateral was cleared at 18:20 by drain service "Hudson Management Co". | Y | N | N | none | none | Gutter line but Public Works recovered all sewer and washdown water | Y | N | N | N/A | 0 | MAINTENANCE OF LATERALS ARE RESIDENTS RESPONSIBILITY, PER CITY ORDINANCE No 472 (02/02/87), Chapter 22.08.070 Private residential sewer lateral overflow at Costa Del Rey Apts. at 2719 Camino Del Mar. Public Works recovered all sewer and washdown water. |  | X
X | 023009 | Quarterly Report | 2003-04-15 13:57 | Kipling Curry | (858) 755-3294 | City of Del Mar | City of Del Mar | 2003-04-15 13:57 | 2003-04-15 14:05 | 2.5 | 20 | 20 | 0 | 501 Rimini Road | Del Mar | 92014 | SD | Private lateral spill at 501 Rimini Road, Del Mar GIS map B7 | 1 | 2002-07-30 | PRIVATE PROPERTY | Plugged Private Lateral | Called owner and advised of overflow, they called plumber to clear lateral. | N | N | N | none | none | Trapped in gutter and vacuumed up | Y | N | N | N/A | 0 | Private residential sewer lateral overflow at 501 Rimini Rd. |  | X
| 023010 | Quarterly Report | 2003-05-06 08:45 | Kipling Curry + David Zilberberg | (858) 755-3295 | City of Del Mar | City of Del Mar | 2003-05-06 08:34 | 2003-05-06 09:01 | 0.75 | 20 | 10 | 10 | 347 Serpentine Drive | Del Mar | 92014 | SD | Del Mar GIS map B6 #04 (Clean out) | 1 | 2002-09-12 | ROOTS | Heavy Roots | Rodded main line up to dead end (Clean out) | N | N | N | none | none | 10 gal. absorbed into the environment | Y | N | N | N/A | 0 | Heavy Roots. Rodded main line up to dead end (Clean out)
X | 023011 | Quarterly Report | 2003-06-07 14:56 | Pat Vergne | (858) 967-1430 | City of Del Mar | City of Del Mar | 2003-06-07 14:55 | 2003-06-07 15:05 | 1 | 10 | 0 | 10 | 1247 Camino Del Mar | Del Mar | 92014 | SD | Private lateral spill at 1247 Camino Del Mar | 2 | 8/1/02 1/7/03 | PRIVATE PROPERTY | Grease and paper clogged private lateral | Rodded main line from manhole #77 to manhole #12 GIS map B8 175' with 6" auger, line was clear. | N | N | N | none | none | Dissipated and evaporated in concrete gutter | Y | N | N | N/A | 0 | Private residential sewer lateral overflow at 1247 Camino Del Mar |  | X
| 023005 | Quarterly Report | 2003-01-07 07:14 | Peter Kiefer, Dan Peters | (858) 755-3294 | City of Del Mar | City of Del Mar | 2003-01-07 07:14 | 2003-01-07 07:45 | 5 | 150 | 0 | 150 | 336 12th Street at Luneta | Del Mar | 92014 | SD | Del Mar GIS map B8 manhole 19 | 1 | 2002-08-01 | ROOTS | Roots in sewer main @ 100' from manhole B8-18 east toward manhole B8-19 | Rodded 120' to overflowing manhole B8-19 from manhole at 12th Street at Maiden Lane | N | N | N | none | none | street surface | Y | N | N | N/A | 0 | Overflow dissipated into soil and onto street surface. Contaminated debris & sewage on street surface removed with street sweeper
| 023006 | David Hanson/ Brian Kelly | 2003-02-20 08:00 | David Zilberberg, Paul Thomas | (858) 755-3294 | City of Del Mar | City of Del Mar | 2003-02-20 08:00 | 2003-02-20 08:28 | 10 | 280 | 0 | 280 | 1130 Cuchara Dr. | Del Mar | 92014 | SD | Del Mar GIS map B8 manhole 24 | 3 | 07/30/2002, 08/1/2002, 01/07/2003 | BLOCKAGE | Sandcloth (Plumbers tape) & Roots | Rodded main 265' two times with 2" and 6" auger. From Luneta East to Cuchara | Y | Y | Y | Pacific Ocean | Pacific Ocean | Pacific Ocean | Y | N | Y | 100 feet north and south from outlet at 1200 block at beach | 3 | See also letter of 2/21/03 to David Hanson.Vacuum unit set up on manhole at 8:28 ending spill. Blockage was not cleared until later and during clearing the vacuum unit removed 500 gallons from manhole location. This amount was later released into the sewer system.
X | 023007 | Quarterly Report | 2003-02-24 23:35 | David Zilberberg | (858) 755-3294 | City of Del Mar | City of Del Mar | 2003-02-24 11:35 | 2003-02-24 12:30 | 1 | 200 | 200 | 0 | 1011 Camino Del Mar | Del Mar | 92014 | SD | Private Lateral at 1011 Camino Del Mar | 0 | N/A | GREASE | Grease and Roots in a private lateral | Rodded main from manhole on 11th Street on to manhole on 10th Street with 2" & 6" augers, twice over a distance of 450'. | N | N | N | N/A | N/A | Sewer system | Y | N | N | N/A | 0 | This was a lateral spill. City ordinance requires owners to maintain their wastewater laterals up to the main. |  | X
| 0203008 | David Hanson, fax (858) 467-2952 | 03/10/03 22:30 PM | CDR Wink | (619) 556-7549 | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2003-03-09 22:30 | 2003-03-03 23:45 | 86 | 6000 | 1000 | 5000 | Pump Stationon Rendova Circle | Coronado | 92135 | SD | Sewer lift station | 3 | 11/12/02, 11/24/2002, 11/29/02 | Pump Station Failure | Pump float on system failed causing pumps not to respond in wet well. | Repaired pump float | N | N | Y | San Diego Bay | N/A | Pacific Ocean | Y | Y | Y | Along fence and bay area on Navy property not accessible to public | 3 | Area is not accessible to general public due to spill being within a controlled military space.
| 0203009 | David Hanson, fax (858) 467-2952 | 04/04/03 17:00 PM | PO 1 Pfeifer | 221-1522 | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2003-04-03 17:00 | 2003-04-03 18:30 | 0.5 | 50 | 0 | 50 | Subase Bldg. 301 Kerrick Street | San Diego | 92106 | SD | Manhole | 0 | 0 | Roots | Intrusion of roots in main line | Hydro-Blasted out with root cutter. | N | N | N | N/A | N/A | N/A | Y | N | N | N/A | N/A | Sewage absorbed into the dirt in the surrounding area.
| 0303010 | David Hanson, fax (858) 467-2952 | 04/14/03 17:25 PM | Leleand Brooks | (619) 553-6402 | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2003-04-14 14:30 | 2003-04-14 15:30 | 0.1 | 6 | 0 | 6 | Project & Gate | San Diego | 92106 | SD | Manhole 3-13 | 0 | N/A | Blockage | Dirt Blockage | Line Hydro-Blasted clear. Line section will be video inspected to check for breaks in pipe. | N | N | N | N/A | N/A | N/A | Y | N | N | N/A | N/A | Manhole was bermed and sewage stayed within the berm. It was raining during the spill but not 72 hours prior to the spill.
| 0303011 | David Hanson, fax (858) 467-2952 | 2003-05-09 14:00 | PWC Code 500 Maint. | (619) 556-7341 | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2003-05-09 10:00 | 2003-05-09 11:00 | 1 | 100 | 80 | 20 | Miramar Way near Bldg. 790 | San Diego | 92145 | SD | Mahhole | 0 | N/A | Rocks / Blockage | Rocks and debris caused blockage. | Hydro blasted line clear. Cleaned and sanitized area. | N | N | N | N/A | N/A | N/A | Y | N | N | N/A | N/A | Sewage seeped up from manhole. Portion of sewage that was not recovered had absorbed into the surrounding soil.
| 0303012 | David Hanson, fax (858) 467-2952 | 2003-05-22 15:00 | T. Couto | (619) 553-4144 | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2003-05-22 13:00 | 2003-05-22 13:10 | 200 | 2000 | 500 | 1500 | Subase Bldg. 400 Catalina Blvd. | San Diego | 92136 | SD | Sewer Cleanout | 0 | N/A | Blockage / Infiltration | Tank being pumped at high volume into sewer lateral. Water caused overflow. Cleaned lines for blockage possibility. | Pump tank at slower volume. | N | N | N | N/A | N/A | N/A | Y | Y | N | N/A | N | OES Control #03-2658. Overflow water was from a test pool that was being pumped down. Pool water was being pumped into lateral and pump rate was to large for lateral to handled causing spill. Water absorbed into soil or was recovered.
| 0303013 | David Hanson, fax (858) 467-2952 | 2003-05-29 11:00 | Larry Sherwood | (619) 556-7349 | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2003-05-29 08:39 | 2003-05-29 09:30 | 5 | 1000 | 200 | 800 | Subase Bldg. 544 Manhole 11/56 | San Diego | 92106 | SD | Manhole | 0 | N/A | Blockage / Debris | Cleared roots from line also debris. | Hydro blasted line clear. Cleaned and sanitized area. | N | Y | Y | San Diego Bay | Pacific Ocean | Pacific Ocean | Y | Y | N | N/A | N | OES Control # 03-2763. Overflow drained into San Diego Bay. Signs were not posted because area is not accessible to public.
| 0303014 | David Hanson, fax (858) 467-2952 | 2003-06-23 09:30 | Ron | ((619) 437-0968 | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2003-06-23 09:25 | 2003-06-23 09:35 | 10 | 100 | 50 | 50 | NAB Manhole 605-1 | Coronado | 92135 | SD | Manhole | 0 | N/A | Power Failure | Breakers were tripped, secondary pump placed online. Investigating pump internals for binding. | Investigating pump internals for binding. | N | N | N | N/A | N/A | N/A | Y | N | N | N/A | N | Area was vacuumed, remaining 50 gallons of sewage that was not recovered perked into ground. Area was decontaminated as per PWC Utilities SOP.
X | 31903 | 1 (858) 571-6972 | 3/19/2003, 0900 | Peggy Mazzeppi | (619) 397-6000 | City of Chula Vista | City of Chula Vista | 2003-03-19 02:00 | 2003-03-19 12:10 |  | 2160 | 648 |  | 1246 Third Ave. | Chula Vista | SD | 91911 | N/A | 0 | GREASE | Grease and Paper, Private Sewer Lateral |  | At 8:30am. The Manager Called All Clear Drain |  | y | y | Telegraph Canyon | San Diego Bay |  | y | y | n |  |  |  |  | X
| 20503 | 1 (858) 571-6972 | 2/05/03, 0730 | Elizabeth Bunker | (619) 425-0132 | City of Chula Vista | City of Chula Vista | 2003-02-05 07:30 | 2003-02-05 08:15 |  | 900 | 800 |  | 960 Fifth Ave. | Chula Vista | SD | 91911 | N/A | 0 | GREASE | Grease |  | The City had Two-Sewer Combination Trucks. One |  | y | y | Telegraph Canyon | San Diego Bay |  | y | n | n
X | 62603 | 1(858)571-6972 | 6/26/03,2230HRS. | Chula Vista Police | (619)691-5151 | City of Chula Vista | City of Chula Vista | 2003-06-26 22:30 | 2003-06-28 |  | 2027.08 | 24 |  | 845 Lazo Ct. | Chula Vista | S.D. | 91911 | Private Grease Trap | 0 | Grease | Grease trap on private property blocked problem |  | The city contained the spill, the manager shut off the |  | y | y | Rice cyn. | S.D. Bay |  | y | N/A | n/a |  |  |  |  | X
| 62403 | 1(858)571-6972 | 6/24/03, 1330HRS. | Quito Barrajas Open Space Inspector | (619)397-6000 | City of Chula Vista | City of Chula Vista | 2003-06-24 13:30 | 2003-06-24 16:00 |  | 2250 | 3200 |  | Morgan Hill & Ferndale | Chula Vista | S.D. | 91913 | Manhole | 0 | Grease,Debris, | Grease and Construction material |  | Remove construction debris from sewer line follow up |  | y | y | Telegraph Cyn. | San Diego Bay |  | y | y | y
| 023003 | Fax | 2-28-03, 16:30 | C. Kamenides | (619) 522-7387 | City of Coronado | City of Coronado | 2003-02-28 15:30 | 2003-02-28 04:15 | 11 | 500 | 500 | 0 | 700 blk B/C alley | Coronado | 92118 | SD | Sewer main line | 1 | 2002-05-09 | ROOTS | Tree roots invading sewer main line | Videoinspected, rodded and treated line with root inhibitor | Y | N | N | None | None | Vactor tank | Y | N | N | N/A
| 023001 | Bob Morris (858) 571-6972 | 2/20/03 2000 | Dennis Cooper | (619) 670-2271 | Otay Water District | Otay Water District | 2003-02-06 | 2/20/03 2300 | 5 | 2500 | 0 | 2500 | 1341 Timberpond Dr. | El Cajon | 92020 | SD | MH 641.40 | 0 | N/A | Roots | Roots growing into a manhole and down to the channel creating intermittent plugging | Jetted the line clean. Cut out all roots. Placed manhole on "problem manhole" list. | N | N | N | None | None | Soaked into ground | Y | Y | N | N/A | 0 | Spill confined to two large backyards. Not reported for two weeks because it was initially believed to be intermittent storm drain leakage.
| 023002 | Bob Baker | 5/8/03 1100 | Dennis Cooper | Dennis Cooper | Otay Water District | Otay Water District | 2003-05-08 08:30 | 2003-05-08 09:30 | 30 | 1800 | 0 | 1800 | 1513 Fairvalley Rd. | El Cajon | 92020 | SD | MH 521.63 | 0 | N/A | Grease | This section of line is fairly flat. It spilled despite regular cleaning. | This section of line will be added to our list of trouble spots for more frequent inspection and/or cleaning | N | N | Y | Earthen stream | Stream | Sweetwater River 2 miles south | Y | Y | N | N/A | 0
| 023003 | Brian Kelly | 6/16/03 1300 | Dennis Cooper | Dennis Cooper | Otay Water District | Otay Water District | 2003-06-14 12:30 | 2003-06-14 14:10 | 20 | 2200 | 200 | 2000 | Fury at Calle Verde | La Mesa | 91941 | SD | MH 570.00 | 0 | N.A. | Grease | This section of line is relatively flat. It spilled despite regular cleaning. | This section of line will be added to our list of trouble spots for more frequent inspection and/or cleaning | N | Y | Y | Earthen stream | Stream | Sweetwater River 1.5 miles south | Y | Y | N | N/A | 0
| 023007 | Bryan Ott, Voice Mail | 2003-04-14 17:30 | Shawn Atherton | 760-753-5018 | City of Encinitas | City of Encinitas | 2003-04-14 15:10 | 2003-04-14 15:40 | 150 | 4500 | 0 | 4500 | Third and B Street | Encinitas | 92024 | SD | Moonlight Beach Pump Station | 3 | 5/17/02, 2/25/03, 3/15/03 | Infiltration | Flows coming into the station were greater than pumps could handle | As mentioned in previous reports, we put together an investigation crew and began searching for a cause of inflow. We feel strongly that we have located and corrected this ongoing problem. An 8-inch stub out was found open to the environment, allowing large amounts of water to enter the sewer system during rains. | y | n | y | Cottonwood Creek | Pacific Ocean | Pacific Ocean | y | n | y | one sign posted at entrance to Moonlight Beach (per Todd - County Hazmat) | 5
X | 020313 | Clay Clifton | 03/03/03 - 11:30 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2003-03-03 10:00 | 2003-03-03 10:30 | 5 | 150 | 650 | 0 | 2045 Corte Del Nogal | Carlsbad | 92008 | SD | Property line clean out | 1 | 2002-06-14 | Unknown | Blockage in lateral caused overflow | Televise lateral to determine possible problems. Take corrective actions if needed. | N | y | y | Drainage ditch | None | We flushed storm drain system and recaptured sewage-pumped back into Buena manhole | Y | N | N | N/A | 0 | I took samples above and below where overflow hit creek |  | X
X | 020314 | Clay Clifton | 03/19/03 - 11:20 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2003-03-19 | 2003-03-19 | 0 | 200 | 0 | 200 | College Blvd/Sunnycreek Rd | Carlsbad | 92008 | SD | Storm drain inlet | 0 | None | Construction | Plumber was excavating to connect sewer lateral and broke sewer main. The developer plugged the sewer manhole and it overflowed a small amount before it was contained by a pumper truck. The developer failed to notify the inspector of this incident. The jobsite was shut down except for the sewer main repairs being done now. | Had contractor make necessary repairs. They also re-cleaned and televised the system. | N | y | n | Storm drain box | Agua Hedionda Creek | n/a | Y | N | N | N/A | 0 | We took samples of Agua Hedionda Creek above and below where storm drain empties into it |  | X
X | 020315 | Clay Clifton | 04/08/03 - 10:45 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2003-04-07 13:00 | 2003-04-07 13:10 | 2 | 20 | 200 | 20 | 6305 El Camino Real | Carlsbad | 92008 | SD | Private sewer lateral | 0 | N/A | Roots | Private sewer lateral overflowed. I assume it was roots/debris. | Owner of building needs to do regular cleaning and/or excavate to make repairs. | N | Y | N | Brow ditch | No significant amount | Brow ditch | Y | N | N | N/A | 0 | Private sewer lateral |  | X
X | 020316 | Clay Clifton | 04/21/03 - 10:45 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2003-04-18 13:00 | 2003-04-18 13:30 | 1 | 30 | 30 | 0 | 2700 State Street | Carlsbad | 92008 | SD | Private plumbing inside business | 1 | 2002-11-20 | unknown | Private stoppage, owner of business is responsible to clear it and clean up. There is a restaurant in the liquor store. | Business establishment has long history of stoppages. It needs prompt attention along with regular cleaning. | N | N | n | N/A | N/A | Inside building at 270 State St (Fiesta Liquor) | Y | N | N | N/A | 0 | None |  | X
| 020317 | Clay Clifton | 05/14/03 - 13:00 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2003-05-14 00:30 | 2003-05-14 11:20 | 1 | 50 | 0 | 50 | Chatham/Brookfield easement | Carlsbad | 92008 | SD | Manhole | 0 | N/A | Roots | Roots from tree above sewer main caused back-up. | Excavate and repair damaged 8" pvc main. | N | N | N | N/A | N/A | Overflowed percolated into ground in ravine | Y | N | N | N/A | 0 | None
X | 023021 | Fax 858-571-6972 | 2003-04-14 10:00 | Jim Miller | (760)-839-4323 | City of Escondido | City of Escondido | 2003-04-13 11:06 | 2003-04-13 13:37 | 50 | 7550 | 3000 | 4550 | 1360 Vista Verde Way | Escondido | 92026 | SD | Private manhole | 0 |  | ROOTS | Roots growing through manhole joints caused the flow to slow, backup and discharge. | A Notice of Correction was issued to the property management association. City Pretreatment Inspector is working with the association to have their system cleaned and inspected. | Y | Y | Y | Escondido Crrek | San Elijo Lagoon |  | Y | Y | Y | Public access points along Escondido Creek | 3 |  |  | X
X | 023022 | Fax 858-571-6972 | 2003-05-06 14:30 | John Vaught | (760)-839-4323 | City of Escondido | City of Escondido | 2003-05-05 09:00 | 2003-05-06 10:00 | 3 | 4500 | 2500 | 2000 | 1125 N. Broadway | Escondido | 92025 | SD | Private cleanout | 1 | 2002-11-12 | UNKNOWN | unknown private system | A Notice of Correction was issued to the property management association. City Pretreatment Inspector is working with the association to have their system cleaned and inspected. | Y | Y | Y | Escondido Crrek | San Elijo Lagoon |  | Y | Y | Y | Public access points along Escondido Creek | 3 |  |  | X
X | 023023 | Fax 858-571-6972 | 2003-05-07 14:30 | John Vaught | (760)-839-4323 | City of Escondido | City of Escondido | 2003-05-06 | 2003-05-06 21:00 | 1 | 960 | 200 | 760 | 1635 E. Washington Ave. | Escondido | 92026 | SD | Private cleanout | 0 |  | UNKNOWN | unknown private system | City Pretreatment Inspector issued a Notice of Correction as well as a specific plan to address their maintenace needs. | N | Y | Y | Escondido Crrek | San Elijo Lagoon |  | Y | N | Y | Public access points along Escondido Creek | 3 |  |  | X
X | 023024 | Fax 858-571-6972 | 2003-06-12 12:30 | John Vaught | (760)-839-4323 | City of Escondido | City of Escondido | 2003-06-12 09:40 | 2003-06-12 09:55 |  | 100 | 70 | 30 | 475 N. Spruce St. | Escondido | 92025 | SD | Private tanker truck | 0 |  | OTHER | 6" discharge line came out of sewer manhole while private tanker truck was discharging. | Reported the issue to the trucking firm Diamond Environmental Services as well as our City Pretreatment Inspector. | N | Y | Y | Escondido Crrek | San Elijo Lagoon |  | Y | N | N |  |  |  |  | X
X | 023025 | Fax 858-571-6972 | 2003-06-19 14:00 | John Vaught | (760)-839-4323 | City of Escondido | City of Escondido | 2003-06-19 09:40 | 2003-06-19 11:30 | 1 | 110 | 65 | 45 | 422 E. Mission Ave. | Escondido | 92025 | SD | Private cleanout | 0 |  | UNKNOWN | Unknown - Private system | City Pretreatment Inspector will issue a Notice of Correction to the property owner. It will require the cleaning, inspection and scheduled maintenance of their collection system. | N | Y | Y | Escondido Crrek | San Elijo Lagoon |  | Y | N | N |  |  |  |  | X
| 023001 | FAX (858) 571-6972 | 2003-06-24 08:30 | Brad Bruington | (949) 425-3543 | Moulton Niguel Water District | Moulton Niguel Water District | 2003-06-23 21:30 | 2003-06-23 22:30 | 0.05 | 300 | 300 | 0 | Jeronimo/Marguerite | Mission Viejo | 92691 | OR | Manhole No. 1 to Manhole No. 2 8" line | 0 | 0 | Debris/Construction debris | Construction debris including 2 bricks and gravel, and private lateral rootball caused stoppage at manhole | Line was video-inspected and cleaned to remove all debris | N | Y | Y | Oso Creek to barrier pumps | None | Barrier pumps located at Oso Creek & Oso Road | Y | NA | N | None | 0 | Barrier pumps located at Oso Creek & Oso Road capture ALL creek flow and pump it to recycled reservoir. Santa Magarita W.D. owns pump station
X | 023012 | FAX 858-571-6972 | 2003-06-05 17:00 | Mike Dunbar | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2003-06-03 18:00 | 2003-06-04 21:00 | 0.09 | 150 | 0 | 150 | 16 N. La Senda | Laguna Beach | 92651 | OC | service lateral broke | 0 | none | PRIVATE PROPERTY | lateral line 6" collapsed due to deterioration possibly of salt air or exposed line | Line was replaced on 6/5/03 with 4" ABS pipe as a temporary service. The owner plans to replace with a permanent above-ground line with coating to protect from natural elements | N | N | Y | Pacific Ocean | n/a | n/a | Y | N | N | n/a | 0 | Private system overflow. At this location, lateral discharge is directe to bluff above the ocean |  | X
| 023008 | faxed | 2003-04-23 11:40 | Jeff Dolan | (760) 726-1340, X-1244 | City of Vista | City of Vista | 2003-04-23 11:40 | 2002-04-23 12:01 | 1 | 30 | 25 | 5 | 1235 Activity drive | Vista | 92084 | SD | V35.XX | 0 | None | Construction | City's sewer main full of clas II aggregate base and gravel from near by trading project. | Crew used sandbags and dirt to control the spill and to minimise sewage from entering the catch basins. The sewer main was cleared, and jetted . Surface areas were vacuumed and washed. | N | Y | N | None | None | sewage saturated into debris inside the existing storm drain. | Y | N/A | N | N/A | N/A | Inspection department notified.
X | 023009 | faxed | 2003-06-06 08:54 | Rancho Fire Distpatch | 858.756-3006 | City of Vista | City of Vista | 2003-06-06 08:54 | 2003-06-06 09:38 | 5 | 220 | 100 | 120 | 333 N. Emerald drive | Vista | 92083 | SD | PRIVATE LATERAL | 0 | 0 | Grease | Blockage to private sewer system caused by heavy grease (see photos). Tom Mueller (maintenance superintendent) was notified to maintain this private sewer system. This is the third blockage at this location over the past 5 years. | During the last blockage staff notified County Health department -- they inspected the site and directed the owner to keep the line clean. City taff has notified Sandy Sotola (Storm water pollution code enforcement officer, 760.726-1340, X1334) of the current situation. | N | Y | Unknown | storm drans | None | Storm drains | Y | N/A | Y | Buena Vista Creek at Emeral drive | 3 | 1)Water samples taken at Buena Vista Creek near Emerald drive. In addition, a bench mark sample was taken approximatelly 500-ft upstream of this location. Open channel is difficult and unsafe to enter. Last known MS4 location is approximatelly 5,000-ft away from spill site. 2)City crew cleaned blockage at private line to eliminate potential enviromental damage. Plumber on site assessing the problem. |  | X
X | 023010 | faxed | 2003-06-10 12:22 | Sheriff's dep't | unknown | City of Vista | City of Vista | 2003-06-10 12:22 | 2003-06-10 13:34 | 1 | 112 | 106 | 6 | 148 Los Angeles drive | Vista | 92083 | SD | PRIVATE LATERAL | 0 | 0 | Grease | Blockage to private sewer system caused by heavy grease. | incident refered to Keri Martinez City Storm Water Manager, 726-1340, X-1373) for citation, and follow up. | N | Y | N | None | None | Storm drains | Y | N/A | N | N/A | N/A | Private Sewer System |  | X
| 023027 | Phone | 4/4/2003 12:45:00 PM | Graham Wright | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2003-04-04 07:00 | 2003-04-04 10:10 | 0.005 | 1 | 0 | 1 | 1198 Jefferson Way | Laguna Beach | 92651 | OR | Manhole #76 | 0 |  | Roots | We received notification at our office on April 4, 2003 from Mr. Alex Celento who is the resident at 1198 Jefferson Way. He stated that he had noticed a small amount of sewage seeping from the manhole to the rear of the property at 7 a.m. this morning. Crews responded to the rear of the property and noticed that the line was plugged with roots from manhole #75 to manhole #76. | We opened up the line with a high pressure jetter, cleaning upstream from manhole #75 to manhole #76 and removed a large amount of roots. | N | N | N | N/A | N/A | Soaked into the ground and vegetation | Y | N | N
| 023028 | Voice Mail | 4/11/2003 8:30:00 AM | Lloy Thompson | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2003-04-11 09:25 | 2003-04-11 09:30 | 0.2 | 1 | 0.99 | 0.1 | 1741 Ocean Way | Laguna Beach | 92651 | OR | 4 inch private cleanout | 0 |  | Construction | The Sewer Division received a telephone call from a City contractor who stated that the manhole on Ocean Way was full of water. The contractors dewatering pump was pumping sand silt into the manhole which plugged the gravity line going into Pearl Street Lift Station #6. | City crews opened the blockage by jetting from the lift station. We cleaned all gravity lines and the storm drain box on Ocean Way. | N | N | N | N/A | N/A | N/A | Y | N | N | Catch Basin |  | Trace amounts dipped into the invert of the storm drain catch basin. All trace amounts were successfully removed from the catch basin invert. The remaining amount soaked into the ground in the planter box area
| 023029 | Phone | 4/21/2003 12:50:00 PM | Lloy Thompson | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2003-04-21 12:50 | 2003-04-21 12:51 | 200 | 200 | 30 | 170 | San Joaquin Street/N. Coast Hwy | Laguna Beach | 92651 | OR | By-Pass Line | 0 |  | Construction | While our City contractor was installing a by-pass line on our sewer lining project, a faulty fitting that was connected to a hose ramp began to leak. The leak was located closest to the intersection of San Joaquin and N. Coast Hwy. | The contractor immediately stopped operation and re-checked all hose connections. A sand berm was built at the beach, but no sewer water reached the ocean. Corrective measures will include pre-charging all hoses with clean water to check the clamp cone | N | Y | N | Storm Drain | N/A | Soaked into the sand and removed the sand | Y | N | Y | Storm Drain Outlet |  | One warning sign was placed at the storm drain outlet as a precaution only. No beach closure was implemented per the direction received from Mike Fennessey of the OCHCA
X | 023030 | Voice Mail | 5/5/2003 12:45:00 PM | Graham Wright | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2003-05-05 10:30 | 2003-05-05 10:35 | 9 | 45 | 25 | 20 | 2790 Queda Way | Laguna Beach | 92651 | OR | Discharge Pipe from Sump Pump | 0 |  | Line Break | At approximately 10:30 a.m. City water staff noticed water rerunning down Highland Way. Upon investigation staff found a lateral running over which was coming from the residence at 2790 Queda Way. Staff made contact with the maid and advised her not to use running water until repairs has been made to the lateral. The wrong types of clamps were being used for this pressure system. | Staff set up the Aquatech on Alta Vista to recover the overflow and approximately 25 gallons was recovered. The owner was advised to call a plumber to make the necessary repairs. Temporary repairs to the system were made by City staff. | N | N | N | N/A | N/A | See Remarks | Y | N | N |  |  | The overflow traveled approximately two blocks from the residence and the vacuum truck was used for recovery. |  | X
| 023031 | Phone | 5/6/2003 11:12:00 AM | Lloy Thompson | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2003-05-06 08:40 | 2003-05-06 08:50 | 50 | 500 | 450 | 50 | La Brea/N. Coast Hwy | Laguna Beach | 92651 | OR | Bypass at Manhole #12 | 0 |  | Construction | City crews noticed excessive run time at Fairview Lift Station. Upon arriving at La Brea/N. Coast Hwy where our City contractor had set up a bypass, we noticed that the discharge hose had not been put into the manhole. This delay in pumping also caused the downstream manhole to surcharge which caused sewer water to run onto a construction site at 830 Cliff Drive and on other surface streets. The contractor, WESCO, failed to adequately operate the bypass equipment. | The storm drain was flushed and all sewer water pumped back into the City's sewer system. Some sewage soaked into the sand at the beach and was removed by City crews. Work has been stopped until the contractor comes up with a plan to prevent future sewer spills | N | Y | N | Storm Drain | N/A | Pumped back into the City's sewer system | Y | Y | Y | Storm Drain Outlet at Shaws Cove |  | As a precaution only, a warning sign was placed at the storm drain outlet to Shaws Cove. There was no beach closure and the sign remained up for several hours until the contaminated soil was removed. The contractor had dedicated personnel onsite to monitor the bypass and they did not carry out their responsibilities. The contractor will pay for the cost of cleanup and may face additional liquidated damages due to the delay associated with the spill. OES Report #03-2355.
| 023032 | Phone | 5/12/2003 9:00:00 AM | Graham Wright | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2003-05-11 09:15 | 2003-05-11 10:00 | 0.07 | 3 | 0 | 3 | 568 Alta Vista | Laguna Beach | 92651 | OR | Manhole #unk | 0 |  | Roots | Sewer crews received a call from LBPD Dispatch who stated that a manhole was overflowing at 568 Alta Vista. Sewer crews responded and upon inspection of the City's 8-inch main line it was determined that the main line was plugged with tree roots. | Crews worked from the downstream manhole and jetted upstream to break the stoppage. They then opened up the main line with a high pressured jetter and cleaned upstream from 550 Alta Vista to the manhole in front of 568 Alta Vista. | N | N | N | N/A | N/A | Trickled down the road approximately 50ft. And evaporated. | Y | N | N |  |  | Subsequent to clearing the roots from the main line, surface cleanup was done to mitigate released overflow.
| 023033 | Phone | 5/21/2003 8:00:00 AM | Graham Wright | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2003-05-20 13:30 | 2003-05-20 14:00 | 6.66 | 200 | 198 | 2 | 777 Gainsborough Drive | Laguna Beach | 92651 | OR | Manhole in Easement | 0 |  | Construction | City staff were advised by a contractor that there was sewage trickling out of the ground at the bottom of 777 Gainsborough Drive. City staff arrived on scene and proceeded to the bottom of the property on Crestview where they sandbagged the storm drain. I advised City crews that there was a buried manhole at the bottom of the property. Crews jetted the line from the downstream manhole but were unable to open up the line. A local contractor who was also on scene assisted us with a backhoe to locate the buried manhole and (See correction column for further info) | open it up. We had our City contractor (WESCO) televise the line and discovered that there was an 8-inch screw plug that had been installed in the City's main line by persons unknown. This caused the manhole to surcharge and overflow. (See Remarks Column for more info) | N | Y | N | Storm Drain | N/A | Pumped back into the City's vacuum truck | Y | N | N |  |  | Crews vacuumed up the surcharged manhole and the storm drain. Crews also flushed the street with water and swept everything back up into the vacuum truck.
| 023034 | Phone | 5/22/2003 1:00:00 PM | Graham Wright | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2003-05-21 13:00 | 2003-05-21 13:20 | 2.5 | 50 | 49 | 1 | 1647 Hillcrest Drive | Laguna Beach | 92651 | OR | Residence at 1647 Hillcrest Drive | 2 | 3/24/2003 | Roots | The Water Quality Division received a call from the resident Jane Longwell at 12:50. She stated that there was sewer overflowing into her residence at 1647 Hillcrest. Crews immediately responded to the location and arrived at 13:00. There was a plumber on scene who stated that the manhole in front of this location was surcharged. Field staff confirmed the surcharged manhole. A plumber was also observed cleaning a lateral approx. 5 times upstream of this location. | City crews jetted from the downstream manhole #12 upstream to manhole #13 and cleared the stoppage in the main line. An emergency cleaning company was called to clean up the residence. The blockage was unusual in nature (see remarks column for further information) | N | N | N | N/A | N/A | Cleaned from the residence at 1647 Hillcrest Drive | Y | N | N |  |  | (From Overflow Collection Column)....... A video truck was dispatched to determine the condition of the main line along the reaches immediately downstream and upstream of the blockage. During cleaning operations, minor roots and dark soot like material was observed. Nothing substantial was captured in the rake downstream of the apparent blockage. The plumbers found at the two different residences along the same block were questioned. Roots were being cleared from the private lateral upstream of the blockage. The amount of roots pushed into the main could not be quantified.
| 023035 | Voice Mail | 5/22/2003 3:30:00 AM | Graham Wright | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2003-05-22 02:30 | 2003-05-22 02:40 | 50 | 500 | 499 | 1 | 464 Cliff Drive | Laguna Beach | 92651 | OR | Bypass Discharge Hose | 0 |  | Construction | A City contractor (WESCO) was bypassing a City main line using a portable pump. The pump's discharge hose failed at a joint and released sewage into the street. Cause of the hose failure has been identified to be three hose clamps loosening from the cycling of the pipe pressurizing | The bypass pump was turned off on site. A vacuum truck was immediately used to recover the spill | N | Y | N | Storm Drain | N/A | Vacuumed up all overflow with a vacuum truck | Y | N | N |  |  | An air plug had been installed in the nearest downstream catch basin by the City as a preventative measure. This provided emergency retention and prevented any sewage from reaching the beach. This bypass had been operating for approximately 17 hours prior to the discharge hose failure. As a result of this hose clamp failure, all clamps will be checked at a minimum of three hours on future bypass operations.
X | 023036 | Phone | 5/22/2003 12:10:00 PM | Graham Wright | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2003-05-22 12:05 | 2003-05-22 12:15 | 4 | 40 | 10 | 30 | 658 S. Coast Hwy | Laguna Beach | 92651 | OR | Private Lateral | 0 |  | Roots | Water quality staff received a call from a citizen alerting us to a sewer problem at 658 S. Coast Hwy. Staff arrived on scene and checked the City's main line and determined that the problem was from the private lateral. | Staff used a vacuum truck until a plumber arrived and made repairs to the lateral. We also televised and cleaned our City's main line. Staff washed down the area and recovered all water in the area. The previous property owner was legally obligated to effect repairs on the offending private lateral. The current owner has been notified. The owners representative indicated that repairs will be immediately pursued. While traces of overflow were identified at the outlet, the OCHCA determined that no further action was required. | N | Y | N | Storm Drain | N/A | Trace amounts at Sleepy Hollow storm drain outlet were identified. All overflow was removed. | Y | N | N |  |  |  |  | X
X | 023037 | Phone | 5/30/2003 4:00:00 PM | Graham Wright | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2003-05-30 15:15 | 2003-05-30 15:30 | 0.37 | 40 | 39 | 1 | 187 N. Coast Hwy | Laguna Beach | 92651 | OR | Public Restrooms | 0 |  | Debris | Water Quality staff reported to a call of the North Main Beach restrooms backing up and responded to the scene. Upon arrival we found that the lateral serving the public restrooms at 187 N. Coast Hwy was plugged with paper towels. This caused water to back up into the restroom, flow out of the floor drains and onto the restroom entry. | A plumber was hired to snake the lateral from the roof vent. This restored the flow to the collection system. City staff recovered all overflow water and cleaned up the area. | N | N | N | N/A | N/A | Backed up into the restroom and onto a public walkway area. All water was recovered by City Staff | Y | N | N |  |  |  |  | X
| 023038 | Phone | 6/5/2003 11:00:00 AM | Graham Wright | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2003-06-05 08:30 | 2003-06-05 08:40 | 7.5 | 75 | 0 | 75 | 635 Alta Vista Way | Laguna Beach | 92651 | OR | Manhole in Driveway | 2 | 5/11/2003 | Roots | Water Quality staff received a call from the resident at 635 Alta Vista Way in reference to a sewer problem on his driveway. Staff arrived on scene and confirmed that a City manhole had surcharged and had overflowed into a dirt area. | City staff removed a large amount of roots from the manhole and the City main line. These roots had been pushed down from a private lateral. Staff used a high pressure jetter and cleaned upstream and downstream of this location. | N | N | N | N/A | N/A | Soaked into the dirt area at 635 Alta Vista Way | Y | N | N |  |  | The surface area of the dirt soaked by the spill was removed. All visible solids were disposed of.
| 023039 | Phone | 6/5/2003 4:15:00 PM | Graham Wright | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2003-06-05 14:45 | 2003-06-05 15:15 | 0.5 | 15 | 10 | 5 | 875 Katella | Laguna Beach | 92651 | OR | Lateral Cleanout Cover | 0 |  | Roots | Water Quality Staff were notified by a plumber that he had encountered problems while cleaning a lateral at 875 Katella. Staff responded to the location and determined that the plumber had pushed roots in to the City's main line from the lateral cleanout, which caused water to back up into and out of the cleanout. | Staff used a high pressure jetter and were able to open the City's main line from the downstream manhole. This allowed the standing water in the lateral to drain. | N | N | N | N/A | N/A | Staff estimated that five gallons soaked into the vegetation and dirt. Ten gallons drained back into the cleanout. | Y | N | N
| 023024 | Voice Mail | 04/10/03 1613 | Armond Badillo | 7608010867 | City of Oceanside | City of Oceanside | 2003-04-10 14:30 | 2003-04-10 14:48 | 3 | 54 | 0 | 54 | 501 San Luis Rey Drive | Oceanside | 92054 | SD | Manhole | 0 |  | ROOTS | Roots and Grease in City Main. | Line will be TV'd. | N | Y | N | None |  | "Perc" Basin at I-5 & San Luis Rey Drive. | Y | N | N |  |  | City will "jet" lines in area and TV condition.
| 023025 | David Harisson | 04/22/03 0857 | Mark Patnode | 7604355840 | City of Oceanside | City of Oceanside | 2003-04-22 07:25 | 2003-04-22 08:15 | 1 | 150 | 150 | 0 | 3760 Vista Campana South | Oceanside | 92054 | SD | Manhole | 0 |  | ROOTS | Roots and Grease in City Main. | Line will be TV'd. | Y | Y | N | None |  | Spill absorbed by debris in storm drain. Vactor recovered entire contents of storm drain. | Y | N | N |  |  | City will "jet" lines in area and TV condition.
| 023026 | Quarterly Report |  | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 2003-04-28 10:20 | 2003-04-28 10:20 | 0 | 25 | 0 | 0 | 2302 La Paz | Oceanside | 92054 | SD | Manhole | 0 |  | ROOTS | Roots in City Main | Area maintained by rodder. Line will be TV'd. | N | N | N | None |  | Dried up in the street. | Y | N | N |  |  | Small wet spot in middle of street. Starter manhole has very little flow.
| 023027 | Quarterly Report |  | Michael Heiser | 7604355870 | City of Oceanside | City of Oceanside | 2003-06-25 16:02 | 2003-06-25 16:52 | 8 | 400 | 0 | 400 | 3202 Vista Way | Oceanside | 92054 | SD | Manhole | 1 | 2003-03-19 | ROOTS | An upstream blockage moved downstream to roots and forced a manhole ring and lid ajar. | Line was jetted and roots removed. | N | N | N | None |  | Soaked into ground. | Y | N | N
X | 023023 | QUARTERLY REPORT |  | Joel V. Holt | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2003-04-02 12:50 | 2003-04-02 13:15 | 2 | 50 | 40 | 10 | 304 E. Mission Road | Fallbrook | 92028- | SD | Cleanout | 0 |  | PRIVATE PROPERTY | Shredded up T-shirt with roots wrapped around it. | Rodded cleanout and sprayed disinfectant. Used vactor to recover 40 gallons. | N | N | N | None. | None. | Side of road and evaporated on asphalt. | Y | N | N |  | 0 | COURTESY NOTIFICATION. Disinfected area. Recovered as much as possible. |  | X | 0
X | 023024 | FAX 858-571-6972 | 04/21/2003 14:23 | Kyle Drake | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2003-04-21 09:00 | 2003-04-21 09:30 | 1 | 30 | 1 | 29 | 1000 block S. Mission Road | Fallbrook | 92028- | SD | Cleanout | 0 |  | PRIVATE PROPERTY | Property cleanout was plugged with roots and rags approximately 10 feet down. | Rodded 6" cleanout with 6" cutter. | N | Y | Y | Fallbrook Creek | Lake O'Neill, Santa Margarita, Pacific Ocean | NA | Y | N | Y | Along Creek | 3 | COURTESY NOTIFICATION. 6" cleanout was unplugged with rodder. Wash down water was used and all wash down water was recovered. Signs were posted and will remain for 3 days. And in 6 weeks, we will camera lateral for future maintenance. We also vactore |  | X | 1
X | 023025 | FAX 858-571-6972 | 04/29/2003 13:20 | Patti S. Page | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2003-04-28 14:00 | 2003-04-28 14:15 | 2 | 30 | 27 | 3 | 404 E. Mission Road | Fallbrook | 92028- | SD | 4" cleanout | 0 |  | PRIVATE PROPERTY | The cleanout overflowed due to grease in the lateral. | The cleanout was rodded with the rodding machine with the 4" cutter on it twice. Dammed up and vactored. | N | Y | N | None. | None. | Somewhere in the storrm drain system. Do not believe it reached surface waters. | Y | N | N |  | 0 | COURTESY NOTIFICATION. Told owner not to put grease into sewer system. Flushed storm drain with approximately 50 gallons of water. Do not know exactly where storm drain system flows (County owned). |  | X | 1
| 023026 | QUARTERLY REPORT |  | Joel V. Holt | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2003-05-27 09:00 | 2003-05-27 09:45 | 0.889 | 40 | 40 | 0 | 215 W. Fallbrook Street | Fallbrook | 92028- | SD | Manhole | 0 |  | GREASE | Grease blockage in mainline. | Cleared blockage and flushed line. Used a chain flail cutter nozzle on second run and brought back grease. TV'd mainline and it was clear. | N | N | N | None. | None. | Sewage ran down the road and got dammed up before it hit the storm drain. | Y | N | N |  | 0 | Recovered all of overflow. |  |  | 0
| 023027 | FAX 858-571-6972 | 06/08/2003 12:30 | Kyle Drake | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2003-06-07 13:15 | 2003-06-07 14:00 | 20 | 900 | 0 | 900 | 526 W. Aviation | Fallbrook | 92028- | SD | Manhole. | 0 |  | ROOTS | Root blockage in mainline. | Cleaned between manhole C17 and C18 with flush truck using flail nozzle and regular nozzle. Ran line 3 times. | N | Y | Y | Fallbrook Creek | Lake O'Neill, Santa Margarita River, Pacific Ocean |  | Y | N | Y | Every 100 Feet Along Creek | 3 | Went downstream on Naval Weapons Station and vacuumed 1000 gallons of water from creek. |  |  | 1
| 023028 | FAX 858-571-6972 | 06/17/2003 12:15 | Patti S. Page | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2003-06-17 08:05 | 2003-06-17 08:20 | 15 | 225 | 50 | 175 | Intersection of E. Dougherty & N. Main | Fallbrook | 92028- | SD | Manhole | 1 | 09-08-02 | GREASE | Grease blockage in mainline. | Flushed mainline 3 times and vacuumed. Also flushed downstream mainline and vacuumed out two top manholes. | N | Y | N | None. | None. | Dirt ditch on private property. Property was fenced. | Y | N | N |  | 0 | Overflow that was not recovered, soaked into dirt drainage ditch on private property. Ditch has heavy vine and brush growth in it. |  |  | 1
| 023029 | FAX 858-571-6972 | 06/19/2003 07:45 | Patti S. Page | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2003-06-18 18:00 | 2003-06-18 18:30 | 2 | 60 | 30 | 30 | Intersection of W. Ivy St. & Pasadena St. | Fallbrook | 92028- | SD | Manhole | 1 | 12-06-02 | ROOTS | Roots in manhole by B100. | Flushed from manhole B178 to B100. At 95 feet hit stoppage and cleared mainline and washed down road. Flushed and vactored storm drain on both sides of road on N. Mission at W. Alvarado Street. | N | Y | N | None. | None. | Evaporated on blacktop and went into storm drain. Flushed & vactored storm drain. | Y | N | N |  | 0 | Will follow up with CCTV inspection. Returning on 6-19-03 to run flail through mainline. |  |  | 1
| 023003 | FAX (858) 571-6972 | 2003-04-01 09:00 | Dave Seymour | (949) 459-6540 | Santa Margarita Water District | Santa Margarita Water District | 2003-04-01 07:45 | 2003-04-01 08:08 | 35 | 805 | 150 | 655 | Alas de Paz/Via Amistosa | Rancho Mission Viejo | 92688 | OC | Manhole | 0 | N/A | Other | Unknown - Probably rootball. Line blockage cleared up before crew set trap. An inspection of the line after the incident failed to reveal a cause. Line last cleaned in July 2002. | Blockage cleared itself. Crews inspected the line to make sure the line was clean and intact. | N | Y | Y | Trabuco Creek | San Juan Creek/Pacific Ocean | 150 Gallons - Vactor Truck 655 Gallons - Environment | Y | Y | N
| 023004 | FAX (858) 571-6972 | 2003-06-25 09:30 | Dave Seymour | (949) 459-6540 | Santa Margarita Water District | Santa Margarita Water District | 2003-06-25 07:30 | 2003-06-25 07:40 | 0.4 | 25 | 0 | 25 | Oso/Felipe Road | Mission Viejo | 92688 | OC | Manhole | 0 | N/A | GREASE | Grease ball lodged in pipe on downstream side of manhole located on Felipe & Oso Pkwy causing sewage to back up and flow out of manhole. | Jet rodded 8-inch sewer line segment from Felipe Rd to Oso Pkwy; Vactored grease particles. Video line segment. | Y | Y | Y | Oso Creek | Doheny/Pacific Ocean |  | Y | N | N
| 023012 | Clay Clifton DEH 619-338-2174 | 1000hr. - 5/7/03 | William Wiltse | 619-660-2007 | County of San Diego | County of San Diego | 2003-05-06 09:30 | 2003-05-06 10:30 | 3 | 180 | 0 | 180 | Quary Rd. (Easement) | Co.S.D. | na | SD | 586-052-633C | 0 | na | OTHER | Pihole in steel pipe | Contractor Repaired | N | N | N | na | na | Dry sandy area | Y | N | N | na | 0
| 023005 | Fax | 4-11-03 11:00am | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2003-04-10 20:00 | 2003-04-10 20:15 | 20 | 300 | 290 | 10 | 380 Ave. Pico San Clemente | San Clemente | 92672 | OC | Solids Dewatering Station | 0 | 0 | OTHER | Alarm and Controller Failure | Alarm and controller repaired | N | Y | Y | Flood Channel |  | Pacific Ocean | Y | N | N
| 023006 | Phone | 5-23-03 2:35pm | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2003-05-23 09:00 | 2003-05-23 09:30 | 6.6 | 200 | 150 | 50 | 100 Ave Linda Lane | San Clemente | 92672 | OC | Lateral Line | 0 | 0 | CONSTRUCTION | Contractor severed line while constructing a new sewer pump station | Re-connect private lateral line | N | N | N | None | None | Soaked into the surrounding soil | Y | N | N
X |  | Fax | 4-10-03 4:00pm | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2003-04-10 | 2003-04-10 11:00 |  | 0 | 0 |  | 410 Calle Vista Torito | San Clemente | 92672 | OC | Private Lateral | 0 | 0 | Blockage | Line Blockage | Domestic water supply shut off until repairs are complete | N | N | N | None | None | Golf course Landscape | Y | N | N |  |  |  |  | X
X |  | Phone | 6-12-03 5:00pm | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2003-06-12 07:39 | 2003-06-12 10:00 | 1 | 150 | 45 | 105 | 265 W. Marquita | San Clemente | 92672 | OC | Private Lateral | 0 | 0 | LINE BREAK | Broken Lateral on the bluff slope | Private system repaired | N | N | N | None | None | Soaked in the surrounding soil | Y | N | N |  |  |  |  | X
X |  | Fax | 6-25-03 3:00pm | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2003-06-25 | 2003-06-25 12:00 |  | 5 | 5 |  | 101 Ave. Dominguez | San Clemente | 92672 | OC | Private Lateral | 0 | 0 | BLOCKAGE | Private Lateral Blockage | Private system repaired | N | Y | N | None | None | Dry canyon storm drain system | Y | N | N |  |  |  |  | X
| 023001 | VOICEMAIL | 2003-04-05 17:00 | Ramon Zuniga | (760) 728-1178 | Rainbow Municipal Water District | Rainbow Municipal Water District | 2003-04-03 | 2003-04-05 23:00 | 292 | 1200000 | 0 | 1200000 | Mission Rd at N. River Rd | Bonsall | 92003 | SD | LS #2 Forcemain | 0 | 0 | LINE BREAK | 12-inch Cast Iron force main installed in 1973. Failure of pipe. Pipe had signs of deterioration. | Shut down lift station #2 feeding force main, bypass main line by pumping from wet well and transporting with tank trucks to gravitymanhole downstream at N. River Rd and Holly Lane. Called Contractor to repair break. Installed temporary bypass line and connection to bypass river section of Force Main. | N | N | N | None | None | Percolated into ground in sandy area | Y | Y | Y | San Luis Rey River & Pacific Ocean | 3 | Water samples at mouth of river showed no signs of reaching ocean
| 023002 | Victor Vasquez | 2003-04-14 08:00 | Ramon Zuniga | (760) 728-1179 | Rainbow Municipal Water District | Rainbow Municipal Water District | 2003-04-11 09:46 | 2003-04-11 10:10 | 1000 | 24000 | 0 | 24000 | 30516 Old River Road | Bonsall | 92003 | SD | Lift Station #2 | 1 | 2003-04-03 | PUMP STATION FAILURE | SDG&E Power Outage and simultaneous failure of emergency backup generator | Called in pump trucks to bypass lift station. Repaired emergency generator. SDG&E restored power to area. | N | N | N | None | None | Open field - heavy brush | Y | Y | N | NA | 0
|  | FAX | 2003-04-21 | Joe Smith | 619 336-4587 | City of National City | City of National City | 2003-04-21 | 2003-04-21 | 0 | 1125 | 0 | SD | 91950 | 170 | 0 | Shop rags | a large amount of shop rags found in sewer mainline | Mial clean and locking manhole lid installed | n | y | n/a | n/a | 63 inch storm drain | y | n | n | 0
| 023004 | this report | 2003-07-09 17:00 | D Catone | (619) 825-3810 | City of Lemon Grove | City of Lemon Grove | 2003-06-09 08:15 | 2003-06-19 09:00 | 1 | 45 | 45 | 0 | Jefferson St | Lemon Grove | 91945 | SD | 480-39-02 | 0 | 0 | BLOCKAGE | roots, grease | fully contained on asphalt surface at public works yard.full return by way of property cleanout. | N | N | N | none | none | full containment | Y | N | Y | none | 0 | Easement adjacent to public works facility.
| 023001 | FAX (858) 571-6972 | 2002-07-26 11:53 | D Catone | (619) 582-1413 | City of Lemon Grove | City of Lemon Grove | 2002-07-25 08:15 | 2002-07-26 01:30 | 1.33 | 240 | 50 | 190 | Alford St/Dayton St | Lemon Grove | 91945 | SD | 479-16 NH 01-03 | 0 | none | GREASE | Heavy roots from service lateral 55 ft from MH | Main line jetted & rootcut. TV on 7/26 to check cleaning. | N | N | N | none | none | Dirt Alley | Y | N | N | none | 0 | Phone conversation w/ Environ Health No signs needed.
| 023002 | FAX (858) 571-6972 | 2002-08-19 17:27 | D Catone | (619) 582-1413 | City of Lemon Grove | City of Lemon Grove | 2002-08-19 08:30 | 8-19-02 11 ;00 | 10 | 1500 | 400 | 1100 | Shea Lane | Lemon Grove | 91945 | SD | 576-15 MH 02 | 0 | none | VANDALISM | MH cover stolen. Rocks, debris dropped into system | contained & pumped to downstream mh. Contractor removed rocks from mainline, rejetted, video, City crew lugged manhole lid w/cement | N | Y | N | none | none | Dirt ditch.No sign of flow at city limits | Y | N | N | none | 0 | Photo's of containment site available
| 023003 | Fax 858-571-6972 | 2003-01-28 08:20 | D Catone | (619) 825-3810 | City of Lemon Grove | City of Lemon Grove | 2003-01-27 07:45 | 2003-01-27 09:30 | 0.5 | 60 | 0 | 60 | Taft St Easement | Lemon Grove | 91945 | SD | 576-53-01 | 0 | 0 | BLOCKAGE | paper towels with some roots | Line cleaned & root cut. Will be CCTV'd on1/28/03 for review | N | N | N | none | none | dirt easement | Y | N | Y | Rear easement behind 1509 Woodrow St | 5 | Trickle flow. no solids. dirt easement. vegitation.area sanitized.
| 23020 | Chiara Clemente | SSO QTR Report | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2003-04-10 09:30 | 2003-04-10 09:32 | 5 | 10 | 10 | 0 | MCTSSA, Pump Station 31334 | MCB, CAMP PENDLETON | 92055-5008 | SD | PS 31334 | 1 | 12/11/2002 (Inc #381) | PumpStationFailure | A few bolts on the pump station pipe connection had sheared off during use and when pump was signaled into operation the sewage being pumped was leaking. | CORRECTIVE: The damaged pump number one was taken out of service, and the alternative pump number two was put into service till the first pump is serviced. PREVENTATIVE: The pump vendor will be notified of the problem with the connection bolts. | N | N | N | None | None | None | N | N | N | None. | 0 | Location flowed through: Spill traveled from pump station west 75 feet over asphalt where it was recovered by a pumper truck and the area was limed for disinfection.. Total distance traveled: 75 Feet.
| 23021 | Chiara Clemente | 2003-04-15 08:45 | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2003-04-14 13:15 | 2003-04-14 15:15 | 120 | 14400 | 0 | 14400 | Vandegrift Blvd. ( 22 area) | MCB, CAMP PENDLETON | 92055-5008 | SD | Manholes: 3-Y-2, 3-Y-3, 3-Y-4 and 3-Y-76 | 2 | 9/1/2002 (Inc #322), 2/25/2003 (Inc #413) | Infiltration | The excessive inflow of rain water to the collection system during the rain event caused a mix of storm water and sewage to backup in the 18 inch influent line at STP #3. | CORRECTIVE: Spill stopped after the rain ended and the flow decreased enough that the pipe capacity was adequate to carry the flow. PREVENTATIVE: Regularly scheduled preventative maintenance on upstream storm water culverts. | Y | Y | Y | Santa Margarita River | Pacific Ocean | Pacific Ocean | Y | Y | Y | Del Mar Beach, Camp Pendleton | 4 | According to the Camp Pendleton Weather Station we received 1.27 inches of rain for the day during the incident on 4/14/03. See written report for beach sample data. Total distance traveled: 1215 feet to Santa Margarita River.
| 23022 | Chiara Clemente | 2003-04-18 13:30 | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2003-04-17 13:45 | 2003-04-17 14:10 | 4 | 100 | 0 | 100 | Bldg. 22186, Building 22186 | MCB, CAMP PENDLETON | 92055-5008 | SD | Clean out building # 22186 Line Type: Clay 8 Inch | 0 | NA | Grease | Grease blockage in the line caused an overflow of a cleanout located behind mess hall building 22186. | CORRECTIVE: Line was jetted to clear the debris. PREVENTATIVE: Continue education of mess hall personnel on proper handling and disposal of grease. | Y | Y | N | None | None | Overflow did not reach actual receiving waters but: Storm drain. | N | N | N | None. | 0 | Spill traveled 40 feet North West over pavement to street then 150 feet South West along street to storm drain inlet. Total distance traveled: 190 feet. Expected public contact: No
| 23023 | Chiara Clemente | SSO QTR Report | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2003-04-19 09:20 | 2003-04-19 10:30 | 6.86 | 480 | 350 | 130 | Building 336A Davis Ct | MCB, CAMP PENDLETON | 92055-5008 | SD | Manhole 13Y179 Line Type: VCP Line Size: 8 inch | 0 | NA | Blockage | The sewer line was blocked with debris including ice plant, trash, and toys. | CORRECTIVE: Blockage was cleared from sewer line using jetter. PREVENTATIVE: Continued education of housing tenants. PM of lines base wide. | N | N | N | None | None | Ponded on grassy area between housing units 335 and 336 on Davis Ct. | Y | NA | Y | Signs posted around perimeter where spill ponded and percolated. | 5 | According to the Camp Pendleton Weather Station we received less than 0.01 inches of rain for the day during the incident on 4/17/03. Spill from manhole 200 feet across grassy/dirt area to low spot.
| 23024 | Chiara Clemente | SSO QTR Report | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2003-05-01 09:00 | 2003-05-01 09:05 | 80 | 400 | 0 | 400 | LS # 330216, 33 Area | MCB, CAMP PENDLETON | 92055-5008 | SD | LiftStation #330216 wet well | 0 | NA | Power failure | Electrical problem. Control for lift station fail. | CORRECTIVE: Ran pumps by hand. Replaced control panel of lift station. PREVENTATIVE: This pump station will be connected to the base monitoring system under a project scheduled for 2004. In the meantime daily inspection continues. | N | N | N | None | None | Overflow did not reach actual receiving waters but: Abandoned percolation pond | Y | N | N | None. | 0 | Remarks: Location flowed through: From lift station across dirt road to abandoned perculation pond.. Total distance traveled: 150 ft. Expected public contact: No

## Drop-down lists
Sewer Agency List | County | SSO Cause Short | Yes or No
Buena Sanitary District | OC | BLOCKAGE | Y
Carlsbad Municipal Water District | RV | CONSTRUCTION | N
City of Chula Vista | SD | DEBRIS
City of Coronado |  | FLOOD DAMAGE
City of Del Mar |  | GREASE
City of El Cajon |  | INFILTRATION
City of Encinitas |  | LINE BREAK
City of Escondido |  | MANHOLE FAILURE
City of Imperial Beach |  | OTHER
City of La Mesa |  | POWER FAILURE
City of Laguna Beach |  | PRIVATE PROPERTY
City of Lemon Grove |  | PUMP STATION FAILURE
City of National City |  | ROCKS
City of Oceanside |  | ROOTS
City of Poway |  | UNKNOWN
City of San Clemente |  | VANDALISM
City of San Diego
City of San Juan Capistrano
City of Solana Beach
City of Vista
County of San Diego
Eastern Municipal Water District
Elsinore Valley Municipal Water District
El Toro Water District
Emerald Bay Community Services District
Fairbanks Ranch Community Services District
Fallbrook Public Utilities District
Irvine Ranch Water District
Leucadia County Water District
Moulton Niguel Water District
Murrieta County Water District
Olivenhain Municipal Water District
Otay Water District
Padre Dam Municipal Water District
Pauma Valley Community Services District
Rainbow Municipal Water District
Ramona Municipal Water District
Rancho Santa Fe Community Services District
Rancho California Water District
Santa Margarita Water District
South Coast County Water District
Trabuco Canyon Water District
U.S. Marine Corps, Camp Pendleton
U.S. Navy Public Works Center
Vallecitos Water District
Valley Center Municipal Water District
Whispering Palms Community Services District
Private Party