## Sheet1
San Francisco Bay Water Board - Sanitary Sewer Overflow (SSO) eReporting Program Database Records (from Dec. 1, 2004 to May 2, 2007)
SSO TRACK_NUMBER | AGENCY SSO REPORT NUMBER | VERSION | SSO AGENCY NAME | SUBMIT_DATE | SPILL_VOLUME (in gallons) | VOLUME RECOVERED (in gallons) | OES_CONTROL_NUMBER | DATE_ORIGINALLY_REPORT | ORIGIN_REPORTED_BY | ENTERED_BY | INCIDENT_LOCATION | INCIDENT_CITY | INCIDENT_COUNTY | INCIDENT_ZIP | INCIDENT LONGITUDE | INCIDENTS_LATITUDE | INCIDENT_DATE | INCIDENT_TIME | INCIDENT_END_DATE | INCIDENT_END_TIME | INCIDENT_DESCRIPTION | INCIDENT_SITE | SPILL_CLEANED_UP_BY | SPILL_WEATHER | MAGNITUDE | WATERBODY_WATERSHED_REGION | FINAL_SPILL_DESTINATION | BEACH_CLOSURE? | BEACH_CLOSURE_DETAIL | ANY_FISH_KILL? | HEATH_WARNING_POST? | VISUAL_INSPECTION_RESULT | INITIAL_INCIDENT_DESCRIPTION | CORRECTIVE_RESPONSIVE_ACTION_TAKEN? | CLEANUP_ACTION_TAKEN? | DISINFECT_ACTION_TAKEN? | REPAIRS_MADE? | PROPOSITION65_NOTIFY? | SAMPLE_COLLECTED? | SAMPLE_REPORTED? | INCIDENT_REACH_STATE_WATER_BODY? | ON_GOING_INVESTIGATION? | INVESTIGATION_COMPLETION_DATE | INVESTIGATION_STATUS | STAFF_PERSON_ASSIGNED_TO | REGIONAL_BOARD_PHONE | STAFF_PERSON_EMAIL_SENT_TO | DISCHARGER | SPILL_SOURCE | OTHER_SOURCE_DESCRIPTION | SPILL_CAUSE | BLOCKAGE_DESCRIPTION | INFRASTRUCTURE_DESCRIPTION | OTHER_CAUSE_DESCRIPTION | BRIEF_DISCUSSION | SIG_TITLE | SUBMITTER_NAME | SUBMITTER_SIGNED_DATE | SUBMITTER_PHONE | SUBMITTER_EMAIL | REPORT_TYPE | CONTACT_PARTY_NAME | CONTACT_PARTY_AGENCY | CONTACT_PARTY_PHONE | CONTACT_PARTY_EXTENSION | CONTACT_PARTY_STREET_ADDRESS | CONTACT_PARTY_CITY | CONTACT_PARTY_COUNTY | CONTACT_PARTY_ZIP | SUSPECT_PARTY_NAME | SUSPECT_PARTY_AGENCY | SUSPECT_PARTY_PHONE | SUSPECT_PARTY_EXTENSION | SUSPECT_PARTY_STREET_ADDRESS | SUSPECT_PARTY_CITY | SUSPECT_PARTY_COUNTY | SUSPECT_PARTY_ZIP
5154 | 11 | 2 | Alameda | 2007-04-26 10:57 | 40 | 0 |  | 2007-04-26 10:57 |  | -- | 581 Creedon Circle | Alameda | Alameda | 94501 |  |  | 2007-04-24 |  |  |  | Contacted Alameda County Health Agency Posted signs around lagoon area where spill occured Collected samples for lagoon water contamination. Signs will remain posted until water tests clean | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Maint Supv | Larry Strunk | 2007-04-25 | 510 747-7900
5032 | 10 | 1 | Alameda | 2007-04-03 14:04 | 100 | 0 |  | 2007-04-03 14:04 |  | -- | Barbers Point Rd and Main St. | Alameda | Alameda | 94501 |  |  | 2007-04-02 |  |  |  | Coupling failed in forced main. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | INFRASTRUCTURE FAILURE | -- Select One -- |  | Break in forced main |  | Maint Supv | Larry Strunk | 2007-04-03 | 510 747-7900
4988 | 9 | 1 | Alameda | 2007-03-23 10:42 | 200 | 0 |  | 2007-03-23 10:42 |  | -- | 331 Stardust Place | Alameda | Alameda | 94501 |  |  | 2007-03-22 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Maint Supv | Larry Strunk | 2007-03-23 | 510 747-7900
4118 | 7 | 1 | Alameda | 2006-11-17 15:10 | 200 | 0 |  | 2006-11-17 15:10 |  | -- | 125 Bay Park Terrace | Alameda | Alameda | 94501 |  |  | 2006-11-10 |  |  |  | None | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Maint Supv | Larry Strunk | 2006-11-17 | 510 747-7900
4149 | 8 | 1 | Alameda | 2006-11-24 | 1450 | 1450 | 06-655 | 2006-11-24 | Larry Strunk | Alameda | Tinker Ave between Main Street and Mosely Ave | Alameda | Alameda | 94501 |  |  | 2006-11-08 | 0.70833 |  |  | Leak in 6" forced main |  |  |  | Low |  | STORM DRAIN | No |  | No | No | None |  | Yes | Yes | Yes |  |  | Yes | Yes |  |  |  | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE | Leak in 6" forced main | INFRASTRUCTURE FAILURE | -- Select One -- | BREAKAGE OF COLLECTION SYSTEM |  |  | Supervisor | Larry Strunk | 2006-11-24 | 510 747-7900
4088 | 6 | 1 | Alameda | 2006-11-08 17:28 | 5100 | 5100 | 06-6655 | 2006-11-08 | Larry Strunk |  | Tinker Ave between Main St. and Mosley Ave. | Alameda | Alameda | 94501 |  |  | 2006-11-07 | 5:00:00 AM | 2006-11-08 | 10:00:00 A | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Public Works Supervi | Larry Strunk | 2006-11-08 | 510-747-7900 | sdickson@ci.alameda.ca.us,LStrunk@ci.alameda.ca.us,qnguyen@ci.alameda.ca.us,pcarrai@ci.alameda.ca.us, mnacleri@ci.alameda.ca.us | 24HR |  |  | 510 747-7900 | [6 empty] | Alameda
4259 | 6 | 2 | Alameda | 2006-11-08 | 1450 | 1450 | 06-6655 | 2006-11-08 | Larry Strunk | Alameda | Tinker Ave between Main St. and Mosley Ave. | Alameda | Alameda | 94501 |  |  | 2006-11-07 | 0.20833 | [6 empty] | Low |  | STORM DRAIN | No | None | No | No | None |  | Yes | Yes | Yes |  |  | Yes | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | OTHER |  | INFRASTRUCTURE FAILURE | -- Select One -- | BREAKAGE OF COLLECTION SYSTEM | Hole in 6" forced main | See attached | Public Works Supervisor | Larry Strunk | 2006-11-08 | 510-747-7900
3859 | 5 | 1 | Alameda | 2006-09-08 09:21 | 900 | 0 |  | 2006-09-08 09:21 |  | -- | 1 Singleton Ave | Alameda | Alamed | 94501 |  |  | 2006-09-07 |  |  |  | 200 gallons of the overflow was on the ground and 700 gallons went into the storm drain. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Alameda | PUMP STATION |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Supervisor | Larry Strunk | 2006-09-08 | 510 747-7900 | sdickson@ci.alameda.ca.us,LStrunk@ci.alameda.ca.us,qnguyen@ci.alameda.ca.us,pcarrai@ci.alameda.ca.us, mnacleri@ci.alameda.ca.us | MINOR
3661 | 4 | 1 | Alameda | 2006-07-25 17:01 | 250 | 0 |  | 2006-07-25 17:01 |  | -- | Intersection of Creedon Circle and Nakayama Ct. | Alameda | Alameda | 94501 |  |  | 2006-07-25 |  |  |  | Electrical component failure in sanitary sewer pump station. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Alameda | MANHOLE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Supervisor | Larry Strunk | 2006-07-25 | 510-747-7900 | sdickson@ci.alameda.ca.us,LStrunk@ci.alameda.ca.us,qnguyen@ci.alameda.ca.us,pcarrai@ci.alameda.ca.us, mnacleri@ci.alameda.ca.us | MINOR
3566 | 3 | 1 | Alameda | 2006-06-27 15:41 | 10 | 0 |  | 2006-06-27 15:41 |  | -- | Intersection of Central Avenue and McKay Ave | Alameda | Alameda | 94501 |  |  | 2006-06-27 |  |  |  | Called in by Citizen. Main was down when we arrived at site. Hydro'd main but no apparent stoppage. There was approximately 10 gallons in curb area next to manhole. All 10 gallons was recovered with Vacon. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Alameda | MANHOLE |  | CAUSE UNKNOWN | --Select None-- |  |  |  | Maint Supv | Larry Strunk | 2006-06-27 | 510 747-7900 | sdickson@ci.alameda.ca.us,LStrunk@ci.alameda.ca.us,qnguyen@ci.alameda.ca.us,pcarrai@ci.alameda.ca.us, mnacleri@ci.alameda.ca.us | MINOR
3494 | 2 | 2 | Alameda | 2006-06-16 16:29 | 1500 | 5 | 06-3547 | 2006-06-14 | Larry Strunk | Alameda | Chuck Corica Golf Course Clubhouse Memorial Road | Alameda | Alameda | 94501 |  |  | 2006-06-14 | 7:40:00 AM | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | No | Spill went onto D.I. that discharged into Golf Course Slough. Visual inspection revealed clear liquid. No solids or paper. |  | Yes | Yes | No | No | No | Yes | No | No | No | 2006-06-30 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Alameda | MANHOLE |  | INFRASTRUCTURE FAILURE | --Select None-- | PUMP STATION FAILURE |  | Lift Station failed causing back up that overflowed manhoke in Golf Course Club House parking lot. Overflow went to D.I. that discharges into Golf Course slough. The slough level is controled by pumps that discharge to the Bay. Pumps were disabled until samples are returned. No water was discharged to Bay. | Public Works Supervi | Larry Strunk | 2006-06-14 | 510-747-7900 | sdickson@ci.alameda.ca.us,LStrunk@ci.alameda.ca.us,qnguyen@ci.alameda.ca.us,pcarrai@ci.alameda.ca.us, mnacleri@ci.alameda.ca.us | MAJOR | Larry Strunk | Alameda | 510 747-7900 |  | 1616 Fortmann Wa;y | Alameda | Alameda | 94501 | Larry Strunk | Alameda | 510 747-7900 |  | 1616 Fortmann Way | Alameda | Alameda | 94501
1714 | 1 | 1 | Alameda | 2005-08-23 10:19 | 700 | 0 |  | 2005-08-23 10:19 |  | -- | 1815 Broadway | Alameda | Alameda | 94501 |  |  | 2005-08-22 |  |  |  | Blockage occured at about 8:00pm and was reported to the on call person at around 9:00pm. By the time he was able to respond and clear the stoppage, the main was overflowing through a cleanout at the above address. The clean up occured imediately after the stoppage was relieved. Approximately 200 gallons of spill was recovered. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Alameda | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | Maint Supv | Larry Strunk | 2005-08-23 | 510 747-7900 | sdickson@ci.alameda.ca.us,LStrunk@ci.alameda.ca.us,qnguyen@ci.alameda.ca.us,pcarrai@ci.alameda.ca.us, mnacleri@ci.alameda.ca.us | MINOR
3276 | 5 | 1 | Albany | 2006-05-03 16:27 | 208 | 0 |  | 2006-05-03 16:27 |  | -- | 877 Washington Ave | Albany | Alameda | 94710 |  |  | 2006-05-03 |  |  |  | This manhole is located on an easement at 877 Washington Ave. The blockage occurred right at the manhole inlet. The manhole is an old brick structure and roots from a close tree invaded the manhole and blocked the inlet pipe. The City crew complete removed the roots and removed the blockage, cleaned and disinfected the referenced yard and is now looking for a contractor for a manhole replacement/restoration. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Albany | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Associate Civil Engi | Ana Bernardes | 2006-05-03 | 510-524-3751 | rcunningham@albanyca.org, abernardes@albanyca.org | MINOR
3147 | 3 | 1 | Albany | 2006-04-11 15:55 | 500 | 0 |  | 2006-04-11 15:55 |  | -- | Intersection of Buchanan and Polk | Albany | Alameda | 94706 |  |  | 2006-04-11 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Albany | MANHOLE |  | FLOW CAPACITY DEFICIENCY | --Select None-- |  |  |  | Supervisor | John Medlock | 2006-04-07 | 510-5594270 | rcunningham@albanyca.org, rcunningham@albanyca.org | MINOR
3151 | 4 | 1 | Albany | 2006-04-12 09:04 | 400 | 0 |  | 2006-04-12 09:04 |  | -- | 1059 Peralta Avenue | Albany | Alameda | 94706 |  |  | 2006-04-11 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Albany | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | John Medlock | 2006-04-12 | 5105594270 | rcunningham@albanyca.org, rcunningham@albanyca.org | MINOR
2899 | 2 | 2 | Albany | 2006-02-28 11:52 | 15000 | 0 | 06-1238 | 2006-02-28 | Ana Bernardes | Ana Bernardes | Buchanan Ave at Polk Street | Albany | Alameda | 94710 |  |  | 2006-02-27 | 5:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No | Samples from the Marin Creek outfall on the Bay were taken and submitted to the EBMUD laboratory. We are waiting now for the results. there were no fish kill. | No | No | Precaution Measures Taken: Area was coned off and posted and supervised untill the surcharge stopped. City crew performed cleaning afterwards. |  | Yes | Yes | Yes | No | No | Yes | No | Yes | No | 2006-02-28 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Albany | MANHOLE | This manhole is only 4 feet deep and has a 14-inch running through. Improvements upstream may have increased the flow of rainfall derived I&I to this location. | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | The manhole on Buchanan with Polk surcharged after several days of intense rainfall. Sewage immediately found its way into three storm drain inlets and was discharged to the San Francisco Bay via a closed 18-inch conduit to a closed 84-inch RCP that crosses under I80/580 and into the Bay. The rainfall amount on the 02/27/06 was expected to reach approximately 2 inches in 24 hours, and it followed already several days of rainfall. The area was coned off and posted and supervised until the surcharge passed and clean-up was done. This manhole is only 4 feet deep and recently improvements upstream increased the flow of rainfall derived I&I to this location. We are already smoke testing a large tributary area in order to locate the cross connections and source of inflow upstream. If the smoke testing does not reveal the problem, an emergency project may be necessary to install a relief sewer. | Associate Civil Eng | Ana Bernardes | 2006-02-28 | 510-524-3751 | rcunningham@albanyca.org, abernardes@albanyca.org, rleptien@albanyca.org | MAJOR | Ana Bernardes | Albany | 510-524-9543 |  | 548 Cleveland Ave | Albany | Alameda | 94710 |  | Albany | 510-524-9543 |  | 548 Cleveland Ave | Albany | Alameda | 94710
2636 | 1 | 3 | Albany | 2006-01-17 16:02 | 24000 | 0 | 06-0425 | 2006-01-12 | Ana Bernardes | Ana Bernardes | Buchanan Street at Polk | Albany | Alameda | 94710 |  |  | 2005-12-31 | 6:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | Precautionary Measures Taken: Area was coned off and posted and supervised until the storm passed. |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Albany | MANHOLE | Storm Event: Reported rainfall amounts of approximately 3.5 inches in 24 hours which corresponds roughly to a 15 year event.Problem: This manhole is only 4 feet deep and has a 14 inch line running through. Improvements upstream may have increased hastened the flow of rainfall derived I&I to this location. This pipe line was slip lined approximately 15 years ago. | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | Narrative description: Sewage immediately spilled into three storm drain inlets at the intersection of Polk and Buchanan and was discharged to San Francisco Bay via a closed 18 inch conduit to a closed 84 inch RCP that crosses under I80 / 580 and into the bay. Storm Event: Reported rainfall amounts of approximately 3.5 inches in 24 hours which corresponds roughly to a 15 year event. Precautionary Measures Taken: Area was coned off and posted and supervised until the storm passed. Problem: This manhole is only 4 feet deep and has a 14 inch line running through. Improvements upstream may have increased hastened the flow of rainfall derived I&I to this location. This pipe line was slip lined approximately 15 years ago. Approach to problem: City will smoke test the tributary sewers immediately in order to locate a cross connection or source of inflow upstream. If smoke testing does not reveal the problem, an emergency project may be necessary to install a relief sewer or increase the size of the existing sewer in Buchanan between Polk and Pierce Streets. | Associate Civil Engi | A Bernardes | 2006-01-12 | 510-524-9543 | rcunningham@albanyca.org, abernardes@albanyca.org, Rleptien@albanyca.org | MAJOR | Rich Cunningham | Albany | 510-524-9758 |  | 548 Cleveland ave | Albany | Alameda | 94710 |  | City of Albany | 510-524-9543 |  | 548 Cleveland Ave | Albany | Alameda | 94710
5190 | 8 | 1 | AlmonteSD | 2007-05-01 14:01 | 10 | 0 |  |  |  | -- | 264 Morning Sun Avenue | Mill Valley | Marin | 94941 |  |  | 2007-05-01 |  |  |  | Spill from rod hole LHA 713.11. Serves 2 homes. Reported at 1100 hrs. Roto Rooter cleared at 1130 hrs. Very small amount spilled. Approximately 10 gallons.Not overflowing when Roto Rooter was on scene. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Manager | Bonner Beuhler | 2007-05-01 | 415-388-8775
4075 | 6 | 1 | AlmonteSD | 2006-11-07 10:26 | 300 | 0 |  | 2006-11-07 10:26 |  | -- | 25 Homestead Blvd | Mill Valley | Marin | 94941 |  |  | 2006-11-04 |  |  |  | Spill from rod hole located on easement at 25 Homestead BL. Call reported at 0830 hrs. Overflow intermittent but cleared at 1330 hrs. Roto Rooter cleared. Technician broke cable and had to call for backup which is why it took so long. Spill on property and some in unimproved curb and gutter of street. Cleaned by Roto Rooter with Vactor. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | AlmonteSD | OTHER | Rod Hole | BLOCKAGE | ROOTS |  |  |  | Manager | Bonner Beuhler | 2006-11-07 | (415) 388-8775 | pribking@aol.com, AlmonteSD@aol.com, | MINOR
3220 | 5 | 1 | AlmonteSD | 2006-04-21 10:02 | 150 | 0 |  | 2006-04-21 10:02 |  | -- | 261 Cleveland Avenue | Mill Valley | Marin | 94941 |  |  | 2006-04-19 |  |  |  | LH 645.37, map page 5. Backyard of 261 Cleveland Ave. End of run, 2 houses on line. Cleared by Roto Rooter. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | AlmonteSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Manager | Bonner Beuhler | 2006-04-21 | (415) 388-8775 | pribking@aol.com, AlmonteSD@aol.com, | MINOR
2804 | 4 | 1 | AlmonteSD | 2006-02-14 10:43 | 200 | 0 |  | 2006-02-14 10:43 |  | -- | 138 Stadium Avenue | Mill Valley | Marin | 94941 |  |  | 2006-02-13 |  |  |  | Spill at Rod hole LH A 302.07 in easement @ 138 Stadium Avenue, Mill Valley, CA Reported at 1545 hrs. Roto Rooter responded at 1550 hrs. Stoppage cleared at 1630 hours. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | AlmonteSD | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Manager | Bonner Beuhler | 2006-02-14 | (415) 388-8775 | pribking@aol.com, AlmonteSD@aol.com, | MINOR
2499 | 3 | 1 | AlmonteSD | 2006-01-04 15:05 | 600 | 0 |  | 2006-01-04 15:05 |  | -- | 157 Lark Lane | Mill Valley | Marin | 94941 |  |  | 2005-12-31 |  |  |  | Partial stoppage of district line by root ball caused backup into downstairs of house, mostly water due to infiltration in sewer. 5" of rain on 12/31/05. Spill contained in house. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | AlmonteSD | OTHER | Downstairs of house | BLOCKAGE | ROOTS |  |  |  | Manager | Bonner Beuhler | 2006-01-04 | (415) 388-8775 | pribking@aol.com, AlmonteSD@aol.com, | MINOR
978 | 2 | 1 | AlmonteSD | 2005-02-07 15:26 | 300 | 0 |  | 2005-02-07 15:26 |  | -- | MH #125A - 126 beside 225 Rosemont Avenue | Mill Valley | Marin | 94941 |  |  | 2005-02-05 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | AlmonteSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Manager | Bonner Beuhler | 2005-02-07 | 415-388-8775 | pribking@aol.com, AlmonteSD@aol.com | MINOR
615 | 1 | 1 | AlmonteSD | 2004-12-22 08:13 | 850 | 0 |  | 2004-12-22 08:13 |  | -- | Rod hole in backyard sewer easement behind 215 California Avenue | Mill Valley | Marin | 94941 |  |  | 2004-12-16 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | AlmonteSD | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Manager | Bonner Beuhler | 2004-12-22 | 415-388-8775 | pribking@aol.com, AlmonteSD@aol.com | MINOR
1911 | 1 | 1 | AltoSD | 2005-10-04 09:37 | 100 | 0 |  | 2005-10-04 09:37 |  | -- | 39 Plaza Drive Mill Valley, Ca | Mill Valley | Marin | 94941 |  |  | 2005-09-30 |  |  |  | responded to immediately by roto rooter | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | AltoSD | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Manager | Tom Roberts | 2005-10-04 | 415-388-3696 | tomroberts7@aol.com, TOMROBERTS7@AOL.COM | MINOR
3359 | 1 | 1 | AmericanCanyon | 2006-05-17 09:56 | 1300 | 0 | 06-2528 | 2006-04-27 | Fred Simonson | AmericanCanyon | City of American Canyon | American Canyon | Napa | 94503 |  |  | 2006-04-26 | 4:00:00 PM | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | No | Cleanup is complete. |  | Yes | Yes | Yes | No | No | Yes | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | AmericanCanyon | PUMP STATION |  | ELECTRICAL POWER FAILURE | --Select None-- | --Select None-- |  | After pump maintenance, the pumps failed to trun back on causing an overflow and a release. Cleanup is complete. | Manager | Fred Simonson | 2006-05-17 | 707-647-4368 | FredS@ci.american-canyon.ca.us | MAJOR | Fred Simonson | AmericanCanyon | 707-647-4368 |  | 205 Wetlands Edge Rd | American Canyon | Napa | 94503 |  | City of American Canyon
3360 | 2 | 1 | AmericanCanyon | 2006-05-17 10:13 | 6000 | 0 | 06-0147 | 2006-01-05 | 1/5/2006 | AmericanCanyon | American Canyon Creek to North Napa River | American Canyon | Napa | 94503 |  |  | 2005-12-31 | 5:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Medium |  | SURFACE WATER IMPACT | No |  | No | No | The sewer system was overfilled due to recent excessive rain. |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | AmericanCanyon | PUMP STATION |  | NATURAL DISASTER | --Select None-- | --Select None-- |  | Flood event on 12/31/05 overwhelmed the drainage system and the sewage system exceeded capacity due to inflow and infiltration. SSO occurred on 12/31/05. OES Control Number 06-0147 | Manager | Fred Simonson | 2006-05-17 | 707-647-4368 | FredS@ci.american-canyon.ca.us | MAJOR | Fred simonson | AmericanCanyon | 707-647-4368 |  | 205 Wetlands Edge Road | American Canyon | Napa | 94503 |  | American Canyon
5163 | 2 | 5 | AngleIsland | 2007-04-26 | 1600 | 0 | 07-2541 |  | Eric D. Osman | AngelIsland | Angel Island State Park Immigration Station Sewage Lift Station | Tiburon | Marin | 94920 |  |  | 2007-04-26 | 0.16667 |  |  | 8" line at manhole narrows down to 4" before entering a 90 degree angle bend without a sanitary T. Also, pipe connecting two lift station tanks is only 2"(not affecting this spill). |  |  |  | High | San Francisco Bay | STORM DRAIN | No | Area is currently under construction and is not open to the public. | No | No | Recieving water appeared normal. |  | Yes | No | No |  |  | Yes | No |  |  | 2007-07-01 | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE | 8" line at manhole narrows down to 4" before entering a 90 degree angle bend without a sanitary T. Also, pipe connecting two lift station tanks is only 2"(not affecting this spill). | BLOCKAGE | DEBRIS FROM LATERALS | MULTIPLE CAUSES |  | See attached | Sector Superintendent | Dave Matthews | 2007-04-26 | 415-435-8339
4646 | 1 | 1 | AngleIsland | 2007-01-10 | 1200 | 1195 | 07-0671 | 2007-01-10 | Fernando F Guzman | angelisland | Angel Island State Park(Immigration Station Contruction Site) | Tiburon | Marin | 94920 |  |  | 2007-01-10 | 0.625 | [6 empty] | Low |  | YARD/LAND | No |  | No | Yes | No spillage reached bay |  | Yes | Yes | Yes |  |  | No | Yes |  |  |  | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | PUMP STATION |  | NATURAL DISASTER | -- Select One -- | -- Select One -- |  |  | Water/Wastewater Sup | Fernando F Guzman | 2007-01-31 | 415-435-9221
4843 | 1 | 1 | BayshoreSD | 2007-02-27 | 9000 | 20000 | 07-1283 | 2007-02-27 | Sergio Ramirez | FosterCity/EMID | 909 E. Hillsdale Blvd. and Edgewater Blvd. at Lift Station 29. | Foster City | San Mateo | 94404 |  |  | 2007-02-27 | 0.32292 |  |  | The discharge hose to a 6” bypass pump ruptured, while Lift Sta. No. 29 was being bypassed. The lift station was being bypassed because of an independent failure. |  |  |  | Low | Region 2 | CAPTURED IN STORM DRAIN | No |  | No | No | Foster City's storm drain system is considered a "wet barrel system" meaning the storm drains and catch basins are always surcharged with storm water because of the City's receiving lagoon elevation. The storm drain system and its catch basin are hydraulically plugged from the lagoon. There is no evidence that the spill reached the City's receiving lagoon. |  | Yes | Yes | Yes |  |  | No | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE | The discharge hose to a 6” bypass pump ruptured, while Lift Sta. No. 29 was being bypassed. The lift station was being bypassed because of an independent failure. | BYPASS | -- Select One -- | MULTIPLE CAUSES |  | The discharge hose to the 6” bypass pump ruptured, while Lift Sta. No. 29 was being bypassed. The bypass was put in place because of an independent failure at the lift station. While the bypass was in operation, the discharge hose to the bypass pump developed a pin hole and ruptured causing a sanitary sewer overflow. The overflow was approximately 9000 gallons. The City/District responded to the SSO within 30 minutes of the hose rupture. After shutting off the bypass pump, the Collection System Crew used the Combo-Unit to vacuum the spill from the walkway areas and a sink hole which developed because of the hose rupture. All surface areas were washed down into a catch basin where the spill was being contained. The catch basin was then vacuumed out to recover the spill. All of the released waste water was recovered in addition to 11,000 gallons of storm water that was in the catch basin/storm drain system. | PWSuperintendent | Sergio Ramirez | 2007-03-01 | 650-286-3544
2731 | 6 | 1 | Belmont | 2006-02-01 13:10 | 100 | 0 |  | 2006-02-01 13:10 |  | -- | 317 Middle Rd. | Belmont | San Mateo | 94002 |  |  | 2006-01-24 |  |  |  | Hand rodded sewer main to clear blockage. Cleaned surrounding area of all debris and standing water. The next day we jetted the main line as a follow up measure to make sure the line was clear. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | BELMONT | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Senior Maint. wk. | Tim Murray | 2006-02-01 | 650-637-2932 | kphalen@ci.belmont.ca.us, rdavis@ci.belmont.ca.us | MINOR
2605 | 4 | 3 | Belmont | 2006-01-11 14:19 | 90000 | 0 | 06-0095 | 2006-01-03 | Tim Murray | BELMONT | 1180 Kedieth St.- cross street Old Ralston Rd. | Belmont | SanMateo | 94002 |  |  | 2006-01-02 | 11:01:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Low | Belmont Creek/SF Bay | STORM DRAIN | No |  | No | No | No visual indication of sewage (paper). Receiving water at very high flow and turbid with suspended sediments so could not see any indication of sewage in receiving water |  | Yes | No | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | BELMONT | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | The manhole that overflowed is near the end of the Belmont system. City staff are in communication with our treatment plant (South Bayside System Authority) to verify that lift station was operating appropriately. It appears at storm peak, total flows through City were about 12.4 MGD, exceeding City's discharge rights of 11.8 MGD and lift station pumping capacitity of 12 MGD. We can provide further flow information if requested. | City Engineer | Kathleen Phalen | 2006-01-11 | 650-595-7469 | kphalen@belmont.gov; rdavis.belmont.gov | MAJOR | Kathleen | City of Belmont | 650-595-7469 |  | 1 Twin Pines Lane, Ste 385 | Belmont | San Mateo | 94002 |  | BELMONT
1363 | 3 | 1 | Belmont | 2005-05-05 12:23 | 280 | 0 |  | 2005-05-05 12:23 |  | -- | Heritage Court easement | Belmont | San Mateo | 94002 |  |  | 2005-05-03 |  |  |  | Overflow caused by roots and broken pipe. Upon arrival diverted water into downstream manhole. Retrived 130 gallons from spill site. Cleared line with rodder truck up 14 feet from downstream manhole. Cleaned and disenfected area around spill. Videoed easement line and have scheduled line to be dug up and repaired. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | belmont | PIPE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Senior Maintenance w | Tim Murray | 2005-05-05 | 650-637-2932 | kphalen@ci.belmont.ca.us, rdavis@ci.belmont.ca.us | MINOR
1346 | 2 | 1 | Belmont | 2005-05-02 08:28 | 180 | 0 |  | 2005-05-02 08:28 |  | -- | 1605 Belburn Drive | Belmont | San Mateo | 94002 |  |  | 2005-04-30 |  |  |  | Overflowed caused by paper in main line. Overflow came out of cleanout in rear yard. Clearded main line and cleaned rear yard and retrieved 150 gallons of sewage. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | BELMONT | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | Services Manager | Randy Ferrando | 2005-05-02 | (650) 595-7464 | kphalen@ci.belmont.ca.us, rdavis@ci.belmont.ca.us | MINOR
593 | 1 | 1 | Belmont | 2004-12-20 10:47 | 417 | 0 |  | 2004-12-20 10:47 |  | -- | 1309 Notre Dame Avenue | Belmont | San Mateo | 94002 |  |  | 2004-12-19 |  |  |  | M/H 443309 to 443310. Ran flusher truck to clear blockage. Cleaned area, disinfected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Belmont | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sr Maintenance Worke | Tim Murray | 2004-12-20 | 650-637-2932 | tmurray@ci.belmont.ca.us | MINOR
5085 | 23 | 2 | Benicia | 2007-03-06 | 1000 | 0 | 07-1459 | 2007-03-06 | Rick Silva | Benicia | 2054 Columbus Parkway | Benicia | Solano | 94510 |  |  | 2007-03-06 | 0.39583 |  |  | Contractor was flushing a new Water Main on a construction site. They were flushing the water into the new sewer main on site that was tied into the City system. The amount of water they were flowing overwhelmed the Cities Sewer Lift Station causing the manhole in the street to overflow. |  |  |  | Low | Carquinez Straits | STORM DRAIN | No |  | No | No | No visual observation of any clean up needed. Was all clear water that overflowed. |  | Yes | No | No |  |  | Yes | Yes |  |  |  | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE | Contractor was flushing a new Water Main on a construction site. They were flushing the water into the new sewer main on site that was tied into the City system. The amount of water they were flowing overwhelmed the Cities Sewer Lift Station causing the manhole in the street to overflow. | INFLOW & INFILTRATION | -- Select One -- | -- Select One -- | Construction Water |  | Field Utilities & St | Rick Silva | 2007-03-06 | 707-746-4396
3672 | 22 | 1 | Benicia | 2006-07-28 08:37 | 100 | 0 |  | 2006-07-28 08:37 |  | -- | 365 Military East | Benicia | Solano | 94510 |  |  | 2006-07-28 |  |  |  | The backup/overflow spilled out of a manhole in front of above address continuing east alone the curb barely reaching the SD catch basin located in front of 457 Military East. Once the blockage was cleared,the City crew set up the Vaccon Truck at said SDCB and captured the majority of the spill via flowing the fire hydrant( just west of the spill)as a wash down until all signs of the spill was removed. The spill was reported to the OES and Control # 06-4481 was obtained. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Benicia | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Foreman | Ed Tanzo | 2006-07-28 | (707)726-4296 | Jerry Gall@ci.benicia.ca.us, ctomasik@ci.benicia.ca.us | MINOR
3449 | 21 | 1 | Benicia | 2006-06-03 20:33 | 100 | 0 |  | 2006-06-03 20:33 |  | -- | N/E Corner of Polk and Jackson Sts. | Benicia | Solano | 94510 |  |  | 2006-06-03 |  |  |  | The backup/overflow spilled around the immediate area surrounding the overflow manhole(located behind the sidewalk on Polk St.)continuing south alone the sidewalk for approximately 30 ft. collecting in the storm drain catch basin located at the incident site. The Office of Emergency Services (OES) was contacted and control number (#06-3313). | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Benicia | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Foreman | Ed Tanzo | 2006-06-03 | (707)746-4296 | jbailey@ci.benicia.ca.us, ctomasik@ci.benicia.ca.us | MINOR
2799 | 17 | 2 | Benicia | 2006-02-14 08:01 | 100 | 100 | 06-0887 | 2006-02-10 | Ed Tanzo | Benicia | 365 Military East in basement of residence | Benicia | Solano | 94510 |  |  | 2006-02-10 | 8:41:00 AM | [5 empty] | SUNNY WEATHER | Low |  | BUILDING/STRUCTURE | No |  | No | No | SSO backed up in comncrete basement. Once main was cleared sewage went back into line. Ideal Corporation responded to perform cleanup in basement. |  | Yes | Yes | No | No | No | No | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Benicia | OTHER | Homeowner had lateral problem on 2/9/06 plumber cleared lateral. Did not contact City. On 2/10/06 homeowner had problem again, called City. City crew cleaned main and found some roots and a cordless drill battery was lodged in line. | BLOCKAGE | MULTIPLE CAUSES | --Select None-- |  |  | Foreman | Ed Tanzo | 2006-02-10 | 707-746-4296 | jgall@ci.benicia.ca.us, RSilva@ci.benicia.ca.us, CTomasik@ci.benicia.ca.us, MThrone@ci.benicia.ca.us | MAJOR | Rick Silva | Benicia | 707-746-4296 |  | 2400 East 2nd street | Benicia | Solano | 94510 | City of Benicia | benicia | 707-746-4296 |  | 2400 East 2nd street | Benicia | Solano | 94510
2755 | 16 | 1 | Benicia | 2006-02-02 15:32 | 500 | 0 |  | 2006-02-02 15:32 |  | -- | Bayshore at Harbor | Benicia | CA | 94510 |  |  | 2006-02-02 |  |  |  | Overflow occurred at a force main air relief. The air relief broke allowing raw sewage to leak out. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Benicia | PIPE |  | INFRASTRUCTURE FAILURE | MULTIPLE CAUSES |  |  |  | Superintendent | John Bailey | 2006-02-02 | (707) 746-4294 | jbailey@ci.benicia.ca.us, rsilva@ci.benicia.ca.us | MINOR
2821 | 18 | 1 | Benicia | 2006-02-16 12:24 | 600 | 0 |  | 2006-02-16 12:24 |  | -- | East 7th & J street | Benicia | Solano | 94510 |  |  | 2006-01-14 |  |  |  | original report inadvertently filed as a 24Hr notice. This is an ammended report | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Benicia | PUMP STATION |  | BLOCKAGE | DEBRIS |  |  |  | Superintendent | Gerald Gall | 2006-02-16 | 707-746-4294 | jgall@ci.benicia.ca.us | MINOR
2878 | 20 | 1 | Benicia | 2006-02-27 07:35 | 300 | 0 |  | 2006-02-27 07:35 |  | -- | 300 East H Street (next to space #1) | Benicia | Solano | 94510 |  |  | 2006-01-09 |  |  |  | All overflow was captured and cleaned up. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | benicia | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | P.W. Supervisor | Rick Silva | 2006-02-27 | 707-746-4396 | rsilva@ci.benicia.ca.us, ctomasik@ci.benicia.ca.us | MINOR
2646 | 14 | 1 | Benicia | 2006-01-18 11:17 | 270 | 0 |  | 2006-01-18 11:17 |  | -- | 168 Carlisle Way | Benicia | Solano | 94510 |  |  | 2005-12-31 |  |  |  | Power failure caused by high winds and rain. Crews responded with portable emergency generator. This overflow was originally reported in the wrong (public) category - original tracking number was 2458. OES Control Number 06-0087 | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Benicia | PUMP STATION |  | ELECTRICAL POWER FAILURE | --Select None-- |  |  |  | Superintendent | John Bailey | 2006-01-18 | (707) 746-4294 | jbailey@ci.benicia.ca.us, ctomasik@ci.benicia.ca.us | MINOR
3042 | 15 | 2 | Benicia | 2006-03-20 12:06 | 11625 | 0 | 06-0098 | 2006-01-18 | John Bailey | Benicia | 111 & 113 El Bonito Way | Benicia | Solano | 94510 |  |  | 2005-12-31 | 4:15:00 AM | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | No | No inspection performed, extremely high tides and flooding at shore line. Not known whether overflow reached receiving water, however I reported that it did discharge runs overland. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Benicia | PUMP STATION |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | Overflow was caused by excessive flow due to rain storm, possibly inflow/infiltration. Overflow went directly to storm drain which then flows overland onto private property owned by Valero Refinery. This overflow was originally reported in the wrong category (public) therefore it was not properly logged to the data base. Original tracking number was 2460. | Superintendent | John Bailey | 2006-01-18 | (707) 746-4294 | jbailey@ci.benicia.ca.us, ctomasik@ci.benicia.ca.us | MAJOR | John Bailey | Benicia | 707-746-4294 |  | 614 East 5th Street | Benicia | Solano | 94510 | City of Benicia | Benicia | 707-746-4294 |  | 614 East 5th Street | Benicia | Solano | 94510
2819 | 13 | 3 | Benicia | 2006-02-16 11:44 | 10000 | 0 | 06-0086 | 2006-01-18 | John Bailey | Benicia | Chelsea Hills at Panorama Drive(s) | Benicia | Solano | 94510 |  |  | 2005-12-31 | 2:00:00 AM | [5 empty] | RAINY WEATHER | Low | Carquinez Strait | STORM DRAIN | No |  | No | No | No inspection performed extremely high tides and flooding at water line. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Benicia | PUMP STATION | Power failure caused by high winds and rain storm. High flow due to infiltration resulted in minor overflow persisting after emergency generator was started. | ELECTRICAL POWER FAILURE | --Select None-- | --Select None-- |  | The overflow was caused by a power failure. Crews responded with stand by generator. Heavy rains made normal clean-up impractical. Site of overland overflow was inspected, very little solid material escaped lift station hatch. Hard to estimate whether overflow actually reached water way. This overflow was originally reported in the wrong category (public) therefore it was not properly logged to the data base. Original tracking number was 2455. | Superintendent | John Bailey | 2006-01-18 | (707) 746-4294 | jbailey@ci.benicia.ca.us, ctomasik@ci.benicia.ca.us | MAJOR | John Bailey | Benicia | 707-746-4294 |  | 614 East 5th Street | Benicia | Solano | 94510 | City of Benicia | Benicia | 707-746-4294 |  | 614 East 5th Street | Benicia | Solano | 94510
2217 | 11 | 2 | Benicia | 2005-12-05 11:00 | 900 | 800 | 05-6956 | 2005-12-02 | Jim Phillips | Benicia | 2015 East 3rd Street (Robert Semple Elementary School- large grass field) | Benicia | Solano | 94510 |  |  | 2005-12-02 | 9:04:00 AM | [5 empty] | CLOUDY WEATHER | Medium |  | YARD/LAND | No |  | No | No | 8" SS Main overflowed approx. 900 gallons onto dirt/grass field area. |  | Yes | Yes | Yes | No | No | No | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Benicia | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES | --Select None-- |  | Overflowed called in by school district employee. Crews responded and jetted 8" City SS Main between manhole 309 and 310. Cleared roots, grease, paper, and rags. Approx. 300' of SS Main cleaned. Placed sump pump and flushed affected area with hydrant water, Used approx. 2-3 thousand gallons to washdown. Water was diverted into City sewer sytem. Placed barricades and caution tape around affected area and advised school of actions taken. | Maint. Worker 3 | Jim Phillips | 2005-12-02 | 707-746-4296 | RSilva@ci.benicia.ca.us, jbailey@ci.benicia.ca.us, ctomasik@ci.benicia.ca.us | MAJOR | Rick Silva | Benicia | 707-746-4396 |  | 2400 East 2nd St. | Benicia | Solano | 94510 | City of Benicia | Benicia | 707-746-4396 |  | 2400 East 2nd St. | Benicia | Solano | 94510
2111 | 10 | 3 | Benicia | 2005-11-14 15:03 | 1000 | 0 | 05-5265 | 2005-09-10 | Raymond Borquez | Benicia | 281 West "I" street, back yard | Benicia | Solano | 94510 |  |  | 2005-09-10 | 4:30:00 PM | [5 empty] | SUNNY WEATHER | Low |  | YARD/LAND | No | The original report stated that there was a fish kill and beach closure. There was not, the overflow was contained and did not reach any water way. | No | No | The s/s lateral at 281 West "I" street overflowed in the back yard due to a blockage in the main in the street. |  | Yes | Yes | Yes | No | No | Yes | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Benicia | OTHER |  | BLOCKAGE | MULTIPLE CAUSES | --Select None-- |  |  | P.W. Supervisor | Rick Silva | 2005-09-11 | 707-746-4396 | rsilva@ci.benicia.ca.us, ctomasik@ci.benicia.ca.us | MAJOR | Rick Silva | Benicia | 707-746-4396 |  | 2400 East 2nd Street | Benicia | Solano | 94510 | City of Benicia | Benicia | 707-746-4396 |  | 2400 East 2nd Street | Benicia | Solano | 94510
1485 | 9 | 1 | Benicia | 2005-06-03 14:34 | 500 | 0 |  | 2005-06-03 14:34 |  | -- | 266 East 2nd St. cross st. East B St. | Benicia | Solano | 94510 |  |  | 2005-06-03 |  |  |  | The backup/overflow was confined to the immediate area surrounding the overflow manhole. The Office of Emergency Services(OES)was contacted and a control number obtained(# 05-3323). | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Benicia | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Foreman | Ed Tanzo | 2005-06-03 | (707) 746-4296 | jbailey@ci.benicia.ca.us, ctomasik@ci.benicia.ca.us | MINOR
1351 | 8 | 1 | Benicia | 2005-05-03 13:05 | 100 | 0 |  | 2005-05-03 13:05 |  | -- | 480 Vista Ct. | Benicia | Solano | 94510 |  |  | 2005-05-03 |  |  |  | The backup/overflow was confined to the downstairs bathroom. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Benicia | OTHER | downstairs bathroom toilet | BLOCKAGE | ROOTS |  |  |  | supervisor | rick silva | 2005-05-03 | (707) 746-4396 | rsilva@ci.benicia.ca.us | MINOR
1176 | 7 | 1 | Benicia | 2005-03-14 08:45 | 100 | 0 |  | 2005-03-14 08:45 |  | -- | In alley behind 1023 West K Street | Benicia | Solano | 94510 |  |  | 2005-03-12 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Benicia | CLEAN OUT |  | CAUSE UNKNOWN | --Select None-- |  |  |  | Maint. Foreman | Ed Tanzo | 2005-03-14 | 707-746-4299 | jbailey@ci.benicia.ca.us, ETanzo@ci.benicia.ca.us | MINOR
1142 | 5 | 1 | Benicia | 2005-03-09 08:47 | 5 | 5 | 05-1544 | 2005-03-09 | Jim Phillips |  | 1845 East 3rd Street | Benicia | Solano | 94510 |  |  | 2005-03-08 | 9:00:00 AM | 2005-03-08 | 10:00:00 A | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Maint. Worker III | Jim Phillips | 2005-03-09 | 707-746-4296 | jphillips@ci.benicia.ca.us, jbailey@ci.benicia.ca.us | 24HR |  |  | 707-746-4296 | [6 empty] | Benicia
1144 | 6 | 1 | Benicia | 2005-03-09 09:11 | 5 | 0 |  | 2005-03-09 09:11 |  | -- | 1845 East 3rd Street | Benicia | Solano | 94510 |  |  | 2005-03-08 |  |  |  | 8" main line plugged with roots. Less than five gallons backed up into bathroom of church at above location. Customer cleaned up spill. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Benicia | PIPE |  | BLOCKAGE | ROOTS |  |  |  | Maint. Worker III | Jim Phillips | 2005-03-09 | 707-746-4296 | jphillips@ci.benicia.ca.us, jbailey@ci.benicia.ca.us | MINOR
1041 | 3 | 1 | Benicia | 2005-02-16 14:36 | 100 | 100 | 05-1055 | 2005-02-16 | Rick Silva |  | 1024 East 2nd Street | Benica | Solano | 94510 |  |  | 2005-02-16 | 11:08:00 A | 2005-02-16 | 12:15:00 P | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | P. W Supervisor | Rick Silva | 2005-02-16 | 707-746-4396 | rsilva@ci.benicia.ca.us, ctomasik@ci.benicia.ca.us | 24HR |  |  | 707-746-4396 | [6 empty] | Benicia
1043 | 4 | 1 | Benicia | 2005-02-16 14:44 | 100 | 0 |  | 2005-02-16 14:44 |  | -- | 1024 East 2nd Street | Benicia | Solano | 94510 |  |  | 2005-02-16 |  |  |  | 6" A.C. main line plugged with roots. Backed up into three vacant units. Photos were taken. Clean up inside performed buy Ideal Restoration. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Benicia | PIPE |  | BLOCKAGE | ROOTS |  |  |  | P.W. Supervisor | Rick Silva | 2005-02-16 | 707-746-4396 | rsilva@ci.benicia.ca.us, ctomasik@ci.benicia.ca.us | MINOR
5018 | 26 | 1 | BerkeleyCity | 2007-03-28 13:21 | 200 | 0 |  | 2007-03-28 13:21 |  | -- | 2017 Prince St | Berkeley | Alameda | 94703 |  |  | 2007-03-26 |  |  |  | Debris entered sanitary sewer mainline while city contractor was working on the traffic calming device (circle) at Prince/King. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | BLOCKAGE | DEBRIS |  | School drains/toilets |  | Sr PW Supv. | Undra Brown | 2007-03-28 | 5106446622x236
4182 | 26 | 1 | BerkeleyCity | 2006-12-04 | 800 | 0 |  | 2006-12-04 | Undra Brown |  | 1731 Prince St (Malcom X School) | Berkeley | Alameda | 94703 |  |  | 2007-03-26 | [10 empty] | No |  | No | No |  |  | No | No | No |  |  | No | No | [15 empty] | Sr. Supervisor | Undra Brown | 2006-12-04 | 510-644-6620
4347 | 30 | 1 | BerkeleyCity | 2006-12-15 12:50 | 100 | 0 |  | 2006-12-15 12:50 |  | -- | 1517 Alcatraz Ave. | Berkeley | Alameda | 94703 |  |  | 2006-12-15 |  |  |  | Entered on the wrong form. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sr PW Supv | Undra Brown | 2006-09-27 | 5106446620
4343 | 28 | 1 | BerkeleyCity | 2006-12-15 12:40 | 100 | 0 |  | 2006-12-15 12:40 |  | -- | 1539 Solano Ave. | Berkeley | Alameda | 94706 |  |  | 2006-12-15 |  |  |  | Entered on the wrong form. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Sr PW Supv | Undra Brown | 2006-12-15 | 5106446620
4184 | 27 | 1 | BerkeleyCity | 2006-12-04 11:19 | 800 | 0 |  | 2006-12-04 11:19 |  | -- | 2017 Prince St | Berkeley | Alameda | 94703 |  |  | 2006-11-30 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | SR. PW Supv. | Undra Brown | 2006-12-04 | 5106446620
4071 | 25 | 1 | BerkeleyCity | 2006-11-06 12:00 | 500 | 0 |  | 2006-11-06 12:00 |  | -- | 210 Alvarado Rd. | Berkeley | Alameda | 94705 |  |  | 2006-11-03 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | berkeleycity | MANHOLE |  | CAUSE UNKNOWN | --Select None-- |  |  |  | Senior PW Superviso | Undra Brown | 2006-11-06 | 5106446620 | jegeberg@ci.berkeley.ca.us, cford@ci.berkeley.ca.us | MINOR
4013 | 24 | 1 | BerkeleyCity | 2006-10-19 18:11 | 100 | 0 |  | 2006-10-19 | Undra Brown |  | 1539 Solano Ave | Berkeley | Alameda | 94706 |  |  | 2006-10-17 | 5:30:00 PM | 2006-10-17 | 7:00:00 PM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Sr. PW Supervisor | Undra Brown | 2006-10-19 | 510-644-6620 | jegeberg@ci.berkeley.ca.us, cford@ci.berkeley.ca.us | 24HR |  |  | 5106446620 | [6 empty] | berkeleycity
4345 | 29 | 1 | BerkeleyCity | 2006-12-15 12:45 | 125 | 0 |  | 2006-12-15 12:45 |  | -- | 1841 Berkeley Way | Berkeley | Alameda | 94704 |  |  | 2006-09-27 |  |  |  | Entered on the wrong form. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | CAUSE UNKNOWN | -- Select One -- |  |  |  | Sr PW Supv | Undra Brown | 2006-12-15 | 5106446620
3933 | 23 | 1 | BerkeleyCity | 2006-09-27 12:40 | 125 | 0 |  | 2006-09-27 | Undra Brown |  | 1841 Berkeley Way | Berkeley | Alameda | 94806 |  |  | 2006-09-26 | 10:00:00 A | 2006-09-26 | 11:15:00 A | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Senior PW Supervisor | Undra Brown | 2006-09-27 | 510-644-6620 | jegeberg@ci.berkeley.ca.us, cford@ci.berkeley.ca.us | 24HR |  |  | 5106446620 | [6 empty] | berkeleycity
3928 | 22 | 1 | BerkeleyCity | 2006-09-26 08:19 | 100 | 0 |  | 2006-09-26 | Undra Brown |  | 1517 Alcatraz Ave. | Berkeley | Alameda | 94703 |  |  | 2006-09-23 | 5:05:00 PM | 2006-09-23 | 5:35:00 PM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Senior Public Works | Undra Brown | 2006-09-26 | 510-644-6620 | jegeberg@ci.berkeley.ca.us, cford@ci.berkeley.ca.us | 24HR |  |  | 5106446620 | [6 empty] | berkeleycity
3517 | 21 | 1 | BerkeleyCity | 2006-06-20 08:51 | 200 | 0 |  | 2006-06-20 08:51 |  | -- | 3407 Adeline | Berkeley | Alameda | 94608 |  |  | 2006-06-19 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | berkeleycity | MANHOLE |  | CAUSE UNKNOWN | --Select None-- |  |  |  | Sr.PW Sir sup. | Undra Brown | 2006-06-20 | 5106446620 | jegeberg@ci.berkeley.ca.us, cford@ci.berkeley.ca.us | MINOR
3460 | 8 | 1 | BerkeleyCity | 2006-06-06 15:41 | 100 | 0 |  | 2006-06-06 15:41 |  | -- | 2753 Buena Vista Way | Berkeley | Alameda | 94708 |  |  | 2006-05-26 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | berkeleycity | CLEAN OUT |  | CAUSE UNKNOWN | --Select None-- |  |  |  | Sr PW Supervisor | Undra Brown | 2006-05-26 | 5106446620 | jegeberg@ci.berkeley.ca.us, cford@ci.berkeley.ca.us | MINOR
3456 | 7 | 1 | BerkeleyCity | 2006-06-06 15:37 | 200 | 0 |  | 2006-06-06 15:37 |  | -- | 65 Panoramic Way | Berkeley | Alameda | 94705 |  |  | 2006-05-05 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | berkeleycity | OTHER | Lamphole | CAUSE UNKNOWN | --Select None-- |  |  |  | Sr PW Supervisor | Undra Brown | 2006-05-05 | 5106446620 | jegeberg@ci.berkeley.ca.us, cford@ci.berkeley.ca.us | MINOR
3462 | 9 | 1 | BerkeleyCity | 2006-06-06 15:53 | 100 | 0 |  | 2006-06-06 15:53 |  | -- | 3090 Buena Vista Way | Berkeley | Alameda | 94708 |  |  | 2006-03-30 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | berkeleycity | MANHOLE |  | CAUSE UNKNOWN | --Select None-- |  |  |  | Sr PW Supervisor | Undra Brown | 2006-06-06 | 5106446620 | jegeberg@ci.berkeley.ca.us, cford@ci.berkeley.ca.us | MINOR
3464 | 10 | 1 | BerkeleyCity | 2006-06-06 15:58 | 100 | 0 |  | 2006-06-06 15:58 |  | -- | Codornices Park | Berkeley | Alameda | 94708 |  |  | 2006-02-06 |  |  |  | A small amount of the 100 gallon estimate might have made it into Codornices Creek | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | berkeleycity | MANHOLE |  | CAUSE UNKNOWN | --Select None-- |  |  |  | Sr PW Supervisor | Undra Brown | 2006-06-06 | 5106446620 | jegeberg@ci.berkeley.ca.us, cford@ci.berkeley.ca.us | MINOR
3508 | 16 | 1 | BerkeleyCity | 2006-06-20 08:11 | 200 | 0 |  | 2006-06-20 08:11 |  | -- | # 64 Panoramic | Berkeley | Alameda | 94705 |  |  | 2005-11-06 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | berkeleycity | MANHOLE |  | CAUSE UNKNOWN | --Select None-- |  |  |  | Sr. Sup | Undra Brown | 2006-06-20 | 510 644 --6620 | jegeberg@ci.berkeley.ca.us, cford@ci.berkeley.ca.us | MINOR
3515 | 20 | 1 | BerkeleyCity | 2006-06-20 08:40 | 900 | 0 |  | 2006-06-20 08:40 |  | -- | 1034 Keith | Berkeley | Alameda | 94708 |  |  | 2005-10-19 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | berkeleycity | MANHOLE |  | CAUSE UNKNOWN | --Select None-- |  |  |  | Sr PW Supervisor | Undra Brown | 2006-06-20 | 510 644-6620 | jegeberg@ci.berkeley.ca.us, cford@ci.berkeley.ca.us | MINOR
3499 | 12 | 1 | BerkeleyCity | 2006-06-19 09:52 | 300 | 0 |  | 2006-06-19 09:52 |  | -- | 783 Contra Costa | Berkeley | Alameda | 94706 |  |  | 2005-01-23 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | berkeleycity | MANHOLE |  | CAUSE UNKNOWN | --Select None-- |  |  |  | Sr PW Supervisor | Undra Brown | 2006-06-19 | (510)644-6620 | jegeberg@ci.berkeley.ca.us, cford@ci.berkeley.ca.us | MINOR
3497 | 11 | 1 | BerkeleyCity | 2006-06-19 09:46 | 100 | 0 |  | 2006-06-19 09:46 |  | -- | 1923 University Ave | Berkeley | Alameda | 94710 |  |  | 2005-01-21 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | berkeleycity | CLEAN OUT |  | CAUSE UNKNOWN | --Select None-- |  |  |  | Sr PW Supervisor | Undra Brown | 2006-06-19 | (510) 644-6620 | jegeberg@ci.berkeley.ca.us, cford@ci.berkeley.ca.us | MINOR
588 | 4 | 1 | BerkeleyCity | 2004-12-18 10:29 | 720 | 0 | 04-6641 | 2004-12-18 | Undra Brown |  | 1307 Alcatraz Ave. (City clean-out) | Berkeley | Alameda | 94702 |  |  | 2004-12-17 | 2:00:00 AM | 2004-12-17 | 4:00:00 AM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Assistant Supervisor | Ionatana Ieremia | 2004-12-18 | 5106446620 |  | 24HR |  |  | 5106446620 | [6 empty] | BerkeleyCity
628 | 5 | 1 | BerkeleyCity | 2004-12-23 14:14 | 1100 | 0 | 04-6641 | 2004-12-23 | Undra Brown | BerkeleyCity | 1307 Alcatraz (City Clean-out) | Berkeley | Alameda | 94702 |  |  | 2004-12-17 | 2:00:00 AM | [5 empty] | SUNNY WEATHER | Medium | Derby Creek (Oakland/Emeryville) | STORM DRAIN | No |  | No | No | Did not check outfall in Emeryville, creek is mostly culverted |  | Yes | Yes | No | No | No | No | No | Yes | No | 2005-01-15 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | BerkeleyCity | CLEAN OUT |  | BLOCKAGE | GREASE | --Select None-- |  | There were two events discharging for an estimated 3-hours elasped time. Follow-up investigation will consist of recleaning the mainline to determine if this site should be placed on a semi-annual follow up. | Sr PW Supervisor | Undra Brown | 2004-12-23 | 510-644-6620 | jegeberg@ci.berkeley.ca.us; rcardinaux@ci.berkeley.ca.us; mramirez@ci.berkeley.ca.us | MAJOR | Jeffery Egeberg | City of Berkeley | 510-981-6400 |  | 1947 Center St | Berkeley | Alameda | 94704 | Department of Public Works | City of Berkeley | 510-981-6400 |  | 1947 Center Street | Berkeley | Alameda | 94704
517 | 2 | 1 | BerkeleyCity | 2004-12-13 16:09 | 1800 | 0 | 04-6526 | 2004-12-13 | Undra Brown |  | 1126 Parker St | Berkeley | Alameda | 94702 |  |  | 2004-12-12 | 8:00:00 PM | 2004-12-12 | 8:45:00 PM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Assistant Supervisor | Michael Fermin | 2004-12-13 | 510-644-6620 |  | 24HR |  |  | 510-644-6620 | [6 empty] | BerkeleyCity
1062 | 6 | 2 | BerkeleyCity | 2005-02-18 16:08 | 1800 | 0 | 4-6526 | 2004-12-12 | Undra Brown | BerkeleyCity | 1126 Parker St | Berkeley | Alameda | 94702 |  |  | 2004-12-12 | 8:00:00 PM | [5 empty] | SUNNY WEATHER | Medium | Potter Creek | STORM DRAIN | No |  | No | No | No visual inspection of the outfall was done. |  | No | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | BerkeleyCity | CLEAN OUT |  | BLOCKAGE | GREASE | --Select None-- |  |  | Sr Supervisor | Undra Brown | 2005-02-18 | 510-644-6620 | jegeberg@ci.berkeley.ca.us, dakagi@ci.berkeley.ca.us, mramirez@ci.berkeley.ca.us | MAJOR | Jeffery Egeberg | City of Berkeley | 510-981-6400 |  | 1947 Center St | Berkeley | Alameda | 94704 | Department of Public Works | City of Berkeley | 510-981-6400 |  | 1947 Center Street | Berkeley | Alameda | 94704
411 | 1 | 1 | BerkeleyCity | 2004-12-05 09:35 | 2000 | 0 |  | 2004-12-05 | Undra Brown |  | 140 Panoramic Way-Backline main sewer rear of property. | Berkeley | Alameda | 94704 |  |  | 2004-12-04 | 8:00:00 AM | 2004-12-04 | 9:20:00 AM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Assistant Supervisor | Jamie Valencia | 2004-12-05 | 510-644-6620 |  | 24HR |  |  | 510-600-6620 | [6 empty] | BerkeleyCity
541 | 3 | 1 | BerkeleyCity | 2004-12-14 17:09 | 2000 | 0 | 046383 | 2004-12-14 | Undra Brown | BerkeleyCity | 140 Panoramic Way - Manhole #17-503-A2 (rear of the property) | Berkeley | Alameda | 94704 |  |  | 2004-12-04 | 8:00:00 AM | [5 empty] | SUNNY WEATHER | Low | Potter Creek | STORM DRAIN | No |  | No | No | When the responding supervisor responded to the complaint, he observed an overflow rate of approx. 20-25 gpm. The homeowner reported that he believes that the overflow started prior to him contacting the city crews. The actual start time of the of the overflow is unknown. Our estimate is based on what was observed when the crew arrived and the work was completed. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jyl@rb2.swrcb.ca.gov | BerkeleyCity | MANHOLE |  | BLOCKAGE | DEBRIS | --Select None-- |  |  | Sr PW Supervisor | Undra Brown | 2004-12-14 | 510-644-6620 |  | MAJOR | Undra Brown | City of Berkeley | 510-644-6620 |  | 2180 Milvia St | Berkeley | Alameda | 94704 | City of Berkeley | Dept. of Public Works | 510-644-6620 |  | 2180 Milvia St | Berkeley | Alameda | 94704
4665 | 7 | 1 | Brisbane | 2007-02-02 12:05 | 300 | 0 |  | 2007-02-02 12:05 |  | -- | Sierra Point Parkway and 101 Overpass (Force main from Sierra Point Lift Station) | Brisbane | San Mateo | 94005 |  |  | 2007-01-29 |  |  |  | Force main on City's Sierra Point Lift Station cracked on the bottom of the 8" HDPE pipe. Flow eventually surfaced through pavement on Sierra Point Parkway, which is how failure was detected. Maintenance crew member said street was dry the previous evening (1/28/07) at approximately 7 PM. Wet pavement was identified at approximately 7:30 AM the next morning (1/29/07). Flow was leaking out from pavement into gutter and into catch basin. Crews mobilized vactor truck by 8 AM and sucked out material from catch basin and jet cleaned the storm drain line. Some wastewater was likely not recovered that discharged to catch basin prior to crew response that morning. Staff traced storm drain line to final outlet in a brushy area near a tidally influenced drainage channel and did not observe evidence of significant discharge; any flow that came out of the end of the line appears to have infiltrated into the ground within several feet. There did not appear to be any surface water impact or public health threat. The end of the storm drain line outlet is about 75% plugged by debris, limiting any discharge. Spill estimate is approximate, given uncertainty of what time flow started coming out from under pavement. City had contractors on site to initiate repair on the line within several hours. City hired three additional vactor trucks to transport wastewater inflow to the lift station to a downstream lift station while the repair was ongoing. Line was repaired by 10 PM that night and pumps back online by 10:30 PM. No material was allowed to enter the storm drain after crew's initial response that morning. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | PIPE |  | INFRASTRUCTURE FAILURE | -- Select One -- |  | Lift Station Force Main |  | Assoc. Civil Eng. | Matthew Fabry | 2007-02-02 | 415-508-2134
3214 | 6 | 1 | Brisbane | 2006-04-20 17:25 | 150 | 0 |  | 2006-04-20 17:25 |  | -- | 3708 Bayshore Boulevard | Brisbane | San Mateo | 94005 |  |  | 2006-04-20 |  |  |  | Blockage occured in City's mainline gravity sewer along Bayshore Boulevard. Overflow was from a manhole in a vegetated area next to the road. Overflow volume is a very rough estimate, as there is already a lot of water in the overflow area due to groundwater/stormwater runoff from the adjacent slope, which made it difficult to determine volume attributed to the overflow, as well as how far the overflow actually went. Runoff in the area flows along the side of Bayshore Boulevard in a semi-vegetated swale, before dropping into a storm drain inlet. It was difficult to tell if the overflow actually reached the storm drain inlet. Overflow was identified by maintenance crews who were in the same area the previous day when there was no overflow. The blockage was cleared within approximately 25 minutes of identification using the City's vactor truck. Blockage appeared to be due to accumulated gravel and roots. Digital pictures are available of the overflow area upon request. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Brisbane | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Assoc. Civil Eng. | Matthew Fabry | 2006-04-20 | 415-508-2134 | mfabry@ci.brisbane.ca.us, rbreault@ci.brisbane.ca.us | MINOR
2915 | 4 | 1 | Brisbane | 2006-03-03 08:33 | 100 | 0 |  | 2006-03-03 08:33 |  | -- | Manhole at 381 Kings Road in Brisbane | Brisbane | San Mateo | 94402 |  |  | 2006-03-02 |  |  |  | City crews received a call from the public around 2 PM on 3/2/06 regarding flow from a manhole at 381 Kings Road. Crews immediately responded to the site. There was evidence of flow from the manhole going to a catch basin approximately 50 feet away, but the manhole was not overflowing when crews arrived. This manhole only has two homes connecting to it, so flows are minimal. Crews popped the manhole cover and it was approximately 3/4 full. Crews were unable to get the rodding machine into the sewer line and began using a digging bar to feel around for the opening of the sewer line. At this point, it became clear there was debris blocking the sewer outlet from the manhole, and by moving the debris with the digging bar, the manhole quickly drained. The source of the debris was large chunks of asphalt, apparently the result of a paving job done a couple months ago. Eventually, the asphalt debris and other material accumulated to plug the outlet. Crews set up the vactor on the downstream manhole and used a fire hydrant to flush the sewer line for about a 1/2 hour to make sure any asphalt debris in the pipe was removed. Overflow volume is a visual estimate based on the wetness observed on the road, but crews never saw the manhole while it was overflowing. Since it was not overflowing when crews arrived, there was no overflow volume that could be captured and returned to the sewer system. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Brisbane | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Assoc. Civil Eng. | Matthew Fabry | 2006-03-03 | 415-508-2134 | mfabry@ci.brisbane.ca.us, rbreault@ci.brisbane.ca.us | MINOR
1341 | 2 | 1 | Brisbane | 2005-04-29 12:26 | 20 | 0 |  | 2005-04-29 12:26 |  | -- | Behind 1002 San Bruno Avenue | Brisbane | San Mateo | 94005 |  |  | 2005-04-12 |  |  |  | Volume is a visual estimation. Overflow seeped from cleanout, infiltrated into ground in the vicinity of cleanout. Line is in an easement in a heavily vegetated area, no impacts to water. Used rod equipment to clear blockage, followed up with Vactor to further clear line. Videoed line and will have contractor fix two root intrusion/broken joint locations. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Brisbane | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Assistant Civil Eng. | Matthew Fabry | 2005-04-29 | 415-508-2134 | mfabry@ci.brisbane.ca.us | MINOR
1167 | 1 | 1 | Brisbane | 2005-03-11 12:57 | 300 | 0 |  | 2005-03-11 12:57 |  | -- | 148 Trinity Road | Brisbane | San Mateo | 94010 |  |  | 2005-03-11 |  |  |  | Overflow was leaking slowly from cleanout. Maintenance crew checks catch basin daily where overflow ultimately goes, heard flow there this AM around 0630. There was no flow the previous day, so the overflow was definitely less than 24 hours. Spill volume is estimated at 2 gallons per minute from 0630 to 0900, when a vactor truck was set up in the catch basin to vacuum out any additional flow. Blockage was cleared by 1038 AM. Video inspection of line indicates heavy root intrusion. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | brisbane | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Assistant Civil Eng. | Matthew Fabry | 2005-03-11 | 415-508-2134 | mfabry@ci.brisbane.ca.us | MINOR
4970 | 20 | 2 | Burlingame | 2007-03-19 | 2250 | 500 | 07-1762 | 2007-03-19 | Vincent Falzon | Burlingame | 525 California Drive | Burlingame | San Mateo | 94010 |  |  | 2007-03-19 | 0.40972 | [6 empty] | Low |  | STORM DRAIN | No |  | No | No | Visual of receiving water was clear. |  | Yes | Yes | Yes |  |  | Yes | Yes |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | CLEAN OUT |  | BLOCKAGE | GREASE | -- Select One -- |  | SSO overflow came out of a 4" cleanout. This sanitary sewer line collects all the waters from the downtown area that is populated with eateries. Our crews were able to plug off the storm drain line and stop the sso and retrieve some of the overflow. They cleaned the storm drain lines and catch basins and disinfected the area. The line was serviced by the crews and will be TV inspected in the next few days. This line is undersized and is part of the Capital Improvement Project that will take place in a few months. At that time this line will be replaced with a larger diameter pipe. | Asst. Superintendant | Vincent Falzon | 2007-03-20 | 650-558-7679
4908 | 19 | 2 | Burlingame | 2007-03-10 | 4500 | 500 | 07-1540 | 2007-03-10 | Vincent Falzon | Burlingame | 600 blk. of Califonia Drive at Oak Grove Ave | Burlingame | San Mateo | 94010 |  |  | 2007-03-10 | 0.375 | [6 empty] | Low |  | STORM DRAIN | No |  | No | No | Visual Inspection of Recieving water was clear. |  | Yes | Yes | Yes |  |  | Yes | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | DEBRIS | -- Select One -- |  |  | Asst. Superintendant | Vincent Falzon | 2007-03-10 | 650-558-7679
4888 | 18 | 1 | Burlingame | 2007-03-07 | 600 | 500 | 07-1507 | 2007-03-07 | Vincent Falzon | Burlingame | 124 El Camino Real | Burlingame | San Mateo | 94010 |  |  | 2007-03-08 | 0.33333 |  |  | The blockage was caused by grease, paper and rags. |  |  |  | Low |  | STORM DRAIN | No |  | No | No | Crews diked catch basin and were able to recover the majority of the overflow. The grey water that entered the box culvert is underground and not accessible to the public. There was no visual of sewer in the recieving water. |  | Yes | Yes | Yes |  |  | No | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | OTHER | The blockage was caused by grease, paper and rags. | BLOCKAGE | MULTIPLE CAUSES | -- Select One -- | 6" cleanout |  | Asst. Superintendent | Vincent Falzon | 2007-03-08 | 650-558-7679
4431 | 16 | 2 | Burlingame | 2006-12-21 | 1500 | 450 | 06-7517 | 2006-12-21 | Phil Scott | burlingame | 1235 Oak Grove Ave | Burlingame | San Mateo | 94010 |  |  | 2006-12-20 | 0.54028 |  |  | Cause of blockage was grease that collected plastic bottles, rags and syringes that the crews recoverged from the contained spill. Grey water that entered the box culvert that is under the road is not accessible and we could not recover and take water samples. There is runoff water from previous rains that diluted the grey water in the box culvert. |  |  |  | Low |  | STORM DRAIN | No |  | No | No | Visual inspection of receiving water was normal and clear. |  | Yes | Yes | Yes |  |  | No | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE | Cause of blockage was grease that collected plastic bottles, rags and syringes that the crews recoverged from the contained spill. Grey water that entered the box culvert that is under the road is not accessible and we could not recover and take water samples. There is runoff water from previous rains that diluted the grey water in the box culvert. | BLOCKAGE | MULTIPLE CAUSES | -- Select One -- | Cleanout | Sorry for the delay of the long form report due to the holidays and vacation time. San Mateo County Health was notified the same day of the spill. | Public Work Superintendant | Phil Scott | 2006-12-21 | 650-558-7673
3810 | 14 | 1 | Burlingame | 2006-08-28 17:12 | 84 | 34 | 06-5138 | 2006-08-28 | Vincent Fazlon | Burlingame | 1500 Blk of Vancouver Avenue | Burligame | San Mateo | 94010 |  |  | 2006-08-26 | 10:30:00 A | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | No | Clear |  | Yes | Yes | Yes | No | No | No | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Burlingame | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS | --Select None-- |  | Manhole overflowed into a nearby catch basin. Duty person relieved the stoppage upon arrival by hand rodding the main. The stoppage was caused by rags and paper that the duty person retrived on the cutter. The main was serviced by the Hydro jet and the area and catch basin cleaned and disinfected. There was no solids that entered the catch basin only grey water. Creek is unaccessible and dry. Grey water soaked into ground. San Mateo Couty Heatlh was also notified on 8/28/2006 at 3:30pm. | Asst. Superintendent | Vincent Falzon | 2006-08-28 | 650-558-7679 | pscott@burlingame.org; vfalzon@burlingame.org, | MAJOR | Vincent Falzon | Burlingame | 650-558-7679 |  | 1361 N. Carolan Ave. | Burlingame | CA | 94010 |  | Burlingame | 650-558-7679 |  | 1361 N. Carolan Ave. | Burligname | San Mateo | 94010
3008 | 13 | 1 | Burlingame | 2006-03-15 09:42 | 800 | 0 |  | 2006-03-15 09:42 |  | -- | 799 California Drive | Burlingame | San Mateo | 94010 |  |  | 2006-03-14 |  |  |  | The blockage was a combination of grease and I&I (inflow & infiltration)during a heavy rain downpour. The crews managed to relief the grease blockage within 20 minutes and recover 100 gallons of the spill. The overflow was mainly grey water and the crews were able to block the storm drain when they got there. OES was contacted and Sibyl gave us this report number 06-1552. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Burlingame | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Asst. Superintendent | Vincent Falzon | 2006-03-15 | 650-558-7679 | pscott@burlingame.org; vfalzon@burlingame.org, | MINOR
2653 | 12 | 1 | Burlingame | 2006-01-18 15:13 | 600 | 0 |  | 2006-01-18 15:13 |  | -- | 1405 Los Montes | Burlingame | San Mateo | 94010 |  |  | 2006-01-18 |  |  |  | Blockage was caused from rags and paper. The city crew diked the drainage area and was abel to recover 450 gallons of the overflow. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Burlingame | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Asst. Superintendent | Vincent Falzon | 2006-01-18 | 650-558-7679 | pscott@burlingame.org; vfalzon@burlingame.org, | MINOR
2447 | 11 | 2 | Burlingame | 2006-01-03 15:49 | 400 | 0 | 06-0096 | 2006-01-03 | Phil Scott | Burlingame | 1500 Willow Avenue x ECR | Burlingame | San Mateo | 94010 |  |  | 2005-12-31 | 7:40:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | 3.5 inches of rain in less than 12 hours. Creeks were overwhelmed. |  | Yes | No | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Burlingame | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | LEAKS OF COLLECTION SYSTEM |  | The whole Peninsula was inundated with rain. SCADA shows 3.5 inches in less than 12 hours. Manhole overflowed slightly into street. | Public Work Superint | Phil Scott | 2006-01-03 | 650-558-7673 | pscott@burlingame.org; vfalzon@burlingame.org, | MAJOR | Phil Scott | City of Burlingame | 650-558-7673 |  | 1361 N. Carolan Ave | Burlingame | San Mateo | 94010 | City of Burlingame | Burlingame | 650-558-7670 |  | 1361 N. Carolan Ave | Burlingame | San Mateo | 94010
1928 | 10 | 1 | Burlingame | 2005-10-06 16:25 | 500 | 0 |  | 2005-10-06 16:25 |  | -- | 1479 El Camino Real | Burlingame | San Mateo | 94010 |  |  | 2005-09-24 |  |  |  | The overflow occured in a below grade parking garage and all of the overflow sewage was returned back into the sanitary sewer system. The duty person retieved a brick from the main upon relieving the stoppage, which appears to be the main cause of the stoppage. This main line is on a monthly sewer preventative maintenance schedule and it was serviced earlier in the month. A city hired consultant is reviewing the sanitary sewer main in this area which is scheduled to be replaced in the next CIP project. This overflow is being reported late due to the fact that it was understood by some that since the overflow was all contained in a private garage and all of the sewer overflow returned back into the system, that it counted as zero overflow. We will review and further train our personnel on reporting SSO's in the future. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Burlingame | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | Asst. Superintendent | Vincent Falzon | 2005-10-06 | 650-558-7679 | pscott@burlingame.org; vfalzon@burlingame.org, | MINOR
1700 | 9 | 1 | Burlingame | 2005-08-18 08:38 | 100 | 0 |  | 2005-08-18 08:38 |  | -- | 2651 Summit Drive | Burlingame | San Mateo | 94010 |  |  | 2005-08-15 |  |  |  | 7483 and 7485 responded to call. They attempted to relieve it from the downstream manhole but were unsuccessful. They were forced to remove upstream lamphole cover which was under pressure from backup. It overflowed when the cover was removed. The crews were able to stop the overflow within one minute. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Burlingame | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PW Supt | Phil Scott | 2005-08-18 | 650-558-7673 | pscott@burlingame.org; vfalzon@burlingame.org, | MINOR
1690 | 8 | 3 | Burlingame | 2005-08-15 07:55 | 18000 | 0 | 05-4644 | 2005-08-07 | Vincent Falzon | Burlingame | 2319 Easton Drive | Burlingame | San Mateo | 94010 |  |  | 2005-08-06 | 8:30:00 AM | [5 empty] | SUNNY WEATHER | Low |  | UNKNOWN | No |  | No | Yes | Gray water going down the creek. Crews contained and cleaned out the solids from the creek. Returned 8-12-05 and flushed approx. 40,000 gallons into creek. Removed debris and recovered approx. 10,000 at dike in creek. Creek appears clear of debris, odor free and the water is clear. |  | Yes | Yes | Yes | No | No | Yes | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Burlingame | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- | RAGS |  | Asst. Superintendent | Vincent Falzon | 2005-08-08 | 650-558-7679 | pscott@burlingame.org; vfalzon@burlingame.org, | MAJOR | Vincent Falzon | Burlingame | 650-558-7679 |  | 1361 N. Carolan Ave. | Burlingame | CA | 94010 |  | Burlingame
1613 | 6 | 1 | Burlingame | 2005-07-14 11:51 | 10 | 0 |  | 2005-07-14 11:51 |  | -- | 1141 Capuchino Ave | Burlingame | San Mateo | 94010 |  |  | 2005-07-14 |  |  |  | This report replaces the Long Form report SSO Track Num:1570 upon the request of Micheal Shea of RWQB. The cause of this minor spill was due to a 6 inch sanitary main line that was broken during the installation of a PG&E utility pole. The main line was clearly marked with USA markings when the pole was installed. The overflow occured in the building of the US Post Office in the bathroom area. All of the overflow was retrived by Ideal Restoration who perfomed the cleanup of the area where the overflow occured. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Burlingame | OTHER | Floor drain in bathroom | INFRASTRUCTURE FAILURE | CONSTRUCTION DEBRIS |  |  |  | Asst. Superintendent | Vincent Falzon | 2005-07-14 | 650-558-7679 | pscott@burlingame.org; vfalzon@burlingame.org, | MINOR
1617 | 7 | 1 | Burlingame | 2005-07-14 13:35 | 90 | 0 |  | 2005-07-14 13:35 |  | -- | 1900 & 1901 Garden Dr | Burlingame | San Mateo | 94010 |  |  | 2005-07-14 |  |  |  | All of the spill was recovered by Ideal Restoration Company who perfomed the cleanup and disinfected the area of the spill. The spill was contained in the underground parking garages. The floor dranis are lower than the next upstream city manhole which was the reason for this sewer overflow in these parking garages. The City's Engineering Division has issued letters to the building owneres advising them to install a sewer backwater valve to comply with the City's BACKWATER PROTECTION CERTIFICATION PROGRAM ORDINANCE. #1710, and MUNICIPAL CODE SECTION 15.12.110. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | burlingame | OTHER | Floor Drains | BLOCKAGE | GREASE |  |  |  | Asst. Superintendent | Vincent Falzon | 2005-07-14 | 650-558-7679 | pscott@burlingame.org; vfalzon@burlingame.org, | MINOR
1319 | 5 | 1 | Burlingame | 2005-04-25 09:55 | 300 | 0 |  | 2005-04-25 09:55 |  | -- | 2113 Ray Drive | Burlingame | San Mateo | 94010 |  |  | 2005-04-20 |  |  |  | Overflowing manhole is located in the middle of the street. Half of the overflow (approx. 150 gallons) went into gutter on the notrh side of the street and traveled six blocks, never entering a storm drain. The other half went into the gutter on the south side of the street and traveled approx. 725' to a catch basin. The mayority of the overflow was either absorved into the ground or evaporated. Both side of the street were cleaned using the street sweeper. The small amount that made it to the catch basin was absorbed and contained to the catch basin by the leaves and debris was cleaned up and vacumed. From our observation, it appears that no sewage entered the creek. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Burlingame | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Asst. Superintendent | Vincent Falzon | 2005-04-25 | 650-558-7679 | pscott@burlingame.org; vfalzon@burlingame.org, | MINOR
1112 | 4 | 1 | Burlingame | 2005-03-03 16:55 | 600 | 0 |  | 2005-03-03 16:55 |  | -- | 1900-01 Garden Dr. | Burlingame | San Mateo | 94010 |  |  | 2005-02-27 |  |  |  | City crew recovered all of the overflow that was contained in the parking garage and it was retured back into the sanitary sewer. | [5 empty] | NO WATER INVOLVED | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Burlingame | OTHER | Garage floor drains | BLOCKAGE | GREASE |  |  |  | Asst. Superintendent | Vincent Falzon | 2005-03-03 | 650-558-7679 | pscott@burlingame.org; vfalzon@burlingame.org, | MINOR
1039 | 2 | 2 | Burlingame | 2005-02-16 12:30 | 21900 | 0 | 05-1029 | 2005-02-16 | Vince Falzon | Burlingame | 1461 Hale Drive | Burlingame | San Mateo | 94010 |  |  | 2005-02-15 | 3:00:00 PM | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | Yes | Gray water and paper entering storm drain; no solids. |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | Burlingame | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Public Work Assistan | Vincent Falzon | 2005-02-16 | 650-558-7679 | vfalzon@burlingame.org; vfalzon@burlingame.org, | MAJOR | Vincent Falzon | Burlingame | 650-558-7679 |  | 1361 N. Carolan Ave. | Burlingame | CA | 94010 |  | Burlingame
1040 | 3 | 2 | Burlingame | 2005-02-16 12:46 | 13500 | 0 | 05-1028 | 2005-02-16 | Vince Falzon | Burlingame | 2800 Easton Drive | Burlingame | San Mateo | 94010 |  |  | 2005-02-15 | 3:30:00 PM | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | No | Gray water entering entering storm drain; no solids. |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | Burlingame | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Public Work Assistan | Vincent Falzon | 2005-02-16 | 650-558-7673 | pscott@burlingame.org; vfalzon@burlingame.org, | MAJOR | Vincent Falzon | Burlingame | 650-558-7679 |  | 1361 N. Carolan Ave | Burlingame | CA | 94010 |  | Burlingame
451 | 1 | 2 | Burlingame | 2004-12-09 06:05 | 18000 | 0 | 04-6405 | 2004-12-09 | Phil Scott | Burlingame | 2804 Easton | Burlingame | San Mateo | 94010 |  |  | 2004-12-08 | 6:00:00 AM | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No | Barricades with signage were posted during overflow. Due to heavy rains no sampling was possible. Rains diluted and washed street surface | No | Yes | No solids visible. Heavy rains caused infiltration in old sewers upstream and caused line to surcharge at a shallower MH downstream. |  | Yes | No | No | No | No | No | No | No | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | Burlingame | MANHOLE | There was no blockage. We jetted to make sure but overflow was caused strictly by infiltration. When rain subsided so did overflow. | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | We will be planning to upsize this portion of sewer main in our CIP planning meeting in January. THis project may be completed as early as summer/fall of 05. | PW Supt | PScott | 2004-12-09 | 558-7670 |  | MAJOR | PScott | Burlingame | 650-558-7670 |  | 1361 N. Carolan Ave | Burlingame | San Mateo | 94010 |  | Burlingame
2925 | 1 | 1 | CaliforniaVeteransHome | 2006-03-03 10:27 | 150 | 0 |  | 2006-03-03 10:27 |  | -- | Admin. parking lot | Yountville | Napa | 94599 |  |  | 2005-07-03 |  |  |  | As per Michael Chee request to log via e-record of this event | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | CaliforniaVeteransHome | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Chief Eng.II | Pat Gilleran | 2006-03-03 | 707.944.4809 | Andrew.ellicock@cdva.ca.gov, Pat.Gilleran@cdva.ca.gov,Bill.Hargis@cdva.ca.gov | MINOR
3763 | 2 | 1 | Calistoga | 2006-08-21 10:41 | 14400 | 0 | 06-0120 | 2006-01-02 | Bill McBride | Louise Harrison | Intersection of Fair Way and Park Street. | Calistoga | Napa | 94515 |  |  | 2005-12-31 | 12:30:00 P | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STREET/CURB & GUTTER | No |  | No | No | There were no storm drains located in the vicinity of the spill. There were no impacts noted in the area of the spill. No clean up occurred due to high surface water City-wide. |  | Yes | No | No | No | No | No | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Calistoga | MANHOLE |  | NATURAL DISASTER | --Select None-- | --Select None-- |  |  | Ms. | Louise Harrison | 2006-08-21 | (707) 942-2828 | bmcbride@ci.calistoga.ca.us, pwade@ci.calistoga.ca.us; jlam@waterboards.ca.gov; mchee@waterboards.ca.gov | MAJOR | Bill McBride | Calistoga | (707) 942-2828 |  | 1232 Washington Street | Calistoga | Napa | 94515 |  | City of Calistoga | (707) 942-2828 |  | 1232 Washington St. | Calistoga | Napa | 94515
3764 | 3 | 1 | Calistoga | 2006-08-21 10:48 | 4800 | 0 | 06-0119 | 2006-01-02 | Bill McBride | Louise Harrison | Adjacent to the Springs Lift Station on Lower Washington St. | Calistoga | Napa | 94515 |  |  | 2005-12-31 | 12:30:00 P | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STREET/CURB & GUTTER | No |  | No | No | There were no storm drains located in the vicinity of the spill. There were no impacts noted in the area of the spill. No clean-up occurred due to high surface water City-wide. |  | Yes | No | No | No | No | No | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Calistoga | MANHOLE | Overflow was caused by a storm which resulted in localized flooding throughout the City of Calistoga. | NATURAL DISASTER | --Select None-- | --Select None-- |  |  | Ms. | Louise Harrison | 2006-08-21 | (707) 942-2828 | bmcbride@ci.calistoga.ca.us, pwade@ci.calistoga.ca.us, jlam@waterboards.ca.gov, mchee@waterboards.ca.gov | MAJOR | Bill McBride | Calistoga | (707) 942-2828 |  | 1232 Washington St. | Calistoga | Napa | 94515 |  | City of Calistoga | (707) 942-2828 |  | 1232 Washington St. | Calistoga | Napa | 94515
3762 | 1 | 2 | Calistoga | 2006-08-21 10:32 | 2400 | 0 | 06-0121 | 2006-01-02 | Bill McBride | Calistoga | Sixty (60) feet west of the Myrtle and Elm Street intersection, on Myrtle Street. | Calistoga | Napa | 94515 |  |  | 2005-12-31 | 12:30:00 P | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STREET/CURB & GUTTER | No |  | No | No | There were no storm drains located in the vicinity of the spill. There were no impacts noted in the area of the spill. No clean up occurred due to high surface water City-wide. |  | Yes | No | No | No | No | No | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Calistoga | MANHOLE |  | NATURAL DISASTER | --Select None-- | --Select None-- |  |  | Ms. | Louise Harrison | 2006-08-21 | (707) 942-2828 | bmcbride@ci.calistoga.ca.us, pwade@ci.calistoga.ca.us | MAJOR | Louise Harrison | Calistoga | 707- 942-2780 |  | 1232 Washington St. | Calistoga | Napa | 94515 |  | City of Calisoga | (707) 942-2828 |  | 1232 Washington St. | Calistoga | Napa | 94515
5130 | 15 | 2 | CastroValley | 2007-04-24 09:57 | 225 | 0 |  | 2007-04-24 09:57 |  | -- | 4634 Mira Loma Drive Mh 27-89 to MH 27-88 | Castro Valley | Alameda | 94546 |  |  | 2007-04-13 |  |  |  | Recieved call of backyard being wet around manhole in easemant. Responded to find mainline blockage and water trickeling out of manhole. Stoppage was broken by manchine rodder. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | CSM Supervisor | Elliott S. Johnson | 2007-04-19 | (510)537-0757
4948 | 14 | 1 | CastroValley | 2007-03-16 14:33 | 400 | 0 |  | 2007-03-16 14:33 |  | -- | Intersetion of Vaughn Ave and Lux Ave | Castro Valley | Alameda | 94546 |  |  | 2007-03-14 |  |  |  | Recieved a call from Alameda County Fire Dept. stating a MH was overflowiing. We arrived on site to find the MH overflowing was sewer. We broke the stoppage using the machine rodder. The cause of the blockage was roots from a private lateral had grown into the main. The sewage did reach a catch basin but was absorbed by sand in the catch basin. The catch basin was cleand out and the stree was washed down. No sewage made it into waters of the state. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | CSM Supervisor | Elliott S. Johnson | 2007-03-16 | (510)537-0757
4785 | 13 | 1 | CastroValley | 2007-02-21 15:00 | 115 | 0 |  | 2007-02-21 15:00 |  | -- | 20099 Santa Maria Avenue. MH 20-88 to MH 20-32 | Castro Valley | Alameda | 94546 |  |  | 2007-02-11 |  |  |  | At 4:45PM the District received a call stating that the above residence was experiencing a back-up within their lateral. They also stated that it was beginning to come out of the clean-out and they had installed a cap to stop the overflow. When we arrived we broke the blockage 10' from the downstream manhole, where we noticed severe grease. This line section was televised and noticed no structual damage within the line segment. This line was not on a PM schedule, but now it is. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | CSM Supervisor | Elliott S. Johnson | 2007-02-21 | (510) 537-0757
4687 | 12 | 1 | CastroValley | 2007-02-07 13:58 | 67 | 0 |  | 2007-02-07 13:58 |  | -- | 4107 Ravenwood Place Castro Valley, CA 94546. Site: Front Yard. | Castro Valley | Alameda | 94546 |  |  | 2007-02-01 |  |  |  | After blockage was relieved the line was televised. It was determined that the cause of this blockage was severe roots and multiple sags troughout the mainline. Though the line was on a HF PM Cycle, it has been changed to Hydro Rootsaw and put on the Districts annual Chemical Root Control Program. THis line will also be evaluated by our engineering department for repair/replacement. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Coll. Supervisor | Elliott S. Johnson | 2007-02-07 | (510)537-0757
4400 | 11 | 1 | CastroValley | 2006-12-27 07:38 | 875 | 0 |  | 2006-12-27 07:38 |  | -- | Intersection of Stanton Avenue and Laredo Rd. Blockage was between Manhole 3-96 and Manhole 3-3. | Castro Valley | Alameda | 94546 |  |  | 2006-12-22 |  |  |  | After breaking blockage, we recovered a root mass approximately 4" in diamiter and 12-14" long. We then televised the sewer line. We did not see any evidence of roots in the sewer main. Therefore, leading us to believe the roots were cut out of a private lateral. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Mr. | Elliott S. Johnson | 2006-12-27 | (510)537-0757
3655 | 10 | 1 | CastroValley | 2006-07-24 15:50 | 132 | 0 |  | 2006-07-24 15:50 |  | -- | 5004 Foxboro Drive | Castro Valley | Alameda | 94546 |  |  | 2006-07-14 |  |  |  | The Spill occurred on and off over a two hour period. When the first responder arrived the spill had evaporated but, restarted while the responder attempted to relieve the stoppage. The spoppage was relieved soon after. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | CastroValley | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | CollMaintSupervisor | Sergio Ramirez | 2006-07-24 | 510-909-8725 | sergio@cvsan.org, | MINOR
2698 | 9 | 2 | CastroValley | 2006-01-30 09:34 | 81 | 0 |  | 2006-01-30 09:34 |  | -- | 2493 Yaffe Dr. | Castro Valley | Alameda | 94546 |  |  | 2006-01-22 |  |  |  | The spill occurred for a total of approximately 45 minutes. When District personnel arrived it was no longer spilling, the sewage had began to dry and had evaporated from the street and gutter area. The sewage dissipated 60 feet down stream in the gutter and did not make it to the catch basin. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | CastroValley | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Coll.Maint.Supervisr | Sergio Ramirez | 2006-01-27 | 510-537-0757 | sergio@cvsan.org, | MINOR
2644 | 8 | 1 | CastroValley | 2006-01-18 11:11 | 945 | 0 |  | 2006-01-18 11:11 |  | -- | 4000 E. Castro Valley Blvd. | Castro Valley | Alameda | 94546 |  |  | 2006-01-12 |  |  |  | The blockage occurred on 1/12/06 However, Transfiguration Church reported the spill into the church and around the clean outs on 1/13/06. Apperantly, the sewage exited the clean outs on the eastside of the building, then traveled west throught the church and out through the rear door. The clean out on the westside of the church also spilled over. The sewage appears to have been captured within the property and did not impact waters of the State. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | CastroValley | CLEAN OUT |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | CollectionSupervisor | Sergio Ramirez | 2006-01-18 | 510-909-8725 | sergio@cvsan.org, | MINOR
2633 | 7 | 1 | CastroValley | 2006-01-17 13:38 | 2916 | 0 | 06-0417 | 2006-01-17 | Sergio Ramirez | CastroValley | 18721 Loukos Place. | Castro Valley | Alameda | 94546 |  |  | 2006-01-02 | 9:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low | 2 | STORM DRAIN | No |  | No | No | No evidence of spill existed in the storm gutter and storm drain catch basin. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | CastroValley | CLEAN OUT |  | FLOW CAPACITY DEFICIENCY | --Select None-- | --Select None-- |  | The SSO occurred on 1/2/06 durring a storm event however, the homeowner cleaned up the spill with a garden hose so when CVSD arrived the clean outs were not overflowing and appeared not to have overflowed. Because of conflicting data further isvestigation was performed on 1/11/06 the investigation revealed the above information. ALCO Flood Control was notified. | CollectionSupervisor | Sergio Ramirez | 2006-01-17 | 510-909-8725 | sergio@cvsan.org, | MAJOR | Sergio Ramirez | CastroValley | 510-537-0757 | 18 | 21040 Marshall St | Castro Valley | Alameda | 94546 |  | Castro Valley San. Dist. | 510-537-0757 | 18 | 21040 Marshall St. | Castro Valley | Alameda | 94546
2185 | 6 | 1 | CastroValley | 2005-11-28 15:51 | 1821 | 100 | 056848 | 2005-11-28 | Sergio Ramirez | CastroValley | 4635 Seven Hills Road | Castro Valley | Alameda | 94546 |  |  | 2005-11-26 | 8:30:00 AM | [5 empty] | SUNNY WEATHER | Low | Region 2 | STORM DRAIN | No |  | No | No | It appears that the solids were contained within the property and did not reach the storm drain system. We calculate that half on the 1821 gallon spill was contained within the property and was absorbed into the soil. |  | Yes | Yes | Yes | No | No | Yes | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | CastroValley | OTHER | One clean out and indoor plumbing. | BLOCKAGE | MULTIPLE CAUSES | MULTIPLE CAUSES |  | The SSO primarily occurred out a 4" private clean out. It them traveled to the back yard area, approximately half of the SSO was absorbed into the dirt area in the back yard; the rest went into a sump pump basin and then pumped back up to the gutter area and into the storm drain system. A small quantity of the SSO entered the home(100gal +/-). | CollSys Supervisor | Sergio Ramirez | 2005-11-28 | 510-909-8725 | sergio@cvsan.org, | MAJOR | Sergio Ramirez | CastroValley | 510-537-0757 | 18 | 21040 Marshall St | Castro Valley | Alameda | 94546 |  | Castro Valley San. Dist. | 510-537-0757 | 18 | 21040 Marshall St. | Castro Valley | Alameda | 94546
1817 | 5 | 1 | CastroValley | 2005-09-22 09:09 | 1200 | 0 | 05-5516 | 2005-09-22 | Sergio Ramirez | CastroValley | 2666 Watson St. | Castro Valley | Alameda | 94546 |  |  | 2005-09-21 | 10:30:00 A | [5 empty] | SUNNY WEATHER | Low | Region 2 | STORM DRAIN | No |  | No | No | There were no visual signs of sewage in the storm drain concrete culvert. Wastewater solid did not enter the storm drain. |  | Yes | Yes | Yes | No | No | Yes | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | CastroValley | MANHOLE | The cause is unknow, the main sewer line was CCTV inspected; the main did not appeared to have signs of a stoppage. Something may have been hung up in Manhole 31-90. | CAUSE UNKNOWN | --Select None-- | --Select None-- |  | Something may have become lodged in MH 31-90 which then became surcharged, then overflowed onto the street, gutter area, and a storm culvert. We were not able to ID what caused the blockage. The CCTV inspection did not demonstrate a specific cause. | Coll.Sys.Supervisor | Sergio Ramirez | 2005-09-22 | 510-909-8725 | sergio@cvsan.org, | MAJOR | Sergio Ramirez | CastroValley | 510-537-0757 | 18 | 21040 Marshall St. | Castro Valley | Alameda | 54546 |  | Castro Valley San. Dist. | 510-537-0757 | 18 | 21040 Marshall St. | Castro Valley | Alameda | 94546
1313 | 4 | 1 | CastroValley | 2005-04-22 10:21 | 600 | 0 |  | 2005-04-22 10:21 |  | -- | 5060 Camino Alta Mira, Lift Station No. 3 | Castro Valley | Alameda | 94546 |  |  | 2005-04-22 |  |  |  | The Lift Station's bubbler system failed. The pumps cavitated which allowed the wet well and near by manhole to overflow. The issue was address and the overflow ceesed within 25 minutes, after learning of the problem. Fortunately the overflow occured durring the "low flow" period. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | CastroValley | PUMP STATION |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Coll.Sys.Supervisor | Sergio Ramirez | 2005-04-22 | 510-537-0757 | sergio@cvsan.org, | MINOR
1213 | 3 | 1 | CastroValley | 2005-03-24 09:04 | 1119 | 0 | 05-1839 | 2005-03-24 | Sergio Ramirez | CastroValley | 19400 Santa Maria Ave. Castro Valley High School's Staff parking lot. Manhole No. 19-38. | Castro Valley | Alameda | 94546 |  |  | 2005-03-23 | 6:30:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low | ALCO. No. D- Storm Culvert | STORM DRAIN | No |  | Yes | No | No visible evidence of spill in storm culvert, a storm event was taking place. |  | Yes | Yes | Yes | No | No | Yes | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | CastroValley | MANHOLE | Spill caused by minor grease build up in the line coupled with high flows related to I/I. | FLOW CAPACITY DEFICIENCY | MULTIPLE CAUSES | --Select None-- |  | SSO caused by grease build up which restricted the capacity of the pipe during the storm event. The heavily diluted sewer then entered the storm drain system, then into a storm culvert. The storm drain and storm culvert were flushed out with hydrant water. | Coll.Sys.Maint.Super | Sergio Ramirez | 2005-03-24 | 510-909-8725 | sergio@cvsan.org, | MAJOR | Sergio Ramirez | CastroValleySan. Dist. | 510-537-0757 | 18 | 21040 Marshall St. | Castro Valley | Alameda | 94546 |  | Castro Valley San. Dist. | 510-537-0757 | 18 | 21040 Marshall St. | Castro Valley | Alameda | 94546
915 | 2 | 1 | CastroValley | 2005-01-26 09:15 | 2281 | 1140 | 05-0624 | 2005-01-26 | Sergio Ramirez | CastroValley | Overflow site is inside a home at 4789 Heyer Ave. and a nearby Manhole (MH.35-58) | Castro Valley | Alameda | 94546 |  |  | 2005-01-25 | 8:00:00 AM | [5 empty] | CLOUDY WEATHER | Low | two storm catch basins several miles upstream of a | STORM DRAIN | No |  | No | No | The two catch basins are several miles from were the storm drain "Day Lights" into a cuvert. No signs of sewage were noticed. John Raven with Alameda County Flood Control inspected the area as well. A sample was taken at this location. |  | Yes | Yes | Yes | No | No | Yes | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | CastroValley | MANHOLE | residential bathroom | BLOCKAGE | --Select None-- | --Select None-- |  | Although the amount of the spill was 2281 gallons. Approximately half was contained within the property at 4789 Heyer Ave. | Coll. Sys.Supervisor | Sergio Ramirez | 2005-01-26 | 510-9098725 | sergio@cvsan.org | MAJOR | Sergio Ramirez | CastroValley | 510-5370757 | 18 | 21040 Marshall St | Castro Valley | Alameda | 94546 |  | Castro Valley Sanitary District | 510-5370757 | 18 | sergio@cvsan.org | Castro Valley | Alameda | 94546
632 | 1 | 1 | CastroValley | 2004-12-27 10:19 | 410 | 0 |  | 2004-12-27 10:19 |  | -- | 16978 | Castro Valley | Alameda | 94546 |  |  | 2004-12-27 |  |  |  | Generator transfer switch did not engage after power failure. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | CastroValley | PUMP STATION |  | ELECTRICAL POWER FAILURE | --Select None-- |  |  |  | Coll.Sys.Sup. | Sergio Ramirez | 2004-12-27 | 510-9098725 | sergio@cvsan.org and oneserg@sbcglobal.net | MINOR
4594 | 2 | 1 | CCCPublicWorks | 2007-01-02 | 1000 | 1000 | 07-0020 | 2007-01-02 | John Mercurio | CCCPublicWorks | 110 Canyon Lake Dr. | Port Costa | Contra Costa | 94569 |  |  | 2006-12-23 | 0.60417 | [6 empty] | Low |  | YARD/LAND | No |  | No | No | No receiving waters were impacted. |  | Yes | Yes | No |  |  | No | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | PIPE |  | BLOCKAGE | DEBRIS FROM LATERALS | -- Select One -- |  |  | Program Analyst | John Mercurio | 2007-01-23 | 925-313-2191
4593 | 1 | 1 | CCCPublicWorks | 2006-12-12 | 1000 | 1000 | 06-7335 | 2006-12-12 | John Mercurio | CCCPublicWorks | 110 Canyon Lake Dr. | Port Costa | Contra Costa | 94569 |  |  | 2006-12-11 | 0.3125 | [6 empty] | Low |  | YARD/LAND | No |  | No | No | No receiving waters were impacted. |  | Yes | Yes | No |  |  | No | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | PIPE |  | BLOCKAGE | ROOTS | -- Select One -- |  |  | Program Analyst | John Mercurio | 2007-01-23 | 925-313-2191
5054 | 49 | 2 | CCCSD | 2007-03-27 | 15000 | 13000 | 07-1934 | 2007-03-27 | Bill Echols | cccsd | Easement area behind 1058 Via Robles | Lafayette | Contra Costa | 94549 |  |  | 2007-03-26 | 0.25 | [6 empty] | Low |  | STORM DRAIN | No |  | No | No | Discoloration of the small tributary to the larger Laffayette Creek was observed. |  | Yes | Yes | Yes |  |  | No | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES | DAMAGE TO COLLECTION SYSTEM |  | The district received an odor complaint at 6:00 PM 03/26/2007 Crew unplugged root blockage with hand rod. There is very heavy brush and poison oak in the easement where the lines are located. The lines in this area are very shallow. One area had a piece of pipe that had been covered with concrete to protect the shallow clay pipe. Tree trimmers working in the area above this section of the line let a large piece of Oak wood roll down the hill that struck the concrete jacket on the pipe cracking the concrete and damaging the bottom of the pipe in two places. Attempts to patch the damaged pipe were unsuccessful the first night. Crews returned the following morning and installed a down stream dam and began pumping flushing operations as well as the repair of the pipe. We pumped approximately 31000 gallons of dechlorinated water through the creek and returned it to our Collection System. The creek, once we stopped flushing, had almost no flow. We feel the majority of this overflow was captured and returned to our system. The 2000 gallons being reported as lost is an over estimation of the amount. | Superintendent | Bill Echols | 2007-03-27 | 925-229-7162
4902 | 47 | 2 | CCCSD | 2007-02-23 | 1100 | 0 | 07-1184 | 2007-02-23 | Bill Echols | cccsd | easement area behind620 Golf Club Way | Pleasant Hill | Contra Costa | 94523 |  |  | 2007-02-22 | 0.13194 |  |  | Blockage was caused by roots and rags. |  |  |  | Low |  | SURFACE WATER IMPACT | No |  | No | No | No obvious effects noted in creek |  | Yes | Yes | No |  |  | No | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE | Blockage was caused by roots and rags. | BLOCKAGE | MULTIPLE CAUSES | -- Select One -- |  | A call was recieved at approximately 3:10 PM reporting an odor. The On Call crew was dispatched and arrived at 3:30 and unplugged line at approximately 4:00 PM. The overflow ran from the Manhole through heavy underbrush, berry bushs and poison oak thus filtering most if not all of the solids from reaching the creek. Terrain issues precluded us from setting up a dam and pumps. We returned the next morning and removed the brush with a back hoe and cleaned all evidence of solids from the area. There were no observable effects in the creek noted. Of the 1100 estimated gallons spilled there is no way to estimate how much of the overflow reached the creek and how much soaked into the soil. We are reporting that the entire overflow amount reached the creek but in all likelyhood the amount was much less | superintendent | Bill Echols | 2007-02-23 | 925-229-7162
4866 | 48 | 1 | CCCSD | 2007-03-05 12:58 | 350 | 0 |  | 2007-03-05 12:58 |  | -- | 7 Knickerbocker Ln | Orinda | Contra Costa | 94563 |  |  | 2007-02-03 |  |  |  | Approximately 300 Gallons was capturd and returned to the system. The plug was caused by rags | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Superintendent | Bill Echols | 2007-03-05 | (925)229-7162
4433 | 46 | 1 | CCCSD | 2007-01-03 06:28 | 300 | 0 |  | 2007-01-03 06:28 |  | -- | 1250 Walker Ave | Walnut Creek | Contra Costa | 94598 |  |  | 2006-12-20 |  |  |  | Blockage was from rags and debris. Approximately 200 gallons was returned to the sanitary sewer | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Superintendent | Bill Echols | 2006-12-21 | (925)2297162
4311 | 45 | 1 | CCCSD | 2006-11-30 | 7000 | 7000 | 06-7080 | 2006-11-30 | Bill Echols | cccsd | 244 Ivy Dr. | Orinda | Contra Costa | 94563Morag |  |  | 2006-11-30 | 0.33333 | [6 empty] | Low | Moraga Creek | SURFACE WATER IMPACT | Yes |  | No | Yes | Turbidity at spill site |  | Yes | Yes | No |  |  | Yes | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | DEBRIS | -- Select One -- |  | The call was recieved at approximately 8:00 am. A crew was dispatched and unplugged the line at 9:28. The blockage was caused by rags and debris.The Overflow discharged into Moraga Creek. A dam and pumps were put in place approximately 1/4 mile downstream of the overflow.Flushed creek with approximately 15,000 gallons of dechlorinated water. We began the pumping operation at 10:10 am and completed at approximately 4:45 pm. We took samples of the creek from the upstream site. the overflow site and downstream site and transported them to our lab and posted warning signs at various locations along the creek. Signs were removed when lab samples indicated the site and downstream areas were similar to the upstream sample. | Superintendent | Bill Echols | 2006-12-14 | (925)229-7162
3923 | 43 | 1 | CCCSD | 2006-09-25 13:32 | 800 | 0 |  | 2006-09-25 13:32 |  | -- | 5342 likens Ave | Martinez | Contra Costa | 94553 |  |  | 2006-09-23 |  |  |  | The spill was approximately 800 gallons. Approximately 700 gallons was captured and returned to the Sanitary System.The line was inspected with a closed circuit TV camera. The line was on a 24 month cleaning schedule and was scheduled to be cleaned next month, in October. The line has been placed on a 12 month evaluation schedule | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Bill Echols | 2006-09-25 | (925)229-7162 | Roseanna@centralsan.dst.ca.us, | MINOR
3760 | 42 | 1 | CCCSD | 2006-08-21 07:29 | 500 | 0 |  | 2006-08-21 07:29 |  | -- | 1231 Homestead | Walnut Creek | Contra Costa | 94596 |  |  | 2006-08-12 |  |  |  | Line segment was blocked with roots and grease. Relieved under house by way of uncapped clean out. Line has been inspected with closed circuit TV and placed on an evaluation schedule. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | CLEAN OUT |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Superintendent | Bill Echols | 2006-08-21 | 9925)229-7162 | Roseanna@centralsan.dst.ca.us, | MINOR
3735 | 41 | 1 | CCCSD | 2006-08-14 16:32 | 200 | 0 |  | 2006-08-14 16:32 |  | -- | 2206 Lakeridge Dr. | Martinez | Contra Costa | 94553 |  |  | 2006-07-29 |  |  |  | Spill soaked into dirt area. Creek Crossing is scheduled for replacement in 2007 | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Superintendent | Bill Echols | 2006-08-14 | (925)2297162 | Roseanna@centralsan.dst.ca.us, | MINOR
3673 | 40 | 2 | CCCSD | 2006-07-31 13:47 | 5000 | 4500 | 06-4167 | 2006-07-14 | Bill Echols | cccsd | Easement area approx. 100 yards northeast from the intersection of Reliez Valley Rd and Silverhill Way | Pleasant Hill | Contra Costa | 94523 |  |  | 2006-07-14 | 10:00:00 A | [5 empty] | SUNNY WEATHER | Low | Grayson Creek | STORM DRAIN | No |  | No | Yes | Turbidity noted in area imeadiately downstream of spill area |  | Yes | Yes | No | No | No | Yes | Yes | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | cccsd | MANHOLE | Broken manhole lid collapsed into structure. Vandalisim suspected | INFRASTRUCTURE FAILURE | VANDALISM | DAMAGE TO COLLECTION SYSTEM |  | A crew was dispatched to the site of the reported overflow at approx 10:00 AM,7/14/06 they found the Manhole overflowing into an area that flowed to a storm drain. They called for additional crews to assist. Crews were on site and had installed pumps and containment dams by 10:45. A site and downstream/upstream samples were collected and delivered to our Labratory. Sewage spill warning signs were posted. The obstruction was cleared and flow was restored at aproximately 11:00am. Large pieces of the manhole lid were observed in the base of the Manhole that overflowed. A confined space entry was performed and the pieces were removed. A closed circuit TV inspection of the line was performed and additional pieces of the lid were observed in the line ,these were removed with a high pressure jetter. The area downstrem of the overflow was flushed with approximately 70,000 gallons of dechlorinated water. The flushing water was captured and pumped back into the sanitary sewer system. The following day7/15/ 2006 an inspection of he site was performed. It was noted that the site where the overflow occured was basically a pond and that no flow was entering the storm drain. We had made our original estimate based on observation of the flow rate approximately 1/4 of a mile down stream from the overflow site, this was the site where the second dam had been installed. There in dense poison oak in the area downstream of the spill site that precluded inspection of the creek in the area up stream of the second dam. The inspection on Sat 7/15 2006 revealed that two additioal flows that were not impacted by the overflow fed into the area above the second dam. We were unaware of this when we made our original volume estimate. We are amending our original estimate to 5000 gals with 4500 gal captured based on the observations made on 7/15/06. Additional tests were performed on 7/17/06 as well as on 7/19/06 When sample results indicated the site matched the upsream background sample the signs were removed. Based on the location of the manhole we strongly suspect vandalism was the cause of the broken Manhole lid | Superintendent | Bill Echols | 2006-07-14 | 925-229-7162 | Roseanna@centralsan.dst.ca.us, | MAJOR | Bill Echols | cccsd | (925)229-7162 | 162 | 5019 Imhoff Pl | Martinez | Contra Costa | 94553 |  | cccsd
3588 | 39 | 2 | CCCSD | 2006-06-30 14:31 | 300 | 200 | N/A<1000 Gal | 2006-06-16 | Bill Echols | cccsd | 44 Camino Encinas | Orinda | Contra Costa | 94563 |  |  | 2006-06-16 | 10:23:00 A | [5 empty] | SUNNY WEATHER | Low | San Pablo Creek | SURFACE WATER IMPACT | No |  | No | No | No impacts were observed |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | cccsd | PIPE |  | BLOCKAGE | ROOTS | --Select None-- |  | The City of Orinda called in to CCCSD dispatch to report an overflow at 10:23 AM 06/16/2006. A crew was dispatched to the site and upon arrival observed the overflow coming out of cracks in the pavement. The crew arrived at approx. 10:45 and relieved the blockage at approx. 11:30. The crew called for assistance, a combination jetter vacume truck was dispatched. The vacume truck vaced up approx 200 gal of the spill and returned it to the sanitary system. A TV crew performed a TV inspection the day of the spill 06/16/2006 and determined that the spill was a result of a root blockage, and there were no obvious breaks in the main line this info led the Tv crew to the conclusion that the break was in the customer lateral. This info was shared with the property owner. The line was placed on a evaluation schedule | Superintendent | Bill Echols | 2006-06-16 | 925-229-7162 | Roseanna@centralsan.dst.ca.us, | MAJOR | Bill Echols | cccsd | (925)229-7162 |  | 5019 Imhoff Pl | Martinez | Contra Costa | 94553 |  | cccsd
3552 | 38 | 2 | CCCSD | 2006-06-23 09:40 | 350 | 350 | 06-3467 | 2006-06-11 | Paul Louis | cccsd | In front of #3949 South Peardale, out of a manhole into a storm culvert into Lafayette Creek | Lafayette | Contra costa | 94549 | -122.149 | 37.898 | 2006-06-11 | 8:30:00 AM | [5 empty] | SUNNY WEATHER | Low | Lafayette Creek | STORM DRAIN | No |  | No | No | Tested water of Lafeyette Creek #3949 South Peardale Drive and tested positive for sewage. Creek had no solids and minimal murkiness. This creek runs fairly good with the spring runoffs. Tests after flushing were negative for sewage. |  | Yes | Yes | Yes | No | No | Yes | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | cccsd | MANHOLE | paper build up in manhole channel | BLOCKAGE | DEBRIS | --Select None-- | paper build up in manhole channel | Paper build in the downstream channel of M25 on South Peardale, Lafayette. Overflow went 20' to drain inlet and then into Lafayette Creek. Dam was set up on Los Aribas and was pumped into m4. Creek was flushed with approx. 5000 gallons of de-clorinated EBMUD hydrant water. Samples of the creek were taken to the CCCSD lab. On 6/15 06 the channel of m25 was reworked so as to improve the flow through the structure. This line is on a 1 month hydro-flush schedule. | Maintenance Supervis | Paul Louis | 2006-06-11 | 925-229-7165 | paul@centralsan.dst.ca.us | MAJOR | Paul louis | CCCSD | (925)229-7165 |  | 5019 Imhoff Pl | Martinez | Contra Costa | 94553 |  | CCCSD | 925 229-7165 |  | 5019 Imhoff Place | Martinez | Contra Costa | 94553
3097 | 37 | 2 | CCCSD | 2006-03-29 15:03 | 5000 | 500 | 06-1602 | 2006-03-16 | Bill Echols | cccsd | approx. 500 yards west of Via Roble in the easement area off the 24 freeway | Lafayette | Contra Costa | 94553 |  |  | 2006-03-16 | 12:30:00 P | [5 empty] | RAINY WEATHER | Low | Lafayette Creek | STORM DRAIN | No |  | No | Yes | None noted. Heavey recent rains diluted the flow into the creek to a point where it was undetectable using our Hach Field test for Ammonia |  | Yes | No | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 925-229-7162 | bill@centralsan.dst.ca.us | cccsd | MANHOLE | 'Infiltration of ground water into our Manhole through the barrel sections caused formation of mineral deposits in the channel of the Manhole and caused the blockage. | BLOCKAGE | --Select None-- | --Select None-- |  | A district crew was responding to a request from our cleaning section to locate a manhole. They located the structure in an area covered in heavy Poison Oak. The structure was overflowing. They called for additional crews to assist. The downstream structure and the structure overflowing were both in an easement area inaccesible to power equipment. Crews used hand rod to relieve the blockage. Follow up TV inspection revealed heavy mineral deposits in the structure. The blockage was removed by manhole entry on 03/23/2006 | Superintendent | Bill Echols | 2006-03-16 | 925-229-7162 | Roseanna@centralsan.dst.ca.us | MAJOR | Bill Echols | cccsd | 925-229-7162 |  | 5019 IMHOFF PLACE, | Martinez | CA | 94553 | Bill Echols | cccsd | 925-229-7162 |  | 5019 IMHOFF PLACE, MARTINEZ |  | CA | 94553
2995 | 36 | 1 | CCCSD | 2006-03-13 08:43 | 150 | 0 |  | 2006-03-13 08:43 |  | -- | 140 Brookwood | Orinda | Contra Costa | 94523 |  |  | 2006-03-05 |  |  |  | Line has been moved to a one month alternating schedule. Line is being considered for rehabilitation on this years Capital Project that begins summer 06 | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | Superintendent | Bill Echols | 2006-03-13 | (925)229-7162 | Roseanna@centralsan.dst.ca.us, | MINOR
2993 | 35 | 1 | CCCSD | 2006-03-13 08:34 | 175 | 0 |  | 2006-03-13 08:34 |  | -- | 140 Brookwood | Orinda | Contra Costa | 94563 |  |  | 2006-02-09 |  |  |  | Closed Circuit TV inspection revealed several flat spots in the line where grease,grit and disposal are accumulating.Recleaned line with high presure water and with a root saw. The line had been on a 12 month cleaning schedule, it was placed on a 6 month schedule | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | uperintendent | Bill Echols | 2006-03-13 | (925)220-7162 | Roseanna@centralsan.dst.ca.us | MINOR
2664 | 34 | 1 | CCCSD | 2006-01-20 08:08 | 250 | 0 |  | 2006-01-20 08:08 |  | -- | 61 El Toyonal | Orinda | Contra Costa | 94563 |  |  | 2006-01-20 |  |  |  | Line was plugged with rags and paper. TV inspection revealed a bad joint,line has been located and marked out for repair | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | superintendendent | Bill Echols | 2006-01-20 | (925)2297162 | Roseanna@centralsan.dst.ca.us, | MINOR
2388 | 31 | 1 | CCCSD | 2005-12-31 13:59 | 4500 | 0 | 057585 | 2005-12-31 | Bill Echols |  | Easement line behind 111 Karen Lane, cross street Homestead | Walnut Creek | Contra Costa | 94596 |  |  | 2005-12-31 | 8:15:00 AM | 2005-12-31 | 11:15:00 A | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Superintendendent | Bill Echols | 2005-12-31 | 925-229-7386 | Roseanna@centralsan.dst.ca.us, | 24HR |  |  | (925)229-7162 | [6 empty] | cccsd
2632 | 33 | 1 | CCCSD | 2006-01-17 11:29 | 4500 | 0 | 057585 | 2005-12-31 | Home owner at 111 Karen Lane | cccsd | 111 Karen Lane | Walnut Creek | Contra Costa | 94596 |  |  | 2005-12-31 | 8:15:00 AM | [5 empty] | CLOUDY WEATHER | Low | Indian Creek | STORM DRAIN | No |  | No | No | No visible impact due to high volume of rain water from major storm event |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | cccsd | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES | --Select None-- |  | Call was recieved by answering service at 8:15, crew was dispatched, arrived at location at 9:00 removed blockage at approx. 11:15. The rate of flow from the recent rain events was so great we were unable to dam the creek. Line was inspected on 01/02/2006 with closed circuit TV. A bad joint was identified and the dig up and repair was completed on 01/04/2006 | Superintendent | Bill Echols | 2006-01-17 | (925)229-7162 | Roseanna@centralsan.dst.ca.us, | MAJOR | Bill Echols | cccsd | (925)229-7162 |  | 5019 Imhoff Pl | Martinez | Contra Costa | 94553 | cccsd | cccsd | (925)229 7162 |  | 5019 Imhoff Place | Martinez | Contra Costa | 94553
2471 | 32 | 1 | CCCSD | 2006-01-04 10:16 | 400 | 0 |  | 2006-01-04 10:16 |  | -- | 7 Abby Ct. cross St. El Curtola | Walnut Creek | Contra Costa | 94596 |  |  | 2005-12-23 |  |  |  | The amount of storm water in the creek precluded any efforts to contain the Overflow. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendendent | William Echols | 2006-01-04 | )925)229-7162 | Roseanna@centralsan.dst.ca.us, | MINOR
2190 | 30 | 1 | CCCSD | 2005-11-29 14:51 | 2100 | 2070 | 05-6881 | 2005-11-29 | CCCSD | cccsd | intersection of Contada Circle and Bali Court | Danville | Contra Costa | 94526 |  |  | 2005-11-25 | 12:00:00 P | [5 empty] | CLOUDY WEATHER | Low |  | STREET/CURB & GUTTER | No |  | No | No | Storm Drain catch basin and gutter system at intersection of Contada Circle and Bali Court |  | Yes | Yes | Yes | No | No | No | No | No | No | 2005-12-02 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | cccsd | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- |  | Crew arrived to find sewage overflow at manhole towards storm drain catch basin. Damming devices were laid over the catch basin to contain the sewer. After releiving the plugged sewer line, the sewage on the street and gutter was returned to the sewer system. The street and storm catch basin were cleaned and disenfected and returned to prior condition | Maint. Supervisor | Paul Louis | 2005-11-29 | 925-229-7165 | jkelly@centralsan.dst.ca.us, | MAJOR | Paul Louis | cccsd | (925)229-7165 |  | 5019 Imhoff Pl | Martinez | Contra Costa | 94553 | cccsd | cccsd | (925)229 7162 |  | 5019 Imhoff Place | Martinez | Contra Costa | 94553
2133 | 29 | 1 | CCCSD | 2005-11-17 07:08 | 185 | 0 |  | 2005-11-17 07:08 |  | -- | 15 Tappan Lane | Orinda | Contra Costa | 94563 |  |  | 2005-11-05 |  |  |  | Easement line was plugged with roots. Closed Circuit TV revealed a break in pipe . Line has been marked out for repair and turned over to our Construction section | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | PIPE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Bill Echols | 2005-11-17 | (925)229-7162 | Roseanna@centralsan.ca.us | MINOR
2061 | 28 | 1 | CCCSD | 2005-10-28 13:06 | 800 | 0 |  | 2005-10-28 13:06 |  | -- | 143 Moraga Way | Orinda | Contra Costa | 94563 |  |  | 2005-10-28 |  |  |  | We responded to a call at 143 Moraga Way in the Town of Orinda. We cleared a partial blockage in the main line that appeared to be primarily rags and debris. The manhole where the bypass pipe overflowed into the creek was located along a creek bank. The pipe was located in thick Ivy and brush and had gone undetectd. The by pass pipe was plugged the following day with concrete by Dist forces. The creek was pumped and flushed the day of the incident at a location that was detemined to be clear based on the results of a Hach field test for ammonia. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | OTHER | By Pass | BLOCKAGE | DEBRIS |  |  |  | Superintendent | Bill Echols | 2005-10-28 | (925)229-7162 | Roseanna@centralsan.dst.ca.us, | MINOR
2059 | 27 | 1 | CCCSD | 2005-10-28 12:40 | 200 | 0 |  | 2005-10-28 12:40 |  | -- | 334Cameo Dr. | Danville | Contra Costa | 94526 |  |  | 2005-10-20 |  |  |  | Overflow was caused by concrete slurry that was holding back solids. We were unable to determine the point source for the introduction of the concrete. We performed a closed circuit TV inspection of the pipe on 10/21/05 as well of the areas upstream and were not able to determine where the slurry had entered the system. We cleared the obsruction with a chain flail. We vacuumed, flushed and cleaned the storm drain the overflow was contained in. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Superintendent | Bill Echols | 2005-10-28 | (925)229-7162 | Roseanna@centralsan.dst.ca.us, | MINOR
1962 | 26 | 1 | CCCSD | 2005-10-14 14:25 | 400 | 0 |  | 2005-10-14 14:25 |  | -- | 5 Arbolado Court | Orinda | Contra Costa | 94563 |  |  | 2005-10-14 |  |  |  | plugged with paper and grease | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | CLEAN OUT |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Maint. Supervisor | Paul Louis | 2005-10-14 | 925 229-7165 | jkelly@centralsan.dst.ca.us, | MINOR
1960 | 25 | 1 | CCCSD | 2005-10-14 14:18 | 200 | 200 |  | 2005-10-14 | Paul Louis |  | 3223 Andreasen Drive | Lafayette | Contra Costa | 94549 |  |  | 2005-10-11 | 4:00:00 PM | 2005-10-11 | 5:30:00 PM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Maint. Supervisor | Paul Louis | 2005-10-14 | 925-229-7165 | jkelly@centralsan.dst.ca.us, | 24HR |  |  | 925 229-7165 | [6 empty] | cccsd
1901 | 21 | 1 | CCCSD | 2005-10-02 13:53 | 4000 | 4000 | 05-5706 | 2005-10-02 | Bill Echols |  | Easement area North of #44 Sweetwater Dr, | Danville | Contra Costa | 94526 |  |  | 2005-10-01 | 3:15:00 AM | 2005-10-01 | 5:40:00 AM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Superintendent | Bill Echols | 2005-10-02 | 925-229-7386 | Roseanna@centralsan.dst.ca.us, | 24HR |  |  | (925)229-7162 | [6 empty] | cccsd
1955 | 23 | 1 | CCCSD | 2005-10-13 13:53 | 150 | 0 |  | 2005-10-13 13:53 |  | -- | 2475 Pleasant Hill Rd. | Pleasant Hill | Contra Costa | 94523 |  |  | 2005-10-01 |  |  |  | CCCSD recieved a call at 11:51AM from the home owner at 2475 Pleasant Hill Rd in the city of Pleasant Hill 0n10/01/05 reporting an over flowing clean out on their property.A crew was dispatched and arrived at 12:35. The cew relieved a root blockage at approx. 12:50.A TV inspection was performed on 10/03/05. The line segment has been placed on an evaluation schedule | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Bill Echols | 2005-10-13 | (925)229-7162 | Roseanna@centralsan.dst.ca.us, | MINOR
1956 | 24 | 1 | CCCSD | 2005-10-13 15:47 | 4000 | 4000 | 05-5706 | 2005-10-01 | Bill Echols | cccsd | #44 Sweet Water Ct. | Danville | Contra Costa | 94526 |  |  | 2005-10-01 | 3:10:00 AM | [5 empty] | SUNNY WEATHER | Medium | West Alamo Creek | SURFACE WATER IMPACT | No |  | No | Yes | Discoloration of Recieving water observed |  | Yes | Yes | Yes | No | No | Yes | No | Yes | No | 2005-10-07 | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | cccsd | MANHOLE |  | BLOCKAGE | DEBRIS | --Select None-- |  | The District recieved a call from a passer by reporting an overflowing manhole in the easement area behind #44 Sweetwater Ct. in the City of Danville at 3:10 PM on Saturday 10/01/2005.A Crew was dispatched and arrived at 3:50. The crew cleared the root blockage at approx. 5:35 Additional crews were dispatched with pumps and Overflow response equipment. A series of tests were taken for ammonia with a Hach test kit.A damn was set up and a pumping operation began at aprox. 6:30 and continued until approx. 10:00at a site that was deemed clear based on the Hach tests. Crews returned the next morning and began washing down and pumping deep pond areas the following morning.Flushing with dechlorinated water and pumping continued until clear tests were attained. | Superintendent | Bill Echols | 2005-10-13 | (925)229-7162 | Roseanna@centralsan.dst.ca.us, | MAJOR | Bill Echols | cccsd | (925)229-7162 |  | 5019 Imhoff Pl | Martinez | Contra Costa | 94553 | cccsd | cccsd | (925)229 7162 |  | 5019 Imhoff Place | Martinez | Contra Costa | 94553
1918 | 22 | 1 | CCCSD | 2005-10-05 15:21 | 200 | 0 |  | 2005-10-05 15:21 |  | -- | #29 El Toynal | Orinda | Contra Costa | 94563 |  |  | 2005-09-21 |  |  |  | Blockage was a combination of rock and tile. A contractor was installing a lateral Upstream of the blockage. Tv inspection revealed no obvious defects that would account for the rock and tile in the pipe.District crews were able to clear the blockage and capture the overflow with a combination vacuum jetter truck. It is our belief that the overflow was caused by the work done upstream by the contractor and that the entire overflow was captured and returned to the sewer system | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Soperintendent | Bill Echols | 2005-10-05 | (925)229-7162 | Roseanna@centralsan.dst.ca.us, | MINOR
1637 | 20 | 1 | CCCSD | 2005-07-25 07:41 | 400 | 0 |  | 2005-07-25 07:41 |  | -- | IFO #387 Pimlico Drive | Walnut Creek | Contra Costa | 94596 |  |  | 2005-07-16 |  |  |  | Root mass inside manhole | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Maint. Supervisor | Paul Louis | 2005-07-25 | 925-229-7165 | jkelly@centralsan.dst.ca.us, | MINOR
1608 | 19 | 1 | CCCSD | 2005-07-12 11:35 | 800 | 0 |  | 2005-07-12 11:35 |  | -- | 135 Jennifer Ln. X Street, Vernal Dr | Alamo | Contra Costa | 94507 |  |  | 2005-06-30 |  |  |  | The stopage was caused by a grease blockage. The overflow was contained in a storm drain system. The Storm Drain was cleaned and flushed with dechlorinated water. The flushing water was returned to the sewer system. The line segment was inspected on 7/01/05 with a closed circuit TV. Additional cleaning was needed and was completed the same day. The line had been a 12 month cleaning schedule and has now been moved to a 6 month schedule | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Superintendent | Bill Echols | 2005-07-12 | (925)229-7162 | Roseanna @centralsan>dst.ca.us | MINOR
1397 | 18 | 2 | CCCSD | 2005-05-13 15:27 | 1800 | 1800 | 05-2611 | 2005-05-01 | cccsd | cccsd | 15 Queensbrook Ct. cross st.Hall Dr. | Orinda | Contra Costa | 94563 |  |  | 2005-04-30 | 1:15:00 AM | [5 empty] | SUNNY WEATHER | Low | Upper Moraga Creek | SURFACE WATER IMPACT | No |  | No | No | Discoloration of the area of the creek where discharge occured |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | cccsd | MANHOLE |  | BLOCKAGE | DEBRIS | MULTIPLE CAUSES |  | On Sat. 03/30/005 the Dist recieved a call from a homeowner at 15 Queensbrook Pl in the city of Orinda reporting an overflowing Manhole. A crew was dispatched and the blockage was cleared within one and a half hours of recieving the call. Additional crews were dispatched and they set up a dam downstream of the overflow at a point where field tests for ammomia indicated the creek was clear.Two 3"pumps were set up and dechlorinated flushing water was introduced into the creek. The crews returned on Sunday and completed additional clean up and flushing, pumping operations.After identifying two areas in the pipe with closed circuit TV inspection repairs were completed on the pipe 05/13/005. | superintendent | Bill Echols | 2005-05-01 | 925-229-7386 | Roseanna@centralsan.dst.ca.us, | MAJOR | Bill Echols | cccsd | (925)229-7162 |  | 5019 Imhoff Pl | Martinez | Contra Costa | 94553 |  | cccsd
1337 | 17 | 2 | CCCSD | 2005-04-28 14:28 | 13500 | 50000 | 05-2301 | 2005-04-18 | Bill Echols | cccsd | In the Intersection of Dos Rios and Carousel | San Ramon | Contra Costa | 94583 |  |  | 2005-04-17 | 10:30:00 A | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | No | There was an observed discoloration in the area where the storm drain discharged into San Catanio Creek. San Cataino Creek is a small tributary to San Ramon Creek. There were no observed effects in San Ramon Creek. |  | Yes | Yes | No | No | No | No | No | Yes | No | 2005-05-10 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | cccsd | MANHOLE | 'Infiltration of ground water into our Manhole through the barrel sections caused formation of mineral deposits in the channel of the Manhole and caused the blockage. | BLOCKAGE | MULTIPLE CAUSES | --Select None-- |  | On 04/17/2005 the District recieved a call reporting an overflowing manhole in the intersection of Dos Rios and Carousel in the town of San Ramon. The overflow ran into a storm drain catch basin that discharged into San Catanio Creek. The volume was estimated to be approximately 100 gals a minute and the duration was approximately 135 min. A site was identified approximately two miles downstream on the San Ramon creek that the tributary runs into and a 6" pump was set up. Based on the pump curve for the 6" pump we estimate that we pumped approximately 50,000 gal of blended discharge and creek water back into our system. We were unable to halt and capture the entire flow in the creek because of the volume of flow in the creek at the time. We took a series of samples during and leading up to the pumping operation as well as after and the results were either zero or in the .02-.04 range. We have completed our post-TV inspection of the line segments up stream of the blockage and have determined that grease and rags were the cause of the overflow. We have determined that the source of the rags is the Twin Creeks Elementary School. Our source control division is working with the school and that effort is ongoing. We have not determined any obvious large contributers of grease in the upstream segments we have televised to date.We feel that possibly the rags held back flow causing the grease build up. Our source control division is continueing their investigation at the elementary school in an attempt to determine the point source of the grease. | Superintendent | Bill Echols | 2005-04-18 | 925-229-7162 | Roseanna@centralsan.dst.ca.us, | MAJOR | Bill Echols | CCCSD | (925) 229-7162 |  | 5019 Imhoff Pl. | Martinez | Contra Costa | 94553 |  | cccsd
1265 | 16 | 1 | CCCSD | 2005-04-08 09:33 | 150 | 0 |  | 2005-04-08 09:33 |  | -- | 3564 Silver Springs Rd. | Laffayette | Contra Costa | 94549 |  |  | 2005-04-08 |  |  |  | The spill was caused by a combination of roots and grease. The line has been inspected via closed circuit TV. A rerun using a chain flail has been completed based on the TV inspection. None of the Over flow reached the waters of the state. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Bill Echols | 2005-04-08 | (925) 229-7162 | Rozanna@centralsan.dst.ca.us, | MINOR
1185 | 15 | 2 | CCCSD | 2005-03-15 14:31 | 500 | 0 | 05-1437 | 2005-03-03 | Bill Echols | cccsd | 2840 Castro St. cross St. D St. | Martinez | Contra Costa | 94553 |  |  | 2005-03-02 | 8:15:00 PM | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | No | None observed |  | Yes | No | No | No | No | No | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | cccsd | MANHOLE | Attached to this report is a picture of the plastic crayola box that caused the blockage | BLOCKAGE | VANDALISM | --Select None-- |  | On 03/02/0005 we recieved a call from the Martinez Police reporting an overflowing Manhole at 8:15PM A crew was dispatched and relieved the blockage by 9:30 PM. The crew retrieved a plastic crayola box from the Manhole that was lodged in the line. A picture of the box is attached. The level of the creek was so high that daming the creek was impractical. The crew washed down the street and vacumed up the wash down water. A TV inspection of the line segment the following day revealed no other obstructions in the line | Superintendent | Bill Echols | 2005-03-03 | 925-229-7386 | roseanna@centralsan.dst.ca.us, | MAJOR | Bill Echols | cccsd | (925)229-7162 |  | 5019 Imhoff Pl. | Martinez | Contra Costa | 94553 |  | cccsd
1121 | 13 | 2 | CCCSD | 2005-03-07 14:34 | 7500 | 7500 | 05-1243 | 2005-02-23 | Bill Echols | cccsd | Alhambra Ave. cross St. Donegal Way, Martinez | Martinez | Contra Costa | 94553 |  |  | 2005-02-23 | 8:30:00 AM | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | No | No obvious effects were observed |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | cccsd | MANHOLE | Roots infiltrated into Manhole around the base | BLOCKAGE | ROOTS | --Select None-- | Roots infiltrated into Manhole around the base | A large root mass infiltrated into the Manhole at the base and blocked the channel. The Manhole that was plugged was 20 feet deep . We had to use a surcharged Manhole upstream of the blockage to relieve the plug utilizing a rodding truck. After conducting a series of field tests for the presense of amonia we installed a dam in the concrete culvert downstream in an area that had tested clear.We flushed the creek using dechlorinated water and pumped all of the flow back into the sanitary system. We pumped for approximately five hours using a 6" Gorman Rupp pump. After the pumping operation was complete we observed no negative effect on the creek. The line has been inspected with a closed circuit TV. The manhole has been placed on an inspection schedule and the base will be treated with a chemical root control herbicide this summer | Superintendent | Bill Echols | 2005-02-23 | 925-229-7386 | Roseanna@centralsan.dst.ca.us, | MAJOR | Bill Echols | CCCSD | (925)229-7162 |  | 5019 Imhoff Place | Martinez | Contra Costa | 94553 | cccsd | cccsd | (925)229 7162 |  | 5019 Imhoff Place | Martinez | Contra Costa | 94553
1090 | 14 | 1 | CCCSD | 2005-02-25 14:09 | 250 | 0 |  | 2005-02-25 14:09 |  | -- | Stanley Dallar Cross St. Tice Creek Dr. | Walnut Creek | Contra Costa | 94596 |  |  | 2005-02-15 |  |  |  | Manhole overflowed due to a blockage consisting if rags and debris. The spill was contained in the curb and gutter area and did not reach a storm drain. The spill was vacumed up with a combination truck and returned to the sanitary sewer system | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | superintendendent | Bill Echols | 2005-02-25 | (925)229-7162 | jkelly@centralsan.dst.ca.us, | MINOR
1014 | 12 | 1 | CCCSD | 2005-02-10 15:07 | 150 | 0 |  | 2005-02-10 15:07 |  | -- | 703 Terra California | Walnut Creek | Contra Costa | 94596 |  |  | 2005-02-05 |  |  |  | A root mass infiltrated the base of a Manhole and blocked flow in the manhole. We have just taken over this system, it had been owned and maintained by the Rossmore Retirement Village up until very recently. CCCSD will now place this line segment on an evaluation schedule | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendendent | Bill Echols | 2005-02-10 | 925-229-7386 | Roseanna@centralsan.dst.ca.us, | MINOR
971 | 10 | 1 | CCCSD | 2005-02-04 13:13 | 200 | 0 |  | 2005-02-04 13:13 |  | -- | 202 Wellington Ave. | Clyde | Contra Costa | 94520 |  |  | 2005-02-04 |  |  |  | Line has been moved from a 6 month schedule to a 3 month schedule | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Bill Echols | 2005-02-04 | (925)229-7162 | Roseanna@centralsan.dst.ca.us | MINOR
1038 | 11 | 2 | CCCSD | 2005-02-16 12:09 | 1400 | 1300 | 05-0808 | 2005-02-04 | City of Danville Public Works | cccsd | 140 Belgian Dr. cross St. Maiden Ln. | Danville | Contra Costa | 94526 |  |  | 2005-02-04 | 8:17:00 AM | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | No | Slight turbidity in tributary to E, Branch of Green Vlly. Creek |  | Yes | No | No | No | No | No | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | cccsd | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- |  | On 2/04/005 CCCSD recieved a call from the City of Danville Public Works Dept. reporting an overflowing Manhole at apporoximately 8:17.A crew working in the area was dispatched and relieved the root plug at approximately 9:30. An additional crew was dispatched to perform clean up and pumping operations. The crew set up downstream of the overflow at a point in The East Branch of Green Valley Creek utilizing a natural damn existing in the creek. The crew , using a 3" and 4" pump pumped for approximately 3 hours. Utilizing a field Hach test for ammonia the crew determined that the creek was clear and pumping ceased at 14:00 hours. It is estimated that approximately 1300 gallons of the discharge was returned to our system. We have performed a closed circuit TV on the line segment and determined that the cause of the stoppage was a root mass. We have removed the root mas using a chain flail and have verified the results with a closed circuit TV inspection | Superintendent | Bill Echols | 2005-02-04 | (9250229 7162 | Roseanna@centralsan.dst.ca.us | MAJOR | Bill Echols | cccsd | (925)2297162 |  | 5012Imhoff Place | Martinez | Contra Costa | 94553 |  | cccsd
969 | 9 | 1 | CCCSD | 2005-02-04 11:55 | 300 | 0 |  | 2005-02-04 11:55 |  | -- | 2300 Oakvale cross St. Terrace | Walnut Creek | Contra Costa | 94596 |  |  | 2005-01-28 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Bill Echols | 2005-02-04 | (925)2290162 | Roseanna@centralsan.dst.ca.us | MINOR
892 | 7 | 2 | CCCSD | 2005-01-21 13:08 | 1500 | 1400 | 05-0362 | 2005-01-13 | Bill Echols | cccsd | 2383 Royal Oaks Dr. | Alamo | Contra Costa | 94507 |  |  | 2005-01-13 | 8:07:00 AM | [5 empty] | CLOUDY WEATHER | Low | Small tributary to San Ramone Creek | SURFACE WATER IMPACT | No |  | No | No | We set up our dam and pumping operation at a spot in the creek where no impact was visible |  | Yes | Yes | Yes | No | No | No | No | Yes | No | 2005-01-15 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | cccsd | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- |  | At approximately 08:07 AM on 01/13/2005 the District received a call reporting an overflowing manhole in the street in front of 2383 Royal Oaks Drive in the town of Alamo. A crew was dispatched to the site and arrived at approximately 08:30AM. The crew relieved the root plug at approximately 09:15. An additional crew had been dispatched during the time the cleaning crew was working to relieve the blockage. The second crew installed a dam downstream of the overflow and began pumping at approximately 09:30. A small amount of the overflow estimated at less than 100 gallons got past the dam. We estimate that 1400 gallons were pumped back into the sanitary sewer system. We flushed the storm drain and culvert with several thousand gallons of dechlorinated water that was also pumped back into the sewer system. We tested the water for ammonia until we had clear readings then pulled the dam and continued to flush for an additional 45 minutes. At the end of the clean-up flushing operation there were no observable effects on the culvert or downstream of the area where the dam had been placed. We went out the next day and performed a closed-circuit television inspection of the line segment. A root mass was identified in the line segment that apparently originates from a windbreak of recently planted (in the last 10 years) redwood trees. The closed-circuit TV operator, assisted by a high-pressure jetter cleaner crew utilizing a chain flail, eliminated the root mass. The line has been placed on a one-year cleaning evaluation cycle. | superintendent | Bill Echols | 2005-01-13 | [925]229-7162 | roseanna@centralsan.dst.ca.us | MAJOR | Bill | Echols | [925] 229-7162 |  | 5019 Imhoff Place | Martinez | Contra Costa | 94553 |  | cccsd
701 | 2 | 1 | CCCSD | 2004-12-31 13:24 | 9000 | 0 | 04-6978 | 2004-12-31 | Moraga Country Club |  | #1600 St Andrews Dr. cross street Moraga Way | Moraga | Contra Costa | 94556 |  |  | 2004-12-31 | 8:15:00 AM | 2004-12-31 | 11:30:00 A | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | superintendent | William Echols | 2004-12-31 | (925)229-7162 | jRoseanna@centralsan.dst.ca.us | 24HR |  |  | 925 3762253 | [6 empty] | cccsd
816 | 4 | 3 | CCCSD | 2005-01-11 12:07 | 9000 | 0 | 04-6920 | 2004-12-31 | Bill Echols | cccsd | 1600 St. Andrews Drive | Moraga | Contra Costa | 94556 |  |  | 2004-12-31 | 8:15:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low | Lower Moraga Creek | STORM DRAIN | No |  | No | No | None observed |  | Yes | Yes | No | No | No | No | No | Yes | No | 2005-01-31 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | cccsd | MANHOLE | Diversion gate support chain connector failure | INFRASTRUCTURE FAILURE | --Select None-- | BREAKAGE OF COLLECTION SYSTEM | Diversion gate support chain connector failure |  | Superintendent | Bill Echols | 2005-01-07 | (925) 229-7162 | roseanna@centralsan.dst.ca.us | MAJOR | Bill Echols | CCCSD | (925) 229-7162 |  | 5019 Imhoff Place | Martinez | Contra Costa | 94553 |  | CCCSD
683 | 1 | 1 | CCCSD | 2004-12-29 15:09 | 250 | 0 |  | 2004-12-29 15:09 |  | -- | #8 WildwoodRd. cross St.Spring Rd. | Orinda | Contra Costa | 94563 |  |  | 2004-12-26 |  |  |  | The District recieved a call via our answering service on Sunday 12/26/04 reporting an overflow coming out of a clean out in front of a property located at #8 Wildwood Rd.in the City of Orinda.The call was recieved at approx.10:55 AM.The crew arrived at aprox. 11:40 and relieved the blockage at 11:45. The blockage appeared to be a combination of roots and rock. The area in which the overflow occured has had multible EBMUD line breaks as evidenced by the numerous paving patches I observed in my followup visit to the site.This potentially is the cause of the rock infiltration into our system.After relieving the blockage an additional crew responded to the site with a combination jetter/vacume truck and vacumed up the sewage that had been contained in a depression in the unpaved roadway.On Wed.12/29/04 we televised the line segment an identified a sag in the line in the area of the pipe where the blockage occured. The rest of the line segment appears to be in seviceable condition. We will increase the frequency of cleaning on this line segment and continue to monitor the line to determine the most appropriate long term solution | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | Supreintendent | William Echols | 2004-12-29 | (925)229-7162 | Roseanna@centralsan.dst.ca.us | MINOR
790 | 5 | 1 | CCCSD | 2005-01-07 15:44 | 200 | 0 |  | 2005-01-07 15:44 |  | -- | 00 Deerhiil Rd. | Lafayette | Contra Costa | 94549 |  |  | 2004-12-14 |  |  |  | We recieved a call from a City of Laff. Inspector reporting an overflowing Manhole. The crew rodded the line and retrieved a air plug that had been left in the line. We have the line segment on a 120 month schedule and have not experienced problems in the past on this line segment. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | OTHER | Contractor air plug | BLOCKAGE | --Select None-- |  |  |  | Superintendent | Bill Echols | 2005-01-07 | [925]229-7162 | Roseanna@centralsan.dst.ca.us | MINOR
851 | 6 | 1 | CCCSD | 2005-01-13 14:04 | 350 | 0 |  | 2005-01-13 14:04 |  | -- | #1 Rose Ln | Orinda | Contra Costa | 94563 |  |  | 2004-12-04 |  |  |  | CCCSD recieved a call on 12/04/04 reporting a Overflowing Manhole at #1 Rose Ln in the city of Orinda at 10:15 AM. A cleaning crew working in the area was dispatched and arrived at 10:30. The blockage was relieved at approximately 10:40. The release of approximately 350 gallons was primarily contained in the street area. A small amount reached the storm drain. A combination jetter vacume truck cleaned the storm system. CCCSD perfomed a TV inspetion of the line segment and found a sag in the area of the blockage. This line is scheduled to be replaced this year as part of our renovation project. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Superintendent | Bill Echols | 2005-01-13 | [925]229-7162 | Barrett@centralsan.dst.ca.us | MINOR
774 | 3 | 1 | CCCSD | 2005-01-06 14:57 | 120 | 0 |  | 2005-01-06 14:57 |  | -- | 3028 Vessing Rd. | Pleasant Hill | Contra Costa | 94523 |  |  | 2004-12-03 |  |  |  | Overflow did not reach waters of the state.Line segment is currently on a 3 month cleaning schedule. CCCSD is doing a capital project that will address this beginning in summer of 05 | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | cccsd | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | superintendent | William Echols | 2005-01-06 | [925]229-7162 | jkelly@centralsan.dst.ca.us | MINOR
4642 | 4 | 1 | Colma | 2007-01-22 | 25200 | 0 | 07-0455 | 2007-01-22 | Phil Scramaglia | colma | Between B Street and C Street intersections on El Camino Real/Mission Street | Colma | San Mateo | 94014 |  |  | 2007-01-21 | 0.41667 | [6 empty] | Low | Colma SD system | STORM DRAIN | No |  | No | No | SD manhole was plugged on the receiving end to contain water. contained water was then pumped back into the vac truck for treatment. No traces of contaminants observed downstream. |  | Yes | Yes | Yes |  |  | Yes | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS | -- Select One -- |  | SD manhole was plugged on the receiving end to contain water. contained water was then pumped back into the vac truck for treatment. No traces of contaminants observed downstream. | Assistant Engineer | Muneer Ahmed | 2007-01-30 | 650-757-8888
2140 | 2 | 1 | Colma | 2005-11-18 09:12 | 4500 | 0 | 05-6685 | 2005-11-18 | Will Anderson |  | El Camino Real at Mission Road | Colma | San Mateo | 94014 |  |  | 2005-11-17 | 2:15:00 PM | 2005-11-17 | 3:00:00 PM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Assistant City Engin | Will Anderson | 2005-11-18 | 650-757-8888 | will.anderson@colma.ca.gov, rick.mao@colma.ca.gov | 24HR |  |  | 650-757-8895 | [6 empty] | Colma
1511 | 1 | 2 | Colma | 2005-06-10 14:45 | 500 | 0 |  | 2005-06-10 14:45 |  | -- | Treasure Island Trailer Court (Rue 10, slot 30) 1700 El Camino Real | South San Francisco | San Mateo | 94080 |  |  | 2005-05-22 |  |  |  | The manhole that overflowed is located adjacent to the yard of a trailer home and Colma Creek. Sewage spilled out onto the land of the trailer home and some also went into Colma Creek. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Colma | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Meliza | Cruz | 2005-05-23 | 650-757-8888 | meliza.cruz@colma.ca.gov, rick.mao@colma.ca.gov | MINOR
5068 | 26 | 1 | ConcordCity | 2007-04-17 13:21 | 800 | 0 |  | 2007-04-17 13:21 |  | -- | 1682 Clayton Road | Concord | Contra Costa | 94519 |  |  | 2007-04-15 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Maintenance Manager | Bruce Good | 2007-04-17 | 925-671-3045
4954 | 25 | 1 | ConcordCity | 2007-03-19 09:02 | 500 | 0 |  | 2007-03-19 09:02 |  | -- | 3703 San Michelle Drive | Concord | Contra Costa | 94520 |  |  | 2007-03-17 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Maintenance Manager | Bruce Good | 2007-03-19 | 925-671-3045
4527 | 24 | 1 | ConcordCity | 2007-01-17 07:51 | 200 | 0 |  | 2007-01-17 07:51 |  | -- | 4450 Melody Drive | Concord | Contra Costa | 94521 |  |  | 2007-01-15 | [9 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Maintenance Manager | Bruce Good | 2007-01-17 | 925-671-3045
4534 | 23 | 2 | ConcordCity | 2007-01-08 | 1000 | 100 | 07-0150 | 2007-01-08 | Bruce Good | ConcordCity | Easement line between the end of Silverspur Court and the Contra Costa Canal. | Concord | Contra Costa | 94518 |  |  | 2007-01-08 | 0.25 | [6 empty] | Low |  | YARD/LAND | No |  | No | No | An estimated 100 gallons entered the Contra Costa Canal, which had been drained for cleaning the prior week. The potentially contaminated area was isolated and the remaining canal water/wastewater mix was collected and discharged back into the sanitary sewer system. |  | Yes | Yes | Yes |  |  | Yes | Yes |  |  |  | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | GREASE | -- Select One -- |  | An estimated 1,000 gallons overflowed from an easement line manhole into an adjacent drainage swale, where it soaked into the ground. But there was a ground squirrel hole in the overflow drainage area that surfaced near the Contra Costa Canal, which allowed an estimated 10% of the overflow to enter the canal, which had been drained for cleaning on 01/02/07. This wastewater co-mingled with the sludgey water remaining in the canal. The potentially affected area was isolated approx 1500 ft upstream and downstream of the spill location and the liquid in the contained area was collected and pumped back into the sanitary sewer system. | Maintenance Manager | Bruce Good | 2007-01-17 | 925-671-3045
4413 | 22 | 1 | ConcordCity | 2006-12-28 09:30 | 100 | 0 |  | 2006-12-28 09:30 |  | -- | 4173 Chaucer Drive | Concord | Contra Costa | 94521 |  |  | 2006-12-23 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Maintenance Manager | Bruce Good | 2006-12-28 | 925-671-3045
3990 | 21 | 1 | ConcordCity | 2006-10-16 09:55 | 100 | 0 |  | 2006-10-16 09:55 |  | -- | 1230 Chicot Place | Concord | Contra Costa | 94521 |  |  | 2006-10-14 |  |  |  | The affected storm drain was thoroughly hydrocleaned and disinfected. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | ConcordCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Maintenance Manager | Bruce Good` | 2006-10-16 | 925-671-3045 | bgood@ci.concord.ca.us | MINOR
3747 | 20 | 1 | ConcordCity | 2006-08-17 08:10 | 300 | 0 |  | 2006-08-17 08:10 |  | -- | 3300 Euclid Ave | Concord | Contra Costa | 94519 |  |  | 2006-08-16 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | ConcordCity | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Maintenance Manager | Bruce Good | 2006-08-17 | 925-671-3045 | bgood@ci.concord.ca.us | MINOR
3568 | 19 | 1 | ConcordCity | 2006-06-27 16:40 | 800 | 0 |  | 2006-06-27 16:40 |  | -- | 5535 Merritt Dr | Concord | Contra Costa | 94521 |  |  | 2006-06-26 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | ConcordCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Maintenance Manager | Bruce Good | 2006-06-27 | 925-671-3045 | bgood@ci.concord.ca.us | MINOR
3416 | 18 | 1 | ConcordCity | 2006-05-26 10:41 | 700 | 0 |  | 2006-05-26 10:41 |  | -- | 2101 Solano Way | Concord | Contra Costa | 94520 |  |  | 2006-05-25 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | ConcordCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Maintenance Manager | Bruce Good | 2006-05-26 | 925-671-3045 | bgood@ci.concord.ca.us | MINOR
3044 | 17 | 1 | ConcordCity | 2006-03-21 16:22 | 250 | 0 |  | 2006-03-21 16:22 |  | -- | 1515 Garcez Drive | Concord | Contra Costa | 94521 |  |  | 2006-03-19 |  |  |  | Sewage overflowed from a rodding inlet on an easement line in the middle of a field between Garcez Drive and Terry Lynn Ln. All liquid wastewater had soaked into the ground before responding crews could effect any recovery effort but all solids were recovered and the area disinfected. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | ConcordCity | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Maintenance Manager | Bruce Good | 2006-03-21 | 925-671-3045 | bgood@ci.concord.ca.us | MINOR
3006 | 16 | 1 | ConcordCity | 2006-03-15 08:42 | 250 | 0 |  | 2006-03-15 08:42 |  | -- | 1561 Matheson Rd | Concord | Contra Costa | 94521 |  |  | 2006-03-14 |  |  |  | 40% recovered, including all solids. The rest had soaked into the ground. The affected area was disinfected. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | ConcordCity | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Maintenance Mgr | Bruce Good | 2006-03-15 | 925-671-3045 | bgood@ci.concord.ca.us | MINOR
2880 | 15 | 1 | ConcordCity | 2006-02-27 09:04 | 250 | 0 |  | 2006-02-27 09:04 |  | -- | 2883 La Salle Ave | Concord | Contra Costa | 94520 |  |  | 2006-02-25 | [9 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | ConcordCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Maintenance Mgr | Bruce Good | 2006-02-27 | 925-671-3045 | bgood@ci.concord.ca.us | MINOR
2808 | 14 | 1 | ConcordCity | 2006-02-14 12:45 | 150 | 0 |  | 2006-02-14 12:45 |  | -- | 4326 Blenheim Way | Concord | Contra Costa | 94521 |  |  | 2006-02-11 |  |  |  | Spillage was flushed to downstream storm drain manhole and removed. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | ConcordCity | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Maintenance Mgr | Bruc e Good | 2006-02-14 | 925-671-3045 | bgood@ci.concord.ca.us | MINOR
2717 | 13 | 1 | ConcordCity | 2006-01-31 15:26 | 150 | 0 |  | 2006-01-31 15:26 |  | -- | 1771 Laguna St. | Concord | Contra Costa | 94520 |  |  | 2006-01-31 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | ConcordCity | OTHER | rodding inlet | BLOCKAGE | GREASE |  |  |  | Maintenance Manager | Bruce Good | 2006-01-31 | 925-671-3045 | bgood@ci.concord.ca.us | MINOR
2389 | 11 | 1 | ConcordCity | 2005-12-31 14:21 | 2500 | 0 | 057586 | 2005-12-31 | Bruce Good |  | 3471 Turner Court | Concord | Contra Costa | 94519 |  |  | 2005-12-31 | 8:00:00 AM | 2005-12-31 | 11:00:00 A | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Maintenance Mgr | Bruce Good | 2005-12-31 | 925-671-3045 | bgood@ci.concord.ca.us | 24HR |  |  | 925-671-3045 | [6 empty] | ConcordCity
2393 | 12 | 1 | ConcordCity | 2005-12-31 14:38 | 2500 | 2500 | 057586 | 2005-12-31 | Bruce Good | ConcordCity | 3471 Turner Court | Concord | Contra Costa | 94519 |  |  | 2005-12-31 | 8:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | YARD/LAND | No |  | No | No | N/A, all sewage was contained within/under the home and in a low spot on the property behind the home. |  | Yes | Yes | Yes | No | No | No | No | No | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | ConcordCity | OTHER | inside home, from sinks and toilets | BLOCKAGE | ROOTS | --Select None-- |  | Roots partially blocked an easement line. The resulting backup overflowed out of the 1st floor sinks and toilets of a home at 3471 Turner Court (there was no property line or building cleanout). The kitchen sink plumbing did have a screw-on access cap on the back side of the house. This was removed and the overflow then when directly into the back yard, where it pooled up in a low spot behind the property. A contract restoration company (Paul Davis Restoration) is now on scene and will recover all standing sewage and then clean up and deodorize the property, and the house and furnishings. I also submitted a short form report (tracking #2389) on this same spill. | Maintenance Mgr | Bruce Good | 2005-12-31 | 925-671-3045 | bgood@ci.concord.ca.us | MAJOR | Bruce Good | Concord | 925-671-3045 |  | 1455 Gasoline Alley | Concord | Contra Costa | 94520 | Bruce Good | City of Concord | 925-671-3045 |  | 1455 Gasoline Alley | Concord | Contra Costa | 94520
2181 | 9 | 1 | ConcordCity | 2005-11-28 11:25 | 200 | 0 |  | 2005-11-28 11:25 |  | -- | 4248 Satinwood Drive | Concord | Contra Costa | 94519 |  |  | 2005-11-24 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | ConcordCity | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Maint Mgr | Bruce J. Good | 2005-11-28 | 925-671-3045 | bgood@ci.concord.ca.us | MINOR
2101 | 8 | 1 | ConcordCity | 2005-11-14 09:09 | 400 | 0 |  | 2005-11-14 09:09 |  | -- | 3625 Sanford St. | Concord | Contra Costa | 94520 |  |  | 2005-11-11 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | ConcordCity | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Maint Mgr | Bruce Good | 2005-11-14 | 925-671-3045 | bgood@ci.concord.ca.us | MINOR
1865 | 7 | 1 | ConcordCity | 2005-09-26 09:49 | 300 | 0 |  | 2005-09-26 09:49 |  | -- | 2125 Northwood Circle | Concord | Contra Costa | 94520 |  |  | 2005-09-25 |  |  |  | All spillage into storm drain was recovered and properly disposed of. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | ConcordCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Maint Mgr | Bruce J. Good | 2005-09-26 | 925-671-3045 | bgood@ci.concord.ca.us | MINOR
1592 | 6 | 1 | ConcordCity | 2005-07-05 12:32 | 100 | 0 |  | 2005-07-05 12:32 |  | -- | 2821 Prospect Avenue | Concord | Contra Costa | 94519 |  |  | 2005-07-02 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | ConcordCity | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Maint Mgr | Bruce Good | 2005-07-05 | 925-671-3045 | bgood@ci.concord.ca.us | MINOR
1248 | 5 | 1 | ConcordCity | 2005-04-04 16:43 | 100 | 0 |  | 2005-04-04 16:43 |  | -- | 238 Roundhill Place | Concord | Contra Costa | 94520 |  |  | 2005-04-03 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | concordcity | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Maintenance Manager | Bruce J. Good | 2005-04-04 | 925-671-3045 | bgood@ci.concord.ca.us | MINOR
1202 | 4 | 1 | ConcordCity | 2005-03-18 09:26 | 500 | 0 |  | 2005-03-18 09:26 |  | -- | Manhole 042 on easement line west of Bloching Circle. | Clayton | Contra Costa | 94517 |  |  | 2005-03-17 |  |  |  | Overflow at MH 042 adjacent to Donner Creek observed by citizen walking dog at 0900. We received call at 1000, arrived on site at 1030, and cleared blockage by 1035. Evidence of solids on ground adjacent to Donner Creek but no visable evidence of sewage in Donner Creek. Field test in 4 creek locations for ammonia was negative. 4 grab samples from creek sent to lab for coliform analysis; results expected by 3/21/05. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | ConcordCity | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Maintenance Manager | Bruce Good | 2005-03-18 | 925-671-3045 | bgood@ci.concord.ca.us | MINOR
1118 | 3 | 1 | ConcordCity | 2005-03-07 10:01 | 450 | 0 |  | 2005-03-07 10:01 |  | -- | 4248 Satinwood Drive | Concord | Contra Costa | 94520 |  |  | 2005-03-04 |  |  |  | Sewage spill was confined to the yard (at building cleanout)and two bathrooms of the above address. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | ConcordCity | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Manager | Bruce Good | 2005-03-07 | 925-671-3045 | bgood@ci.concord.ca.us | MINOR
936 | 2 | 1 | ConcordCity | 2005-02-01 07:59 | 150 | 0 |  | 2005-02-01 07:59 |  | -- | 1682 Clayton Road | Concord | Contra Costa | 94520 |  |  | 2005-01-28 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | ConcordCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Manager | Bruce Good | 2005-02-01 | 925-671-3045 | bgood@ci.concord.ca.us | MINOR
772 | 1 | 1 | ConcordCity | 2005-01-06 14:42 | 500 | 0 |  | 2005-01-06 14:42 |  | -- | 1265 Monument Boulevard | Concord | Contra Costa | 947520 |  |  | 2004-12-30 | [9 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | ConcordCity | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Manager | Bruce Good | 2005-01-06 | 925-671-3045 | bgood@ci.concord.ca.us | MINOR
4912 | 11 | 1 | CountySD2-3 | 2007-03-14 16:30 | 900 | 0 |  | 2007-03-14 16:30 |  | -- | 12555 Tallent Ave | San Jose | Santa Clara | 95127 |  |  | 2007-03-14 |  |  |  | Grease, Roots and gravel. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  | Flushing Inlet |  | Field Inspector | Adam LaBare | 2007-03-14 | 408-255-2137
4381 | 10 | 1 | CountySD2-3 | 2006-12-21 15:27 | 300 | 0 |  | 2006-12-21 15:27 |  | -- | 3551 East Hills Dr. at corner of Laumer Ave. | San Jose | Santa Clara | 95127 |  |  | 2006-12-20 |  |  |  | Received report from property owner at 0930 12/20/06 of overflow from an onsite clean out adjacent to his house. He had called the City of San Jose the previous day in the P.M. when he first was aware of the overflow. City forces responded and inspected the sewer manhole at the intersection of East Hills and Laumer Ave. They observed that flow was unrestricted in the East Hills main and apparently told the property owner the blockage must be within his property. The property owner then called a private plumbing company which was unable to clear the line and indicated they would return the next day but told him the problem was likely in the District's main on Laumer. The property owner, Mr. Ben Shelton, called the District, as stated above, and District personnel were dispatched to the site and verified a mainline stoppage. A hydro flusher Crew was dispatched to the location by 1000 hrs and commenced to clear the blockage in the Laumer main. The blockage was found to be a solid clump of grease within 10 feet of the manhole at the above referenced intersection. A pumper truck also arrived to clean the subject yard and landscaping of contaminated material and vactor and clean the street gutter and a storm water inlet that had received approximately 50 gallons of the effluent. No waters reached streams that flow to the bay. Of the estimated 300 gallons of overflow, most was retained within the property, soaking into the lawn area or standing adjacent to the house foundation. Landscape areas, cleaned of contaminated materials, were disinfected and landscape materials replaced in kind in compliance with current accepted practices. The balance of waters (50+/-gal.) flowing to the public right of way and storm drain were contained within the storm system, evacuated and then the system flushed. No feces or papers were observed to have entered the storm drain system. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Administrator | Sid Nash | 2006-12-21 | 408-255-2137
3976 | 9 | 1 | CountySD2-3 | 2006-10-11 18:00 | 300 | 0 |  | 2006-10-11 18:00 |  | -- | 11265 Canyon Drive | San Jose | Santa Clara | 95127 |  |  | 2006-10-11 |  |  |  | Received call @ 11:15AM that claenout was overflowing at the subject address. Arrived at the site and observed that cleanout was overflowing due to a stoppage in the District's main in Easement #11250. Contacted ABLE Co. crew doing maintenance of District mains in a nearby neighborhood. Stoppage was cleared by noon. Crew then cleaned up papers, debris etc. from the yard and then disinfected the area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | CountySD2-3 | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Administrator | Sid Nash | 2006-10-11 | (408) 255-2137 | snash@markthomas.com, dross@cupertinosanitarydistrict.com | MINOR
3970 | 8 | 1 | CountySD2-3 | 2006-10-09 14:26 | 200 | 0 |  | 2006-10-09 14:26 |  | -- | 15780 Alta Vista Way | San Jose | Santa Clara | 95127 |  |  | 2006-10-07 |  |  |  | Overflow was contained in rear yard of subject property. All solid waste material was removed and put in garbage bagd for proper disposal. Contaminated soils, vegetation etc. were removed from site and replaced. Walkway areas were disinfected. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | CountySD2-3 | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Administrator | Sid Nash | 2006-10-09 | 408-255-2137 | snash@markthomas.com, dross@cupertinosanitarydistrict.com | MINOR
3645 | 7 | 2 | CountySD2-3 | 2006-07-21 14:48 | 2000 | 500 | 06-4308 | 2006-07-21 | Larry Mercado | countySD2-3 | 10969 Brundage Way | San Jose | Santa Clara | 95127 |  |  | 2006-07-21 | 12:30:00 P | [5 empty] | SUNNY WEATHER | Low |  | CAPTURED IN STORM DRAIN | No | None | No | No | Yes |  | Yes | Yes | No | No | No | No | No | No | No | 2006-07-22 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | countySD2-3 | PIPE |  | BLOCKAGE | ROOTS | BREAKAGE OF COLLECTION SYSTEM | Root, grease and Debris |  | Inspectior | Larry Mercado | 2006-07-21 | 408-255-2137 | lmercado@markthomas.com | MAJOR | Sid Nash | CountySD2-3 | 408-255-2137 | 316 | 20833 | Cupertino | CA | 95014 | Larry Mercado | countySD2-3 | 408-255-2137 | 305 | lmercado@markthomas.com | San Jose | Santa Clara | 95127
3596 | 5 | 1 | CountySD2-3 | 2006-07-05 09:54 | 2000 | 0 | 06-3964 | 2006-07-05 | Larry Mercado |  | 10141 Miguelito Road | San Jose | Santa Clara | 95127 |  |  | 2006-07-04 | 8:30:00 AM | 2006-07-04 | 9:30:00 AM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Field Inspector | Larry Mercado | 2006-07-05 | 408-255-2137 | snash2@markthomas.com, dross@cupertinosanitarydistrict.com | 24HR |  |  | (408) 255-2137 | [6 empty] | CountySD2-3
3599 | 6 | 1 | CountySD2-3 | 2006-07-05 10:54 | 2000 | 0 | 06-3964 | 2006-07-05 | Larry Mercado | CountySD2-3 | 10142 Miguelito Road | San Jose | Santa Clara | 95127 |  |  | 2006-07-04 | 8:30:00 AM | [5 empty] | SUNNY WEATHER | Low |  | YARD/LAND | No |  | No | No | Manhole overflowed into dry creekbed. No visable solids or paper. |  | Yes | Yes | No | No | No | No | No | No | No | 2006-07-12 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | CountySD2-3 | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- | Sanitary Wipes (paper) with Kitchen Grease | Sanitary Manhole in County Easement overflowed into drainage swale called Miguelito Creek. Creek is dry during summer months. Effluent soaked into ground. No visable solids or paper. | Field inspector | Larry Mercado | 2006-07-05 | (408) 255-2137 | snash2@markthomas.com, dross@cupertinosanitarydistrict.com | MAJOR | Sid Nash | CountySD2-3 | 408-255-2137 | 316 | 20833 | Cupertino | CA | 95014 |  | County Sanitation District 2-3 | (408) 255-2137 |  | 20833 Stevens Creek Blvd. No. 104 | Cupertino | Santa Clara | 95014
3195 | 4 | 1 | CountySD2-3 | 2006-04-17 14:01 | 655 | 0 |  | 2006-04-17 14:01 |  | -- | 2 Holmes Drive | San Jose | Santa Clara | 95127 |  |  | 2006-04-16 |  |  |  | Standard overflow | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | countySD2-3 | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Field Inspector | Larry Mercado | 2006-04-17 | 408-255-2137 | snash2@markthomas.com, dross@cupertinosanitarydistrict.com | MINOR
3038 | 3 | 1 | CountySD2-3 | 2006-03-17 18:07 | 4500 | 3750 | 06-1620 | 2006-03-14 | Sid Nash | CountySD2-3 | 14030 Woodhaven St 14010&020 Woodhaven St 860 S. White Rd | San Jose CA | Santa Clara | 95127 |  |  | 2006-03-11 | 4:00:00 AM | [5 empty] | CLOUDY WEATHER | High |  | STORM DRAIN | No |  | No | No | County Communications received report of sso from SS manhole in front of 14040 Woodhaven at 1556hrs and contacted L. Mercado(LRM) of CSD#2-3. LRM observed small magnitude of sso through pick hole of SSMH cover and contacted ABLE Underground Construction Inc (ABLE) to respond with emergency crew and flushing equipment. ABLE arrived at location at 1515hrs. Cones and Hazard warning tape was set in place by the crew to cordon off public access to the contaminated areas. The crew commence flushing the maniline to break up the stoppage and flow from the manhole was stopped by 1630hrs. LRM called Sid Nash(SFN) at 1700hrs to notify that he had received another call from County Communications reporting that residents at 14010, 14020 and 14030 Woodhaven complained of sewage overflow at toilets and floor drains in their residence or business. Overflow at buildings was caused by splashback during the flushing operation while breaking up and removing the grease that had plugged the line. Additional crew members were called to the site by SFN to clean up the sewage, disinfect surfaces, remove carpet and padding and dispose of contminated materials. SFN arrived at site at 1830hrs to meet with property owners, view damage and determine extent of remediation work necessary. Carpet and padding are being replaced in one residence and indoor-outdoor carpet in one business. Due to the time of day the damage occurred the businesses were near closing time for the day. The market at 856 S. White Rd. was able to continue business with the public while store staff cleaned the rear of the store not accessible by or a health threat to the public. |  | Yes | Yes | Yes | No | No | No | No | No | No | 2006-03-19 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | CountySD2-3 | MANHOLE | Plugged siphon in adjacent (City of San Jose)jurisdiction's main immediately downstream of overflowing manhole. | BLOCKAGE | GREASE | MULTIPLE CAUSES |  | The following actions are being taken to prevent a re-occurance of this incident: 1. This area will be monitored and cleaned monthly 2. A subsurface overflow pipe will be installed between manholes to a parallel 6" District main which connects to the City of San Jose system on the downstream side of the siphon. 3. The 6" main in Woodhaven will be increased to an 8" main by pipe bursting. See attached map. 4. Backflow protective devices will be installed at each of the side sewers serving 1 residence and 3 commercial uses. 5. The City of San Jose maintenance supervisor will be asked to put the siphon on a priority schedule for more frequent cleaning. 6. A flier included with a CSD#2-3 Annual Report will be sent to the constituents with a message discouraging the disposal of grease, fats and oils into sinks and drains. | Administrator | Sid Nash | 2006-03-14 | 408-253-3849 | snash@markthomas.com, dross@cupertinosanitarydistrict.com | MAJOR | Sid Nash | CountySD2-3 | 408-255-2137 | 316 | 20833 | Cupertino | CA | 95014 |  | TBD
1372 | 2 | 1 | CountySD2-3 | 2005-05-05 17:55 | 300 | 0 |  | 2005-05-05 17:55 |  | -- | 15761 East Alta Vista | San Jose | Santa Clara | 95127 |  |  | 2005-05-04 |  |  |  | Owner while enroute to residence was made aware of spill @ 3:30 PM 5/04/2005 by phone call. Housekeeper mopped up floors of grey water and toilet paper prior to owner arrival at 5:30 PM. Owner initially believed spill source to be internal. Owner called service company to clear onsite lines. Service operator found water standing in cleanout riser indicating source to be in main within adjacent District easement. District Inspector was contacted at 9:30 PM and agreed to meet owner at site at 9:00 AM 5/04/2005. District Inspector contacted District Administrator at 10:00 PM to attend the 9:00 AM meeting next morning. Administrator then left a voice mail message with the District Manager to advise of the spill. District Inspector and Administrator met at the site at the appointed time and inspected adjacent properties to determine range of any overflows. No evidence was found of any SSO at other cleanouts or manholes on the system. They then met with the property owner to assess the damage within the residence. Water Damage Experts was called to clean and disinfect the spill area, remove and dispose of contaminated carpet pads and deliver area rugs and carpets to a carpet cleaner. The owner was advised to contact his contractor who had installed his hardwood floor to remove same, properly dispose of contaminated underlayment and flooring, replace same and send bill to district for reimbursement. This residence has two lateral connections to the district main. Owner has been advised to connect secondary lateral to primary lateral and install a backflow protection device on the district side of the service cleanout. The secondary connection to the main (upstream) will be abandoned. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | CountySD2-3 | MANHOLE | Toilet in Residence | BLOCKAGE | ROOTS |  |  |  | Administrator | Sid Nash | 2005-05-05 | 408-453-5373 | snash2@markthomas.com, dross@cupertinosanitarydistrict.com | MINOR
462 | 1 | 1 | CountySD2-3 | 2004-12-09 12:01 | 500 | 0 |  | 2004-12-09 12:01 |  | -- | Vicinity 10145 Roseview Dr. (APN 612-50-029) | San Jose | Santa Clara | 95127 |  |  | 2004-12-03 |  |  |  | Overflow effluent consisted of water only. Solids and paper etc. were retained in manhole. Manhole was vactored of all retained water and solids. Stoppage 75+/- ft. downstream of manhole in easement line was cleared with hydroflusher. Surface areas around manhole were cleaned, repaired and disinfected. Spill waters soaked into ground before reaching nearby Miguelito Creek (dry). | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | CountySD2-3 | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Administrator | Sidney F. Nash | 2004-12-09 | 408-453-5373 |  | MINOR
4606 | 5 | 3 | Crockett-Valona | 2006-11-28 | 33000 | 3000 | 06-7043 | 2006-11-28 | Kent Peterson | Crockett-Valona | Sewage pump station (approx. 400 Port St, Crockett) | Crockett | Contra Costa | 94525 |  |  | 2006-11-28 | 0.33333 | [6 empty] | Low | Carquinez Strait | SURFACE WATER IMPACT | No |  | No | No | No visible evidence seen. |  | Yes | Yes | No |  |  | No | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | PUMP STATION |  | BLOCKAGE | DEBRIS | -- Select One -- |  | Report of sewage overflowing from the District's pump station under the Carquinez Bridge was received from Caltrans at 14:09 on Dec. 28. A debris blockage in a 4" drain line serving grit removal equipment had occurred. The grit system was turned off at 14:18 and a trash pump was immediately employed to pull water back in from pools outside the fenceline. The blockage was found to be a 6-1/4" screwdriver wrapped with fibrous materials that could not pass a bend in the drain line. It seems impossible that such an item could ever have gotten that far thru the system. There is no alarm mechanism for a blockage in this drain line. Some sewage soaked into the surrounding ground, but most of it traveled the very short distance to the adjacent creek. Directly above this location is a bridge being demolished, and the creek is entirely covered over and inaccessible so that concrete debris will not enter. The creek could not be inspected or cleaned of sewage. This covering extends all the way to the Carquinez Strait, so we had no possibility of recovering anything from the creek. As an active demolition area the ground could not be cleaned or sanitized by us, but is off limits to the public. Photos have been taken. Calculations have been made for the pump output and the estimated spill volume. Solid materials were retained on land. This pump station is unmanned, and we are trying to design an alarm for future blockage of this drain line. Note added 1/24/07: Our contractor, West County Wastewater District modified our grit removal equipment earlier this month to prevent any recurrence of this particular event. | Gen. Mgr. | Kent Peterson | 2006-11-28 | 510-787-2992
3886 | 4 | 1 | Crockett-Valona | 2006-09-15 11:42 | 100 | 0 |  | 2006-09-15 11:42 |  | -- | 414 Bay Street | Crockett | Contra Costa | 94525 |  |  | 2006-09-15 |  |  |  | Possible structural failure to be determined. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Crockett-Valona | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Gen. Mgr. | Kent G. Peterson | 2006-09-15 | 510-787-2992 | manager@town.crockett.ca.us | MINOR
3399 | 3 | 2 | Crockett-Valona | 2006-05-23 15:48 | 1000 | 0 | 06-2948 | 2006-05-17 | Kent Peterson | Crockett-Valona | 242 Kendall Ave | Crockett | Contra Costa | 94525 | -122.2 | 38.05 | 2006-05-16 | 6:30:00 PM | [5 empty] | SUNNY WEATHER | Low | Carquinez Strait | STORM DRAIN | No |  | No | No | Not applicable |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Crockett-Valona | CLEAN OUT |  | BLOCKAGE | ROOTS | --Select None-- |  |  | Dist. Mgr. | Kent Peterson | 2006-05-17 | 510-787-2992 | manager@town.crockett.ca.us | MAJOR | Kent Peterson | Crockett-Valona | 510-787-2992 |  | PO Box 578 | Crockett | Contra Costa | 94525 | Kent G. Peterson | Crockett-Valona San. Dist. | 510-787-2992 |  | PO Box 578 | Crockett | Contra Costa | 94525
2456 | 2 | 2 | Crockett-Valona | 2006-01-03 17:29 | 64000 | 0 | 05-7603 | 2005-12-31 | Kent Peterson | Crockett-Valona | (1) Loring Ave & Rolph Ave intersection (2) South shoreline Carquinez Strait under Carquinez Bridge | Crockett | Contra Costa | 94525 |  |  | 2005-12-31 | 4:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low | Carquinez Strait | SURFACE WATER IMPACT | No |  | No | No | Receiving water was heavily muddy from severe stormwater runoff throughout the region. Nothing else could be observed during the night or in the morning. |  | Yes | No | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Crockett-Valona | MANHOLE |  | BLOCKAGE | GREASE | PUMP STATION FAILURE |  | A period of exceptionally high rainfall had our pump station running at full capacity due to I&I. Rising water in the wet well caused transfer pump #5 to come on in order to send excess water to our equalization tank. The automated alarm alerted me by phone at 1:15 AM on 12/31. Arriving quickly at the pump station, I found the interior flooding. Investigation of the remote equalization tank revealed no water arriving. Our maintenance contractor responded but was not able to make pump #5 pull any water. The rain lessened and 1 SSO ended at 07:20 while the 2nd ended at 08:30. The entire area was severely flooded, and no recovery of water was possible under storm conditions. Only 24 hours later was our maintenance contractor able to clear a severe blockage of grease from the suction pipe to pump #5. The pump itself had not been at fault, and there would have been no SSO's had it been available to us. | District Manager | Kent Peterson | 2006-01-03 | 510-787-2992 | manager@town.crockett.ca.us | MAJOR | Kent Peterson | Crockett-Valona | 510-787-2992 |  | PO Box 578 | Crockett | Contra Costa | 94525 | Kent Peterson | Crockett-Valona | 510-787-2992 |  | PO Box 578 | Crockett | Contra Costa | 94525
1827 | 1 | 2 | Crockett-Valona | 2005-09-22 11:50 | 250 | 0 |  | 2005-09-22 11:50 |  | -- | 1929 Merchant St | Crockett | Contra Costa | 94525 |  |  | 2005-09-21 |  |  |  | This report replaces tracking #1819. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Crockett-Valona | CLEAN OUT |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Dist. Manager | Kent G. Peterson | 2005-09-22 | 510-787-2992 | cvsd@earthlink.net, | MINOR
3495 | 4 | 3 | Cupertino | 2006-06-16 17:16 | 36000 | 1500 | 06-3562 | 2006-06-15 | George Santos | Cupertino | Paramount Drive and Stewart Ct, Saratoga | Saratoga | Santa Clara | 95070 |  |  | 2006-06-14 | 7:30:00 AM | [5 empty] | SUNNY WEATHER | Low | Rodeo Creek | YARD/LAND | No |  | No | Yes | Inspection found overflow from manhole in easement off of Paramount Dr vic Setwart Ct Saratoga effluent from manhole overflowed several parcels and reached the headwaters of Rodeo Creek. |  | Yes | Yes | Yes | No | No | Yes | No | No | No | 2006-07-16 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Cupertino | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES | --Select None-- | Construction debris and grease | Inspection found overflow from manhole in easement off of Paramount Dr. vic. Stewart Ct. Saratoga. Effluent reached the headwaters of Rodeo Creek and may have traveled 1,000 feet where the stream bed became dry. The area was posted for sewage spill and the cleanup was completed 6/15/06. Samples were taken 6/16/06 and are to be tested for E. coli; coliforms and amonia with results to be read 6/17/06 and published 6/19/06 | Administrator | Carl Beckham | 2006-06-15 | 408-253-7071 | cbeckham@cupertinosanitarydistrict.com, dross@cupertinosanitarydistrict.com | MAJOR | Dave Ross | Cupertino | 408-253-7071 |  | 20833 Stevens Creek Blvd | Cupertino | Santa Clara | 95014 | Dave Ross | Cupertino Sanitary District | 408-253-7071 |  | 20833 Stevens Creek Blvd, Suite 104 | Cupertino | Santa Clara | 95014
2440 | 3 | 1 | Cupertino | 2006-01-03 12:20 | 2000 | 0 | 06-0089 | 2006-01-03 | Mr. Jackson | cupertino | Cupertino Rd. | Cupertino | Santa Clara | 95014 |  |  | 2005-12-31 | 12:00:00 P | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | Yes |  | No | Yes | Yes |  | Yes | Yes | Yes | No | No | No | Yes | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | cupertino | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | Overflow into storm drain | Inspector | George Santos | 2006-01-03 | 408-253-7071 | cbeckham@cupertinosanitarydistrict.com, dross@cupertinosanitarydistrict.com | MAJOR | Carl Beckham | Cupertino | 408-253-7071 |  | 20833 Stevens Creek Blvd. # 104 | Cupertino | Santa Clara | 95014 |  | Cupertino
2381 | 2 | 1 | Cupertino | 2005-12-29 14:14 | 1500 | 500 | 05-7523 | 2005-12-29 | Carl Beckham |  | 19500 Pruneridge Ave | Cupertino | Santa Clara | 95014 |  |  | 2005-12-29 | 9:00:00 AM | 2005-12-29 | 10:40:00 A | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | District Administrat | Carl Beckham | 2005-12-29 | 408-253-7071 | cbeckham@cupertinosanitarydistrict.com, dross@cupertinosanitarydistrict.com | 24HR |  |  | 408-253-7071 | [6 empty] | Cupertino
934 | 1 | 1 | Cupertino | 2005-01-31 16:08 | 600 | 0 |  | 2005-01-31 16:08 |  | -- | 10241 Miller Ave. | Cupertino | Santa Clara | 95014 |  |  | 2005-01-22 |  |  |  | Hydro-flushed storm drains and disinfect affected area.All clean up water and disinfectant was contained and hauled away in a vac truck | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Cupertino | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Inspector | George Santos | 2005-01-31 | 408-253-7071 | cbeckham@cupertinosanitarydistrict.com | MINOR
4172 | 15 | 1 | DeltaDiabloSD | 2006-11-30 08:54 | 800 | 0 |  | 2006-11-30 08:54 |  | -- | At the corner of West 9th Street and F Street | Antioch | Contra Costa | 94509 |  |  | 2006-11-23 |  |  |  | This spill was caused by a leak from our 24" force main. The flows were shiifted to the other force main and a contractor has been scheduled to make the necessary repairs to the line. The approximately 750 gallons of waste water was captured and returned to the collection system. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | PIPE |  | CAUSE UNKNOWN | -- Select One -- |  |  |  | CSWII | Robert Wright | 2006-11-30 | 925-382-8937
3268 | 14 | 2 | DeltaDiabloSD | 2006-05-03 08:59 | 30000 | 28500 | 06-2154 | 2006-04-10 | Dennis F. Lanohan | DeltaDiabloSD | Foot of Main Street Port Chicago Naval Base | ConCord | Contra costa | 94520 |  |  | 2006-04-10 | 9:00:00 AM | [5 empty] | CLOUDY WEATHER | Low |  | YARD/LAND | No |  | No | No | This is an update of a previous report to include sampling data that was collected on the dat of the spill. Water was contained to swale adjacent to pump station. Emergency pump was already onsite. Pumping commenced to return the leakage to the collection system immediately after the repair was complete. |  | Yes | Yes | No | No | No | Yes | No | No | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | DeltaDiabloSD | MANHOLE |  | INFRASTRUCTURE FAILURE | --Select None-- | BREAKAGE OF COLLECTION SYSTEM |  |  | Plant Manager | Dennis F. Laniohan | 2006-05-03 | (925) 756 1930 | gp@rb2.swrcb.ca.gov,dennisl@ddsd.org,kerryy@ddsd.org,miked@ddsd.org,jackie.oravitz@navy.mil,gregb@ddsd.org | MAJOR | Dennis F. Laniohan | DeltaDiabloSD | (925) 756 1930 |  | 2500 Pittsburg Antioch Highway | Antioch | Contra Costa | 94509 | Dennis F. Laniohan | Delta Diablo Sanitation District | (925) 756 1930 |  | 2500 Pittsburg Antioch Highway | Antioch | Contra costa | 94509
3092 | 13 | 2 | DeltaDiabloSD | 2006-03-28 16:09 | 90 | 0 |  | 2006-03-28 16:09 |  | -- | Willow Pass Road | Bay Point | Contra Costa County | 94565 |  |  | 2006-02-13 |  |  |  | While District contractor was doing a bypass pump around for a mainline replacement project. The discharge hose come out of the manhole and inadvertently pumped less than 100 gallons of sanitary water on to ground and into storm drain. The contract contained the spill and vacuumed it up with thier pot holing equipment,putting it back into the sanitary system. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | DeltaDiabloSD | OTHER | Contractor bypass pump | BYPASS | --Select None-- |  |  |  | Plant Manager | Dennis F. Laniohan | 2006-03-28 | 925-756-1900 | dennisl@ddsd.org, miked@ddsd.org | MINOR
3094 | 12 | 3 | DeltaDiabloSD | 2006-03-28 16:10 | 100 | 0 |  | 2006-03-28 16:10 |  | -- | Port Chicago Highway and Main Street | Port Chicago | Contra Costa | 94565 |  |  | 2006-01-27 |  |  |  | This item is related to SSO tracking number 2791. The line segment was full of rock. A bypass pump was put in place and floats for the pump became tangled the Operator removed the floats and before he could restore the system to operation the manhole overflowed approximately 100 gallons. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | DeltaDiabloSD | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Plant Manager | Dennis F. Laniohan | 2006-03-28 | 925 756 1930 | dennisl@ddsd.org | MINOR
2791 | 11 | 1 | DeltaDiabloSD | 2006-02-13 13:07 | 50 | 0 |  | 2006-02-13 13:07 |  | -- | Port Chicago Highway and Main Street | Port Chicago | Contra Costa | 94565 |  |  | 2006-01-26 |  |  |  | The line had a significant amount of crushed rock in it. Several days later while inspecing the upstream manholes staff found a manhole that also had a considerable amount of crushed rock in it. Military Base utility staff were called to investigate. This system is operated under contract by Delta Diablo for the United States Navy. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | DeltaDiabloSD | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Plant Manager | Dennis F. Laniohan | 2006-02-13 | 925 7561930 | dennisl@ddsd.org | MINOR
2794 | 10 | 2 | DeltaDiabloSD | 2006-02-13 13:19 | 35000 | 3200 | 06-0064 | 2006-01-02 | Enrique Gloria | DeltaDiabloSD | End of North Broadway. (No street adress for station.) | Bay Point | Contra Costa | 94565 |  |  | 2006-01-02 | 2:28:00 PM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | YARD/LAND | No |  | No | No | As it has been raining for several days it is believed most of the flow was rainwater. Estimate approximately 80% of flow to be rainwater based on normal daily flows for that station. Overflowed out onto a flat plain area with hundreds of acres of pervious soil and approximately 3200 gallons was able to be retreived by pumping. There was no fecal matter observed in any of the overflow. It is believed that very little if any entered the receiving water. Area of overflow is a remote flat plain area with no public access. Significant storm activity was in progress and was unsafe for district personnel to attempt any river sampling. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | DeltaDiabloSD | PUMP STATION |  | INFRASTRUCTURE FAILURE | --Select None-- | PUMP STATION FAILURE |  | Broadway Diversion Pump Station was in diversion mode diverting to an emergency storage basin when the diversion pump tripped off. The backup pump high temperature alarm apparently caused it to trip off also causing the overflow. A plant operator was in the area and responded IMMEDIATELY. Overflow was stopped within 1 minute of his arrival at the diversion station. | Plant Manager | Dennis F. Laniohan | 2006-01-03 | (925) 756 1930 | dennisl@ddsd.org | MAJOR | Dennis F. Laniohan | DeltaDiabloSD | (925) 756 1930 |  | 2500 Pittsburg Antioch Highway | Antioch | Contra Costa | 94509 | Dennis F. Laniohan | Delta Diablo Sanitation District | (925) 756 1930 |  | 2500 Pittsburg Antioch Highway | Antioch | Contra costa | 94509
1734 | 9 | 1 | DeltaDiabloSD | 2005-08-29 11:51 | 30 | 0 |  | 2005-08-29 11:51 |  | -- | 297 Highway Ave. | Bay Point | Contra Costa | 94565 |  |  | 2005-08-19 |  |  |  | District Collection crew vacuumed up solids from cleanout that had overflowed. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | DeltaDiabloSD | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Plant Manager | Dennis F. Laniohan | 2005-08-29 | 925 756 1930 | dennisl@ddsd.org | MINOR
1653 | 8 | 2 | DeltaDiabloSD | 2005-07-27 14:18 | 6000 | 5300 | 05-4324 | 2005-07-21 | Enrique Gloria | DeltaDiabloSD | Bridgehead Pump Station. Bridgehead Road | Oakley | Contra Costa | 94561 |  |  | 2005-07-21 | 10:20:00 A | [5 empty] | SUNNY WEATHER | Low |  | YARD/LAND | No |  | No | No | No receiving water contamination. All leakage was contained on pump station site. |  | Yes | Yes | No | No | No | No | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | DeltaDiabloSD | PUMP STATION |  | INFRASTRUCTURE FAILURE | --Select None-- | PUMP STATION FAILURE |  | 2 weeks previous to this incident the City of Antioch had a contractor removing a large amount of rock from the up stream collection system. After the operation was complete, District staff decided to clean the pump station wetwell as a precautionary measure. Staff decided to practice using the District's emergency bypass pumps to effect the cleaning operation. Shortly after bypass pumping was placed in service one of the discharge hoses separated from it's fitting. Staff immediately isolated the bypass line and returned the pump station to service and initiated response procedures. These procedures included returning as much sewage as possible to the collection system (approx. 5300 gallons) and cleaning the area of the leakage. 2 vac con trucks were used. All leakage was either returned to the collection system or absorbed into the pervious soil on the pump station site (estimated 700 gallons). | Plant Manager | Dennis F. Laniohan | 2005-07-27 | 925 756 1930 | dennisl@ddsd.org | MAJOR | Dennis F. Laniohan | DeltaDiabloSD | 925 756 1930 |  | 2500 Pittsburg Antioch Highway | Antioch | Contra Costa | 94509 |  | Delta Diablo Sanitation District | 925 756 1930 |  | 2500 Pittsburg Antioch Highway | Antioch | Contra Costa | 94509
1586 | 7 | 1 | DeltaDiabloSD | 2005-07-01 08:17 | 200 | 0 |  | 2005-07-01 08:17 |  | -- | Camino Andres Court. Cross Street is Anchor. | Bay Point | Contra Costa | 94565 |  |  | 2005-06-29 |  |  |  | A large piece of SDR26 (new construction drain pipe) was wedged in the District's 8 inch mainline causing the backup. District Crew cleaned the affected area and returned some of the overflow to the collection system. District Construction Inspector met with Developer staff person and discussed how to prevent debris from entering into the collection system. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | DeltaDiabloSD | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Plant Manager | Dennis F. Lanihan | 2005-07-01 | 925-756-1930 | dennisl@ddsd.org | MINOR
1556 | 6 | 1 | DeltaDiabloSD | 2005-06-23 10:28 | 15 | 0 |  | 2005-06-23 10:28 |  | -- | 180 Riverside Drive | Bay Point | Contra Costa | 94565 |  |  | 2005-06-18 |  |  |  | Leak responded to and area cleaned by City of Pittsburg on call staff. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | DeltaDiabloSD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Plant Manager | Dennis F. Laniohan | 2005-06-23 | (925) 756 1930 | dennisl@ddsd.org | MINOR
1521 | 5 | 1 | DeltaDiabloSD | 2005-06-13 16:58 | 900 | 0 |  | 2005-06-13 16:58 |  | -- | 6th and O St. | Antioch | Contra Costa | 94509 |  |  | 2005-06-10 |  |  |  | Cause of spill was 2 very small pinholes due to corrosion in the air release line at the location specified above. The leaking line was taken out of service in less than an hour of receiving notice. The area was cleaned by District vac con crew. Also alot of spill was returned to the collection system by District staff. Affected soil was excavated on 6/13/2005 and repairs will be made on 6/15/2005. Line will be tested after repairs are completed. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | DeltaDiabloSD | PIPE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Plant Manager | Dennis F. Laniohan | 2005-06-13 | (925) 756 1930 | dennisl@ddsd.org | MINOR
1483 | 4 | 1 | DeltaDiabloSD | 2005-06-03 14:22 | 80 | 0 |  | 2005-06-03 14:22 |  | -- | Pittsburg Antioch Highway. Cross Street Verne Roberts Circle. | Antioch | Contra Costa | 94509 |  |  | 2005-06-02 |  |  |  | Air release stuck in open position. Noticed by employees almost immediately forcemain isolated with in 20 minutes. 90% of spill returned to collection system. Area flushed with clean water. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | DeltaDiabloSD | OTHER | Air release valve | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Plant Manager | Dennis F. Laniohan | 2005-06-03 | 1-925-756-1930 | dennisl@ddsd.org | MINOR
1181 | 3 | 1 | DeltaDiabloSD | 2005-03-15 08:03 | 3000 | 2200 | Not applicable | 2005-03-10 | Dennis Laniohan |  | Foot of Main Street. Concord Naval Weapons Station. | Port Chicago | Contra Costa | 94520 |  |  | 2005-03-09 | 3:10:00 AM | 2005-03-10 | 4:30:00 AM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Plant Manager | Dennis F. Laniohan | 2005-03-15 | 9257561930 | dennisl@ddsd.org | 24HR |  |  | 9257561930 | [6 empty] | DeltaDiabloSD
715 | 1 | 1 | DeltaDiabloSD | 2005-01-03 14:02 | 150 | 0 |  | 2005-01-03 14:02 |  | -- | 148 Peninsula Road | Bay Point | Contra Costa | 94565 |  |  | 2004-12-20 |  |  |  | All of the wastewater was vacuumed up by the District Vac Con and ther area flushed with fresh water. Roto Rooter was contacted to inspect the plugged line segment. The current planned maintenance itemhas been modified from a yearly clean to every 6 months and a back flow preventer installed | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | deltadiablosd | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Mr. | Dennis F. Laniohan | 2004-12-22 | 925 756 1930 | dennisl@ddsd.org | MINOR
718 | 2 | 1 | DeltaDiabloSD | 2005-01-03 14:05 | 100 | 0 |  | 2005-01-03 14:05 |  | -- | 137 Peninsula Road. (Beach Street, Cross street) | Bay point | Contra Costa | 94565 |  |  | 2004-12-13 |  |  |  | All wastewater recovered with Vac Con. street gutters and Homeowner yard cleaned. Flushed area. No sewage to storm drains. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | deltadiablosd | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Mr. | Dennis F. Laniohan | 2004-12-16 | 925 756 1930 |  | MINOR
4903 | 4 | 2 | DublinSanRamon | 2007-03-01 | 66000 | 0 | 07-1323 | 2007-03-01 | Levi Fuller | DublinSanRamon | 4362 Roscommon Way | Dublin | Alameda | 94568 |  |  | 2007-02-27 | 0.35417 | [6 empty] | Low |  | STORM DRAIN | No |  | No | No | No observable ecological damage to Tassajara Creek |  | Yes | Yes | Yes |  |  | Yes | No |  |  |  | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS | -- Select One -- |  |  | Operatios Supervisor | Levi Fuller | 2007-03-01 | 925-875-2300
3197 | 3 | 1 | DublinSanRamon | 2006-04-17 14:01 | 900 | 0 |  | 2006-04-17 14:01 |  | -- | Davis Street South of 8th Street- On the PARKS Military Base | Dublin | Alemeda | 94568 |  |  | 2006-04-17 |  |  |  | Rural Area - It appears that the Grade Ring was dislodged by a industrial weed mower. This allowed debris to enter the line causing plugging. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | DublinSanRamon | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Plant Operations Sup | Levi Fuller | 2006-04-17 | 925-875-2300 | anderson@dsrsd.com; fuller@dsrsd.com,misra@dsrsd.com, fowler@dsrsd.com | MINOR
2637 | 1 | 1 | DublinSanRamon | 2006-01-17 17:15 | 10125 | 0 | 05-4424 | 2005-07-26 | Levi Fuller | DublinSanRamon | 9033 Craydon Circle | San Ramon | Contra Cost | 94551 |  |  | 2005-07-26 | 8:30:00 AM | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No | Storm Drain - ph 8.43 Ammonia 0.902 Alamo Creek upstream - ph 8.43 Ammonia 0.3062 Alamo Creek downstream - ph 8.43 Ammonia 0.8213 | No | No | No visible damage to aquatic life |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | DublinSanRamon | MANHOLE |  | BLOCKAGE | DEBRIS | --Select None-- |  |  | Ops Supervisor | Levi Fuller | 2006-01-17 | 925-875-2300 | anderson@dsrsd.com; fuller@dsrsd.com,misra@dsrsd.com, fowler@dsrsd.com | MAJOR | Levi Fuller | DublinSanRamon | 925-875-2300 |  | 7399 Johnson Drive | Pleasanton | Alameda | 94588 |  | DSRSD
2638 | 2 | 1 | DublinSanRamon | 2006-01-17 17:32 | 1100 | 300 | 05-0393 | 2005-01-14 | Levi Fuller | DublinSanRamon | 4895 Hacienda Dublin, Ca. 94568 | Dublin | Alameda | 94568 |  |  | 2005-01-14 | 12:30:00 P | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | No | No damage to Aquatic Life |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | DublinSanRamon | MANHOLE |  | BLOCKAGE | --Select None-- | --Select None-- |  |  | Opr. Supervisor | Levi FUller | 2006-01-17 | 925-875-2300 | anderson@dsrsd.com; fuller@dsrsd.com,misra@dsrsd.com, fowler@dsrsd.com | MAJOR | Levi Fuller | DublinSanRamon | 925-875-2300 |  | 7399 Johnson Drive | Pleasanton | Alameda | 94588 |  | Shell Gas Company |  |  | 4895 Haceinda | Dublin | Alameda | 94588
2895 | 1 | 1 | EastPaloAlto | 2006-02-28 10:05 | 500 | 0 |  | 2006-02-28 10:05 |  | -- | Mainline blockage on Westeria at Sage street. manhole overflowed into storm drain. approximately 500 gallons spilled | East Palo Alto | San Mateo | 94303 |  |  | 2006-02-26 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | EastPaloAlto | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | General Manager | Lee Hawkins | 2006-02-28 | 650-325-9021 | lhawkins@epasd.com, lhawkins@epasd.com | MINOR
4766 | 8 | 2 | EBDA | 2007-02-13 | 1115000 | 0 | 07-977 | 2007-02-13 | Karl D. Royer | EBDA | 2600 Grant Ave | San Lorenzo | Alameda | 94580 |  |  | 2007-02-13 | 0.40278 | [6 empty] | Low | San Francisco Bay Area | SURFACE WATER IMPACT | No |  | No | No | Oro Loma Sanitary District (OLSD) staff inspected the receiving waters at 11:00 AM while grabbing a sample to test for chorine residual. The tide was out allowing for only a single sample to be grabbed from a puddle located in the old outfall channel, which is located on the bay side of the levee. The release occurred between 9:40 AM and 10:17 AM. The residual in the OLSD contact tank at the time of release was 3.5 mg/l. The sample grabbed from the recieving waters registered a chorine residual of 2.1 mg/l. There were no visual affects of the release on the receiving water. |  | No | No | Yes |  |  | Yes | Yes |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BYPASS | -- Select One -- | -- Select One -- |  | Preventative maintenance was occurring at the Oro Loma Effluent Pump Station (OLEPS). The pump station has four pumping units. Two electric and two diesel operated pumps. Each unit has a right angle gear drive. Each of the gear drives has external heat exchangers that are removed from service to have their internal tubes cleaned annually. The normal procedure is to take both an electric and an engine operated pump out of service at the same time to expedite the cleaning process. The south side or bank of gear drives were removed from service and cleaned without incident. The release occurred when the north bank was in the process of being cleaned. A single electric pump was unable to keep up with the flow and the engine was called on to operate. The engine came on line at the required time but remained in the idle speed position and was unable to keep up with the flow. The engine is programmed to idle for 30 seconds for warm up purposes prior to ramping up to its full operating speed. When the south bank of gear drives were cleaned it was necessary to lock and tag out the units per safety procedures. The engine is locked out by shutting off electrical power to the control computer. When the computer is re-energized the controller defaults to an idle position on the speed toggle switch. This switch is required to be reset to the rated speed position for proper operation. The Operator on duty returned the engine to service. He received an alarm from another area of the OLSD plant that needed his attention. He inadvertently forgot to reset the toggle switch and neglected to watch the engine ramp up to full operating speed prior to leaving the pump station to respond to the other alarm. The engine while in the idle position was unable to keep up with the flow. The wet well levels rose and activated the high wet well level alarm. The Operator responded to the high wet well level alarm and immediately identified the problem. He reset the toggle switch and the engine ramped up to full speed alleviating the alarm condition and subsequent overflow. The East Bay Dischargers Authority (EBDA) Operations and Maintenance (O&M) Manager spoke with OLSD staff to develop procedures that will enable an Operator to stay on site during these type of maintenance procedures. In addition the O&M Manager has instructed the EBDA instrumentation contactor to research options to adjust the engine’s proprietary programming. Specifically to program the speed control switch to default from idle to rated speed when resetting the computer controller. Attached to this documen as a PDF file is a letter from the OLSD’s Director of Water Quality Services on the incident. | Operation & Maintenance Manager | Karl Royer | 2007-02-13 | 510-278-5910
3129 | 6 | 1 | EBDA | 2006-04-05 06:45 | 61012 | 0 | 06-2024 | 2006-04-05 | Karl D. Royer |  | 2600 Grant Ave | San Lorenzo | Alameda | 94580 |  |  | 2006-04-04 | 6:41:00 PM | 2006-04-04 | 6:48:00 PM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Operation & Maintena | Karl Royer | 2006-04-05 | 510-278-5910 | kroyer@ebda.org, cweir@ebda.org | 24HR |  |  | 510 278-5910 | [6 empty] | EBDA
3132 | 7 | 1 | EBDA | 2006-04-06 08:23 | 61012 | 0 | 06-2024 | 2006-04-05 | Karl D. Royer | EBDA | 2600 Grant Ave | San Lorenzo | Alameda | 94580 |  |  | 2006-04-04 | 6:41:00 PM | [5 empty] | RAINING FOR SEVERAL DAYS | Low | SF Bay/Region 2 | SURFACE WATER IMPACT | No |  | No | No | The EBDA O&M Manager was notified via phone at 7:00 PM of a secondary treated chlorinated effluent release at the Oro Loma Effluent Pump Station. The O&M Manger arrived on site by 7:30 PM. The station was returned to automatic operation prior to inspecting the discharge location. High tide was at 8:25 PM and was recorded at a level of 5.6'. A sample was grabbed at 8:00 PM from the old outfall channel, which is located on the bay or storm side of the levee and measured for chlorine residual. No residual was measured within the sample. No further samples were grabbed. |  | Yes | No | No | No | No | Yes | Yes | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | EBDA | PUMP STATION |  | INFRASTRUCTURE FAILURE | --Select None-- | --Select None-- |  | The EBDA O&M Manager was notified via phone at 7:00 PM of a release at the Oro Loma Effluent Pump Station (OLEPS). The release consisted of secondary treated chlorinated effluent. The Oro Loma Sanitary District's old outfall channel effluent weir overflowed between 6:41:08 PM and 6:48:39 PM for a total of 7 minutes and 31 seconds. Two engine driven pumps, each capable of pumping up to 115 mgd each were in operation prior to the release. The flows were beginning to subside and the pumping units shut down via ladder logic and were in a cool down sequence. Two 350 HP electric operated pumps each capable of pumping 64 mgd were called for service by the controller. One of the VFD units failed during start up, allowing for only single pump operation. The failed VFD would not immediatly re-set and the wet well level rose requiring operation of the engine driven pump(s). These units were programmed not to operate in the automatic mode until the discharge valves close after their cool down sequencing is complete. A high level alarm was activated, which was responded to by the Operator on duty. The engines were available for operation in manual and would have started in auto once their discharge valves closed. The Operator responding to a high wet well scenario, seeing the engines in cool down mode; made a decision to reset the entire control system. This action required the ladder logic to start from the beginning of the operating program, effectively slowing down the pumping units' response time. It took several minutes for the units to come back on line in automatic operation alleviating the high wetwell/overflow condition. The engine cool down sequence takes 5 minutes. At the end of the cool down period the discharge valve will close. The engines are designed not to come on line in automatic unless these vavles are in the closed position. The discharge valves are 48-inch butterfly actuated valves that can open and close completely in 120 seconds. Previously an adjustment was made to slow down the valve open/closing speed; to control both flow and pressure fluctuations that were adversely affecting the down stream operation of the Marina Dechlorination Facility and San Leandro Effluent Pumping Station. This adjustment added approximatly an additional 60 seconds to the shutdown time. Two new registers were programmed into the OLEPS's controller to allow the discharge valves of the diesel driven pumps to open and close with a shorter time interval, shortening the entire process from 180 to 100 seconds. In addition the discharge valves are programmed to close upon initiation of the cool down sequencing. These changes has shortened the start up of the electric motors driven pumps from a possible 8 minutes to 100 seconds. In addition the high wet well level alarm was lowered 6-inches to afford a longer reaction time for operators and a sign was posted above the controllers to remind the operators to control the station in manual during high alarm conditions. | O&M Manager | Karl D. Royer | 2006-04-05 | (510) 278-5910 | kroyer@ebda.org, cweir@ebda.org | MAJOR | Karl D Royer | East Bay Dischargers Authority | 510 278 5910 |  | 2651 Grant Ave | San Lorenzo | Alameda | 94580 | Karl D Royer | East Bay Dischargers Authority | 510 278 5910 |  | 2651 Grant Ave | San Lorenzo | Alameda | 94580
2522 | 5 | 2 | EBDA | 2006-01-05 14:51 | 609230 | 0 | 05-7578 | 2005-12-31 | Karl Royer | EBDA | 2600 Grant St. | San Lorenzo | Alameda | 94580 |  |  | 2005-12-31 | 4:20:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low | SF Bay/Region 2 | SURFACE WATER IMPACT | No |  | No | No | There were four seperate releases totalling 85 minutes over a period of several hours, from 0420 to 1305. With the exception of a single 10 minute period, the EBDA forcemain was discharging and flowing at or above conplete designed flow capacity. High tide at the source of the discharge reached 8.6 feet at 1130. The chlorine residual leaving the OLSD was 1.5 mg/l. A sample was grabbed 0830 from what is called the old outfall channel, which is located just on the bay side of a levee and measured for chlorine residual. No residual was measured within the sample. No further samples were grabbed due to the results of the initial sample and what was deemed an unsafe location in terms of tide and storm. Release No.1 lasted for 6 minutes cresting the weir at an average 0.2' at a calculated rate of 3370 gpm for a total release of 20220 gallons. Release No.2 lasted for 15 minutes cresting the weir at an average 0.2' at a calculated rate of 3370 gpm for a total release of release of 50550 gallons. Release No.3 lasted for 60 minutes cresting the weir at an average 0.3' at a calculated rate of 6325 gpm for a total release of release of 379500 gallons. Release No.4 lasted for 5 minutes cresting the weir at an average 0.8' at a calculated rate of 31792 gpm for a total release of 158960 gallons. |  | Yes | No | No | No | No | Yes | Yes | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | EBDA | PUMP STATION |  | INFRASTRUCTURE FAILURE | --Select None-- | PUMP STATION FAILURE |  | The Operations and Maintenance Manager responded to a computer generated page of an alarm conditon at the Oro Loma Effluent Pumping Station. One of two engine driven pumps each capable of pumping up to 115 MGD was in automatic operation while the other unit was failed. The OLSD operator was manually running two additional electric operated pumps in hand to keep up with the flow. The failed unit was out of service due to a high jacket exit temperature alarm, an indication of a failed cooling system within the engine itself. The flows continued to rise during the day due to the diurnal flow pattern as well as storm conditions. In addition the line pressure increased with the significant bay tides. Staff called in a caterpillar service technician to help identify the problem. The primary cause of the engine failure was associated with the diesel fuel supply. The diesel fuel system is designed to have a primary electric transfer pump with a back up unit for redundancy. In addition a manual hand pump is plumbed into the system as a tertirary backup. The locking mechanism (angle iron L-bracket) for the manual hand pump was discovered to be bent and inoperable. Failure analysis detertimed that high fuel system line pressure weakened the bracket causing it to bend during this situation, due to the extended load on the pump engines. The bracket failure enabled the hand crank to spin freely causing the diesel fuel to partially recirculate. The flow recirculation issue provided only enough fuel for a single engine to maintain operation. Staff bent the bracket back and locked out the handle. The fuel supply was restored to normal condition within minutes allowing both engines to operate, which subsquently mitigated the overflow release. The angle iron L-bracket was repaired after the weekend and the alarm system associated with this substation is being upgraded due to this incident to facilitate quicker diagnosis of problems with this subsystem. | Operation & Maintena | Karl Royer | 2006-01-05 | 510-278-5910 | kroyer@ebda.org, cweir@ebda.org | MAJOR | Karl Royer | EBDA | 510 278 5910 |  | 2651 Grant Ave | San Lorenzo | Alameda | 94580 | Karl Royer | EBDA | 510 278 5910 |  | 2651 Grant Ave | San Lorenzo | Alameda | 94580
1435 | 4 | 2 | EBDA | 2005-05-20 13:47 | 300000 | 0 | 05-2958 | 2005-05-18 | Karl D Royer | EBDA | 2600 Grant Ave | San Lorenzo | Alameda | 94580 |  |  | 2005-05-18 | 10:00:00 A | [5 empty] | CLOUDY WEATHER | Low | San Francisco Bay | SURFACE WATER IMPACT | No |  | No | No | I inspected the receiving water immediately after the release and again 1.5 hours later. There was no visible impact to animal or plant life. |  | Yes | No | No | No | No | Yes | Yes | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | EBDA | MANHOLE |  | BYPASS | --Select None-- | --Select None-- | This release was the result of human error. |  | O&M Manager | Karl Royer | 2005-05-19 | 510 410 5904 | kroyer@ebda.org, cweir@ebda.org | MAJOR | Karl D Royer | East Bay Dischargers Authority | 510 278 5910 |  | 2651 Grant Ave | San Lorenzo | Alameda | 94580 | Karl D Royer | East Bay Dischargers Authority | 510 278 5910 |  | 2651 Grant Ave | San Lorenzo | Alameda | 94580
777 | 3 | 1 | EBDA | 2005-01-06 15:27 | 520750 | 0 | 04-6887 | 2004-12-30 | Karl D. Royer | EBDA | 3000 Davis Street | San Leandro | Alameda | 94577 |  |  | 2004-12-30 | 4:54:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low | San Francisco Bay | SURFACE WATER IMPACT | No |  | No | No | An inspection of the discharge site at the end of the release showed no visual damage to equatic, aniamal or plant life in the immediate vicinity. |  | Yes | No | Yes | No | No | Yes | No | Yes | No | 2005-01-31 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | EBDA | PUMP STATION |  | ELECTRICAL POWER FAILURE | --Select None-- | --Select None-- |  | On December 30, 2004 an unauthorized release of secondary treated wastewater occurred at this station. The station lost power from 4:54 AM to 6:59 AM, for a total of 2 hours and 5 minutes. The initial report calculated the release to be 500,000 gallons. The actual release has been calculated to be 520,750 gallons. PG&E reported that they have no recorded loss of power at this location in the time period reported. The engine generator was found to be in an “over crank” alarm condition and needed a “jump” to start. (Subsequently, the batteries were replaced.) Power was not restored upon initiation of generator operation. The Operators on duty stated they manually operated the “automatic transfer switch” several times prior to power restoration. A 30 HP VFD failed once the power was restored. The associated motor was found to be failed later in the same day. A second 30 HP motor failed while attempting to operate the station under auxiliary power approximately 36 hours after the initial event. The transfer switch was in a neutral position, not allowing the station to run on either PG&E or auxiliary power. The two motors were pulled and sent to a local electrical shop for failure analysis and repairs. A VFD unit was ordered and designated for immediate shipping. The most recent load test for the generator at this location was August of 2003. In addition, the engine received its annual servicing in September of 2004. Staff arranged for the generator to be load tested shortly after the station failure, which confirmed proper operation and power generation. An additional service provider was hired to inspect the transfer switch to insure proper operation of this unit. It too, passed the testing process. Failure analysis from the electrical shop has identified two separate issues with the motors. The first being the unit connected to the failed VFD. The heater used to keep the insulation dry was not shielded and was attached in such a way that it burnt the motor’s winding. The second motor had water damage identified by, water and rust lines inside the housing. It is assumed that the heater block was not functioning as designed. This is consistent with the actual failure. The motor smoked during a “cold” start. Summary: PG&E states that they supplied constant and clean power to the station during this time period, but as of this writing are still researching possibilities. They have found no record of a power failure or power blip at this station. One of the station’s 30 HP motors had a significant motor short. The engine sensed no primary power source and attempted to initiate operation. The engine failed to start. The transfer switch was in the neutral position. The electrical short may have momentarily impeded the PG&E power supply, which would have called for auxiliary power operation. The engine attempted to operate but did not start, leaving the transfer switch in a neutral position. The operators responded to an alarm at the station and found the engine failed. They evaluated the situation and jump started the engine. Upon noticing no resolution with the engine start up, progressed to the transfer switch. They returned the switch to the normal (PG&E) position, which restored the station to operation. EBDA is in the process of restoring the station to full operation and continuing to research possible scenarios that may have contributed to the cause of the release. All measurers for remedial and corrective answers will be considered and forwarded as identified. | O&M Manager | Karl D. Royer | 2005-01-06 | 510 278 5910 | kroyer@ebda.org | MAJOR | Karl D Royer | East Bay Dischargers Authority | 510 278 5910 |  | 2651 Grant Ave | San Lorenzo | Alameda | 94580 | Karl D Royer | East Bay Dischargers Authority | 510 278 5910 |  | 2651 Grant Ave | San Lorenzo | Alameda | 94580
416 | 2 | 1 | EBDA | 2004-12-06 12:32 | 10000 | 0 | 046244 | 2004-12-06 | Karl D Royer | EBDA | 3000 Davis Street | San Leandro | Alameda | 94577 |  |  | 2004-11-30 | 7:49:00 PM | [5 empty] | SUNNY WEATHER | Low | San Francisco Bay | SURFACE WATER IMPACT | No |  | No | No | The treated secondary wastewater flowed to the "old san leandro outfall". The tide was in a low position. There was no standing water at this location when inspected approximately 45 minutes after the release. No impact was apparent to wild life or the surrounding plants. |  | Yes | No | No | No | No | Yes | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jyl@rb2.swrcb.ca.gov | EBDA | PUMP STATION |  | ELECTRICAL POWER FAILURE | --Select None-- | --Select None-- |  | PG&E reported that a raccoon entered one of their facilites causing some shorts to occur. These shorts resulted in some fuses failing on PG&E equipment, which created what is known as a "single phase condition". This single phased condition provided power to operate the effluent pumping station's lights but not the pumps. In addition, the power supply was such that the engine generator did not trip and come on line (it saw a power supply). A high level alarm sounded to which, Operators responded and manually started the engine generator set in less than 4 minutes. This incident was completely beyond the control of EBDA and/or San Leandro personel. All equipment operated as designed. Operations staff responded pursuant to policy, procedures and training. | O&M Manager | Karl D Royer | 2004-12-06 | 510 278-5910 |  | MAJOR | Karl D Royer | East Bay Dischargers Authority | 510 278 5910 |  | 2651 Grant Ave | San Lorenzo | Alameda | 94580 | Karl D Royer | East Bay Dischargers Authority | 510 278 5910 |  | 2651 Grant Ave | San Lorenzo | Alameda | 94580
2318 | 3 | 2 | EBMUD | 2005-12-23 13:20 | 9100000 | 0 | 057271 | 2005-12-19 | Dan Jackson | EBMUD | OV-5 Shellmound Street Temescal Creek Overflow structure | Emeryville | Alameda | 94649 |  |  | 2005-12-18 | 8:30:00 AM | [5 empty] | RAINY WEATHER | Low | Central SF Bay | SURFACE WATER IMPACT | No |  | No | No | Visual observations made on 12/19, no impacts observed. Sampling not possible at this location due to restricted access. |  | Yes | No | No | No | No | No | No | Yes | No | 2006-01-31 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | EBMUD | MANHOLE |  | ELECTRICAL POWER FAILURE | --Select None-- | --Select None-- |  |  | Senior EHS Specialis | Dan Jackson | 2005-12-19 | 510-287-0509 | dejackso@ebmud.com, dwilliam@ebmud.com | MAJOR | Dan Jackson | EBMUD | 510-287-0509 |  | PO Box 24055 | Oakland | Alameda | 94623 |  | EBMUD
2321 | 2 | 3 | EBMUD | 2005-12-23 13:32 | 900000 | 0 | 057271 | 2005-12-19 | Dan Jackson | EBMUD | OV-2 Foot of Webster Street | Alameda | Alameda | 94501 |  |  | 2005-12-18 | 7:30:00 AM | [5 empty] | RAINY WEATHER | Low |  | SURFACE WATER IMPACT | No |  | No | No | Observations made 12/19/05, no impacts observed. Samples collected, results not available at time of this report. |  | Yes | No | No | No | No | Yes | No | Yes | No | 2006-01-31 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | EBMUD | MANHOLE |  | ELECTRICAL POWER FAILURE | --Select None-- | --Select None-- |  |  | Senior EHS Specialis | Dan Jackson | 2005-12-19 | 510-287-0509 | dejackso@ebmud.com, dwilliam@ebmud.com | MAJOR | Dan Jackson | EBMUD | 510-287-0509 |  | PO BOx 24055 | Oakland | Alameda | 94623 |  | EBMUD
2322 | 1 | 3 | EBMUD | 2005-12-23 13:32 | 600000 | 0 | 057271 | 2005-12-19 | Dan Jackson | EBMUD | OV-1 Foot of Alice St South of Jack London Sq. | Oakland | Alameda | 94612 |  |  | 2005-12-18 | 8:30:00 AM | [5 empty] | RAINY WEATHER | Low |  | SURFACE WATER IMPACT | No |  | No | No | Observations made 12/19/05, no impacts observed. Samples collected, results not available at time of this report |  | Yes | No | No | No | No | Yes | Yes | Yes | No | 2005-01-31 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | EBMUD | MANHOLE |  | ELECTRICAL POWER FAILURE | --Select None-- | --Select None-- |  |  | Senior EHS Specialis | Dan Jackson | 2005-12-19 | 510-287-0509 | dejackso@ebmud.com, dwilliam@ebmud.com | MAJOR | Dan Jackson | EBMUD | 510-287-0509 |  | PO Box 25055 | Oakland | Alameda | 94623 |  | EBMUD
4082 | 5 | 1 | EBRegionalPark | 2006-11-08 10:52 | 800 | 0 |  | 2006-11-08 10:52 |  | -- | Del Valle Regional Park 7000 Del Valle Rd. | Livermore | Alameda | 94550 |  |  | 2006-10-22 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | EBRegionalPark | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Water Resources Mgr. | Neal Fujita | 2006-11-08 | 510-649-3313 | nfujita@ebparks.org, | MINOR
4078 | 3 | 1 | EBRegionalPark | 2006-11-08 10:48 | 800 | 0 |  | 2006-11-08 10:48 |  | -- | Del Valle Regional Park 7000 Del Valle Rd. | Livermore | Alameda | 94550 |  |  | 2006-10-10 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | EBRegionalPark | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Water Resources Mgr. | Neal Fujita | 2006-11-08 | 510-649-3313 | nfujita@ebparks.org, | MINOR
4080 | 4 | 1 | EBRegionalPark | 2006-11-08 10:49 | 800 | 0 |  | 2006-11-08 10:49 |  | -- | Del Valle Regional Park 7000 Del Valle Rd. | Livermore | Alameda | 94550 |  |  | 2006-10-10 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | EBRegionalPark | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Water Resources Mgr. | Neal Fujita | 2006-11-08 | 510-649-3313 | nfujita@ebparks.org, | MINOR
3837 | 2 | 1 | EBRegionalPark | 2006-09-05 12:49 | 900 | 0 |  | 2006-09-05 12:49 |  | -- | Del Valle Regional Park 7000 Del Valle Road | Livermore | Alameda | 94550 |  |  | 2006-09-02 |  |  |  | Office Of Emergency Services notified after overflow (OES#065252). | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | EBRegionalPark | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Water Resources Mgr. | Neal Fujita | 2006-09-05 | 510-649-3313 | nfujita@ebparks.org, | MINOR
1506 | 1 | 1 | EBRegionalPark | 2005-06-09 23:10 | 500 | 0 |  | 2005-06-09 23:10 |  | -- | Del Valle Regional Park 7000 Del Valle Road | Livermore | Alameda | 94550 |  |  | 2005-05-30 |  |  |  | Sewage lift station failure caused sewage overflow of 300-500 gallons at the west beach area of Del Valle Regional Park. Sewage flowed from lift station across a lawn area and onto adjacent beach where sewage was captured by containment trenches. Public evacuation of the involved area along with proper notifications were executed. Subsequent sampling | [5 empty] | NO WATER INVOLVED | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | EBRegionalPark | PUMP STATION |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | None | Neal Fujita | 2005-06-08 | 510-649-3313 | nfujita@ebparks.org | MINOR
5167 | 13 | 1 | FairfieldCity | 2007-04-26 16:43 | 300 | 0 |  | 2007-04-26 16:43 |  | -- | 1000 Travis Blvd. | Fairfield | Solano | 94533 |  |  | 2007-04-16 |  |  |  | Fully contained SSO in storm drain and returned to sewer system. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Public Works Manager | James Pritchard | 2007-04-26 | 707-428-7415
4966 | 12 | 1 | FairfieldCity | 2007-03-19 | 6500 | 0 | 07-1772 | 2007-03-19 | James Pritchard | FairfieldCity | 3950 Paradise Valley Drive Paradise Valley Golf Course Manhole located along hole #1 | Fairfield | Solano | 94533 |  |  | 2007-03-19 | 0.57292 | [6 empty] | Medium |  | YARD/LAND | No |  | No | Yes | SSO flowed into french drains on golf course. Sampled creek and pond in vicinity with no indication of ammonia. |  | Yes | Yes | Yes |  |  | Yes | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS | -- Select One -- |  | SSO entered french drain near manhole on golf course. Nearest surface water location approximately four hundred feet away. No indication of ammonia in any surface water. Entire SSO contained in turf area and french drain. We posted area and will leave posted until golf course aerates affected area and puts down ammonia nitrate. | Public Works Manager | James Pritchard | 2007-03-20 | 707-428-7415
4426 | 11 | 1 | FairfieldCity | 2006-12-30 12:50 | 150 | 0 |  | 2006-12-30 12:50 |  | -- | Intersection of Mathew Dr./Scott St. | Fairfield | Solano | 94533 |  |  | 2006-12-29 |  |  |  | Overflow occurred from grease blockage in 8" sewer main. Overflow went into gutter, storm drain and then ran into storm water creek. Unable to recover overflow due to amount of water in creek from storm run-off. Vacuumed 1,000 gallons from creek and returned to sanitary sewer. After vacuming water from creek, no visible evidence of overflow. Took Amonia sample from Drain inlet and then 50' downstream in creek, amonia samples were negative. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Public Works Supervi | George Shimboff | 2006-12-30 | (707) 428-7057
4376 | 10 | 1 | FairfieldCity | 2006-12-20 15:53 | 500 | 0 |  | 2006-12-20 15:53 |  | -- | 1220 Dana Dr. | Fairfield | Solano | 94533 |  |  | 2006-12-18 |  |  |  | Overflow occurred from grease blockage in 8" sewer main. Overflow went into gutter then reached storm drain. 400 gallons recovered from storm drain, unable to recover other 100 gallons due to SSO reaching large box culvert that was conveying storm run-off. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Public Works Supervi | George Shimboff | 2006-12-20 | 707 428-7057
3948 | 9 | 1 | FairfieldCity | 2006-10-01 07:21 | 1375 | 1375 | 06-5834 | 2006-10-01 | George Shimboff | FairfieldCity | 1941 Grande Cir. | Fairfield | Solano | 94533 |  |  | 2006-09-30 | 9:50:00 AM | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | No | Contained completely in storm drain. |  | Yes | Yes | No | No | No | Yes | Yes | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | FairfieldCity | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- |  | SSO caused by grease blockage. Overflow contained in storm drain, pumped 20,000 gallons from storm drain to capture all of SSO. Amonia testing prior and post pumping of storm drain to confirm complete capture of SSO. | Public Works Manager | James C. Pritchard | 2006-10-01 | 707 428-7415 | jpritchard@ci.fairfield.ca.us, | MAJOR | Jim Pritchard | FairfieldCity | (707) 428-7415 |  | 420 Gregory | Fairfield | Solano | 94533 |  | City of Fairfield
3855 | 8 | 1 | FairfieldCity | 2006-09-07 09:53 | 210 | 0 |  | 2006-09-07 09:53 |  | -- | Capitola Drive approximately two hundred feet North of Calaveras Drive. | Fairfield | Solano | 94533 |  |  | 2006-09-04 |  |  |  | Water treatment plant discharging treated water from reservoir into sanitary sewer system at too high of a rate. Ammout of clean water released from reservoir surcharged sanitary sewer system which caused SSO at first manhole downstream from water treatment facility. Recovered approximately one hundred gallons and returned to sanitary sewer system. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | FairfieldCity | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | Public Works Manager | James C. Pritchard | 2006-09-07 | 707-428-7415 | jpritchard@ci.fairfield.ca.us, | MINOR
2618 | 6 | 1 | FairfieldCity | 2006-01-12 11:36 | 525 | 0 |  | 2006-01-12 11:36 |  | -- | North side Manuel Campos Parkway approximately 300 feet East of Paradise Valley Drive. | Fairfield | Solano | 94533 |  |  | 2006-01-10 |  |  |  | Approximately 350 gallons of overflow was captured in field and returned to system. The rest flowed into approximately four hundred feet of storm drain that was flushed and vacuumed. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | FairfieldCity | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Public Works Manager | James Pritchard | 2006-01-12 | 707-428-7415 | jpritchard@ci.fairfield.ca.us, | MINOR
2435 | 5 | 1 | FairfieldCity | 2006-01-03 08:37 | 2400 | 0 | 057601 | 2005-12-31 | James Pritchard | FairfieldCity | Fifth Street at Indiana Street and Third Street at Empire Street. | Fairfield | Solano | 94533 |  |  | 2005-12-31 | 12:30:00 P | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | Area storm drains that overflow discharged to were flooded. Amount of overflow compared to run off negligible. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | FairfieldCity | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | Sewer overflowed due to significant storm event. Lines unable to handle flow due to inflow and infiltration. | Public Works Manager | James Pritchard | 2006-01-03 | 707-428-7415 | jpritchard@ci.fairfield.ca.us, | MAJOR | James Pritchard | FairfieldCity | 707-428-7415 |  | 420 Gregory Street | Fairfield | Solano | 94533 |  | City of Fairfield
2099 | 4 | 3 | FairfieldCity | 2005-11-10 15:50 | 125000 | 125000 | 05-6203 | 2005-10-26 | James Pritchard | FairfieldCity | 200 feet East of the end of Strassberger Drive | Fairfield | Solano | 94533 |  |  | 2005-10-08 | 1:00:00 PM | [5 empty] | SUNNY WEATHER | Medium |  | SURFACE WATER IMPACT | No |  | No | Yes | Discharge into retention basin holding approximately 2.5 million gallons of water. No evidence of sewer or any effects to basin. Material on ground where sewer flowed to basin cleaned up immediately. |  | Yes | Yes | No | No | No | Yes | Yes | No | No | 2005-11-10 | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | FairfieldCity | PUMP STATION |  | INFRASTRUCTURE FAILURE | --Select None-- | PUMP STATION FAILURE |  | Pump station failed when pump caused circuit breaker to trip. The telemetry no signal alarm failed at same time and the condition was not discovered until a visual inspection was performed. Overflow discharged to retention basin and was fully contained. Discharge was calculated using previous SCADA data on the wet well. There was approximately 2.5 million gallons of water in the basin. Initial ammonia samples taken showed a range of .203 mg/l to .355 mg/l. We have resloved all of the pump station issues by having both pumps serviced, replaced the power panel and cleaned the wet well. We resolved the telemetry issues by adding an additional low water alarm, making sure the non-signal alarm is functional and having the operators include the pump station levels in their log books six times a day. We contacted Warden Jim Jones of Fish and Game to view the site and inform him of our clean up measures. He was pleased with our efforts in resolving the pump station issues and our clean up efforts which are to pump approximately five hundred thousand gallons from the retention basin back into the sanitary sewer. After this we will re-sample for ammonia in the retention basin and determine if more pumping is needed at that time. This process should be completed by November 10, 2005. Starting November 3,2005 and continuing through November 7, 2005 we pumped approximately five hundred thousand gallons out of the basin back into the sanitary sewer. On November 9, 2005 we had the basin tested again for ammonia. We took three samples at the same two locations as the first time and all samples came back 0 mg/l for ammonia. On November 10, 2005 we contacted Fish and Game to report our results and then removed the warning signs. | Sewer Maintenance Ma | James Prichard | 2005-10-26 | 707-428-7415 | jpritchard@ci.fairfield.ca.us, | MAJOR | James Pritchard | City of Fairfield | 707-428-7415 |  | 420 Gregory Street | Fairfield | Solano | 94533 |  | FairfieldCity
1896 | 3 | 1 | FairfieldCity | 2005-09-30 08:55 | 1200 | 1200 | 05-5676 | 2005-09-29 | Fairfield Police Dispatch | FairfieldCity | Intersection of Eisenhower Street and East Tennessee Street | Fairfield | Solano | 94533 |  |  | 2005-09-29 | 7:45:00 AM | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | No | SSO flowed into storm drain that was blocked with material and vegetation at mouth of drain. |  | Yes | Yes | No | No | No | Yes | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | FairfieldCity | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- |  | SSO reported to dispatch by passerby at 7:44 a.m. We recieved call from dispatch, responded and had SSO stopped by 8:00 a.m. SSO flowed into 1300 feet of 42" storm drain that had standing water due to blockage at outflow. Flushed and pumped out storm drain to sanitary sewer for clean up. | Public Works Manager | James Pritchard | 2005-09-30 | 707-428-7415 | jpritchard@ci.fairfield.ca.us, | MAJOR | James Pritchard | FairfieldCity | 707-428-7415 |  | 420 Gregory Street | Fairfield | Solano | 94533 |  | City of FAirfield | 707-428-7415 |  | 420 Gregory Street | Fairfield | Solano | 94533
1513 | 2 | 1 | FairfieldCity | 2005-06-10 15:46 | 800 | 0 |  | 2005-06-10 15:46 |  | -- | Fourth Street | Fairfield | Solano | 94533 |  |  | 2005-06-06 |  |  |  | Spill was contained in storm drain, approximately seven hundred gallons recovered. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | FairfieldCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Public Works Manager | James Pritchard | 2005-06-10 | 707-428-7415 | jpritchard@ci.fairfield.ca.us, | MINOR
606 | 1 | 1 | FairfieldCity | 2004-12-21 09:46 | 300 | 0 |  | 2004-12-21 09:46 |  | -- | Strassberger Drive | Fairfield | Solano | 94533 |  |  | 2004-12-17 |  |  |  | Pump station failed due to short in floats that caused power outage. Pacific Gas and Electric repaired transformer and City repaired pump station. Initially I didn't believe sewage reached water body, no sign of material, no fish kill, no human health effect. Took samples to be on the safe side. Removed contaminated soil on Monday December 20, 2004. Received information from lab that sample from surface water had sewage. Contacted Fish and Game and Regional board on December 21, 2004. Pumped area around storm drain outfall in surface water. Will re-sample after pumping. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | FairfieldCity | MANHOLE |  | ELECTRICAL POWER FAILURE | --Select None-- |  |  |  | Public Works Manager | James C. Pritchard | 2004-12-21 | 707-428-7415 | tborman@ci.fairfield.ca.us | MINOR
4012 | 9 | 1 | FairfieldSuisunSD | 2006-10-19 14:02 | 800 | 0 |  | 2006-10-19 14:02 |  | -- | Intersection of Silver Creek Road and Lopes Road | Fairfield | Solano | 94534 |  |  | 2006-10-18 |  |  |  | Spill occurred due to bypass pumping from our sewer repair contractor (Pacific Liners). The bypass pumping had been working successfully since 8 am (spill occurred at 18:40), however the overflow occurred when evening peak flows rose and no throttle adjustments were made on the bypass pumps. Overflow was contained in the storm drain system and pumped out. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | FairfieldSuisunSD | MANHOLE |  | BYPASS | --Select None-- |  |  |  | Engineer | Kevin Cullen | 2006-10-19 | 707-428-9129 | mbodeaux@fssd.com, rluthy@fssd.com | MINOR
3573 | 8 | 1 | FairfieldSuisunSD | 2006-06-28 11:37 | 750 | 0 |  | 2006-06-28 11:37 |  | -- | Cordelia Road, east of Link Road (adjacent to 4132 Cordelia Road) | Fairfield | Solano | 94534 |  |  | 2006-06-25 |  |  |  | Spill occurred approximately ½ mile east of Cordelia Pump Station. Primary cause was mechanical failure at pump station. Spill was 100% contained and recovered. Spillage was captured by vacuum truck. Area was washed down, vacuumed and contaminated top soil was removed. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | FairfieldSuisunSD | PUMP STATION |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Sr. Env. Engr. | Marcie Bodeaux | 2006-06-28 | 707.429.8930 | mbodeaux@fssd.com, rluthy@fssd.com | MINOR
3432 | 7 | 3 | FairfieldSuisunSD | 2006-05-30 16:37 | 12000 | 3000 | OES063042 | 2006-05-20 | Marcie Bodeaux | Marcie Bodeaux | Lopes Road 1/4 mile south of Gold Hill Road. | Fairfield | Solano | 94534 |  |  | 2006-05-20 | 12:30:00 P | [5 empty] | SUNNY WEATHER | Low |  | SURFACE WATER IMPACT | No |  | Yes | Yes | Observed several small dead fish (1-3 inches in length) in receiving water. |  | Yes | Yes | No | No | No | Yes | No | Yes | No | 2006-06-02 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | FairfieldSuisunSD | PUMP STATION |  | INFRASTRUCTURE FAILURE | --Select None-- | PUMP STATION FAILURE |  | Pump Station level control equipment failed to call on pump. Pump Station wetwell backed up into collection system and overflowed at low point. Pump station operator responded, and had pumps operating, within 30 minutes of being notified by City crew. Samples were taken and analyzed for ammonia (0.24 ppm) and dissolved oxygen (5.8 ppm). | Senior Environmental | Marcie Bodeaux | 2006-05-30 | 707.688.8343 | mbodeaux@fssd.com, rluthy@fssd.com | MAJOR | Marcie Bodeaux | FSSD | 707 429-8930 | 139 | 1010 Chadbourne Road | Fairfield | Solano | 94534 |  | FairfieldSuisunSD
2619 | 6 | 2 | FairfieldSuisunSD | 2006-01-12 11:36 | 500000 | 0 | 057583 | 2005-12-31 | Larry Bahr | FairfieldSuisunSD | Pitman and Cordelia Roads in Fairfield, Califonia. | Fairfield | Solano | 94534 |  |  | 2005-12-31 | 7:30:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | SURFACE WATER IMPACT | No |  | No | No | Due to high amounts of flood water in the area, there was no discernable effect on surrounding water. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | FairfieldSuisunSD | PUMP STATION |  | NATURAL DISASTER | --Select None-- | --Select None-- |  | On Saturday, December 31, 2005, central Solano County experienced an extended period of torrential rainfall resulting in massive flooding from all area creeks. The Cordelia Pump Station, located at the intersection of Pitman and Cordelia Roads in Fairfield, is in between and adjacent to Green Valley and Dan Wilson Creeks. Green Valley Creek overtopped the floodwall surrounding the pump station inundating the grounds, support facilities, and the pump station wetwell and drywell. This flooding resulted in an electrical failure that stopped all pumps at the pump station. This stoppage occurred at approximately 7:30 AM. Due to flooding of the surrounding area caused by flows from Green Valley Creek and Dan Wilson Creek, the pump station could not be accessed until around 12:30 PM. Maintenance crews entered the facility at that time and began immediately taking steps to bring the pump station back into full operation. By 1:30 PM, the pump station was restored to service and any loss of sewage from the collection system stopped soon thereafter. It is estimated that approximately 500,000 gallons of sewage was lost during the pump station outage. This estimate is based on the following analysis: • The normal dry weather flow for Saturdays from 7:30 AM to 1:30 PM averages about 2.0 mgd (million gallons per day). • Six hours of flow at 2.0 mgd = 500,000 gallons • The pump station flow prior to the electrical failure was 8.8 mgd. • Since there was extensive surface flooding in the Cordelia Pump Station Collection system and since the ground was completely saturated, it is a reasonable assumption that 6.8 mgd of 8.8 mgd was inflow and infiltration. The pump station failure was reported to the California State Officer of Emergency Services twice on December 31, 2005 by Aquarion Operating Services (OES Report Number: 057569) and Fairfield-Suisun Sewer District (OES Report Number: 057583). Attempts to leave a message on the Regional Board’s general number failed. The phone was neither answered in person nor electronically. A message was left on Bill Johnson's voice mail describing the nature and magnitude of the problem at approximately 1:40 PM on December 31. It is noteworthy that, once the station could be accessed after extensive flooding, it only required one hour for maintenance crews to restore it to operation. | Engineer | Kevin Cullen | 2006-01-11 | 707-429-8930 | mbodeaux@fssd.com, rluthy@fssd.com, lbahr@fssd.com, kcullen@fssd.com | MAJOR | Larry | FairfieldSuisunSD | Bahr | 137 | 1010 Chadbourne Road | Fairfield | Solano | 94534 |  | Fairfield-Suisun Sewer District | 707-429-8930 |  | 1010 Chadbourne Road | Fairfield | Solano | 94534
2368 | 5 | 3 | FairfieldSuisunSD | 2005-12-29 11:35 | 1800 | 270 | 05-7319 | 2005-12-21 | Marcie Bodeaux | Marcie Bodeaux | Dover Avenue at East Pacific Avenue | Fairfield | Solano | 94533 |  |  | 2005-12-20 | 9:48:00 AM | [5 empty] | CLOUDY WEATHER | Low |  | STORM DRAIN | No |  | No | No | Stromwater channel downstream of SSO was inspected and no sign of SSO was observed due to dilution. |  | Yes | Yes | No | No | No | Yes | Yes | Yes | No | 2006-01-31 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | FairfieldSuisunSD | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- |  | Samples of the stormwater channel downstream of the SSO were taken and compared to an upstream stormwater channel. Results in the channel downstream of the SSO were 6 ppm dissolved oxygen and 0 ppm ammonia. Results for the upstream stormwater channel were the same at 6 ppm dissolved oxygen and 0 ppm ammonia. Report Version 2: SSO was reported to District at approximately 10:45 on 12/20/05. The District experienced problems with e-reporting system which resluted in missing the 24-hour reporting deadline by approximately 2.5 hours. This is a resubmittal of the original report for the 12/20/05 SSO. Report Version 3: Due to original problem with e-reporting, the Regional Board may have entered report information into the database from a copy of FSSD’s report provided via e-mail attachment. It was later noticed that some of the information entered into the database did not match the original report sent via e-mail attachment. Corrections are made in this revised report, 12/29/05; 11:37 A.M. | Sr.Env. Engineer | Marcie Bodeaux | 2005-12-29 | 7074298930 | mbodeaux@fssd.com; marciexyz@comcast.net | MAJOR | Marcie Bodeaux | FairfieldSuisunSD | 7074298930 | 139 | 1010 Chadbourne Road | Fairfield | Solano | 94534 |  | Fairfield-Suisun Sewer District | 707-429-8930 |  | 1010 Chadbourne Road | Fairfield | Solano | 94534
2124 | 4 | 1 | FairfieldSuisunSD | 2005-11-16 14:43 | 6500 | 2000 | 05-6590 | 2005-11-14 | Kevin Cullen | Kevin Cullen | 1320 Travis Blvd. | Fairfield | Solano | 94533 |  |  | 2005-11-12 | 10:07:00 P | [5 empty] | CLOUDY WEATHER | Low | Alonzo Drain/Alonzo/Region 2 | SURFACE WATER IMPACT | No |  | No | No | Visual inpsection occurred Monday, 11/12/2005 at 10 am. Stormwater drop inlets inspected and were clean. Downstream outfall was sampled for Ammonia. Results from the downstream samping events indicated no Ammonia present. |  | Yes | Yes | No | No | No | Yes | Yes | Yes | No | 2006-11-16 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | FairfieldSuisunSD | PIPE |  | BLOCKAGE | GREASE | --Select None-- |  | On Monday 11/14/2005 at 8:15 am the Fairfield-Suisun Sewer District received a call from the City of Fairfield regarding a sanitary sewer overflow which occurred in front of 1320 Travis Boulevard. The spill was reported to the City of Fairfield on Saturday, 11/12/05 at 10:07 pm, the spill was then stopped at 11:19 pm. It was estimated that 6,500 gallons of sewage was spilled and that 2,000 gallons of sewage was recovered. The primary cause of the sanitary sewer overflow was grease, which we believe is coming from the restaurants at the Gateway Plaza Mall. All spilled sewaage, which was recoverable was immediatedly vacuumed from the strom drain drop inlets which were impacted by the spill. The affected areas were then hosed down and the cleanup water was vacuumed up. There was no disinfection procedure performed on the affected areas. The 12-inch line of discussion is included in this year’s sewer cleaning and television inspection contract. This line is now on an annual return period for cleaning and inspection. This line is currently being thoroughly cleaned and inspected by the District's contractor. The District will be working with the City of Fairfield and Solano County's Environmnetal Health Division in a restaurant outreach and Best Management Practice implementation effort to prevent this from happenning again. | Environmental Engine | Kevin Cullen | 2005-11-16 | 707-429-8930 | mbodeaux@fssd.com, kcullen@fssd.com, rluthy@fssd.com | MAJOR | Kevin Cullen | Fairfield-Suisun Sewer District | 707-429-8930 | 129 | 1010 Chadbourne Road | Fairfield | Solano | 94534 |  | Fairfield-Suisun Sewer District | 707-429-8930 | 129 | 1010 Chadbourne Road | Fairfield | Solano | 94534
2026 | 2 | 1 | FairfieldSuisunSD | 2005-10-24 14:27 | 200 | 0 |  | 2005-10-24 14:27 |  | -- | 3200 North Texas Street | Fairfield | Solano | 94533 |  |  | 2005-10-20 |  |  |  | Spill was caused by improper use of sewer plug used to control flow for cleaning and TV inspection. The plug was inadequately monitored and caused the pipe to surcharge and overflow into an adjacent building. Spill was 100% contained and recovered. Incident occurred at 10:00 a.m. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | FairfieldSuisunSD | PIPE |  | BLOCKAGE | --Select None-- |  |  |  | Sr. Engineer | Marcie Bodeaux, P. E. | 2005-10-24 | 707.429.8930 | mbodeaux@fssd.com, rluthy@fssd.com | MINOR
2028 | 3 | 1 | FairfieldSuisunSD | 2005-10-24 14:42 | 200 | 0 |  | 2005-10-24 14:42 |  | -- | Intersection of North Texas Street and Marigold Drive | Fairfield | Solano | 94533 |  |  | 2005-10-20 |  |  |  | Spill caused by sewer cleaning contractor hired by FSSD. Spill resulted from improper use of sewer plug to control flow in pipe for sewer cleaning and TV inspection. Plug was inadequately monitored and caused surcharge in line and overflow from upstream manhole. This was the second SSO in same morning caused by same contractor. Spill occurred at 11:30 a.m. Situation was caught immediately and spill was 100% captured and recovered. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | FairfieldSuisunSD | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Sr. Engineer | Marcie Bodeaux, P. E. | 2005-10-24 | 707.429.8930 | mbodeaux@fssd.com, rluthy@fssd.com | MINOR
1330 | 1 | 2 | FairfieldSuisunSD | 2005-04-25 16:04 | 500 | 0 |  | 2005-04-25 16:04 |  | -- | Adjacent to 1450 Travis Boulevard | Fairfield | Solano | 94533 |  |  | 2005-04-17 |  |  |  | Spill was 100% captured and site was completely restored. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | FairFieldSuisunSD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Senior Engineer | Marcie Bodeaux, P. E. | 2005-04-25 | 707.429.8930 | mbodeaux@fssd.com, rluthy@fssd.com | MINOR
3957 | 4 | 1 | GGNRA | 2006-10-02 17:16 | 500 | 0 |  | 2006-10-02 17:16 |  | -- | Alcatraz Island - Boat Dock | San Francisco | San Francisco | 94123 |  |  | 2006-09-25 |  |  |  | The amount spilled is unknown. This spill was caused by a sewer valve being left open by an unknown party. Sewage hose was found in open position on the dock upon arrival of the first Alcatraz Cruises ferry to the island Monday morning. The spill reached the SF Bay. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | GGNRA | OTHER | Open valve at pumpout on dock | CAUSE UNKNOWN | --Select None-- |  |  |  | Env. Prot. Spec. | Laura Castellini | 2006-10-02 | 415-561-4436 | Laura_Castellini@nps.gov; Patricia_S_Reischl@nps.gov, Don_Mannel@nps.gov, Dan_Collman@nps.gov | MINOR
3955 | 3 | 1 | GGNRA | 2006-10-02 15:23 | 100 | 0 |  | 2006-10-02 15:23 |  | -- | Alcatraz Island - China Alley | San Francisco | San Francisco | 94123 |  |  | 2006-09-19 |  |  |  | This spill was caused by a crack in the pipe in China Alley. The spill was first reported by Jim Adams of Blue and Gold Fleet. Paul Robinson from NPS Pacific West Region followed up on the spill and made additional observations in a memo dated September 21, 2006. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | GGNRA | PIPE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Env. Prot. Spec. | Laura Castellini | 2006-10-02 | 415-561-4436 | Laura_Castellini@nps.gov; Patricia_S_Reischl@nps.gov, Don_Mannel@nps.gov, Dan_Collman@nps.gov | MINOR
3239 | 2 | 1 | GGNRA | 2006-04-26 11:28 | 50 | 0 |  | 2006-04-26 11:28 |  | -- | Building 1048 Fort Cronkhite | Sausalito | Marin | 95965 |  |  | 2006-04-12 |  |  |  | Pump failures | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | GGNRA | MANHOLE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Env. Prot. Spec. | Laura Castellini | 2006-04-26 | 415-561-4436 | Laura_Castellini@nps.gov; Patricia_S_Reischl@nps.gov, Don_Mannel@nps.gov | MINOR
1743 | 1 | 1 | GGNRA | 2005-08-30 15:41 | 157 | 0 |  | 2005-08-30 15:41 |  | -- | Fort Cronkhite, Mitchell Road | Sausalito | Marin | 94965 |  |  | 2005-08-28 |  |  |  | Blockage in sewer line between Lift Stations #1 and #2. Spill stopped when pumper truck began pumping out Lift Station #1 and taking the effluent to Lift Station #5. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | GGNRA | PUMP STATION |  | BLOCKAGE | DEBRIS |  |  |  | ES | Laura Castellini | 2005-08-30 | 415-561-4436 | Laura_Castellini@nps.gov; Patricia_S_Reischl@nps.gov, Don_Mannel@nps.gov | MINOR
3410 | 3 | 1 | Granada | 2006-05-25 13:55 | 200 | 0 |  | 2006-05-25 13:55 |  | -- | Corner of Columbus and Isabella | El Granada | San Mateo | 94018 |  |  | 2006-05-16 |  |  |  | Roots caught in manhole from upstream location unknown. Recovered 20 gallons. Washed down street and vacuumed water from storm drain. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Granada | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Technical Srvs Spvsr | Tony Pullin | 2006-05-25 | 650-726-0124 | tony@samcleanswater.org, jack@samcleanswater.org | MINOR
2687 | 2 | 1 | Granada | 2006-01-26 15:41 | 290 | 0 |  | 2006-01-26 15:41 |  | -- | Corner of Avenue Portola and Alhambra | El Granada | San Mateo | 94018 |  |  | 2006-01-22 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Granada | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Technical Services S | Tony Pullin | 2006-01-26 | 650-726-0124 | mfraser@ci.half-moon-bay.ca.us; b.ptacek@bankofamerica.com; pnagengast@ci.half-moon-bay.ca.us; shartsell@co.sanmateo.ca.us; msd@coastside.net; cduffy@dudek.com; bobptacek@earthlink.net; jeanine@hmbreview.com; ldw@ldworen.net; msd@montara.com; scott@montara.com; scott.kathey@noaa.gov; Jack@samcleanswater.org; tony@samcleanswater.org; ricster@sbcglobal.net | MINOR
5064 | 3 | 1 | HalfMoonBay | 2007-04-16 | 2000 | 100 | 07-2332 | 2007-04-16 | John J. Szabo | John J. Szabo | 100 Correas Ave | Half Moon Bay | San Mateo | 94019 |  |  | 2007-04-15 | 0.83333 | [6 empty] | Low |  | STORM DRAIN | No |  | No | No | spill soaked into ground |  | Yes | Yes | No |  |  | No | No |  |  | 2007-04-17 | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | GREASE | -- Select One -- |  |  | Collection Worker | John J Szabo | 2007-04-16 | 650 726-0124
4637 | 2 | 1 | HalfMoonBay | 2007-01-29 16:25 | 300 | 0 |  | 2007-01-29 16:25 |  | -- | Adjacent to Half Moon Bay Golf Links Maintenance Yard. | Half Moon Bay | San Mateo | 94019 |  |  | 2007-01-19 |  |  |  | Force Main developed a small leak at air release valve location. Pipe was excavated and repaired. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | INFRASTRUCTURE FAILURE | -- Select One -- |  | Force Main |  | Technical Svs Spvsr | Tony Pullin | 2007-01-29 | 650-726-0124
2142 | 1 | 2 | HalfMoonBay | 2005-11-18 13:36 | 750 | 0 |  | 2005-11-18 13:36 |  | -- | Fairway & Miramontes | Half Moon Bay | San Mateo | 94019 |  |  | 2005-09-28 | [9 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | HalfMoonBay | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Technical Svs Spvsr | Tony Pullin | 2005-09-30 | 650-726-9053 | pnagengast@ci.half-moon-bay.ca.us , b.ptacek@bankofamerica.com, bobptacek@earthlink.net, cduffy@dudek.com, msd@coastside.net,jack@samcleanswater.org,ldw@ldworen.net,mjferreira@aol.com,pnagengast@ci.half-moon-bay.ca.us,scott@montara.com,scott.kathey@noaa.gov,shartsell@co.sanmateo.ca.us,tony@samcleanswater.org,jeanine@hmbreview.com,ricster@sbcglobal.net | MINOR
4931 | 10 | 1 | Hayward | 2007-03-15 | 1500 | 500 | 07-1663 | 2007-03-15 | mike higares |  | 3466 Arden Rd | hayward | alameda | 94544 |  |  | 2007-03-14 | 0.40625 | [9 empty] | No |  | No | No |  |  | No | No | No |  |  | No | No | [15 empty] | Deputy Director/Utilities | michael higares | 2007-03-15 | 510-881-7901
4864 | 9 | 1 | Hayward | 2007-03-05 11:24 | 900 | 0 |  | 2007-03-05 11:24 |  | -- | 26942 Clairborne , In backyard, City has an easment running along rear of property. | Hayward | Alameda | 94513 |  |  | 2007-03-03 |  |  |  | This line was recently treated for roots less than 3 months ago. The roots may have died and become hard which resulted in a blockage. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SR Utillity Leader | Stacy A Swithenbank | 2007-03-05 | 510-881-7970
4813 | 8 | 1 | Hayward | 2007-02-26 09:50 | 300 | 0 |  | 2007-02-26 09:50 |  | -- | 1829 Highland , manhole in backyard along easment. | Hayward | Alameda | 94544 |  |  | 2007-02-23 |  |  |  | Sewage was seeping from manhole located in the backyard of the address 1829 Highland. Broke stoppage andplan on following up with CCTV and make determination to resolve this problem. Sewage was absorbed into soil was very small amount. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sr Utillity Leader | Al Swithenbank | 2007-02-26 | 510-881-7970
4566 | 7 | 1 | Hayward | 2007-01-22 08:54 | 300 | 0 |  | 2007-01-22 08:54 |  | -- | 1409 Rosevelt Street near the inter section of Gading Rd. and Rosevelt St. | Hayward | Alameda | 94544 |  |  | 2007-01-20 |  |  |  | We will CCTV this area to further determine the cause. Once we have determined the cause will will take the steps necessary to prevent this from occuring again. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sr Utillity Leader | Stacy Swithenbank | 2007-01-22 | 510-881-7970
4354 | 6 | 1 | Hayward | 2006-12-18 07:39 | 889 | 0 |  | 2006-12-18 07:39 |  | -- | 24955 Cypress Ave | Hayward | Alameda | 95444 |  |  | 2006-12-16 |  |  |  | Grease and Rags caused the stoppage.OES CONTROL NUMBER #067430, John Raven Alameda County Public Works inspector was satified with the clean up of the area and dissmised Haywards crews. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Sr. Utillity Leader | Al Swithenbank | 2006-12-18 | 510-881-7970
3385 | 5 | 1 | Hayward | 2006-05-23 10:29 | 800 | 0 |  | 2006-05-23 10:29 |  | -- | 2714 Tribune Aveanue. Hayward Ca. 94545 | Hayward | USA | 94545 |  |  | 2006-05-23 |  |  |  | Low density area, sewage seeping from manhole, wet weather, large amount of roots retrieved from main sewer line. Affected area is scheduled to be televised tomorrow 5/24/06. Responded to call at aproximately 9.00am removed blockage and cleaned up area by 10.30am. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hayward | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sr Utility Leader | Swithenbank | 2006-05-23 | 510-881-7970 | michael.higares@ci.hayward.ca.us, dennis.butler@ci.hayward.ca.us | MINOR
3140 | 4 | 1 | Hayward | 2006-04-10 09:59 | 3000 | 2900 | 06-2144 | 2006-04-10 | Hayward | Hayward | 29001 Hopkins, Hayward 94545 Ca, | Hayward | Alameda | 94544 |  |  | 2006-04-09 | 8:30:00 AM | [5 empty] | RAINY WEATHER | Low |  | CAPTURED IN STORM DRAIN | No |  | No | No | n/a |  | Yes | Yes | Yes | No | No | No | No | No | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Hayward | CLEAN OUT | Faulty UPS... "uninterupted power source | ELECTRICAL POWER FAILURE | --Select None-- | --Select None-- | Faulty UPS... "uninterupted power source" | All sewage Contained, Restoraration services was called out to clean and sanitize the affected bussiness. Spill was captured, contained and vacumed up with our vacume truck. | Sr. Utility Leader | Al Swithenbank | 2006-04-10 | 510-881-7970 | michael.higares@ci.hayward.ca.us, dennis.butler@ci.hayward.ca.us | MAJOR | Stacy Swithenbank | Hayward | 510-881-7970 |  | 24499 Soto Rd | Hayward | alameda | 94544 | City of Hayward | City of Hayward | 510-881-7970 |  | aswithenbank@hayward-ca.gov | hayward | alameda | 94545
1212 | 3 | 2 | Hayward | 2005-03-23 11:18 | 1400 | 1200 | 05-1816 | 2005-03-23 | H.P.D. | Hayward | 27386 Whitman Ave | Hayward | Alameda | 94544 |  |  | 2005-03-22 | 5:30:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | CAPTURED IN STORM DRAIN | No |  | No | No | none |  | Yes | Yes | No | No | No | No | No | No | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | Hayward | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- | Minimal Roots Detected | Overflowing seweage at 27386 Whitman Ave. Broke stoppage. Vacumed up about 1200 gallons of liquid. Heavy rain at the time . Three person crew ,area clean up. 2.5 hours. Sewage spill was contained and disposed of. Notified O.E.S since over 1000 Gallons. | Sr Utillity Leader | Al Swithenbank | 2005-03-23 | 510-881-7970 | michael.higares@ci.hayward.ca.us, dennis.butler@ci.hayward.ca.us | MAJOR | Al Swithenbank | Hayward | 510-881-7970 |  | 24499 Soto Rd. | Hayward | Alameda | 94544 |  | City of Hayward | 510-881-7970 |  |  | Hayward | Alameda | 94544
854 | 2 | 1 | Hayward | 2005-01-14 08:50 | 50 | 0 |  | 2005-01-14 08:50 |  | -- | A Street and Grand Ave. | Hayward | Alameda | 94544 |  |  | 2005-01-13 |  |  |  | Was noticed from a small amount of sepage coming out of access hole of a "sealed down" clean out cover. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hayward | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Utillity leader | al swithenbank | 2005-01-14 | 510-881-7970 | michael.higares@ci.hayward.ca.us | MINOR
395 | 1 | 2 | Hayward | 2004-12-01 15:21 | 500 | 0 |  | 2004-12-01 15:21 |  | -- | 1562 D Street | Hayward | Alameda | 94544 |  |  | 2004-11-24 |  |  |  | Cleaned up affected area removed affected soil and decorative rocks. Replaced with all new materials. Homeowner very satisfied with our service. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | hayward | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | SrUtillity Leader | Stacy A Swithenbank | 2004-12-01 | 510-881-7970 |  | MINOR
5070 | 34 | 1 | Hillsborough | 2007-04-16 | 20000 | 0 | N/A | 2007-04-16 | public | Hillsborough | 840 Hillsborough blvd | hillsborough | san mateo | 94010 |  |  | 2007-04-14 | 0.33333 | [6 empty] | Medium |  | STORM DRAIN | No |  | No | No | N/A |  | Yes | Yes | Yes |  |  | No | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | ROOTS | -- Select One -- |  | sewer line overflow due to root infiltertion sectional rodding machine had problems which delayed taking care of problem | leadman | thomas barry | 2007-04-18 | 650/375/7507
4997 | 33 | 1 | Hillsborough | 2007-03-26 08:52 | 150 | 0 |  | 2007-03-26 08:52 |  | -- | 20 Glengarry Way | Hillsborough | San Mateo | 94010 |  |  | 2007-03-25 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Tony Geraldi | 2007-03-26 | 650 375-7507
4910 | 32 | 1 | Hillsborough | 2007-03-14 14:05 | 300 | 0 |  | 2007-03-14 14:05 |  | -- | 736 Jacaranda Circle | Hillsborough | san Mateo | 94010 |  |  | 2007-03-14 |  |  |  | Paper wipes, cleaning swipes | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Supervisor | Tony Geraldi | 2007-03-14 | 650 375-7507
4836 | 31 | 1 | Hillsborough | 2007-02-28 10:42 | 475 | 0 |  | 2007-02-28 10:42 |  | -- | Across from 2600 Ralston | Hillsborough | San Mateo | 94010 |  |  | 2007-02-26 |  |  |  | Heavy rains and grease caused the problem. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Supervisor | Tony Geraldi | 2007-02-28 | 650 375-7507
4834 | 30 | 1 | Hillsborough | 2007-02-28 10:35 | 90 | 0 |  | 2007-02-28 10:35 |  | -- | 942 Baileyana Rd. | Hillsborough | San Mateo | 94010 |  |  | 2007-02-26 |  |  |  | Pulled a bunch of cleaning swipes out of line and small amount of roots. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Supervisor | Tony Geraldi | 2007-02-28 | 650 375-7507
4832 | 29 | 1 | Hillsborough | 2007-02-28 | 6000 | 0 | 07-1296 | 2007-02-28 | Hillsborough | Hillsborough | 1600 Floribunda Ave. | Hillsborough | San Mateo | 94010 |  |  | 2007-02-26 | 0.11458 |  |  | Heavy rains |  |  |  | Low |  | STORM DRAIN | No |  | No | No | Yes |  | Yes | Yes | Yes |  |  | Yes | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE | Heavy rains | INFLOW & INFILTRATION | -- Select One -- | -- Select One -- |  | To much water! | Supervisor | Tony Geraldi | 2007-02-28 | 650 375-7507
4619 | 28 | 1 | Hillsborough | 2007-01-25 08:19 | 150 | 0 |  | 2007-01-25 08:19 |  | -- | 940 Jackling Dr. | Town of Hillsborough | San Mateo | 94010 |  |  | 2007-01-24 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | PIPE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Tony Geraldi | 2007-01-25 | 650 375-7507
4153 | 27 | 1 | Hillsborough | 2006-11-27 15:49 | 150 | 0 |  | 2006-11-27 15:49 |  | -- | 25 Mosswood | Hillsborough | San Mateo | 94403 |  |  | 2006-11-27 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Tony Geraldi | 2006-11-27 | 650 375-7507
3974 | 26 | 1 | Hillsborough | 2006-10-11 12:08 | 210 | 0 |  | 2006-10-11 12:08 |  | -- | 2165 Edge Court | Hillsborough | San Mateo | 94010 |  |  | 2006-10-10 |  |  |  | Little bit of grease, but those new cleaning swifters were the main cause,people flushing them down the toilet. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hillsborough | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | tony Geraldi | 2006-10-11 | 650 375-7507 | tgeraldi@hillsca.org, | MINOR
3950 | 25 | 1 | Hillsborough | 2006-10-02 08:44 | 250 | 0 |  | 2006-10-02 08:44 |  | -- | 1208 Kenilworth | Hillsborough | San Mateo | 94010 |  |  | 2006-10-01 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hillsborough | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Anthony Geraldi | 2006-10-02 | 650 375-7507 | tgeraldi@hillsca.org, | MINOR
3633 | 24 | 1 | Hillsborough | 2006-07-20 10:01 | 125 | 0 |  | 2006-07-20 10:01 |  | -- | 1208 Kenilworth | Hillsborough | San Mateo | 94401 |  |  | 2006-07-17 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | hillsborough | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Supervisor | Tony Geraldi | 2006-07-20 | 650 375-7507 | tgeraldi@hillsca.org, | MINOR
3611 | 23 | 1 | Hillsborough | 2006-07-07 14:03 | 175 | 0 |  | 2006-07-07 14:03 |  | -- | 1110 Hayne Rd. | Hillsborough | San Mateo | 94010 |  |  | 2006-07-07 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hillsborough | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Tony Geraldi | 2006-07-07 | 650 375-7507 | tgeraldi@hillsca.org, | MINOR
3609 | 22 | 1 | Hillsborough | 2006-07-07 13:58 | 210 | 0 |  | 2006-07-07 13:58 |  | -- | Easement behind 35 Citrus Crt. | Hillsborough | San Mateo | 94010 |  |  | 2006-07-06 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hillsborough | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Supervisor | Tony Geraldi | 2006-07-07 | 650 375-7507 | tgeraldi@hillsca.org, | MINOR
3577 | 21 | 2 | Hillsborough | 2006-06-28 16:43 | 250 | 0 |  | 2006-06-28 16:43 |  | -- | 17 Stonepine Ct. | Hillsborough | San Mateo | 94010 |  |  | 2006-06-26 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hillsborough | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Tony geraldi | 2006-06-28 | 650 375-7507 | tgeraldi@hillsca.org, | MINOR
3259 | 20 | 1 | Hillsborough | 2006-05-01 16:04 | 275 | 0 |  | 2006-05-01 16:04 |  | -- | 1130 Tartan Trail (easement) | Hillsborough | San Mateo | 94010 |  |  | 2006-05-01 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hillsborough | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | tony Geraldi | 2006-05-01 | 650 375-7507 | tgeraldi@hillsca.org, | MINOR
3022 | 19 | 1 | Hillsborough | 2006-03-17 10:28 | 200 | 0 |  | 2006-03-17 10:28 |  | -- | 55 Berryessa Way | Hillsborough | San Mateo | 94010 |  |  | 2006-03-16 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hillsborough | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Tony Geraldi | 2006-03-17 | 650 375-7507 | tgeraldi@hillsca.org, | MINOR
2680 | 18 | 1 | Hillsborough | 2006-01-25 12:32 | 225 | 0 |  | 2006-01-25 12:32 |  | -- | Easement of 2289 Forestview. | Hillsborough | San Mateo | 94010 |  |  | 2006-01-24 |  |  |  | Diverted overflowing M/H to the next M/H in the easement. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hillsborough | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Supervisor | Tony Geraldi | 2006-01-25 | 650 375-7507 | tgeraldi@hillsca.org, | MINOR
2666 | 17 | 1 | Hillsborough | 2006-01-23 09:00 | 10 | 0 |  | 2006-01-23 09:00 |  | -- | 1015 Macadamia | Hillsborough | San Mateo | 94010 |  |  | 2006-01-20 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hillsborough | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Tony Geraldi | 2006-01-23 | 650 375-7507 | tgeraldi@hillsca.org, | MINOR
2330 | 16 | 1 | Hillsborough | 2005-12-23 21:24 | 3000 | 0 | 05-7416 | 2005-12-23 | Tony Geraldi |  | 5 Mountainwood Ln. | Hillsborough | San Mateo | 94010 |  |  | 2005-12-23 | 2:30:00 PM | 2005-12-23 | 6:05:00 PM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Public Works Supervi | Tony Geraldi | 2005-12-23 | 650 372-0873 | tgeraldi@hillsca.org, | 24HR |  |  | 650 372-0873 | [6 empty] | Hillsborough
2595 | 15 | 2 | Hillsborough | 2006-01-10 12:10 | 30000 | 0 | 057-390 | 2005-12-22 | Tony Geraldi | Hillsborough | 766 El Cerrito Rd | Hillsborough | San Mateo | 94010 |  |  | 2005-12-22 | 3:00:00 PM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | Creek was running like a river at the time of the storm. Mother nature cleaned it better then we ever could. We cleaned up mess in gutter. |  | No | Yes | Yes | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Hillsborough | MANHOLE |  | FLOW CAPACITY DEFICIENCY | --Select None-- | --Select None-- |  |  | Public Works Supervi | Tony Geraldi | 2005-12-22 | 650-375-7507 | tgeraldi@hillsca.org, | MAJOR | Tony Geraldi | Hillsborough | 650 375-7507 |  | 1600 Floribunda Ave | Hillsborough | San Mateo | 94010 |  | Hillsborough | 650 375-7507
2122 | 13 | 1 | Hillsborough | 2005-11-16 09:47 | 200 | 0 |  | 2005-11-16 09:47 |  | -- | 101 Bay Wood | Hillsborough | San Mateo | 94010 |  |  | 2005-11-16 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hillsborough | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Tony Geraldi | 2005-11-16 | 650 375-7507 | tgeraldi@hillsca.org, | MINOR
1677 | 12 | 1 | Hillsborough | 2005-08-05 11:58 | 110 | 0 |  | 2005-08-05 11:58 |  | -- | 18 Farm Lane | Hillsborough | San Mateo | 94010 |  |  | 2005-08-05 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hillsborough | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Tony Geraldi | 2005-08-05 | 650 375-7507 | tgeraldi@hillsca.org, | MINOR
1671 | 11 | 1 | Hillsborough | 2005-08-02 15:21 | 320 | 0 |  | 2005-08-02 15:21 |  | -- | 2335 Oakdale Road | Hillsborough | jSan Mateo | 94010 |  |  | 2005-08-02 | [9 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hillsborough | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Tony Geraldi | 2005-08-02 | 650 375-7444 | tgeraldi@hillsca.org, | MINOR
1523 | 10 | 1 | Hillsborough | 2005-06-14 11:56 | 350 | 0 |  | 2005-06-14 11:56 |  | -- | 726 Jacaranda rd. | Hillsborough | San Mateo | 94010 |  |  | 2005-06-14 |  |  |  | Silk fence from old construction held it all on to the land of the backyard, which we cleaned up. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hillsborough | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Tony Geraldi | 2005-06-14 | 650 375-7507 | tgeraldi@hillsca.org, | MINOR
1503 | 9 | 1 | Hillsborough | 2005-06-09 13:46 | 240 | 0 |  | 2005-06-09 13:46 |  | -- | 1305 Tartan trail | Hillsborough | San Mateo | 94010 |  |  | 2005-06-08 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hillsborough | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Tony Geraldi | 2005-06-09 | 650-375-7507 | tgeraldi@hillsca.org, | MINOR
1235 | 8 | 1 | Hillsborough | 2005-03-31 08:53 | 50400 | 0 | 051976 | 2005-03-31 | Craig West | Hillsborough | 20 Cinnamon Court | Hillsborough | San Mateo | 94010 |  |  | 2005-03-30 | 6:30:00 PM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | YARD/LAND | No |  | No | No | Cleaned up by Sewer Department personell |  | Yes | Yes | Yes | No | No | No | No | No | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | Hillsborough | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- | Roots and Grease Combination |  | Inspector PW | Craig Westt | 2005-03-31 | 650-375-7515 | cwest@hillsca.org, | MAJOR | Craig West | Hillsborough | 650 375-7515 |  | 1320 La Honda Rd. | HIllsborough Ca. | San Mateo | 94010 | Craig West | Hillsborough | 650-375-7515 |  | 1320 La Honda Road | Hillsborough | San Mateo | 94010
2596 | 7 | 2 | Hillsborough | 2006-01-10 12:30 | 50400 | 0 | 051976 | 2005-03-31 | Craig West | Hillsborough | 20 Cinnamon Court | Hillsborough | San Mateo | 94010 |  |  | 2005-03-23 | 6:30:00 PM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | YARD/LAND | No |  | No | No | Cleaned up by sewer Dept. personell. |  | Yes | Yes | Yes | No | No | No | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Hillsborough | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- | Roots and grease combonation. |  | Public Work Director | Craig West | 2005-03-31 | 650-375-7515 | cwest@hillsca.org, | MAJOR | Tony Geraldi | Hillsborough | 650-375-7515 |  | 1600 Floribunda Ave | Hillsborough | San Mateo | 94010 |  | Hillsborough
1120 | 6 | 1 | Hillsborough | 2005-03-07 14:29 | 750 | 0 |  | 2005-03-07 14:29 |  | -- | 720 Chateau | Hillsborough | San Mateo | 94010 |  |  | 2005-03-07 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hillsborough | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Tony Geraldi | 2005-03-07 | 650 375-7507 | tgeraldi@hills.org | MINOR
1024 | 5 | 1 | Hillsborough | 2005-02-15 13:04 | 198000 | 0 | 05-1024 | 2005-02-15 | Craig West |  | Crystal Springs Road at intersection of Merner Rd. | Hillsborough | San Mateo | 94010 |  |  | 2005-02-15 | 9:00:00 AM | 2005-02-15 | 9:00:00 PM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Public Work Director | Craig West | 2005-02-15 | 650-375-7515 | cwest@hillsca.org, | 24HR |  |  | (650)375-7515 | [6 empty] | Hillsborough
2247 | 14 | 1 | Hillsborough | 2005-12-13 14:58 | 198000 | 0 | 05-1024 | 2005-02-15 | Craig West | Hillsborough | Crystal Springs Road at intersection of Merner Rd. | Hillsborough | San Mateo | 94010 |  |  | 2005-02-15 | 9:00:00 AM | [5 empty] | RAINY WEATHER | High |  | STORM DRAIN | No |  | No | No | Creek running like a river during storm, when storm eased up and sewer flow returned to normal capacity, creek was clean as a whistle. |  | No | No | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Hillsborough | MANHOLE |  | FLOW CAPACITY DEFICIENCY | --Select None-- | --Select None-- |  |  | Public Works Inspect | Craig West | 2005-12-13 | 650-375-7515 | cwest@hillsca.org, | MAJOR | Tony Geraldi | Hillsborough | 650 375-7507 |  | 1320 La Honda Rd. | HIllsborough Ca. | San Mateo | 94010 |  | Hillsborough
986 | 4 | 1 | Hillsborough | 2005-02-09 09:02 | 200 | 0 |  | 2005-02-09 09:02 |  | -- | 145 Stonepine Road | Hillsborough | San Mateo | 94010 |  |  | 2005-02-08 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hillsborough | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Tony Geraldi | 2005-02-09 | 650 375-7507 | tgeraldi@hillsca.org | MINOR
818 | 3 | 1 | Hillsborough | 2005-01-11 14:00 | 300 | 0 |  | 2005-01-11 14:00 |  | -- | 75 Rowen Tree Court | Hillsborough | San Mateo | 94010 |  |  | 2005-01-10 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hillsborough | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Tony geraldi | 2005-01-11 | 650 375-7507 | tgeraldi@hillssca.org | MINOR
779 | 2 | 1 | Hillsborough | 2005-01-06 15:50 | 40 | 0 |  | 2005-01-06 15:50 |  | -- | 750 Endfield | Hillsborough | San Mateo | 94010 |  |  | 2005-01-05 |  |  |  | Sewer barely trickling out of manhole,went on neighbors property, we cleaned it up. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hillsborough | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Tony Geraldi | 2005-01-06 | 650 375-7507 | mdebry@hillsca.org | MINOR
516 | 1 | 2 | Hillsborough | 2004-12-13 14:34 | 30 | 0 |  | 2004-12-13 14:34 |  | -- | 951 Baileyanna Rd. | Hillsborough | San Mateo | 94010 |  |  | 2004-12-09 |  |  |  | City clean out backed up in homeowner's driveway rodded main and cleared backup. Never made it too storm drain. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Hillsborough | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Tony Geraldi | 2004-12-13 | 650 3757507 |  | MINOR
4713 | 18 | 1 | LasGallinas | 2007-02-09 07:53 | 900 | 0 |  | 2007-02-09 07:53 |  | -- | 2 Mount Muir Ct | San Rafael | Marin | 94903 |  |  | 2007-02-09 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | BLOCKAGE | DEBRIS |  | Lateral |  | Line Crew Supervisor | Janice Mandler | 2007-02-09 | 415-472-1734
4511 | 17 | 1 | LasGallinas | 2007-01-15 15:01 | 118 | 0 |  | 2007-01-15 15:01 |  | -- | Las Gamos / Lucas Valley | San Rafael | marin | 94903 |  |  | 2007-01-12 |  |  |  | Excessive paper towels were removed from line. Line has been flushed on 12-29-2006 | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Line Crew Supervisor | Janice Mandler | 2007-01-15 | 415-472-1734
4666 | 16 | 3 | LasGallinas | 2007-01-02 | 1860 | 1500 | 07-0011 | 2007-01-02 | Janice Mandler | LasGallinas | 717 Deer Valley Rd. | San Rafael | Marin | 94903 |  |  | 2007-01-02 | 0.14583 | [6 empty] | Medium |  | CAPTURED IN STORM DRAIN | No |  | No | Yes | Overflow went into empty storm storage cement pond. Water leaving pond (360 gals) went into farmer's field. Farmer was advised |  | Yes | Yes | Yes |  |  | No | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | DEBRIS | -- Select One -- |  |  | Line Crew Supervisor | Janice Mandler | 2007-01-02 | 415-472-1734
4411 | 15 | 1 | LasGallinas | 2006-12-28 08:02 | 600 | 0 |  | 2006-12-28 08:02 |  | -- | 1111 Idylberry Street | San Rafael | Marin | 94903 |  |  | 2006-12-26 |  |  |  | An unusual amount of tampons were removed by RotoRooter. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | Line Crew Supervisor | Janice Mandler | 2006-12-28 | 415-472-1734
4263 | 14 | 1 | LasGallinas | 2006-12-07 10:08 | 700 | 0 |  | 2006-12-07 10:08 |  | -- | 1873 Las Gallinas Ave | San Rafael | Marin | 94903 |  |  | 2006-12-07 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Line Crew Supervisor | Janice Mandler | 2006-12-07 | 415-472-1734
3966 | 13 | 1 | LasGallinas | 2006-10-06 14:23 | 30 | 0 |  | 2006-10-06 14:23 |  | -- | 733 Estancia Way | San Rafael | Marin | 94903 |  |  | 2006-10-06 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LasGallinas | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Line Crew Supervisor | Janice Mandler | 2006-10-06 | 415-472-1734 | mwilliams@lgvsd.org, apetrie@lgvsd.org | MINOR
3444 | 12 | 1 | LasGallinas | 2006-06-01 14:13 | 120 | 0 |  | 2006-06-01 14:13 |  | -- | 172 La Perdiz / Cross street El Faisan | San Rafael | Marin | 94903 |  |  | 2006-06-01 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LasGallinas | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Line Crew Supervisor | Janice Mandler | 2006-06-01 | 415-472-1734 | mwilliams@lgvsd.org, apetrie@lgvsd.org | MINOR
2886 | 11 | 1 | LasGallinas | 2006-02-27 12:25 | 100 | 0 |  | 2006-02-27 12:25 |  | -- | 3 Mt Darwin Ct / cross street Mt. Lassen | San Rafael | Marin | 94903 |  |  | 2006-02-27 |  |  |  | Line has been flushed and rodded - 3-27-06 | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LasGallinas | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Line Crew Supervisor | Janice Mandler | 2006-02-27 | 415-472-1734 | mwilliams@lgvsd.org, apetrie@lgvsd.org | MINOR
2771 | 9 | 1 | LasGallinas | 2006-02-07 16:35 | 2610 | 0 | 06-0829 | 2006-02-07 | Janice Mandler |  | 170 Paul Dr | San Rafael | Marin | 94903 |  |  | 2006-02-06 | 10:30:00 A | 2006-02-07 | 3:30:00 PM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Line Crew Supervisor | Janice Mandler | 2006-02-07 | 415-472-1734x1 | mwilliams@lgvsd.org, apetrie@lgvsd.org | 24HR |  |  | 415-472-1734 | [6 empty] | LasGallinas
2780 | 10 | 1 | LasGallinas | 2006-02-08 15:12 | 2610 | 0 | 06-0829 | 2006-02-07 | Janice Mandler | LasGallinas | 170 Paul Dr | San Rafael | Marin | 94903 |  |  | 2006-02-06 | 10:30:00 A | [5 empty] | SUNNY WEATHER | Medium | Gallinas Creek | SURFACE WATER IMPACT | No |  | No | Yes | Water was seeping from street into gutter / stormdrain. Storm drain to surface water drainage ditch. |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | LasGallinas | PIPE |  | INFRASTRUCTURE FAILURE | --Select None-- | BREAKAGE OF COLLECTION SYSTEM |  | Collection crew observed small water seepage on road and determined it to be water (10:30). Marin Municiple Water Dept. was advised 2-6-06 @11:00. On 2-7-06, Marin Municiple Water Dept called us at 2:30 and advised that they didn't think it was their's but was ours. We responded with crew and contractor. Road was dug and force main line was found to have a crack. Crack was repaired that day. | Line Crew Supervisor | Janice Mandler | 2006-02-08 | 415-472-1734 | mwilliams@lgvsd.org, apetrie@lgvsd.org | MAJOR | Janice Mandler | LasGallinas | 415-472-1734 | 13 | 300 Smith Ranch Rd | San Rafael | Marin | 94903 |  | Las Gallinas Valley Sanitary District | 415-472-1734 |  | 300 Smith Ranch Rd | San Rafael | Marin | 94903
2684 | 8 | 1 | LasGallinas | 2006-01-26 12:52 | 300 | 0 |  | 2006-01-26 12:52 |  | -- | 49 Grande Paseo | San Rafael | Sonoma | 94903 |  |  | 2006-01-05 |  |  |  | This was believed to be a "private" sewer system for years and therefore, not maintained by us. On 1-26-06 we found that it was not a private system but was part of our system. This is why SSO on 1-5-06, when original spill occurred, was not reported until now. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LasGallinas | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Line Crew Supervisor | Janice Mandler | 2006-01-26 | 415-472-1734 | mwilliams@lgvsd.org, apetrie@lgvsd.org | MINOR
2150 | 7 | 1 | LasGallinas | 2005-11-21 11:26 | 100 | 0 |  | 2005-11-21 11:26 |  | -- | 708 Butternut - 100 gallons overflowed from homeowner's cleanout. Believed to be a result of grease in mainline | Las Gallinas | Marin | 94903 |  |  | 2005-11-21 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LasGallinas | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Line Crew Supervisor | Janice Mandler | 2005-11-21 | 415-472-1734 | mwilliams@lgvsd.org, apetrie@lgvsd.org | MINOR
1994 | 6 | 1 | LasGallinas | 2005-10-20 15:00 | 105 | 0 |  | 2005-10-20 15:00 |  | -- | 101 Las Gallinas Ave (cross street Las Flores) | San Rafael | Marin | 94903 |  |  | 2005-10-20 |  |  |  | Water was removed from storm ditch with vactor truck | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LasGallinas | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Line Crew Supervisor | Janice Mandler | 2005-10-20 | 415-472-1734 | mwilliams@lgvsd.org, apetrie@lgvsd.org | MINOR
1454 | 5 | 1 | LasGallinas | 2005-05-25 09:55 | 435 | 0 |  | 2005-05-25 09:55 |  | -- | 47 Elda Avenue | San Rafael | Marin | 94903 |  |  | 2005-05-24 |  |  |  | Mainline was root cut on 3-14-05 | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LasGallinas | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Wastewater Facilitie | Janice Mandler | 2005-05-25 | 415-472-1734 | mwilliams@lgvsd.org, apetrie@lgvsd.org | MINOR
1246 | 4 | 1 | LasGallinas | 2005-04-04 10:25 | 135 | 0 |  | 2005-04-04 10:25 |  | -- | Intersection of Las Gallinas and Park Ridge Rd. | San Rafael | Marin | 94903 |  |  | 2005-04-04 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LasGallinas | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Wastewater Tech. | Janice Mandler | 2005-04-04 | 415-472-1734 | mwilliams@lgvsd.org, apetrie@lgvsd.org | MINOR
907 | 3 | 1 | LasGallinas | 2005-01-24 15:29 | 100 | 0 |  | 2005-01-24 15:29 |  | -- | 11 Garden Ave | San Rafael | Marin | 94903 |  |  | 2005-01-23 |  |  |  | Rod Hole overflowed due to roots in main and bellied sections, causing spill into neighbors yard. Stoppage was cleared with 6" blades and was due to roots in system. Overflow was contained to deck of yard | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LasGallinas | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Wastewater Technicia | Janice Mandler | 2005-01-24 | 415-472-1734 | mwilliams@lgvsd.org | MINOR
636 | 1 | 1 | LasGallinas | 2004-12-27 14:25 | 900 | 0 |  | 2004-12-27 14:25 |  | -- | Intersection of Las Gallinas / Manual T. Freitas Parkway | Terra Linda | Marin | 94903 |  |  | 2004-12-27 |  |  |  | Spill occurred due to extremely heavy rainfall. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LasGallinas | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | Wastewater Tech | Janice Mandler | 2004-12-27 | 415-472-1734 | mwilliams@lgvsd.org | MINOR
637 | 2 | 1 | LasGallinas | 2004-12-27 15:25 | 18000 | 0 | 04-6799 | 2004-12-27 | Bob Buchholz | LasGallinas | Arias Court, Intersection of Manuel T Freitas, Las Gallinas | Terra Linda | Marin | 94903 |  |  | 2004-12-27 | 7:30:00 AM | [5 empty] | RAINY WEATHER | Medium |  | STORM DRAIN | No |  | No | No | n/a |  | No | No | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | LasGallinas | MANHOLE | Extremely high rainfall | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Wastewater Tech | Janice Mandler | 2004-12-27 | 415-472-1734 | mwilliams@lgvsd.org | MAJOR | Mark Williams | LasGallinas | 415-472-1734 | 18 | 300 Smith Ranch Rd | San Rafael | Marin | 94903 |  | Las Gallinas Valley Sanitary District
4827 | 17 | 1 | Livermore | 2007-02-27 | 1170 | 1170 | OES unavailable | 2007-02-27 | resident | livermore | 1068 Aberdeen Ave | Livermore | Alameda | 94551 |  |  | 2007-02-27 | 0.30556 | [6 empty] | Low |  | CAPTURED IN STORM DRAIN | No |  | No | No | N/A |  | Yes | Yes | No |  |  | No | No |  |  | 2007-02-27 | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | DEBRIS | -- Select One -- |  | Overflowing Manhole in front of 1068 Aberdeen Ave. All sewage contained and removed from storm system. | MWII | Brent Johnson | 2007-02-27 | 925-960-8151
4398 | 16 | 1 | Livermore | 2006-12-26 09:40 | 900 | 0 |  | 2006-12-26 09:40 |  | -- | In street in front of Noah's Bagels,1412 First St. | Livermore | Alameda | 94550 |  |  | 2006-12-22 |  |  |  | Significant grease and rag build-up causing blockage and overflow of manhole. All flows captured in street curb and gutter and removed using combination trucks. Surrounding pipelines cleaned and manhole rinsed. Mainline will be televised after holiday vacations. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Pub Wks Sup. | Karl Kraft | 2006-12-26 | 925-960-8123
3733 | 15 | 1 | Livermore | 2006-08-14 15:38 | 850 | 0 |  | 2006-08-14 15:38 |  | -- | Westside of N. Livermore Ave./ South of Chestnut Ave. | Livermore | Alameda | 94551 |  |  | 2006-08-10 |  |  |  | Vac'd major construction debris(asphalt chunks/rock) from mainline. Second overflow within 2+ months on sewer line.. Mainline scheduled for CCTV and further investigation is pending. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | livermore | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Maint.WorkerIII | Mike Wells | 2006-08-14 | 9259608127 | dggreenwood@ci.livermore.ca.us, | MINOR
3600 | 14 | 2 | Livermore | 2006-07-05 12:51 | 1650 | 1650 | 06-3810 | 2006-06-27 | Aileen Vicencio | livermore | Westside N. Livermore Ave. @ Chestnut St. | Livermore | Alameda | 94550 |  |  | 2006-06-27 | 7:54:00 AM | [5 empty] | SUNNY WEATHER | Low |  | CAPTURED IN STORM DRAIN | No |  | No | No | N/A |  | Yes | Yes | No | No | No | No | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | livermore | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS | --Select None-- |  |  | Maint. Worker III | Mike Wells | 2006-07-05 | 925-960-8127 | dggreenwood@ci.livermore.ca.us, | MAJOR | Mike Wells | Livermore | (925) 960-8127 |  | 101 W. Jack London Blvd. | Livermore | Alameda | 94551 |  | livermore
3418 | 13 | 1 | Livermore | 2006-05-26 15:07 | 720 | 0 |  | 2006-05-26 15:07 |  | -- | 985 Hansen Road, Cross Street: Wetmore Rd. | Livermore | Alameda | 94550 |  |  | 2006-05-26 |  |  |  | The blockage was caused by asphalt and rocks discarded in the manhole. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Livermore | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Source Control | Jennifer Auton | 2006-05-26 | 925-960-8142 | dggreenwood@ci.livermore.ca.us, | MINOR
3210 | 11 | 1 | Livermore | 2006-04-20 14:00 | 120 | 0 |  | 2006-04-20 14:00 |  | -- | Wagner and Catalina | Livermore | Alameda | 95209 |  |  | 2006-04-20 |  |  |  | Large quantity of rags in the line. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Livermore | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Inspector | Blaine Drewes | 2006-04-20 | 925-960-8162 | dggreenwood@ci.livermore.ca.us, | MINOR
3212 | 12 | 1 | Livermore | 2006-04-20 14:01 | 120 | 0 |  | 2006-04-20 14:01 |  | -- | Wagner and Catalina | Livermore | Alameda | 95209 |  |  | 2006-04-20 |  |  |  | Large quantity of rags in the line. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Livermore | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Inspector | Blaine Drewes | 2006-04-20 | 925-960-8162 | dggreenwood@ci.livermore.ca.us, | MINOR
2798 | 9 | 1 | Livermore | 2006-02-13 15:18 | 30 | 0 |  | 2006-02-13 15:18 |  | -- | 1857 Paseo Laguna Seca | Livermore | Alameda | 94550 |  |  | 2006-02-11 |  |  |  | Soft blockage removed by flushing equipment. Follow-up, Main line will be tv'd | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | livermore | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Maint. wk. 2 | Mike Wells | 2006-02-13 | 9259608100 | dggreenwood@ci.livermore.ca.us, | MINOR
2607 | 6 | 1 | Livermore | 2006-01-11 15:04 | 35 | 0 |  | 2006-01-11 15:04 |  | -- | 2034 Research Dr | Livermore | Alameda | 94550 |  |  | 2006-01-11 |  |  |  | found root ball lodged in sanitary mainline, root ball removed and storm drain line vacuumed out, all sewage recovered. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | livermore | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | MWII | Steven B. Durflinger | 2006-01-11 | 925-960-8100 | dggreenwood@ci.livermore.ca.us, | MINOR
2165 | 4 | 1 | Livermore | 2005-11-22 15:58 | 2700 | 2700 | 05-6760 | 2005-11-22 | Joyce Sanchez, Livermore Unified School District |  | 401 E. Jack London Blvd. Rear of property, on playground. | Livermore | Alameda | 94550 |  |  | 2005-11-22 | 1:32:00 PM | 2005-11-22 | 2:58:00 PM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Water Resources Mana | Karl Kraft | 2005-11-22 | 925-960-8100 | dggreenwood@ci.livermore.ca.us, | 24HR |  |  | 925-606-3319 | [6 empty] | livermore
2166 | 5 | 1 | Livermore | 2005-11-22 16:10 | 2700 | 2700 | 05-6760 | 2005-11-22 | Joyce Sanchez, Livermore Unified School District | livermore | 401 E. Jack London Blvd. Rear of school yard, on playground. | Livermore | Alameda | 94550 |  |  | 2005-11-22 | 1:32:00 PM | [5 empty] | SUNNY WEATHER | Low |  | CAPTURED IN STORM DRAIN | No | Posted puddles on school yard since a few daycare children were present and near vicinity of overflow. | No | Yes | None |  | Yes | Yes | Yes | No | No | No | No | No | No | 2005-11-30 | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | livermore | MANHOLE | Wood debris, unknown origin or how it entered pipline. | BLOCKAGE | CONSTRUCTION DEBRIS | --Select None-- | Wood debris, unknown origin or how it entered pipline. | Minor spill contained on school playground and in storm drain. Total recovery of sewage with minor exception of pecolated liquid into grass playground. | Colletctions Sup | Karl Kraft | 2005-11-22 | 925-960-8100 | dggreenwood@ci.livermore.ca.us, | MAJOR | Karl Kraft | Livermore | (925) 960-8100 |  | 101 W. Jack London Blvd. | Livermore | Alameda | 94551 |  | Livermore
2657 | 8 | 1 | Livermore | 2006-01-19 07:54 | 350 | 0 |  | 2006-01-19 07:54 |  | -- | 1716 Peary Way | Livermore | Alameda | 94551 |  |  | 2005-06-07 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Livermore | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Source Control Inspe | Blaine Drewes | 2006-01-19 | 925-960-8162 | dggreenwood@ci.livermore.ca.us, | MINOR
2651 | 7 | 1 | Livermore | 2006-01-18 15:08 | 3000 | 3000 | 05-3373 | 2005-06-06 | Livermore | Livermore | Charlotte Way near Giambelli Park | Livermore | Alameda | 94550 |  |  | 2005-06-06 | 11:00:00 A | [5 empty] | SUNNY WEATHER | Medium | Arroyo Seco | SURFACE WATER IMPACT | No |  | No | No | Release occurred in the headwaters. No upstream flow into the arroyo. After remedial actions, there was no water in the affected reach of the stream. |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Livermore | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS | --Select None-- |  |  | Source Control Inspe | Blaine Drewes | 2006-01-18 | 925-960-8162 | dggreenwood@ci.livermore.ca.us, | MAJOR | Blaine Drewes | Livermore | (925) 960-8162 |  | 101 W. Jack London Blvd. | Livermore | Alameda | 04551 | City of Livermore | WRD | (925) 960-8162 |  | 101 W. Jack London Blvd. | Livermore | Alameda | 94551
1244 | 3 | 1 | Livermore | 2005-04-04 07:38 | 650 | 0 |  | 2005-04-04 07:38 |  | -- | 187 North 'K' Street, Spill occurred inside the business of Allen's Towing. | Livermore | Alameda | 94551 |  |  | 2005-03-30 |  |  |  | Broken pipe and grease are the main contributors to this spill. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Livermore | PIPE |  | INFRASTRUCTURE FAILURE | MULTIPLE CAUSES |  |  |  | Coordinator | Tom Smith | 2005-04-04 | (925) 960-8127 | dggreenwood@ci.livermore.ca.us, | MINOR
1127 | 2 | 1 | Livermore | 2005-03-08 11:33 | 6000 | 0 | 05-1407 | 2005-03-04 | Tom Smith | Tom Smith | East Avenue at the intersection of Mines Road, The manhole is located in a sidewalk southeast of the intersection 60 feet. | Livermore | Alameda | 94551 |  |  | 2005-03-04 | 7:20:00 AM | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | No | Storm lines are running with average flow to high flow during downpours. Estimate that spill was absorbed by one or two million gallons of rain fall. |  | No | No | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | Livermore | MANHOLE | A contractor building homes in a new subdivision failed to remove a rope tag line from a sewer line pipe segment. The rope is about 400-500 feet long. This is what caused the sewer overflow. | BLOCKAGE | CONSTRUCTION DEBRIS | --Select None-- |  | The reported spill occurred as the result of construction material not being removed from a sewer pipe segment. The material (rope) floated down stream and drifted into a divided sewer line. There are 2 eight inch pipes side-by-side. Both of these pipes were blocked by the length of rope and our crew had to clear both portions of pipe. This additional problem required more time to clear the blockage. | Coordinator | Tom Smith | 2005-03-08 | (925) 960-8127 | Tom Smith@ci.livermore.ca.us, | MAJOR | Tom Smith | Livermore | (925) 960-8127 |  | 101 W. Jack London Blvd. | Livermore | Alameda | 04551 |  | Developer/Contractor
1126 | 1 | 1 | Livermore | 2005-03-08 10:45 | 6000 | 0 | 05-1470 | 2005-03-08 | Tom Smith |  | East Avenue at the intersection of Mines Road, Manhole is in a sidewalk on the south side of East Avenue, bordering a large open field. | California | Alameda | 94551 |  |  | 2005-03-03 | 7:20:00 AM | 2005-03-04 | 9:20:00 AM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Water Resources Coll | Tom Smith | 2005-03-08 | 925-960-8127 | thsmith@ci.livermore.ca.us, | 24HR |  |  | (925) 9608127 | [6 empty] | Livermore
5140 | 5 | 1 | LosAltosCity | 2007-04-24 16:26 | 20 | 0 |  | 2007-04-24 16:26 |  | -- | 11555 Putter Way (Santa Clara County area) | Los Altos | Santa Clara | 94024 |  |  | 2007-04-24 |  |  |  | Crews cleared mainline and vacuumed up 20 gallons that had collected in the driveway area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Brian J. McCarthy | 2007-04-24 | 650/947-2879
4999 | 4 | 1 | LosAltosCity | 2007-03-26 12:59 | 225 | 0 |  | 2007-03-26 12:59 |  | -- | 23 Woods Lane | Los Altos | Santa Clara | 94024 |  |  | 2007-03-25 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Public Works Supt, | Brian McCarthy | 2007-03-26 | 650/947-2879
2481 | 2 | 1 | LosAltosCity | 2006-01-04 13:24 | 100 | 0 |  | 2006-01-04 13:24 |  | -- | 1047 Eastwood Drive. Manhole segment H5 S-407 to H5 S-406. | Los Altos | Santa Clara | 94022 |  |  | 2006-01-03 |  |  |  | Area of spill was cleaned up and decontaminated. No wastewater entered the creek. Dry weather at time of overflow. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LosAltosCity | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Brian J. McCarthy | 2006-01-04 | 650/947-2879 | jim.porter@ci.los-altos.ca.us, Phil.Rose@ci.los-altos.ca.us | MINOR
981 | 1 | 1 | LosAltosCity | 2005-02-08 09:00 | 100 | 0 | 05-0864 | 2005-02-08 | Brian J McCarthy | LosAltosCity | 530 Pine Lane in the backyard is a pump station maintained by City of Los Altos. Spill area was in private residence backyard. | Los Altos | Santa Clara | 94022 |  |  | 2005-02-07 | 11:35:00 A | [5 empty] | CLOUDY WEATHER | Low | Adobe Creek | YARD/LAND | No |  | No | Yes | Overflowing manhole was pumped out and spill area was sandbagged to contain spill into Adobe Creek. |  | Yes | Yes | Yes | No | No | No | No | No | No | 2005-02-08 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | LosAltosCity | PUMP STATION |  | INFRASTRUCTURE FAILURE | --Select None-- | PUMP STATION FAILURE |  | Pump station failure caused wastewater to backup in upstream manhole. Approximately 100 gallons of wastewater overflowed out of manhole into creek bank vegetation and may have entered creek. | Public Works Superin | Brian J McCarthy | 2005-02-08 | 650/947-2879 | jim.porter@ci.los-altos.ca.us | MAJOR | Brian J McCarthy | LosAltosCity | 650/947-2879 |  | 1 N San Antonio Road | Los Altos | Santa Clara | 94022 |  | City of Los Altos | 650/947-2879 |  | 1 N. San Antonio Road | Los Altos | Santa Clara | 94022
5176 | 37 | 1 | LosAltosHills | 2007-04-30 13:40 | 50 | 0 |  | 2007-04-30 13:40 |  | -- | 12387 Stonebrook Dr. MH #48 | Los Altos Hills | Santa Clara | 94022 |  |  | 2007-04-26 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Engineer | Richard Chen | 2007-04-30 | 650-947-2509
5039 | 36 | 3 | LosAltosHills | 2007-04-04 15:22 | 50 | 0 |  | 2007-04-04 15:22 |  | -- | O'keefe at Dover, MH 13 | Los Altos Hills | Santa Clara | 94022 |  |  | 2007-04-02 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | CAUSE UNKNOWN | -- Select One -- |  |  |  | Engineer | Richard Chen | 2007-04-04 | 650-947-2509
5022 | 35 | 1 | LosAltosHills | 2007-03-29 | 1000 | 800 | n/a | 2007-03-29 | Richard Chen | losaltoshills | 25449 Moody Road | Los Altos Hills | Santa Clara | 94022 |  |  | 2007-03-29 | 0.37153 | [6 empty] | Low | Adoby Creek | SURFACE WATER IMPACT | No |  | No | No | The creek was dry |  | Yes | Yes | Yes |  |  | Yes | No |  |  |  | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | -- Select One -- | -- Select One -- |  |  | Associate Engineer | Richard Chen | 2007-03-29 | 650-947-2509
4536 | 31 | 1 | LosAltosHills | 2007-01-17 15:54 | 50 | 0 |  | 2007-01-17 15:54 |  | -- | 12173 Hilltop Drive | Los Altos Hills | Santa Clara | 94022 |  |  | 2006-12-29 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Engineer | Richard Chen | 2007-01-17 | 650-947-2509
4368 | 30 | 1 | LosAltosHills | 2006-12-20 11:19 | 25 | 0 |  | 2006-12-20 11:19 |  | -- | 14495 Miranda Road | Los Altos Hills | Santa Clara | 94022 |  |  | 2006-12-19 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Associate Engineer | Richard Chen | 2006-12-20 | 650-947-2509
4124 | 29 | 1 | LosAltosHills | 2006-11-20 13:58 | 200 | 0 |  | 2006-11-20 13:58 |  | -- | 25525 Adobe Lane | los altos hills | santa clara | 94022 |  |  | 2006-11-18 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | engineer | richard chen | 2006-11-20 | 650-947-2509
4122 | 28 | 1 | LosAltosHills | 2006-11-20 13:50 | 200 | 0 |  | 2006-11-20 13:50 |  | -- | La Cresta at St. Fransis | Los Altos Hills | santa clara | 94022 |  |  | 2006-11-18 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | CAUSE UNKNOWN | -- Select One -- |  | lamphole |  | engineer | richard chen | 2006-11-20 | 650-947-2509
3825 | 26 | 1 | LosAltosHills | 2006-09-05 09:13 | 300 | 0 |  | 2006-09-05 09:13 |  | -- | Tepa Way and Willow Pond Lane Lane | Los Altos Hills | Santa Clara | 94022 |  |  | 2006-08-31 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LosAltosHills | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Engineer | Richard Chen | 2006-09-05 | 650-941-7222 | rchen@losaltoshills.ca.gov, | MINOR
3768 | 25 | 1 | LosAltosHills | 2006-08-21 13:22 | 25 | 0 |  | 2006-08-21 13:22 |  | -- | 27957 Via Ventana | Los Altos Hills | Santa Clara | 94022 |  |  | 2006-08-19 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LosAltosHills | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Engineer | Richard Chen | 2006-08-21 | 650-947-2509 | rchen@losaltoshills.ca.gov, | MINOR
3606 | 23 | 1 | LosAltosHills | 2006-07-06 10:46 | 200 | 0 |  | 2006-07-06 10:46 |  | -- | 25870 Altamont Road | Los Altos Hills | Santa Clara | 94022 |  |  | 2006-07-05 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LosAltosHills | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Engineer | Richard Chen | 2006-07-06 | 650-947-2509 | rchen@losaltoshills.ca.gov | MINOR
2983 | 22 | 2 | LosAltosHills | 2006-03-10 15:22 | 90 | 0 |  | 2006-03-10 15:22 |  | -- | MH in front of 26667 Snell Lane | Los Altos Hills | Santa Clara | 94022 |  |  | 2006-03-09 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LosAltosHills | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Engineer | Richard Chen | 2006-03-10 | 650-941-7222 | rchen@losaltoshills.ca.gov, hlouie@losaltoshills.ca.gov | MINOR
2946 | 21 | 1 | LosAltosHills | 2006-03-07 13:59 | 875 | 0 |  | 2006-03-07 13:59 |  | -- | 26000 Altamont Road, | Los Altos Hills | Santa Clara | 94022 |  |  | 2006-03-07 |  |  |  | 450 gallons of overflow were absorbed by soft soil and leaves. The remaining 425 gallons were retrieved with the Vacumn truck | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LosAltosHills | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Engineer | Richard Chen | 2006-03-07 | 650-947-2509 | rchen@losaltoshills.ca.gov | MINOR
2898 | 20 | 1 | LosAltosHills | 2006-02-28 11:41 | 50 | 0 |  | 2006-02-28 11:41 |  | -- | 25870 Altamont Road | Los Altos Hills | Santa Clara | 94022 |  |  | 2006-01-05 |  |  |  | Sewer main pipes was broken due to tree roots. The pipes were replaced. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LosAltosHills | PIPE |  | BLOCKAGE | ROOTS |  |  |  | Engineer | Richard Chen | 2006-02-28 | 650-941-7222 | rchen@losaltoshills.ca.gov | MINOR
2345 | 19 | 1 | LosAltosHills | 2005-12-28 11:40 | 100 | 0 |  | 2005-12-28 11:40 |  | -- | Fremont Road near Donelson | Los Altos Hills | santa clara | 94022 |  |  | 2005-12-22 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LosAltosHills | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Engineer | Richard Chen | 2005-12-28 | 650-9472509 | rchen@losaltoshills.ca.gov, hlouie@losaltoshills.ca.gov | MINOR
1930 | 18 | 1 | LosAltosHills | 2005-10-07 16:29 | 30 | 0 |  | 2005-10-07 16:29 |  | -- | La Cresta Drive near St. Francis drive | Los Altos Hills | Santa Clara | 94022 |  |  | 2005-10-04 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LosAltosHills | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Engineer | richard Chen | 2005-10-07 | 650-941-7222 | rchen@losaltoshills.ca.gov, hlouie@losaltoshills.ca.gov | MINOR
1668 | 16 | 1 | LosAltosHills | 2005-08-01 13:55 | 5 | 0 |  | 2005-08-01 13:55 |  | -- | 14341 Liddicoat | Los Altos Hills | santa clara | 94404 |  |  | 2005-07-31 |  |  |  | Asphalt concrete falled into the manhole and blocked the main from recent paving project. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LosAltosHills | CLEAN OUT |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Associate Engineer | Richard Chen | 2005-08-01 | 650-941-7222 | rchen@losaltoshills.ca.gov, hlouie@losaltoshills.ca.gov | MINOR
1659 | 14 | 1 | LosAltosHills | 2005-07-28 16:33 | 5 | 0 |  | 2005-07-28 16:33 |  | -- | 25680 Elena Road | Los Altos Hills | Santa Clara | 94022 |  |  | 2005-07-27 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LosAltosHills | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | engineer | richard chen | 2005-07-28 | 650-941-7222 | rchen@losaltoshills.ca.gov, dross@losaltoshills.ca.gov | MINOR
1666 | 15 | 1 | LosAltosHills | 2005-08-01 13:39 | 40 | 0 |  | 2005-08-01 13:39 |  | -- | Backyard of 27743 Via Ventana | Los Altos Hills | Santa Clara | 94022 |  |  | 2005-07-26 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LosAltosHills | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Associate Engineer | Richard Chen | 2005-08-01 | 650-941-7222 | rchen@losaltoshills.ca.gov, hlouie@losaltoshills.ca.gov | MINOR
1624 | 13 | 1 | LosAltosHills | 2005-07-18 16:38 | 250 | 0 |  | 2005-07-18 16:38 |  | -- | El Monte Road at MH 14 | los altos hills | santa clara | 94022 |  |  | 2005-07-12 | [9 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LosAltosHills | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Engineer | Richard Chen | 2005-07-18 | 6509417222 | rchen@losaltoshills.ca.gov, hlouie@losaltoshills.ca.gov, Mike.Ramon@ci.los-altos.ca.us | MINOR
1582 | 12 | 1 | LosAltosHills | 2005-06-30 10:26 | 4 | 0 |  | 2005-06-30 10:26 |  | -- | 11935 Rhus Ridge Road | Los Altos Hills | Santa Clara | 94022 |  |  | 2005-06-25 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LosAltosHills | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | engineer | richard chen | 2005-06-30 | 650-941-7222 | rchen@losaltoshills.ca.gov, dross@losaltoshills.ca.gov | MINOR
1389 | 11 | 1 | LosAltosHills | 2005-05-11 15:37 | 4 | 0 |  | 2005-05-11 15:37 |  | -- | 12500 Barley Hill RD | Los Altos Hills | Santa Clara | 94022 |  |  | 2005-05-11 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LosAltosHills | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Engineer | Richard Chen | 2005-05-11 | 650-940-7222 | rchen@losaltoshills.ca.gov, dross@losaltoshills.ca.gov | MINOR
1187 | 9 | 1 | LosAltosHills | 2005-03-15 14:35 | 150 | 0 |  | 2005-03-15 14:35 |  | -- | 27676 Via Cerra Gordo | Los Altos Hills | Santa Clara | 94022 |  |  | 2005-03-11 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LosAltosHills | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Engineer | Richard Chen | 2005-03-15 | 650-941-7222 | rchen@losaltoshills.ca.gov, dross@losaltoshills.ca.gov | MINOR
1191 | 10 | 1 | LosAltosHills | 2005-03-15 15:01 | 60 | 0 |  | 2005-03-15 15:01 |  | -- | 11629 Dawson Drive | Los Altos Hills | Santa Clara | 94022 |  |  | 2005-03-09 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LosAltosHills | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Engineer | Richard Chen | 2005-03-15 | 650-941-7222 | rchen@losaltoshills.ca.gov, dross@losaltoshills.ca.gov | MINOR
922 | 5 | 1 | LosAltosHills | 2005-01-28 10:22 | 50 | 0 |  | 2005-01-28 10:22 |  | -- | backyard of 12170 Padre Court | los altos hills | santa clara | 94022 |  |  | 2005-01-24 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LosAltosHills | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Associate Engineer | Richard Chen | 2005-01-28 | 650-941-7222 | rchen@losaltoshills.ca.gov | MINOR
794 | 3 | 1 | LosAltosHills | 2005-01-10 09:33 | 75 | 0 |  | 2005-01-10 09:33 |  | -- | 24801 Prospect Avenue | Los Altos Hills | Santa Clara | 94022 |  |  | 2005-01-06 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LosAltosHills | OTHER | cracks on street pavement | BLOCKAGE | ROOTS |  |  |  | Associate Engineer | Richard Chen | 2005-01-10 | 650-941-7222 | rchen@losaltoshills.ca.gov | MINOR
619 | 2 | 1 | LosAltosHills | 2004-12-22 09:01 | 200 | 0 |  | 2004-12-22 09:01 |  | -- | at O'keefe lane near Cantata Way | Lost Altos Hills | Santa Clara | 94022 |  |  | 2004-12-20 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | LosAltosHills | MANHOLE |  | ELECTRICAL POWER FAILURE | --Select None-- |  |  |  | Associate Engineer | Richard Chen | 2004-12-22 | 650-941-7222 | rchen@losaltoshills.ca.gov | MINOR
4876 | 100 | 1 | MarinCountySD1 | 2007-03-07 | 2100 | 0 | 07-1476 | 2007-03-07 | Jeff Yee | MarinCountySD1 | 14 Kentdale Ln. | Kentfield | Marin | 94904 |  |  | 2007-03-06 | 0.072917 | [6 empty] | High | Region 2 | STORM DRAIN | No | None | No | Yes | None |  | Yes | Yes | Yes |  |  | No | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | ROOTS | -- Select One -- |  | Main overflowed onto yard/land, and eventually into a storm drain. Main line will be TVed for condition evaluation, repaired as necessary. it will also be placed on a six-month maintenance program until repaired. Area was cleaned, disinfected, and posted | Supt | Eric Smith | 2007-03-07 | 415 259 2953
4776 | 99 | 1 | MarinCountySD1 | 2007-02-20 07:49 | 110 | 0 |  | 2007-02-20 07:49 |  | -- | Intersection of Almannar and Nadina | Larkspur | Marin | 94939 |  |  | 2007-02-20 |  |  |  | Cleaned and posted area, removed debris | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supt | Eric Smith | 2007-02-20 | 4154611122
4271 | 98 | 1 | MarinCountySD1 | 2006-12-08 13:09 | 150 | 0 |  | 2006-12-08 13:09 |  | -- | Near 60 Fawn Dr. | San Anselmo | Marin | 94960 |  |  | 2006-12-08 |  |  |  | Large amount of papercaused the main to block up. area was cleaned and warning signs were posted. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | supt | Eric Smith | 2006-12-08 | 4154611122
4192 | 97 | 1 | MarinCountySD1 | 2006-12-05 | 2920 | 0 | 06-7159 | 2006-12-05 | Mark Molinari | marincountysd1 | 35 Via Barranca | Larkspur | Marin | 94939 |  |  | 2006-12-04 | 0.39931 | [6 empty] | Low |  | YARD/LAND | No |  | No | Yes | No impact |  | Yes | Yes | No |  |  | No | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | ROOTS | -- Select One -- |  | Line will be put on a six month maintenance program. Crew will tv and repair as ness. | Supt | Eric Smith | 2006-12-05 | 4154611122
4107 | 96 | 1 | MarinCountySD1 | 2006-11-14 09:04 | 365 | 0 |  | 2006-11-14 09:04 |  | -- | 19 Monte Vista Ave | Larkspur | Marin | 94939 |  |  | 2006-11-13 |  |  |  | Main line was routinely cleaned 11-8-06, unknown why line blocked up. Main will be TVed and repaired as needed | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | Supt | Eric Smith | 2006-11-14 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
4042 | 95 | 1 | MarinCountySD1 | 2006-10-30 15:23 | 600 | 0 |  | 2006-10-30 15:23 |  | -- | 900 block of Bolinas road | Fairfax | Marin | 94930 |  |  | 2006-10-30 |  |  |  | Line is being inspected for defects to be repaired. After blockage was broken, the downstream manhole overflowed. the total spill amount is 600 gallons | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supt. | Eric Smith | 2006-10-30 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
3938 | 94 | 1 | MarinCountySD1 | 2006-09-28 09:48 | 1145 | 0 | 065767 | 2006-09-28 | Noel Sandoval | MarinCountySD1 | 2390 Sir Francis Drake Blvd | Fairfax | Marin | 94939 |  |  | 2006-09-27 | 4:45:00 AM | [5 empty] | SUNNY WEATHER | Low |  | SURFACE WATER IMPACT | No |  | No | Yes | Some minor discoloration at entry into creek |  | Yes | Yes | No | No | No | No | No | Yes | No | 2006-09-28 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MarinCountySD1 | MANHOLE | Unknown cause, main cleared it self on arrival. | CAUSE UNKNOWN | --Select None-- | --Select None-- | Unknown cause, main cleared it self on arrival. | Unknown cause, main was cleaned. Will be televised 9/28/2006 and repaired as needed. Posted area | Supt | Eric Smith | 2006-09-28 | 4154611122 | ericlsmith@sbcglobal.net, | MAJOR | Eric Smith | SD #1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
3897 | 93 | 1 | MarinCountySD1 | 2006-09-19 14:58 | 270 | 0 |  | 2006-09-19 14:58 |  | -- | 230 Deer Hollow Dr. | San Anselmo | Marin | 94960 |  |  | 2006-09-16 |  |  |  | Main line failed due to unauthorized construction by a private contractor. Repaired by district crew on 9-18-06 | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | PIPE |  | BLOCKAGE | --Select None-- |  |  |  | Supt. | Eric Smith | 2006-09-19 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
3867 | 92 | 1 | MarinCountySD1 | 2006-09-11 09:22 | 480 | 0 |  | 2006-09-11 09:22 |  | -- | 61 Via La Cumbre | Larkspur | Marin | 94939 |  |  | 2006-09-10 |  |  |  | Blockage removed, area cleaned and posted | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supt | Eric Smith | 2006-09-11 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
3850 | 91 | 2 | MarinCountySD1 | 2006-09-06 14:38 | 450 | 0 |  | 2006-09-06 14:38 |  | -- | 476 Cane St | Larkspur | Marin | 94939 |  |  | 2006-08-31 |  |  |  | Small leak due to congested main and damage to pipe. Cleaned main, stopped leak. Repair to be made 9-1-06. Posted and cleaned area. No visible damage to creek. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | PIPE |  | BLOCKAGE | --Select None-- |  |  |  | Supt | Eric Smith | 2006-09-01 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
3779 | 90 | 1 | MarinCountySD1 | 2006-08-23 10:54 | 150 | 0 |  | 2006-08-23 10:54 |  | -- | 320 Magnolia | Larkspur | Marin | 94939 |  |  | 2006-08-13 |  |  |  | Blockage due to grease, plastic from a restaurant and some roots. Informed owner to clean the trap and to keep plastic out of the system | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Supt | Eric Smith | 2006-08-23 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
3561 | 88 | 1 | MarinCountySD1 | 2006-06-27 08:54 | 388 | 0 |  | 2006-06-27 08:54 |  | -- | 14 Tamalpais Ave | Larkspur | Marin | 94939 |  |  | 2006-06-26 |  |  |  | Blockage was caused by paper products. Cleaned area and posted signs. It was originally reported as 488 gal. by fax on 6-26-06, the correct amount is 388 | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Supt | Eric Smith | 2006-06-27 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
3618 | 89 | 1 | MarinCountySD1 | 2006-07-11 14:37 | 384 | 0 |  | 2006-07-11 14:37 |  | -- | 15 Tamalpais | Larkspur | Marin | 94939 |  |  | 2006-06-26 |  |  |  | Start date unknown to crew until 7-11-06. Originally thought to have started on 6-26-2006, and to be under 100 gal. Informed on 7-11-06 that it may have have started on 6-24-06. (One house on main). Cleaned and posted area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Supt | Eric Smith | 2006-07-11 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
3512 | 87 | 1 | MarinCountySD1 | 2006-06-20 08:29 | 400 | 0 |  | 2006-06-20 08:29 |  | -- | 271 Via La Paz | Greenbrae | Marin | 93939 |  |  | 2006-06-14 |  |  |  | Cleaned main and surrounding area, posted signs. Will recheck in six months to evaluate condition. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supt | Eric Smith | 2006-06-20 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
3487 | 86 | 1 | MarinCountySD1 | 2006-06-14 09:21 | 17850 | 50 | 06-3498 | 2006-06-12 | Jeff Yee | MarinCountySD1 | Easement Between Hampton Ct. & Sir Francis Drake Blvd | San Anselmo | Marin | 94960 |  |  | 2006-06-12 | 12:30:00 P | [5 empty] | CLOUDY WEATHER | High |  | STORM DRAIN | No |  | No | Yes | No Visual impact, many small fish were seen in area |  | Yes | Yes | Yes | No | No | Yes | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MarinCountySD1 | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- |  | The main line was replaced in 2002. We have found a defect that will be repaired, until it is repaired, it has been placed on a six month cleaning schedule. Originally reported (faxed) by crew at 252,000 gallons. Revised to 17850 gallons. The overflow was not reported for 7 days. There are 17 houses on the main. 17 units x 150 gallons x 7 days = 17850. The area was cleaned and the storm drains were flushed and vacuumed. Warning signs were posted. Healthy fish were observed in the receiving water after clean up was completed. | Supt | Eric Smith | 2006-06-14 | 4154611122 | ericlsmith@sbcglobal.net, | MAJOR | Eric Smith | SD #1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
3412 | 84 | 1 | MarinCountySD1 | 2006-05-26 09:32 | 100 | 0 |  | 2006-05-26 09:32 |  | -- | 50-A Ash Ave | San Anselmo | Marin | 94960 |  |  | 2006-05-22 |  |  |  | Main was cleaned two weeks before event, found a large amount of paper products to have caused blockage | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Supt | Eric Smith | 2006-05-26 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
3343 | 83 | 1 | MarinCountySD1 | 2006-05-16 11:04 | 120 | 0 |  | 2006-05-16 11:04 |  | -- | 83 Hatzic Ct. | Larkspur | Marin | 94939 |  |  | 2006-05-15 |  |  |  | Cleaned and posted area will TV for repair, added to 6 month maintenance program until repaired. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | Supt | Eric Smith | 2006-05-16 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
3468 | 85 | 1 | MarinCountySD1 | 2006-06-07 15:44 | 12000 | 0 | 06-3384 | 2006-06-06 | Mark Molinari | MarinCountySD1 | 195 Marina Vista | Larkspur | Marin | 94939 |  |  | 2006-05-06 | 2:46:00 AM | [5 empty] | SUNNY WEATHER | High |  | YARD/LAND | No |  | No | Yes | No impact |  | Yes | Yes | Yes | No | No | No | No | No | No | 2006-06-08 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MarinCountySD1 | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- |  | Overflow was not reported to the district until 6/6/06. RP stated that it could have been overflowing for a month. Only Two houses on the Main. Sched. for repair on 6/8/06 | Supt | Eric Smith | 2006-06-07 | 4154611122 | ericlsmith@sbcglobal.net, | MAJOR | Eric Smith | SD #1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
3235 | 81 | 1 | MarinCountySD1 | 2006-04-25 08:16 | 750 | 0 |  | 2006-04-25 08:16 |  | -- | 18 South Ridgewood | Kentfield | Marin | 94904 |  |  | 2006-04-24 |  |  |  | Blockage was due to a large piece of broken pipe causing solids to accumulate and block the system. The water flowed across land, and into a flowing creek, no visual impact. Posted and cleaned the area. Will evaluate for repair. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Supt | Eric Smith | 2006-04-25 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
3169 | 79 | 1 | MarinCountySD1 | 2006-04-13 14:04 | 8400 | 0 | 06-2219 | 2006-04-12 | Mark Molinari | MarinCountySD1 | Intersection of Porteous and Wood Ln. | Fairfax | Marin | 94930 |  |  | 2006-04-12 | 6:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | High | Fairfax creek | STORM DRAIN | Yes |  | No | Yes | No Visible impact |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MarinCountySD1 | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | Heavy rain, over 6" Barricaded area, cleaned and posted area. | Supt | Eric Smith | 2006-04-13 | 4154611122 | ericlsmith@sbcglobal.net, | MAJOR | Eric Smith | SD #1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
3171 | 80 | 1 | MarinCountySD1 | 2006-04-13 14:19 | 2550 | 0 | 06-2212 | 2006-04-13 | Mark Molinari | MarinCountySD1 | 991 Butterfield Rd. | San Anselmo | Marin | 94960 |  |  | 2006-04-12 | 6:30:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | Yes | No visible impact, heavy rain |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MarinCountySD1 | CLEAN OUT |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | Major storm, over six inches. Cleaned and posted area after event. | Supt | Eric Smith | 2006-04-13 | 4154611122 | ericlsmith@sbcglobal.net, | MAJOR | Eric Smith | SD #1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
3170 | 78 | 2 | MarinCountySD1 | 2006-04-13 14:05 | 1260 | 0 | 06-2218 | 2006-04-12 | Mark Molinari | MarinCountySD1 | 68 Meernaa Ave | Fairfax | Marin | 94930 |  |  | 2006-04-12 | 8:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | YARD/LAND | No |  | No | Yes | no inpact, heavy rains |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MarinCountySD1 | CLEAN OUT |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | Major storm, over six inches. Cleaned and posted area after event. | Supt | Eric Smith | 2006-04-13 | 4154611122 | ericlsmith@sbcglobal.net, | MAJOR | Eric Smith | SD #1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
3158 | 75 | 1 | MarinCountySD1 | 2006-04-12 15:39 | 2550 | 0 | 06-2212 | 2006-04-12 | Mark Molinari |  | 991 Butterfield Rd | San Anselmo | Marin | 94960 |  |  | 2006-04-11 | 6:30:00 AM | 2006-04-12 | 3:00:00 AM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Supt | Eric Smith | 2006-04-12 | 415-461-1122 | ericlsmith@sbcglobal.net, | 24HR |  |  | 415-461-1122 | [6 empty] | MarinCountySD1
3159 | 76 | 1 | MarinCountySD1 | 2006-04-12 16:04 | 1260 | 0 | 06-2218 | 2006-04-12 | Mark Molinari |  | 68 Meernaa ave | Fairfax | Marin | 94930 |  |  | 2006-04-11 | 8:00:00 AM | 2006-04-12 | 3:00:00 AM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Supt | Eric Smith | 2006-04-12 | 415-461-1122 | ericlsmith@sbcglobal.net, | 24HR |  |  | 415-461-1122 | [6 empty] | MarinCountySD1
3160 | 77 | 1 | MarinCountySD1 | 2006-04-12 16:09 | 6000 | 0 | 06-2219 | 2006-04-12 | Mark Molinari |  | Porteous Ave. at Wood Ln. | Fairfax | Marin | 94930 |  |  | 2006-04-11 | 6:00:00 AM | 2006-04-12 | 4:00:00 AM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Supt | Eric Smith | 2006-04-12 | 415-461-1122 | ericlsmith@sbcglobal.net, | 24HR |  |  | 415-461-1122 | [6 empty] | MarinCountySD1
3064 | 74 | 1 | MarinCountySD1 | 2006-03-27 08:49 | 1775 | 0 | 06-1769 | 2006-03-24 | Rafael Zarco | MarinCountySD1 | 234 Magnolia | Larkspur | Marin | 94939 |  |  | 2006-03-24 | 7:19:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | YARD/LAND | No |  | No | Yes | No visable impact |  | Yes | Yes | No | No | No | No | No | Yes | No | 2006-03-27 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MarinCountySD1 | CLEAN OUT |  | INFRASTRUCTURE FAILURE | DEBRIS | BREAKAGE OF COLLECTION SYSTEM | Main line failure | SSO caused by mainline failure. Main to be repaired on 3/27/06 by contractor. Area was cleaned and posted. | Supt | Eric Smith | 2006-03-27 | 4154611122 | ericlsmith@sbcglobal.net, | MAJOR | Eric Smith | SD #1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
3057 | 73 | 1 | MarinCountySD1 | 2006-03-24 09:04 | 100 | 0 |  | 2006-03-24 09:04 |  | -- | 94 Spring Grove | San Anselmo | Marin | 94960 |  |  | 2006-03-22 |  |  |  | Overflow caused by rootsTV for repair on 3-24-06. Posted and cleaned area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supt | Eric Smith | 2006-03-24 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
3028 | 72 | 1 | MarinCountySD1 | 2006-03-17 11:12 | 500 | 0 |  | 2006-03-17 11:12 |  | -- | 96 Hilldale Ave. | San Anselmo | Marin | 94960 |  |  | 2006-03-15 |  |  |  | Removed roots, Grease, and paper from main. TVed for repair to remove sag on 3/17/06. Cleaned area, removed solids | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | CLEAN OUT |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Supt | Eric Smith | 2006-03-17 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
2961 | 71 | 1 | MarinCountySD1 | 2006-03-08 14:05 | 750 | 0 |  | 2006-03-08 14:05 |  | -- | Ledgend @ Butterfield | San Anselmo | Marin | 94960 |  |  | 2006-03-07 |  |  |  | Line was cleaned on 3-1-06 as part of our routine 6 month maintenance program. Misc. debris in main was found in main on 3-7-06. Will TV on 3-9-06 for ness. repairs. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Supt | Eric Smith | 2006-03-08 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
3108 | 70 | 2 | MarinCountySD1 | 2006-03-31 08:10 | 600 | 0 |  | 2006-03-31 08:10 |  | -- | 67 Willow Ave | Fairfax | Marin | 94930 |  |  | 2006-02-24 |  |  |  | Cleaned mainline. cleared away all solids from area | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supt | Eric Smith | 2006-02-24 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
2869 | 69 | 1 | MarinCountySD1 | 2006-02-24 08:59 | 400 | 0 |  | 2006-02-24 08:59 |  | -- | 75 Francis Ave | Larkspur | Marin | 94939 |  |  | 2006-02-18 |  |  |  | Mud from a contractor's drilling rig was accidently released into district main by the contractor, flooding the house at 75 Francis with sewage and mud. All mud and sewage was recovered. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | OTHER | Bathroom fixtures | INFRASTRUCTURE FAILURE | CONSTRUCTION DEBRIS |  |  |  | Supt | Eric Smith | 2006-02-24 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
2598 | 67 | 1 | MarinCountySD1 | 2006-01-11 07:53 | 348 | 0 |  | 2006-01-11 07:53 |  | -- | 254 W. Baltimore | Larkspur | Marin | 94039 |  |  | 2006-01-10 |  |  |  | City of Larkspur broke two private laterals during major storm on 1/1/06 allowing debris into main. laterals have been repaired main has been re-cleaned. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | Supt | Eric Smith | 2006-01-11 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
2492 | 62 | 1 | MarinCountySD1 | 2006-01-04 14:47 | 420 | 0 |  | 2006-01-04 14:47 |  | -- | Diane at William | Larkspur | Marin | 94939 |  |  | 2005-12-31 |  |  |  | Heavy storms, high tides caused flooding in area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | NATURAL DISASTER | --Select None-- |  |  |  | Supt | Eric Smith | 2006-01-04 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
2497 | 64 | 1 | MarinCountySD1 | 2006-01-04 15:05 | 960 | 0 |  | 2006-01-04 15:05 |  | -- | 150 Magnolia Ave | San Anselmo | Marin | 94939 |  |  | 2005-12-31 |  |  |  | Heavy storms, flooding in the areaMost of the sewage flowed back into the clean-out and into the Districts system. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | CLEAN OUT |  | NATURAL DISASTER | --Select None-- |  |  |  | Supt | Eric Smith | 2006-01-04 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
2501 | 65 | 1 | MarinCountySD1 | 2006-01-04 15:12 | 300 | 0 |  | 2006-01-04 15:12 |  | -- | 109 Lagunitas Rd. | Ross | Marin | 94947 |  |  | 2005-12-31 |  |  |  | Heavy storm, high tide in area | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | CLEAN OUT |  | NATURAL DISASTER | --Select None-- |  |  |  | Supt | Eric Smith | 2006-01-04 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
2503 | 66 | 1 | MarinCountySD1 | 2006-01-04 15:23 | 840 | 0 |  | 2006-01-04 15:23 |  | -- | Manor & Sir Francis Drake | Larkspur | Marin | 94939 |  |  | 2005-12-31 |  |  |  | Extreamly heavy storm caused major flooding in the area, cleaned up after storm. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | NATURAL DISASTER | --Select None-- |  |  |  | Supt | Eric Smith | 2006-01-04 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
3262 | 82 | 1 | MarinCountySD1 | 2006-05-02 09:34 | 6000 | 0 | 06-2608 | 2006-05-01 | Todd Lando | MarinCountySD1 | 17 Morningside Dr. | San Anselmo | Marin | 94960 |  |  | 2005-12-31 | 3:30:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | High |  | BUILDING/STRUCTURE | No |  | No | No | None |  | No | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MarinCountySD1 | OTHER | Toilet | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | Informed of the 12-31-05 overflow on 5/1/06. RP stated that he didnt know to call. RP said that his toilet overflowed during the heavy storm for 1 hour at 100 gpm. No evidence of sewage was observed at the time of inspection. House is being remodeled. | Supt | Eric Smith | 2006-05-02 | 4154611122 | ericlsmith@sbcglobal.net, | MAJOR | Eric Smith | SD #1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
2715 | 60 | 3 | MarinCountySD1 | 2006-01-31 14:24 | 480 | 0 |  | 2006-01-31 14:24 |  | -- | 118 Baltimore Ave. | Larkspur | Marin | 94939 |  |  | 2005-12-31 |  |  |  | Extreamly heavy storm caused major flooding in the entire District Flowed into structure. Unknown amount flowed back into the system, some flowed into back yard. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | CLEAN OUT |  | NATURAL DISASTER | --Select None-- |  |  |  | Supt | Eric Smith | 2006-01-04 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
3589 | 68 | 6 | MarinCountySD1 | 2006-06-30 15:09 | 472600 | 0 | 06-0875 | 2005-01-04 | Eric Smith | MarinCountySD1 | 5 Stadium Way | Kentfield | Marin | 94904 |  |  | 2005-12-31 | 6:37:00 PM | [5 empty] | RAINING FOR SEVERAL DAYS | High |  | STREET/CURB & GUTTER | No |  | No | No | No visible impact heavy storm flooding in the area. |  | Yes | Yes | No | No | No | No | Yes | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MarinCountySD1 | OTHER | bathroom fixtures and manholes | INFRASTRUCTURE FAILURE | --Select None-- | PUMP STATION FAILURE | Heavy storm, pump failures due to PG&E brown out | Pump failures were caused by PG&E brown-out. A false signal was sent to pump drives causing equipment to shut down. Contractor has corrected the problem. House at #5 Stadium Way flooded with 4600 gallons of sewage. Approx. 1/2 of which was discharged into street remaining was discharged to land/structure and onto property of 221 McAllister ave. Originally reported as 960 gallons. Determined on 2/9/2006 to be 4600 gallons. Incident was reported about 12 hours after the event had occurred on 12/31/06 2/10/2006. After further investigation, the resident at #5 Stadium Way informed the District on 2/9/06 that the manholes on Stadium Way were overflowing heavily during the storm (reported to the District on 2/9/06) On 2-28-06 Engineers estimated that the total spill was 351000 gallons, discharged to the house at # 5 Stadium Way and surrounding area. Several items have been addressed to ensure that this type of spill does not occur in the future, such as a cell phone back up to the land line alarm system, reprogram/recalibrated electrical equipment, improved design of automatic trip settings, and adding automatic building cooling fans to protect equipment from heat during extreme demands Updated spill volume to 346000 on 6-12-06. Added volume from 5 Stadium Way. Updated volume to 472,600 on 6-29-06. District engineer found three more man holes (12 total) that possibly overflowed. | Supt | Eric Smith | 2006-02-09 | 4154611122 | ericlsmith@sbcglobal.net, | MAJOR | Eric Smith | SD #1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 |  | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
2494 | 63 | 1 | MarinCountySD1 | 2006-01-04 14:55 | 600 | 0 |  | 2006-01-04 14:55 |  | -- | 1165 Butterfield Rd. | San Anselmo | Marin | 94960 |  |  | 2005-12-30 |  |  |  | Heavy storms, flooding in the area, line surcharged | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | CLEAN OUT |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | Supt | Eric Smith | 2006-01-04 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
2266 | 59 | 1 | MarinCountySD1 | 2005-12-19 08:46 | 1400 | 100 | 057275 | 2005-12-19 | Rafael Zarco | marincountysd1 | 10 Terrace Ave. | Kentfield | Marin | 94904 |  |  | 2005-12-17 | 9:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | YARD/LAND | No |  | No | No | None |  | Yes | Yes | No | No | No | No | No | No | No | 2005-12-19 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | marincountysd1 | CLEAN OUT |  | BLOCKAGE | GREASE | --Select None-- | Heavy rain | Unknown start time, RP was away for 24 hrs. Cleared blockage from main, cleaned affected area, removed debris. Main to be TVéd and repaired on 12/19/05 | Supt | Eric Smith | 2005-12-19 | 4154611122 | ericlsmith@sbcglobal.net, | MAJOR | Eric Smith | SD #1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
2176 | 58 | 1 | MarinCountySD1 | 2005-11-28 08:37 | 200 | 0 |  | 2005-11-28 08:37 |  | -- | 325 Madrone | Larkspur | Marin | 94939 |  |  | 2005-11-25 |  |  |  | Mainline has been added to 6 month maintenance program. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Supt | Eric Smith | 2005-11-28 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
1986 | 56 | 1 | MarinCountySD1 | 2005-10-20 08:34 | 10 | 0 |  | 2005-10-20 08:34 |  | -- | 160 Tioga | Greenbrae | Marin | 94939 |  |  | 2005-10-20 |  |  |  | Small drip from pipe uncovered by a contractor. District crew replaced the leaking section. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | PIPE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Supt. | Eric Smith | 2005-10-20 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
2038 | 57 | 1 | MarinCountySD1 | 2005-10-26 08:26 | 10 | 0 |  | 2005-10-26 08:26 |  | -- | 60 Hawthorne | San Anselmo | Marin | 94960 |  |  | 2005-10-20 |  |  |  | Cleaned main, scheduled for repair. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Supt | Eric Smith | 2005-10-26 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
1803 | 55 | 1 | MarinCountySD1 | 2005-09-19 08:08 | 48 | 0 |  | 2005-09-19 08:08 |  | -- | 80 Vista | Kentfield | Marin | 94904 |  |  | 2005-09-15 |  |  |  | Will TV to find problem lateral | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | CLEAN OUT |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Supt. | Eric Smith | 2005-09-19 | 415-461-1122 | ericlsmith@sbcglobal.net, | MINOR
1704 | 54 | 1 | MarinCountySD1 | 2005-08-22 13:48 | 25 | 0 |  | 2005-08-22 13:48 |  | -- | 35 Green Valley Ct. | San Anselmo | Marin | 94960 |  |  | 2005-08-07 |  |  |  | Recovered all of sewage in gutter pan. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supt. | Eric Smith | 2005-08-22 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
1920 | 53 | 2 | MarinCountySD1 | 2005-10-06 08:23 | 36 | 0 |  | 2005-10-06 08:23 |  | -- | 80 Vista Dr. | Kentfield | Marin | 94904 |  |  | 2005-07-23 |  |  |  | Cleaned area, posted signs. Note: Three repairs have been made to this system. Two to main and one to a private lateral. Repairs were done on 12/14/04 | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Supt. | Eric Smith | 2005-07-25 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
1579 | 50 | 3 | MarinCountySD1 | 2005-06-29 11:01 | 13866 | 0 | 05-3826 | 2005-06-27 | Mark Molinary | MarinCountySD1 | Int. of Ardmoore & Marina Vista | Larkspur | Marin | 94939 |  |  | 2005-06-27 | 9:00:00 AM | [5 empty] | SUNNY WEATHER | High |  | STORM DRAIN | No |  | No | Yes | Small Ditch/drainage area was discolored. |  | Yes | Yes | No | No | No | No | No | Yes | No | 2005-06-28 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | MarinCountySD1 | PIPE |  | INFRASTRUCTURE FAILURE | --Select None-- | DAMAGE TO COLLECTION SYSTEM |  | Home owner reported an overflow into a small dranage area next to house. She said that it had been overflowing since 6-23-05 at 9:00. Found that a poorly installed lateral tie in had failed. the Main was leaking into a storm culvert. TVéd main and found leak, dug and repaired. Sample taken on 6-28-05 showed no detectable ammonia | Supt | Eric Smith | 2005-06-28 | 4154611122 | ericlsmith@sbcglobal.net, | MAJOR | Eric Smith | Marin county SD#1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 |  | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
1922 | 51 | 3 | MarinCountySD1 | 2005-10-06 09:10 | 3496 | 0 | 05-3833 | 2005-06-27 | Jeff Yee | MarinCountySD1 | 351 Madrone | Larkspur | Marin | 94939 |  |  | 2005-06-27 | 12:00:00 P | [5 empty] | SUNNY WEATHER | High | Madrone Canyon creek | SURFACE WATER IMPACT | No |  | No | Yes | Discoloration on 6-27-2005, not visible on 6-27-05 |  | Yes | Yes | No | No | No | Yes | Yes | Yes | No | 2005-06-28 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MarinCountySD1 | CLEAN OUT |  | BLOCKAGE | DEBRIS | --Select None-- | Rock | Overflow caused by rock in main. Will TV and evaluate for repair. RP smelled an odor at 5:00pm, heard water at 8:30pm. Called our emergency number at this time. Broke blockage and cleaned area. Posted warning signs. Samples taken on 6-28-05. Samples taken and tested on 6-28-05 showed no detectable ammonia. Originally reported as a total spill of 8550 gallons, spill time from 12:00 to 10:45. Revised to 3496 gallons, total spill time from 5:00pm to 10:45pm. 76 units @ 8 gph X 5.75hrs = 3496 gallons | Supt. | Eric Smith | 2005-06-28 | 415-461-1122 | ericlsmith@sbcglobal.net, | MAJOR | Eric Smith | Marin county SD#1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 |  | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
1921 | 52 | 2 | MarinCountySD1 | 2005-10-06 09:01 | 4400 | 0 | 05-3851 | 2005-06-28 | Mark M. | MarinCountySD1 | 22 Olive | Ross | Marin | 94957 |  |  | 2005-06-25 | 3:00:00 AM | [5 empty] | SUNNY WEATHER | Low |  | STREET/CURB & GUTTER | No |  | No | Yes | None |  | Yes | Yes | No | No | No | No | No | No | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MarinCountySD1 | MANHOLE |  | BLOCKAGE | DEBRIS | --Select None-- |  | Main to be televised and repaired. | Supt | Eric Smith | 2005-06-29 | 415-461-1122 | ericlsmith@sbcglobal.net, | MAJOR | Eric Smith | SD #1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 |  | MarinCountySD1
1543 | 48 | 1 | MarinCountySD1 | 2005-06-17 10:03 | 3075 | 0 | 053623 | 2005-06-16 | Mark Molinari | MarinCountySD1 | 14 Elm Ct. | San Anselmo | Marin | 94960 |  |  | 2005-06-16 | 9:00:00 AM | [5 empty] | RAINY WEATHER | Low |  | YARD/LAND | No |  | No | Yes | None |  | Yes | Yes | No | No | No | No | No | No | No | 2005-06-17 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | MarinCountySD1 | MANHOLE |  | BLOCKAGE | DEBRIS | --Select None-- |  | Not notified by RP for 3 days. Originally reported at 6700 gal, revised to 3075. 5 homes on main. Overflowed for 81 hours 200 gpd X 5 = 3000. 200 / 24 = 8.3 8.3 X 9 = 74.7 Line is being repaired (6-17-2005) | Supt | Eric Smith | 2005-06-17 | 4154611122 | ericlsmith@sbcglobal.net, | MAJOR | Eric Smith | Marin county SD#1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
1558 | 49 | 1 | MarinCountySD1 | 2005-06-24 09:30 | 18375 | 0 | 05-3755 | 2005-06-23 | Jeff Yee | MarinCountySD1 | End of Corte Alegre in easement | Greenbrae | Marin | 94939 |  |  | 2005-06-16 | 9:00:00 AM | [5 empty] | CLOUDY WEATHER | High |  | STORM DRAIN | No |  | No | Yes | None |  | Yes | Yes | Yes | No | No | No | No | No | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | MarinCountySD1 | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS | --Select None-- |  | Overflow was found by District crew. Area resident thought that it might have been overflowing for up to a week. large amounts of rags in main. Area flushed with de-chlorinated water. | Supt | Eric Smith | 2005-06-24 | 4154611122 | ericlsmith@sbcglobal.net, | MAJOR | Eric Smith | Marin county SD#1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 |  | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
1542 | 47 | 1 | MarinCountySD1 | 2005-06-15 14:06 | 40 | 0 |  | 2005-06-15 14:06 |  | -- | 309 Via LaPaz | Greenbrae | Marin | 94939 |  |  | 2005-06-14 |  |  |  | Cleared blockage, removed debris and cleaned area | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Supt | Eric Smith | 2005-06-15 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
1479 | 46 | 1 | MarinCountySD1 | 2005-06-02 10:30 | 50 | 0 |  | 2005-06-02 10:30 |  | -- | 3 Madera Ave | Ross | Marin | 94957 |  |  | 2005-06-01 |  |  |  | During a repair to one of our mains The pipe had a sag, when it was cut, the sewage was released into the trench and soaked into the soil. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | PIPE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Supt | Eric Smith | 2005-06-02 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
1468 | 45 | 1 | MarinCountySD1 | 2005-05-31 11:37 | 100 | 0 |  | 2005-05-31 11:37 |  | -- | 1 Blacklog Rd. | Larkspur | Marin | 94939 |  |  | 2005-05-30 |  |  |  | Mainline has been repaired (5-31-05) Main will be scheduled for rehab. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | PIPE |  | INFRASTRUCTURE FAILURE | DEBRIS |  |  |  | Supt | Eric Smith | 2005-05-31 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
1464 | 43 | 1 | MarinCountySD1 | 2005-05-31 10:04 | 600 | 0 |  | 2005-05-31 10:04 |  | -- | 1 Blacklog Rd. | Larkspur | Marin | 94939 |  |  | 2005-05-29 |  |  |  | Repaired sewer main on 5-31-05 of sewer main Removed as much debris and sewage as possible on 5-29-05. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | PIPE |  | BLOCKAGE | DEBRIS |  |  |  | Supt | Eric Smith | 2005-05-31 | 415-461-1122 | ericlsmith@sbcglobal.net, | MINOR
1466 | 44 | 1 | MarinCountySD1 | 2005-05-31 11:23 | 20 | 0 |  | 2005-05-31 11:23 |  | -- | 412 Geeenfield Ave | San Anselmo | Marin | 94960 |  |  | 2005-05-29 |  |  |  | Blockage was cleared, area cleaned. Added to six month maintenance program. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | CLEAN OUT |  | INFRASTRUCTURE FAILURE | ROOTS |  |  |  | Supt | Eric Smith | 2005-05-31 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
1504 | 42 | 2 | MarinCountySD1 | 2005-06-09 15:47 | 1500 | 0 | 05-3134 | 2005-05-25 | Jeff Yee | MarinCountySD1 | 28 Black log Rd. | Larkspur | Marin | 94939 |  |  | 2005-05-25 | 9:30:00 AM | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | Yes | No visable impact. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | MarinCountySD1 | PIPE |  | INFRASTRUCTURE FAILURE | DEBRIS | DAMAGE TO COLLECTION SYSTEM | Main line failed | Mainline failed, able to clear. Will be repaired ASAP. Main line was repaired on 5-31-05 | Supt | Eric Smith | 2005-05-26 | 4154611122 | ericlsmith@sbcglobal.net, | MAJOR | Eric Smith | Marin county SD#1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 |  | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
1449 | 41 | 1 | MarinCountySD1 | 2005-05-24 11:55 | 900 | 0 |  | 2005-05-24 11:55 |  | -- | 35 Forrest Ave | San Anselmo | Marin | 94930 |  |  | 2005-05-22 |  |  |  | Broke blockage, cleaned area. Re-cleaned main on 5-23-05 | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Supt | Eric Smith | 2005-05-24 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
1402 | 40 | 1 | MarinCountySD1 | 2005-05-16 08:36 | 120000 | 0 | 05-2879 | 2005-05-14 | Mark Molinari | MarinCountySD1 | 237 Southridgewood | Kentfield | Marin | 94904 |  |  | 2005-05-14 | 12:00:00 P | [5 empty] | RAINY WEATHER | Low |  | YARD/LAND | Yes | None | No | Yes | None |  | Yes | Yes | No | No | No | No | No | No | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | MarinCountySD1 | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- |  | Unknown when overflow started. Mainline may have been overflowing as long as a month. Reporting party reported that she has smelled an odor for about a month. Cleaned area and posted warning signs. Will recheck in six months to evaluate condition. | Supt. | Eric Smith | 2005-05-16 | 4154611122 | ericlsmith@sbcglobal.net, | MAJOR | Eric Smith | Marin county SD#1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 |  | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
1391 | 39 | 1 | MarinCountySD1 | 2005-05-12 08:56 | 75 | 0 |  | 2005-05-12 08:56 |  | -- | 444 Scenic Rd | Fairfax | Marin | 94930 |  |  | 2005-05-11 |  |  |  | Cleaned main line, cleaned area and removed debris | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supt | Eric Smith | 2005-05-12 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
1307 | 38 | 1 | MarinCountySD1 | 2005-04-21 13:42 | 5 | 0 |  | 2005-04-21 13:42 |  | -- | 25 Rock Rd. | Kentfield | Marin | 94904 |  |  | 2005-04-20 |  |  |  | minor over flow, seeping from manhole cover cleaned main and removed debris from area | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Supt | Eric Smith | 2005-04-21 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
1305 | 37 | 1 | MarinCountySD1 | 2005-04-21 13:38 | 3000 | 0 | 05-2350 | 2005-04-21 | Jeff Yee | MarinCountySD1 | 1 Oak Springs | San Anselmo | Marin | 94960 |  |  | 2005-04-19 | 7:32:00 AM | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | Yes | No impact |  | Yes | Yes | No | No | No | No | No | No | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | MarinCountySD1 | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- |  | Cleared blockage, cleaned area | Supt | Eric Smith | 2005-04-21 | 4154611122 | ericlsmith@sbcglobal.net, | MAJOR | Eric Smith | Marin county SD#1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 |  | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
1291 | 36 | 1 | MarinCountySD1 | 2005-04-18 10:37 | 250 | 0 |  | 2005-04-18 10:37 |  | -- | 1 Rivera Ave | San Anselmo | Marin | 94960 |  |  | 2005-04-15 |  |  |  | Cleared blockage, cleaned area. No visual impact to creek | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supt | Eric Smith | 2005-04-18 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
1288 | 35 | 1 | MarinCountySD1 | 2005-04-18 10:25 | 7200 | 0 | 05-2177 | 2005-04-11 | Mark Molinari | MarinCountySD1 | 50 Ridge Crest Rd. | Kentfield | Marin | 94904 |  |  | 2005-04-11 | 10:00:00 A | [5 empty] | SUNNY WEATHER | Low | Corte Madera creek | SURFACE WATER IMPACT | No |  | No | Yes | No visual impact or damage to creek |  | Yes | Yes | No | No | No | Yes | Yes | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | MarinCountySD1 | MANHOLE |  | BLOCKAGE | --Select None-- | --Select None-- |  | Overflow was not reported by homeowner until Monday morning. Crew cleared blockage, cleaned debris, and posted area. Samples returned <0.1 | Supt. | Eric Smith | 2005-04-18 | 4154611122 | ericlsmith@sbcglobal.net, | MAJOR | Eric Smith | Marin county SD#1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 |  | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
1210 | 34 | 2 | MarinCountySD1 | 2005-03-23 10:48 | 2625 | 0 | 05-1800 | 2005-03-22 | SD#1 | MarinCountySD1 | 241 The Alameda | San Anselmo | Marin | 94960 |  |  | 2005-03-22 | 10:00:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Low | Sleepy Hollow Creek | SURFACE WATER IMPACT | No | 0.3 ppm downstream 0.3 ppm upstream | No | No | No visible impact, heavy flow due to rain. Samples tested the same upstream as downstream of the spill site. |  | Yes | Yes | No | No | No | Yes | Yes | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | MarinCountySD1 | MANHOLE | Blockage was due to construction debris in the siphon from a rh-hab project. The contractor failed to keep debris from entering the main. Rock and wood was found to have restricted the flow, causing the overflow during heavy rains. The ccontractor had the main cleaned. | BLOCKAGE | CONSTRUCTION DEBRIS | --Select None-- |  | Blockage was due to construction debris in the siphon from a rh-hab project. The contractor failed to keep debris from entering the main, causeing a restriction during high flow in rain. Notified Marin Env Health, down stream school and posted the area. | Supt | Eric Smith | 2005-03-22 | 415-461-1122 | ericlsmith@sbcglobal.net, | MAJOR | Eric Smith | MarinCountySD1 | 415-461-1122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939 | KJ Woods Construction Co. Inc. | MarinCountySD1 | 415-759-0506 |  | 2625 Judah St. #2 | San Francisco | San Francisco | 94122
1163 | 33 | 1 | MarinCountySD1 | 2005-03-10 14:44 | 60 | 0 |  | 2005-03-10 14:44 |  | -- | 375 Vista Grande | Larkspur | Marin | 94939 |  |  | 2005-03-09 |  |  |  | Cleared main line, cleaned and posted area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supt | Eric Smith | 2005-03-10 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
1107 | 31 | 1 | MarinCountySD1 | 2005-03-03 09:58 | 400 | 0 |  | 2005-03-03 09:58 |  | -- | 497 Scenic Ave. | San Anselmo | Marin | 94960 |  |  | 2005-03-02 |  |  |  | Removed Blockage, cleaned area, posted creek area. No visible impact to the creek. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Supt. | Eric Smith | 2005-03-03 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
1099 | 30 | 1 | MarinCountySD1 | 2005-03-01 10:03 | 100 | 0 |  | 2005-03-01 10:03 |  | -- | 4 Sherman | Fairfax | Marin | 944930 |  |  | 2005-02-28 |  |  |  | Whencrew arrived on site, there were only traces of an overflow. Cleaned main, broke blockage, Cleaned area. It is possable that sewage made it into the Fairfax creek, no signs of any impact. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supt | Eric Smith | 2005-03-01 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
1088 | 29 | 2 | MarinCountySD1 | 2005-02-25 12:58 | 250 | 0 |  | 2005-02-25 12:58 |  | -- | 3 Laurel Grove | Kentfield | Marin | 94904 |  |  | 2005-02-24 |  |  |  | Unknown cause, line to be TVed on 2-25-05 to determine cause Will be repaired ASAP On 2-25-05 a broken lateral was located which was causing the District main to block. Owner was notified and will repair | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Supt | Eric Smith | 2005-02-25 | 4154611122 | ericlsmith@sbcglobal.net | MINOR
1072 | 28 | 1 | MarinCountySD1 | 2005-02-22 09:46 | 425 | 0 |  | 2005-02-22 09:46 |  | -- | 671 Magnolia | Larkspur | Marin | 94939 |  |  | 2005-02-17 |  |  |  | Unable to determine the cause of the blockage. Cleaned the area and posted warniung signs. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Supt. | Eric Smith | 2005-02-22 | 4154611122 | ericlsmith@sbcglobal.net | MINOR
965 | 27 | 1 | MarinCountySD1 | 2005-02-04 09:18 | 50 | 0 |  | 2005-02-04 09:18 |  | -- | 400 Bolinas Rd. | Fairfax | Marin | 94930 |  |  | 2005-02-03 |  |  |  | The pipe was not leaking when crew arrived, but showed signs that it had been. This pipe was joint-grouted last summer, District crews are working to locate the problem. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | PIPE |  | CAUSE UNKNOWN | --Select None-- |  |  |  | Supt | Eric Smith | 2005-02-04 | 4154611122 | ericlsmith@sbcglobal.net | MINOR
963 | 26 | 2 | MarinCountySD1 | 2005-02-04 09:13 | 90 | 0 |  | 2005-02-04 09:13 |  | -- | 1117 Sir Francis Drake Blvd. | Kentfield | Marin | 94904 |  |  | 2005-02-03 |  |  |  | Blockage was caused by towels and roots. Area was cleaned by District crew. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Supt | Eric Smith | 2005-02-04 | 4154611122 | ericlsmith@sbcglobal.net | MINOR
931 | 25 | 1 | MarinCountySD1 | 2005-01-31 14:50 | 2400 | 0 | 05-0717 | 2005-01-29 | Jeff Yee | MarinCountySD1 | 45 Hatzic Ct. | Larkspur | Marin | 94939 |  |  | 2005-01-29 | 8:00:00 AM | [5 empty] | SUNNY WEATHER | Low |  | YARD/LAND | No |  | No | No | Sewage did not reach a water way, no damage |  | Yes | Yes | No | No | No | No | No | No | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | MarinCountySD1 | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- |  | Maine line will be re cleaned in six-months to evaluate. maintenance will be scheduled as necessary. | Supt | Eric Smith | 2005-01-31 | 4154611122 | ericlsmith@sbcglobal.net | MAJOR | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939 |  | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
925 | 24 | 1 | MarinCountySD1 | 2005-01-28 13:05 | 500 | 0 |  | 2005-01-28 13:05 |  | -- | 80 Bayview | Ross | Marin | 94957 |  |  | 2005-01-27 |  |  |  | Unable to tell exactly what caused the blockage. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Supt | Eric Smith | 2005-01-28 | 4154611122 | ericlsmith@sbcglobal.net | MINOR
916 | 23 | 1 | MarinCountySD1 | 2005-01-26 10:11 | 4200 | 0 | 05-0620 | 2005-01-26 | Noel Sandoval | MarinCountySD1 | 66 Porteous Ave | Fairfax | Marin | 94930 |  |  | 2005-01-25 | 3:10:00 AM | [5 empty] | RAINY WEATHER | Low | Storm Drain, Fairfax Creek | STREET/CURB & GUTTER | No |  | No | No | No visual damage |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | MarinCountySD1 | OTHER | Repair trench failed causing line to back up and overflow | INFRASTRUCTURE FAILURE | CONSTRUCTION DEBRIS | DAMAGE TO COLLECTION SYSTEM | Repair trench failed causing line to back up and overflow | Repair trench failed causing line to back up and overflow. Line was cleared by a responding crew. Area was cleared of debris Line will be repaired on 1/26/05 Notified Marin Co. Env. Health on 1/26/05 | Supt | Eric Smith | 2005-01-26 | 4154611122 | ericlsmith@sbcglobal.net | MAJOR | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939 |  | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
914 | 22 | 2 | MarinCountySD1 | 2005-01-25 15:57 | 6875 | 0 | 05-0551 | 2005-01-21 | Mike Addy | marincountysd1 | 18 South Ridgewood | Kentwoodlands | Marin | 94904 |  |  | 2005-01-21 | 9:00:00 AM | [5 empty] | CLOUDY WEATHER | Low |  | SURFACE WATER IMPACT | No |  | No | Yes | No visible damage to drainage to drainage creek, water was flowing. |  | Yes | Yes | No | No | No | Yes | Yes | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | marincountysd1 | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- |  | Found grease in line, add to 6 month maintenance from 1 year maintenance schedule. Originally reported as a spill of 33,000 gallons. Counted units on mainline, found 66. 66 * 250gpd = 16500 / 24 = 687.5. 687.5 * 10 hrs = 6875 gallons spilled. Cleaned area of all solids. Samples were taken at the spill site and down stream from spill site, no detectable ammonia was found. | Supt | Eric Smith | 2005-01-24 | 4154611122 | ericlsmith@sbcglobal.net | MAJOR | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939 |  | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
827 | 21 | 1 | MarinCountySD1 | 2005-01-12 08:48 | 5 | 0 |  | 2005-01-12 08:48 |  | -- | 810 Sir Francis Drake Blvd. | Kentfield | Marin | 94904 |  |  | 2005-01-11 |  |  |  | Slow running main, cleared problem. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | marincountysd1 | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supt | Eric Smith | 2005-01-12 | 4154611122 | ericlsmith@sbcglobal.net | MINOR
1021 | 18 | 2 | MarinCountySD1 | 2005-02-14 15:26 | 9000 | 300 | 050074 | 2005-01-04 | Noel Sandoval | MarinCountySD1 | 34 Corte Morada | Green brae | Marin | 94939 |  |  | 2005-01-02 | 12:00:00 P | [5 empty] | SUNNY WEATHER | Low |  | YARD/LAND | No |  | No | Yes | Did not enter a waterway, no damage |  | Yes | Yes | No | No | No | No | No | No | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | MarinCountySD1 | CLEAN OUT | Failed main line allowed rock to block main | INFRASTRUCTURE FAILURE | --Select None-- | --Select None-- | Failed main line allowed rock to block main | Failed main line allowed rock to block main. Main was TV'ed, dug and repaired. Cleaned area. | Supt | Eric Smith | 2005-01-05 | 4154611122 | ericlsmith@sbcglobal.net | MAJOR | Eric Smith | Marin county SD#1 | 4154611122 |  | 2000 Larkspur landing Cir. | Larkspur | Marin | 94939 |  | marincountysd1
707 | 15 | 1 | MarinCountySD1 | 2005-01-03 09:51 | 600 | 0 |  | 2005-01-03 09:51 |  | -- | 3 Sunrise | Larkspur | Marin | 94939 |  |  | 2004-12-31 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | marincountysd1 | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supt | Eric Smith | 2005-01-03 | 4154611122 | ericlsmith@sbcglobal.net | MINOR
756 | 17 | 2 | MarinCountySD1 | 2005-01-05 07:27 | 8640 | 0 | 050048 | 2005-01-03 | Eric Smith | marincountysd1 | 65 Corte Amado | Greenbrae | Marin | 94939 |  |  | 2004-12-31 | 11:00:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | YARD/LAND | No |  | No | Yes | No damage |  | Yes | Yes | No | No | No | No | No | No | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | marincountysd1 | MANHOLE |  | BLOCKAGE | DEBRIS | --Select None-- |  |  | Supt | Eric Smith | 2005-01-03 | 4154611122 | ericlsmith@sbcglobal.net | MAJOR | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939 |  | marincountysd1 | 4154611122
633 | 5 | 1 | MarinCountySD1 | 2004-12-27 13:23 | 4500 | 0 | 046778 | 2004-12-27 | Eric Smith |  | Sir Francis Drake at Elm | Kentfield | Marin | 94939 |  |  | 2004-12-27 | 8:30:00 AM | 2004-12-27 | 9:30:00 AM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | sUPT | Eric Smith | 2004-12-27 | 4154611122 | ericlsmith@sbcglobal.net | 24HR |  |  | 4154611122 | [6 empty] | marincountysd1
671 | 14 | 2 | MarinCountySD1 | 2004-12-29 09:00 | 3000 | 0 | 046820 | 2004-12-28 | Eric Smith | marincountysd1 | 106 Sycamore ave | San Anselmo | marin | 94960 |  |  | 2004-12-27 | 9:45:00 AM | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | No | Note: Had overflowed, crew did not observe it. flow rate is an unseen estimate |  | No | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | marincountysd1 | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- | Extreamly heavy rain, over 6" | Heavy rain caused system to surcharge | Supt | Eric Smith | 2004-12-28 | 4154611122 | ericlsmith@sbcglobal.net | MAJOR | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939 |  | marincountysd1 | 4154611122 |  | 2000 Larkspur landing circle | Larkspur | Marin | 94939
674 | 13 | 2 | MarinCountySD1 | 2004-12-29 10:53 | 22500 | 0 | 046792 | 2004-12-27 | Eric Smith | marincountysd1 | San Anselmo ave at Scenic | San Anselmo | marin | 94960 |  |  | 2004-12-27 | 5:30:00 AM | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | No | heavy rain, no evidence in creek, high flow |  | No | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | marincountysd1 | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- | Heavy rain | Heavy rain surcharged system. Cleaned area of all solids after the event. | Supt | Eric Smith | 2004-12-29 | 4154611122 | ericlsmith@sbcglobal.net | MAJOR | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939 |  | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939
676 | 11 | 2 | MarinCountySD1 | 2004-12-29 11:12 | 3000 | 0 | 04-6807 | 2004-12-27 | Noel Sandoval | marincountysd1 | William at Diane | Larkspur | marin | 94939 |  |  | 2004-12-27 | 11:00:00 A | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | No | No evidence in waterway. |  | No | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | marincountysd1 | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- | Heavy rain |  | Supt | Eric Smith | 2004-12-27 | 4154611122 | ericlsmith@sbcglobal.net | MAJOR | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939 |  | marincountysd1 | 4154611122
678 | 9 | 2 | MarinCountySD1 | 2004-12-29 13:08 | 4800 | 0 | 046795 | 2004-12-27 | Jeff Yee | marincountysd1 | 11 willow ave | Larkspur | marin | 94939 |  |  | 2004-12-27 | 8:00:00 AM | [5 empty] | RAINY WEATHER | Low |  | YARD/LAND | No |  | No | No | no evidence of damage to waterway |  | No | Yes | Yes | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | marincountysd1 | CLEAN OUT |  | BLOCKAGE | DEBRIS | --Select None-- |  | Blockage in main line caused clean to overflow. cleaned outside of house, used disinfectant to clean interor crawl space of house (minor). Some amount soaked in ground, amounnt unknown. | Supt | Eric Smith | 2004-12-27 | 4154611122 | ericlsmith@sbcglobal.net | MAJOR | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939 |  | marincountysd1 | 4154611122
1023 | 8 | 2 | MarinCountySD1 | 2005-02-14 15:54 | 43875 | 0 | 046791 | 2004-12-27 | Jeff Yee | MarinCountySD1 | 730 San Anselmo Ave. | San Anselmo | marin | 94960 |  |  | 2004-12-27 | 3:46:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | Heavy rains, no visible damage |  | No | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | MarinCountySD1 | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- | Heavy rain | Heavy rain, surcharged system | Supt | Eric Smith | 2004-12-27 | 4154611122 | ericlsmith@sbcglobal.net | MAJOR | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 |  | marincountysd1
679 | 10 | 3 | MarinCountySD1 | 2004-12-29 13:15 | 9375 | 0 | 046793 | 2004-12-27 | Eric Smith | marincountysd1 | 38 Cornell | Larkspur | marin | 94939 |  |  | 2004-12-27 | 7:25:00 AM | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | No | No evidence in waterway |  | No | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | marincountysd1 | MANHOLE |  | INFRASTRUCTURE FAILURE | --Select None-- | --Select None-- | Heavy rain | Heavy rain surcharged the system. Contractor working on a Dist. owned pump station failed to provide proper sized standby pumping equipment. this has been corrected by contractor. Cleaned area after event | Supt | Eric Smith | 2004-12-27 | 4154611122 | ericlsmith@sbcglobal.net | MAJOR | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939 | Michael Paul Const. | marincountysd1 | 707-769-1006 |  | 1200 Casa Grande rd. | Petaluma | Sonoma | 94954
680 | 12 | 3 | MarinCountySD1 | 2004-12-29 13:17 | 20250 | 0 | 046796 | 2004-12-27 | Eric Smith | marincountysd1 | Ward St | Larkspur | Marin | 94939 |  |  | 2004-12-27 | 8:30:00 AM | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | No | No evidence in water, high flows due to rains. |  | No | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | marincountysd1 | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- | Heavy rain | Overflow due to heavy rain. Cleaned area after event. No evidence in waterway. | Supt | Eric Smith | 2004-12-27 | 4154611122 | ericlsmith@sbcglobal.net | MAJOR | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur landing Circle | Larkspur | marin | 94939 | Michael Paul Const. | marincountysd1 | 707-769-1006 |  | 1200 Casa Grande rd. | Petaluma | Sonoma | 94954
1022 | 6 | 3 | MarinCountySD1 | 2005-02-14 15:41 | 2625 | 0 | 046789 | 2004-12-27 | Eric Smith | MarinCountySD1 | 2090 Sir Francis Drake | Fairfax | Marin | 94930 |  |  | 2004-12-27 | 9:45:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | Heavy rain, no visible damage |  | Yes | Yes | No | No | No | No | No | No | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | MarinCountySD1 | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- |  | Main line will be cleaned every six months to prevent future problems. | Supt | Eric Smith | 2004-12-27 | 4154611122 | ericlsmith@sbcglobal.net | MAJOR | Eric Smith | Marin county SD#1 | 4154611122 |  | 2000 Larkspur Landing Cir | Larkspur | Marin | 94939 |  | marincountysd1
705 | 7 | 2 | MarinCountySD1 | 2005-01-03 09:45 | 15080 | 200 | 046747 | 2004-12-24 | Jeff Yee | marincountysd1 | 2601 Larkspur Landing Circle | Larkspur | Marin | 94939 |  |  | 2004-12-24 | 9:30:00 AM | [5 empty] | CLOUDY WEATHER | Low |  | STORM DRAIN | No |  | No | No | No visable damage |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | marincountysd1 | MANHOLE | Exact cause unknown. TVed main, found a hole in the pipe. Will repair the week of 1-3-05 | BLOCKAGE | DEBRIS | --Select None-- |  | Originally reported by operator as a 720,000 gallon spill. There are 208 residential units on this system. 208 units at 250gpd = 52,000 gal. X 29% (7hrs) = 15080 gallons. | Supt | Eric Smith | 2004-12-27 | 4154611122 | ericlsmith@sbcglobal.net | MAJOR | Eric Smith | marincountysd1 | 4154611122 |  | 2000 Larkspur Landing Circle | Larkspur | Marin | 94939 |  | marincountysd1 | 4154611122
540 | 4 | 1 | MarinCountySD1 | 2004-12-14 14:20 | 90 | 0 |  | 2004-12-14 14:20 |  | -- | 80 Vista | Kentfield | Marin | 94939 |  |  | 2004-12-13 |  |  |  | performed two repairs on mainline, unable to pinpoint entry point of debris | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | marincountysd1 | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Supt | Eric Smith | 2004-12-14 | 4154611122 |  | MINOR
1123 | 32 | 1 | MarinCountySD1 | 2005-03-07 15:32 | 600 | 0 |  | 2005-03-07 15:32 |  | -- | 80 Vista | Kentfield | Marin | 94904 |  |  | 2004-12-13 |  |  |  | Blockage was due to rock / dirt from a failed lateral. Lateral was repaired 12-13-2004 by SD#1 crew. Originally reported 12-13-04, resubmitted in correct form 3-7-2005 | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD1 | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Supt. | Eric Smith | 2005-03-07 | 4154611122 | ericlsmith@sbcglobal.net, | MINOR
476 | 1 | 2 | MarinCountySD1 | 2004-12-10 08:24 | 4500 | 0 | 04-6428 | 2004-12-09 | Eric Smith | marincountysd1 | 36 Cornell | Larkspur | Marin | 94939 |  |  | 2004-12-08 | 7:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | no visual damage, heavy rain. |  | Yes | No | No | No | No | No | No | No | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | marincountysd1 | MANHOLE | Tempoary pumping system installed by a contractor failed to keep up with heavy storm flow. a fourth pump was installed to correct the problem. | INFRASTRUCTURE FAILURE | --Select None-- | --Select None-- |  | Tempoary pumping system installed by a contractor failed to keep up with heavy storm flow. a fourth pump was installed to correct the problem. | Supt. | Eric Smith | 2004-12-09 | 4154611122 |  | MAJOR | Eric Smith | Sanitary Dist.#1 | 14154611122 |  | 2000 Larkspur Landinng Cir. | Larkspur | Marin | 94939 | Michael Paul Co. | marincountysd1 | 415-457-2877 |  | 1200 Casa Grande Rd. | Petaluma | Sonoma | 94954
5123 | 39 | 1 | MarinCountySD2 | 2007-04-23 11:32 | 30 | 0 |  | 2007-04-23 11:32 |  | -- | #10 lupine | Corte Madera | Marin | 94925 |  |  | 2007-04-20 |  |  |  | Line was opened by mainline rtodder. Upon TV Inspection a break in the sewer line was discovered.The following day a repair crew came in and replaced 18ft. of sewerline | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | PIPE |  | BLOCKAGE | ROOTS |  |  |  | Field Supervisor | Larry Carnashan | 2007-04-23 | 415-717-6492
5051 | 38 | 2 | MarinCountySD2 | 2007-04-09 05:51 | 30 | 0 |  | 2007-04-09 05:51 |  | -- | 355 Willow ave | Corte Madera | Marin | 94925 |  |  | 2007-04-03 |  |  |  | Home owner's cleanout was overflowing, so we ran our main line in front of the house. We cleared the line with a power snake. On 4-4-07 we TV'd our mainline and found the line still had a lot of gravel. So on 4-5-07 we vactored again and did another TV inspection and found multiple fractures and offset joints. So DPW replaced 12 ft. of sewer line. On 4-6-07 a Contractor was brought in the replace over 80 ft. of this section of sewer line. They should be completed by 4-10-07 | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | INFRASTRUCTURE FAILURE | -- Select One -- |  | Private Clean-out |  | Field Supervisor | Larry Carnahan | 2007-04-06 | 415-717-6492
4905 | 37 | 1 | MarinCountySD2 | 2007-03-13 06:26 | 25 | 0 |  | 2007-03-13 06:26 |  | -- | #2 Brich | Corte Madera | Marin | 94925 |  |  | 2007-03-12 |  |  |  | Line was ran W/ power snake and cleared. Line will be run again toady and the clean out repaired | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Field Supervisor | Larry Carnahan | 2007-03-13 | 415-717-6492
4850 | 36 | 1 | MarinCountySD2 | 2007-03-01 14:56 | 250 | 0 |  | 2007-03-01 14:56 |  | -- | 113 Privateer Dr. | Corte Madera | Marin | 94925 |  |  | 2007-02-28 |  |  |  | Spill was from a manhole Q-80. We ran the line from Q-79 to Q-69 With Jetrodder and opened line. We also ran line with main line rodder and found a little paper debris. We then cleaned storm drain lines from Q-74 to Q-67, a total of 567 feet and recovered a total of 2300 gals from storm drain | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Field Supervisor | Larry Carnahan | 2007-03-01 | 415-717-6492
4825 | 35 | 1 | MarinCountySD2 | 2007-02-26 15:15 | 200 | 0 |  | 2007-02-26 15:15 |  | -- | 28 Madera | Corte Madera | Marin | 94925 |  |  | 2007-02-25 |  |  |  | Spill orginated from a manhole in a grassy lawn area and percolated thru the grass to the curb where it was completely contained inside the curb with a earthen dam. The line was cleared and the area was vacumed clean with the vactor and debris was returned to the sanitary sewer | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Field Supervisor | Larry Carnahan | 2007-02-26 | 415-717-6492
4768 | 34 | 1 | MarinCountySD2 | 2007-02-15 15:31 | 10 | 0 |  | 2007-02-15 15:31 |  | -- | 29 Tradewind` | Corte Madera | Marin | 94925 |  |  | 2007-02-14 |  |  |  | Clean out at 29 tradewind had overflowed on the sidewalk. Line was opened with a power snake and TV'ed and found a piece of construction debris was found in the lateral and removed. site was Vactored clean. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Field Supervisor | Larry Carnahan | 2007-02-15 | 415-717-6492
4540 | 33 | 1 | MarinCountySD2 | 2007-01-17 18:16 | 600 | 0 |  | 2007-01-17 18:16 |  | -- | 15 Koch Rd. | Corte Madera | Marin | 94925 |  |  | 2007-01-10 |  |  |  | Manhole P-20 overflowed due to root blockage. The spill ran into the private storm drain system at the 15 Kock Rd. We contacted the managers of the industrial park to shut down the storm water ejector pumps located on their property so that we could contain the spill. However before they could respond the ejector pump came on and placed aprox. 300 gals. of highly diluted sewage into San Clemente Creek. The Town controls the levels in this creek as it is part of our flood control system. On this day, the flood control stations were in low winter mode, so the water level in the creek was at a bare minimum and the flood gate to the bay was closed. With this discharge into the creek, we turned off our flood control pump station to contain the spill. We rented two 4’’ trash pumps rated at 600 GPM. Pumping for 5.5 hrs, we were able to pump over 145,000 gals. into the sanitary sewer. We completely lowered that section of the creek. We also pumped out the wet well of the industrial park with a sewer pumper truck and flushed their storm drain system, removing over 2,000 gal from their wet well. In conclusion, at the end of the day , the SSO was completely contained and recovered. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Field Supervisor | Larry Carnahan | 2007-01-17 | 415-717-6492
4147 | 31 | 1 | MarinCountySD2 | 2006-11-22 12:54 | 300 | 0 |  | 2006-11-22 12:54 |  | -- | 461 Chapman | Corte Madera | Marin | 94925 |  |  | 2006-11-17 |  |  |  | Clear sewage was trapped in gutter with earthen dam and was vacumed up with vactor. Line was cleared with Jet Rodder with Wart Hog nozzle and was later run with main line auger on 11/21/06 | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Field Supervisor | Larry Carnahan | 2006-11-22 | 415-717-6492
4099 | 30 | 1 | MarinCountySD2 | 2006-11-14 07:53 | 250 | 0 |  | 2006-11-14 07:53 |  | -- | 24 Grove | Corte Madera | Marin | 94925 |  |  | 2006-11-12 |  |  |  | Blockage was caused by massive amounts of paper towel and diapers. Spill was captured in storm drain and vactored up. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Field Supervisor | Larry Carnahan | 2006-11-14 | 414-717-6492 | dmontero@ci.corte-madera.ca.us, | MINOR
4097 | 29 | 1 | MarinCountySD2 | 2006-11-13 16:18 | 150 | 0 | 06-6727 | 2006-11-13 | Larry Carnahan | MarinCountySD2 | 100 Madera Del Presidio | Corte Madera | Marin | 92925 | 3755'03.64 | 12230'3090 | 2006-11-11 | 11:30:00 A | [5 empty] | CLOUDY WEATHER | Low |  | STORM DRAIN | No |  | No | No | Sewage coming out of manhole was clear. no sight of Toilet paper |  | Yes | Yes | No | No | No | Yes | No | Yes | No | 2006-11-13 | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MarinCountySD2 | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- |  | Staff had fast reponse to this spill and cleared the blockage with minimal spillage but was ignorant to the fact of reporting and also keeping what sewage had gotton into the creek contained so that it would not have reached the bay waters. Had he contacted his supervisor, the sewage would have been contained and it would have been reported in a timely manner, however since the sewage had run thru the pump station and out the outfall, we have done coliform sampling at 4 location: spill site, 150' upstream and downstream and also at the pump station outfall.Due to the fact that there is a tremendous amount of runoff from current storms in the area, the water sample results showed zero ammonia. Coliform test were not performed on the samples due to the high runoff in the creek. | Field Supervisor | Larry Carnahan | 2006-11-13 | 415-717-6492 | dmontero@ci.corte-madera.ca.us, | MAJOR | Dave Montero | MarinCountySD2 | 415-927-5057 |  | 233 Tamalpais Drive | Corte Madera | Marin | 94925 | David Montero | Marin County SD2 | 415-927-5057 |  | PO Box 159 | Corte Madera | Marin | 94925
4096 | 28 | 1 | MarinCountySD2 | 2006-11-09 14:44 | 100 | 0 |  | 2006-11-09 14:44 |  | -- | 181 Summit | Corte Madera | Marin | 94925 |  |  | 2006-11-08 |  |  |  | Wet soil around cleanout. Line was rodded, stoppage was cleared and line was opened. Area was cleaned and debris was bagged | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Field Supervisor | Larry Carnahan | 2006-11-09 | 415-717-6492 | dmontero@ci.corte-madera.ca.us, | MINOR
4023 | 27 | 2 | MarinCountySD2 | 2006-10-24 09:26 | 1500 | 0 | 06-6290 | 2006-10-23 | David Montero | MarinCountySD2 | Paradise Drive & Antilles Way, Tiburon | Tiburon | Marin | 94920 |  |  | 2006-10-21 | 11:00:00 A | [5 empty] | SUNNY WEATHER | Low | S.F. Bay | STORM DRAIN | No |  | No | No | No evidence of sewage. Water was clear. |  | Yes | Yes | No | No | No | Yes | Yes | Yes | No | 2006-10-24 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MarinCountySD2 | MANHOLE |  | BLOCKAGE | GREASE | DAMAGE TO COLLECTION SYSTEM |  | The SSO occurred at 2300 10/21/06. I did not hear about it until 0900 10/23/06 when Roto-Rooter requested I pay their bill. Upon inspection of site, we took water samples where the spill ended up which was SF Bay. Preliminary results from the lab show no ammonia but a full test result will be to me this morning. Staff swept the curb at the site and inspected the storm drain and found no evidence of sewage in catch basin. Today we are doing maintenance on the sewer main which will consist of using a vactor and doing a complete cleaning of area. | DPW Superintendent | David Montero | 2006-10-23 | 415-927-5069 | dmontero@ci.corte-madera.ca.us, | MAJOR | Dave Montero | MarinCountySD2 | 415-927-5057 |  | 233 Tamalpais Drive | Corte Madera | Marin | 94925 | David Montero | MarinCountySD2 | 415-927-5057 |  | 233 Tamalpais Drive | Corte Madera | Marin | 94925
3962 | 26 | 1 | MarinCountySD2 | 2006-10-03 13:40 | 300 | 0 |  | 2006-10-03 13:40 |  | -- | #2 Fairview | Corte Madera | Marin | 94925 |  |  | 2006-09-29 |  |  |  | Small amount of roots & grease , but a large amount of paper towels and diapers. After, line was TV'ed and roots were found and they were cleaned with a main line auger | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Field supervisor | Larry Carnahan | 2006-10-03 | 415-7176492 | dmontero@ci.corte-madera.ca.us, | MINOR
3901 | 25 | 2 | MarinCountySD2 | 2006-09-19 15:35 | 60 | 0 |  | 2006-09-19 15:35 |  | -- | 459 Montecito Ave | Corte Madera | Marin | 94925 |  |  | 2006-09-19 |  |  |  | Dpw during maintenance observed an SSO at N-5 of Sanitary map. DPW noticed wet dirt around the cleanout. No more sewage was coming out of the cleanout at the time the cap was placed back onto the cleanout to prevent further spillage. Roy's Sewer Service cleraned the sewer line with the Rodder machine and removed small amount of roots. The spill was contained within 5 feet of the cleanout.Area was clean by reomving the spoiled dirt. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Field Supervisor | Wes Sitchler | 2006-09-19 | 415-927-5057 | dmontero@ci.corte-madera.ca.us, | MINOR
3877 | 24 | 1 | MarinCountySD2 | 2006-09-14 08:26 | 60 | 0 |  | 2006-09-14 08:26 |  | -- | 44 Alta Way | Corte Madera | Marin | 94925 |  |  | 2006-09-13 |  |  |  | SD #2 responded to a SSO at 44 Alta WAy. Upon arrival there was very little clear sewage coming from the manhole. SD #2 ran the line with Jet Vactor truck and broke thru the stoppage and repetely ran line till it was clean. Then washed down street and gutter and vacumed gutter to remove all liquid, so that it didnt reach the storm drain. Sewer line will be TV inspected on 9/14/2006 | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Field Supervisor | Wes Sitchler | 2006-09-14 | 927-5057 | dmontero@ci.corte-madera.ca.us, | MINOR
3818 | 23 | 1 | MarinCountySD2 | 2006-08-31 07:38 | 250 | 0 |  | 2006-08-31 07:38 |  | -- | 477 Chapman Drive | Corte Madera | Marin | 94925 |  |  | 2006-08-30 |  |  |  | Recived complaint about an overflowing manhole at 477 Chapman. DPW responded and ran MH K-79 TO J-21 and cleared the the blockage, Pulled back a small amout of gravel. Ran Line several times and TV the sewer line and found no problems. DPW washed down the street and gutter and vacumed the water (no soild materials departed the manhole) with our Vactor truck. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | MANHOLE |  | CAUSE UNKNOWN | --Select None-- |  |  |  | Field Supervisor | Wes Sitchler | 2006-08-31 | 415-927-5057 | dmontero@ci.corte-madera.ca.us, | MINOR
3782 | 22 | 1 | MarinCountySD2 | 2006-08-24 11:41 | 1250 | 900 | 06-5068 | 2006-08-24 | homeowner at 445 montecito | MarinCountySD2 | 455 Montecito Drive | Corte Madera | Marin | 94925 |  |  | 2006-08-23 | 8:30:00 AM | [5 empty] | SUNNY WEATHER | Low |  | CAPTURED IN STORM DRAIN | No |  | No | No | none needed |  | Yes | Yes | Yes | No | No | No | No | No | No | 2006-08-24 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MarinCountySD2 | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- |  | At 8:30 DPW was called to respon to SSOat 445 Montecito. Booms and plugs wrer placed in and around the nearest storm drains to contain the sewer water. The roots that cause the stoppage was removed by a main line rodder. The surface area and the storm drain system was washed and vaccummed. The sewer line is being TV so DPW can repair the sewer line. | Superintendent | David Montero | 2006-08-24 | 415-927-5057 | dmontero@ci.corte-madera.ca.us, | MAJOR | Dave Montero | MarinCountySD2 | 415-927-5057 |  | 233 Tamalpais Drive | Corte Madera | Marin | 94925 | Town Corte Madera | marin County SD2 | 415-927-5057 |  | 233 Tamalpais | Corte Madera | Marin | 94925
3687 | 20 | 1 | MarinCountySD2 | 2006-08-04 08:51 | 35 | 0 |  | 2006-08-04 08:51 |  | -- | 161 Stetson Ave | Corte Madera | Marin | 94925 |  |  | 2006-08-04 |  |  |  | Responded to call at 1430. DPW found a small amount of sewage (clear sewage no material) coming out of the asphalt in front of 161 Stetson. A dirt boom was placed in the gutter to prevent the sewage from goning into the storm drain system. DPW cleaned the sewer line with the Vactor truck and TV the sewer line to inspect the pipe. Roots and a broken pipe were was the cause of the problem. The sewer line will be cleaned and inspected again before repairs are made.The area was cleaned after the job was complete. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | PIPE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Field Supervisor | Wes Sitchler | 2006-08-04 | 415-927-5057 | dmontero@ci.corte-madera.ca.us, | MINOR
3697 | 21 | 1 | MarinCountySD2 | 2006-08-07 14:58 | 50 | 0 |  | 2006-08-07 14:58 |  | -- | 625 Oakdale Avenue | Corte Madera | Marin | 94976 |  |  | 2006-07-21 |  |  |  | Responded to call at 1130. Found Manhole K47 overflowing slight trickle of liquid into the curb. Placed booms and absorbent to prevent liquid entering the storm drain. Ran line and cleared blockage. T.V. camera'd line. Found roots. Called in contractor with main-line rodder to clear roots. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | David Montero | 2006-08-07 | 415-927-5069 | dmontero@ci.corte-madera.ca.us, | MINOR
3216 | 18 | 1 | MarinCountySD2 | 2006-04-21 07:42 | 250 | 0 |  | 2006-04-21 07:42 |  | -- | 175 - 179 Elm Avenue | Larkspur | Marin | 94924 |  |  | 2006-04-20 |  |  |  | Homewowner at 175 Elm reported a sewer smell at 1430 hrs. We responded and found the manhole leaking. Roy's Sewer Service ran a snake through line to clean blockage. The problem was roots. We also ran over 500' of line downwstream of spill. Staff will run our TV camera through line to check for other problems. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | David Montero | 2006-04-21 | 415-927-5057 | dmontero@ci.corte-madera.ca.us, | MINOR
3218 | 19 | 1 | MarinCountySD2 | 2006-04-21 07:47 | 100 | 0 |  | 2006-04-21 07:47 |  | -- | 381 Chapman | Corte Madera | Marin | 94976 |  |  | 2006-04-20 |  |  |  | responded to call at 1330 hrs. Manhole overfowing. Ran line with Vactor and cleared root ball. Water was contained in street and did not reach storm drain. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | David Montero | 2006-04-21 | 415-927-5057 | dmontero@ci.corte-madera.ca.us, | MINOR
3037 | 17 | 1 | MarinCountySD2 | 2006-03-17 12:11 | 50 | 0 |  | 2006-03-17 12:11 |  | -- | 312 Summit Drive | Corte Madera | Marin | 94925 |  |  | 2006-03-17 |  |  |  | DPW responded to a sewer call from the resident at 312 Summit Drive. DPW and Roy's removed the blockage (roots) with an electric snake. All material was contained in the soil within 3-5 feet of the clean out. The ground was wet due to several weeks of rain. Area was cleaned of all material. DPW TV the sewer line and found roots and pipe seperation in several places. DPW is looking into repairing the pipe and the root problem. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Field Supervisor | Wes Sitchler | 2006-03-17 | 927-5057 | dmontero@ci.corte-madera.ca.us, | MINOR
2889 | 16 | 1 | MarinCountySD2 | 2006-02-27 13:27 | 10 | 0 |  | 2006-02-27 13:27 |  | -- | 37 Spindriff | Town Of Corte Madera | Marin | 94925 |  |  | 2006-02-27 |  |  |  | DPW Vactored the sewer line from the SSO manhole. The blockage was removed and the down stream line was also cleaned. The Blockage was grit and debris. The area was washed and all material was vacuummed (no soild material left the manhole.) The area will be schedualed for maintenance | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Field Supervisor | Wes Sitchler | 2006-02-27 | 927-5057 | dmontero@ci.corte-madera.ca.us, | MINOR
2826 | 15 | 2 | MarinCountySD2 | 2006-02-16 13:58 | 150 | 0 |  | 2006-02-16 13:58 |  | -- | 9 Fawn Lane | Corte Madera | Marin | 94925 |  |  | 2006-02-15 |  |  |  | Dpw responded to the sewer call at 9 Fawn Lane. Roy's Sewer Service ran the line with thier power snake and cleared the stoppage. DPW nad Roy's continued to clean the sewer line to the downstream manhole. The sewage spillage went into the surrounding land. DPW cleaned the area with shovels and rakes and dispose the material into are debgris box. On 2-16-06 DPW TV the main line and found more roots. Roy's Sewer Servic is coming out on 2-17-06 to clean the sewer line again. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Field Supervisor | Wes Sitchler | 2006-02-16 | 927-5057 | dmontero@ci.corte-madera.ca.us, | MINOR
2648 | 13 | 1 | MarinCountySD2 | 2006-01-18 11:22 | 100 | 0 |  | 2006-01-18 11:22 |  | -- | 353 Stetson Ave | Corte Madera | Marin | 94925 |  |  | 2006-01-17 |  |  |  | DPW was cleaning the main line upstream when we noticed clear sewage coming out of the manhole. DPW vacuumed the manhole to prevent more water form entering the street. DPW had Roy's Sewer Service clear the line of roots. No clean up was nesecary because no soild material came out of the man hole and the water went into ground. This section of the sewer will be cleaned on 1-18-06 by Roy's Sewer Service. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Field Supervisor | Wes Sitchler | 2006-01-18 | 415-927-5057 | dmontero@ci.corte-madera.ca.us, | MINOR
2527 | 12 | 1 | MarinCountySD2 | 2006-01-05 15:35 | 100 | 0 |  | 2006-01-05 15:35 |  | -- | 624 Corte Madera Ave | Corte Madera | Marin | 94925 |  |  | 2006-01-05 |  |  |  | DPW responded to a sewer call at 624 Corte Madera Ave.Upon arrivel DPW noticed paper material around the cleanout. No sewage water was coming out at this time. Roy's Sewer Service ran the power snake and removed the blockage (roots. The area was cleaned and all material was removed. Heavy rain diluted the sewage water into the ground. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Field Supervisor | Wes Sitchler | 2006-01-05 | 927-5057 | dmontero@CI.CORTE-MADERA.CA.US | MINOR
2089 | 11 | 1 | MarinCountySD2 | 2005-11-07 11:34 | 150 | 0 |  | 2005-11-07 11:34 |  | -- | 4 Pleasant Ave | Cortte Madera | Marin | 94925 |  |  | 2005-11-03 |  |  |  | At 1330 DPW responded to a SSO at 4 Pleasant. Upon (30 min from when we recieved the call)arrivel there was no sewage spilling from the man hole. DPW Vactored out the clear sewage (no material)from the man hole and the sourounding area was cleaned including the catch basin.The SSO was miles away from any body of water. This area will be schedualed to be rodded in the next weel. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Field Supervisor | Wes Sitchler | 2005-11-07 | 927-5057 | dmontero@ci.corte-madera.ca.us, | MINOR
2020 | 10 | 1 | MarinCountySD2 | 2005-10-24 13:02 | 500 | 0 |  | 2005-10-24 13:02 |  | -- | 10 Fifer | Corte Madera | Marin | 94925 |  |  | 2005-10-24 |  |  |  | At 1130 on 10-21-05 DPW responded to a sewer blockage at 10 Fifer. DPW responded within 20 Minutes. DPW created a dam in front of the catch basin and placed sanbags in the catch basin to prevent the clear (no material)sewer water from entering the storm drain system. DPW continued to clean (using the Vactor truck) the area of the spill includung the catch basins. The sewer lines were cleaned in the area of the blockage. Future cleaning of this area is schedualed. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Field Supervisor | Wes Sitchler | 2005-10-24 | 1-415-927-5057 | dmontero@ci.corte-madera.ca.us, | MINOR
1967 | 9 | 1 | MarinCountySD2 | 2005-10-17 10:58 | 500 | 0 |  | 2005-10-17 10:58 |  | -- | 57 Paloma Drive | Corte Madera | Marin | 94925 |  |  | 2005-10-17 |  |  |  | Twin City Police Dept. called DPW which responded to the SSO within 20 min. DPW placed sandbags in front of the strom drain inlets to prevent sewage water from entering the storm drain. DPW cleared the stoppage and washed down and vaccumed the clear sewage water (no material) from the gutters. This area is schedualed for maintenance in the next day or two. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Field Supervisor | Wes Sitchler | 2005-10-17 | 927-5057 | dmontero@ci.corte-madera.ca.us, | MINOR
1651 | 8 | 1 | MarinCountySD2 | 2005-07-26 15:50 | 250 | 0 |  | 2005-07-26 15:50 |  | -- | 78 El Camino Dr. | Corte Madera | Marin | 94976 |  |  | 2005-07-26 |  |  |  | Cleared blockage with mainliner. TV'd line and found it 30% crushed. Contractor will do repairs on 7/27/05. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | MANHOLE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Superintendent | David Montero | 2005-07-26 | 415-927-5069 | dmontero@ci.corte-madera.ca.us, | MINOR
1562 | 7 | 1 | MarinCountySD2 | 2005-06-27 08:33 | 200 | 0 |  | 2005-06-27 08:33 |  | -- | 407 Chapman Drive | Corte Madera | Marin | 94925 |  |  | 2005-06-25 |  |  |  | DPW ran sewer line with Vactor truck from map pages J-21 to N-22. Hit blockage at 156 feet. Blockage material was clothing articles. Material was removed and sewer line was cleaned a total of 298 feet. All sewer water (no sewer material came out from the manhole) was contained by booms and Vacuumed up by Vactor truck. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Field Supervisor | Wes Sitchler | 2005-06-27 | 927-5057 | dmontero@ci.corte-madera.ca.us, | MINOR
1491 | 6 | 1 | MarinCountySD2 | 2005-06-07 10:37 | 60 | 0 |  | 2005-06-07 10:37 |  | -- | 34 Golden Hind (mahhole 44 Page L of Corte Madera's Sanitary maps) | Corte Madera | Marin | 94925 |  |  | 2005-06-05 |  |  |  | There was a grease stoppage at 34 Golden Hind. DPW responded within 20 min. from the time the homeowner saw the clear sewage started(no toilet paper or any soilds) coming from the manhole. DPW cleared the blockage, cuaght and removed all the grease with the grit catcher. The sewer water did not reach any catch basins and no clean up was necessary due to the warm weather. The sewer water evaporated by the time we cleared the stoppage. On 6-6-05 and 6-7-05 Roy's Sewer Service with thier Vactor cleaned this area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Field Supervisor | Wes Sitchler | 2005-06-07 | 927-5057 | dmontero@ci.corte-madera.ca.us, | MINOR
1381 | 5 | 1 | MarinCountySD2 | 2005-05-10 13:58 | 150 | 0 |  | 2005-05-10 13:58 |  | -- | 4875 Paradise Drive | Corte Madera | Marin | 94925 |  |  | 2005-05-05 |  |  |  | DPW noticed a SSO coming from man hole W-3. We had Roy's Sewer Service run the sewer line. The sewer lne was cleared. The cause of the blockage was grease. No soild material come out of the man hole. Everthing was delueded by the rain. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Field Supervisor | Wes Sitchler | 2005-05-10 | 415-927-5057 | dmontero@ci.corte-madera.ca.us, | MINOR
1074 | 3 | 2 | MarinCountySD2 | 2005-02-22 10:57 | 1125 | 600 | 05-1072 | 2005-02-16 | Wes Sitchler | MarinCountySD2 | 37 Harbor Drive | Corte Madera | Marin | 94925 |  |  | 2005-02-16 | 10:45:00 A | [5 empty] | CLOUDY WEATHER | Low |  | STORM DRAIN | No |  | No | No | The area has been inspected and no evidence of any damage has been noticed. |  | Yes | Yes | No | No | No | Yes | No | Yes | No | 2005-02-17 | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | MarinCountySD2 | MANHOLE |  | BLOCKAGE | DEBRIS | --Select None-- |  | Samples from the storm drain system were taken one at the outfall into Muzzy Marsh and the other sample was taken from an upstream storm drain. The results from the outfall are1.1mg/L of Ammonia. | uperintendent | David Montero | 2005-02-17 | 415-927-5069 | dmontero@ci.corte-madera.ca.us, | MAJOR | Dave Montero | Marin County SD2 | 415-927-5057 |  | 233 Tamalpais Drive | Corte Madera | Marin | 94925 | Town of Corte Madera | MarinCountySD2 | 927-5057 |  | 233 Tamalpais Drive | Corte Madera | Marin | 94925
664 | 1 | 1 | MarinCountySD2 | 2004-12-28 11:15 | 500 | 0 |  | 2004-12-28 | David Montero |  | Intersection of Granada Dr. & El Camino Dr. | Corte Madera | Marin | 94976 |  |  | 2004-12-27 | 11:30:00 A | 2004-12-27 | 12:00:00 P | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | superintendent | David Montero | 2004-12-28 | 415-927-5057 | dmontero@ci.corte-madera.ca.us | 24HR |  |  | 415-927-5057 | [6 empty] | MarinCountySD2
670 | 2 | 1 | MarinCountySD2 | 2004-12-29 08:32 | 700 | 0 |  | 2004-12-29 08:32 |  | -- | 613 Meadowsweet Drive & Tamalpais Drive | Corte Madera | Marin | 94976 |  |  | 2004-12-27 |  |  |  | SSO occurred during a 7.2 tide and heavy rainfall with street flooding. The SSO was intermittent. The manhole is being replaced with a lock type manhole that will be sealed. This work is being performed today by Forde Construction. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MarinCountySD2 | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | Superintentent | David Montero | 2004-12-29 | 415-927-5057 | dmontero@ci.corte-madera.ca.us | MINOR
4145 | 24 | 1 | Millbrae | 2006-11-22 12:04 | 750 | 0 |  | 2006-11-22 12:04 |  | -- | 367 MINORCA | MILLBRAE | SAN MATEO | 94030 |  |  | 2006-11-21 |  |  |  | HISTORICALLY, THIS LINE HAS NOT GIVEN US PROBLEMS. I WILL VIDEO INSPECT THE LINE AND REPAIR OR PLACE IT ON OUR ROOT FOAMING LIST. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | PIPE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Martin Crean | 2006-11-22 | (650) 537-0205
3314 | 23 | 3 | Millbrae | 2006-05-08 10:33 | 7000 | 0 | 06-2610 | 2006-05-01 | Martin Crean | Millbrae | 941 VISTA GRANDE | Millbrae | San Mateo | 94030 |  |  | 2006-04-30 | 2:30:00 PM | [5 empty] | SUNNY WEATHER | Low | Region 2 | STORM DRAIN | No |  | No | No | OK |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2333 | mchee@waterboards.ca.gov | Millbrae | MANHOLE | Paper build up as well as construction debris caused the block | BLOCKAGE | CONSTRUCTION DEBRIS | --Select None-- |  | Sewer Line was blocked as a result of construction bebris from upstream line replacements and build up of paper | Supervisor | Martin Crean | 2006-05-08 | 650-259-2374 | mcrean@ci.millbrae.ca.us | MAJOR | Martin Crean | Millbrae | (650) 259-2374 |  | 621 Magnolia Avenue | Millbrae | San Mateo | 94020 |  | Millbrae
3099 | 20 | 2 | Millbrae | 2006-03-30 07:08 | 1400 | 0 | 1773 | 2006-03-25 | Martin Crean | Millbrae | Millbrae Ave @US 101 | Millbrae | San Mateo | 94030 |  |  | 2006-03-25 | 3:20:00 AM | [5 empty] | RAINY WEATHER | Low | Region 2 | STORM DRAIN | No |  | No | No | No visual impact |  | No | No | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Millbrae | MANHOLE |  | FLOW CAPACITY DEFICIENCY | --Select None-- | --Select None-- | Inclement Weather event | Water surcharged through the pick holes of the manhole at a rate of 10 gpm | Supevisor | Martin Crean | 2006-03-25 | 650-259-2374 | mcrean@ci.millbrae.ca.us | MAJOR | Martin Crean | City of Millbrae | 650 259-2374 |  | 621 Magnolia Ave | Millbrae | San Mateo | 94030 | City of Millbrae | Millbrae | 650 259-2374 |  | 621 Magnolia Ave | Millbrae | San Mateo | 94030
3100 | 21 | 2 | Millbrae | 2006-03-30 07:17 | 1400 | 0 | 1774 | 2006-03-25 | Martin Crean | Millbrae | Aviador Ave @ Camino Millenium | Millbrae | San Mateo | 94030 |  |  | 2006-03-25 | 3:20:00 AM | [5 empty] | RAINY WEATHER | Low | Region 2 | STORM DRAIN | No |  | No | No | No visual impact |  | No | No | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Millbrae | MANHOLE |  | FLOW CAPACITY DEFICIENCY | --Select None-- | --Select None-- | Inclement weather event | Water surcharged through the pick holes of the manhole at a rate of 10 gpm | Supervisor | Martin Crean | 2006-03-25 | 650-259-2374 | mcrean@ci.millbrae.ca.us | MAJOR | Martin Crean | Millbrae | 650 259-2374 |  | 621 Magnolia Ave | Millbrae | San Mateo | 94030 | City of Millbrae | Millbrae | 650 259-2374 |  | 621 Magnolia Ave | Millbrae | San Mateo | 94030
3101 | 22 | 2 | Millbrae | 2006-03-30 07:22 | 1400 | 0 | 1775 | 2006-03-25 | Martin Crean | Millbrae | 185 Aviador | Millbrae | San Mateo | 94030 |  |  | 2006-03-25 | 3:20:00 AM | [5 empty] | RAINY WEATHER | Low | Region 2 | STORM DRAIN | No |  | No | No | No visual impact |  | No | No | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Millbrae | MANHOLE |  | FLOW CAPACITY DEFICIENCY | --Select None-- | --Select None-- | Inclement weather event | Water surcharged through the pick holes of the manhole at a rate of 10 gpm | Supervisor | Martin Crean | 2006-03-25 | 650-259-2374 | mcrean@ci.millbrae.ca.us | MAJOR | Martin Crean | City of Millbrae | 650 259-2374 |  | 621 Magnolia Ave | Millbrae | San Mateo | 94030 | City of Millbrae | Millbrae | 650 259-2374 |  | 621 Magnolia Ave | Millbrae | San Mateo | 94030
2865 | 19 | 2 | Millbrae | 2006-02-22 10:15 | 1500 | 0 | 06-1013 | 2006-02-17 | Martin Crean | Millbrae | 171 Minorca Way | Millbrae | San Mateo | 94030 |  |  | 2006-02-16 | 9:30:00 AM | [5 empty] | SUNNY WEATHER | Low | Region 2 | STORM DRAIN | No |  | No | No | Recieving Water is approximately 1.5 miles downstream of the blockage. Inspection of downstream waters - ok |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Millbrae | MANHOLE | This line segment is currently being replaced. Construction material blocked the line. | BLOCKAGE | CONSTRUCTION DEBRIS | --Select None-- | This line segment is currently being replaced. Construction material blocked the line. | The city of Millbrae is currently completing a Capital Improvement Project. This line is being replaced. Construction debris cased the blockage in this line. The contractor has been made aware of the blockage. | Supervisor | Martin Crean | 2006-02-17 | 650-259-2374 | mcrean@ci.millbrae.ca.us | MAJOR | Martin Crean | City of Millbrae | (650) 259-2374 |  | 621 Magnolia Ave | Millbrae | San Mateo | 94030 | J Howard Engineering | Millbrae | (650) 375-8314
2576 | 16 | 2 | Millbrae | 2006-01-09 08:28 | 840 | 0 | 05-7587 | 2005-12-31 | Craig Centis | Martin Crean | Taylor Ave @ Elder Ave | Millbrae | San Mateo | 94030 |  |  | 2005-12-31 | 6:00:00 AM | [5 empty] | RAINY WEATHER | Low | Region 2 | STORM DRAIN | No |  | No | No | Because of the magnitude of the storm, one could not tell between the storm water and the SSO. |  | No | No | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Millbrae | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- | PG&E power failures | MH 314042 surcharged as a result of an immense volume of Inflow and Infiltration during the storm. The treatment plant was incapable of pumping this volume due to PG&E power failure through out the city. | Supervisor | Martin Crean | 2006-01-09 | 650-259-2374 | mcrean@ci.millbrae.ca.us, | MAJOR | Martin Crean | City of Millbrae | 650-259-2374 |  | 621 Magnolia | Millbrae | San Mateo | 94030 |  | Pacific Gas & Electric
2578 | 15 | 2 | Millbrae | 2006-01-09 08:54 | 700 | 0 | 05-7587 | 2005-12-31 | Craig Centis | Martin Crean | Landing Lane c/s San Anselmo | Millbrae | San Mateo | 94030 |  |  | 2005-12-31 | 6:00:00 AM | [5 empty] | RAINY WEATHER | Low | Region 2 | STORM DRAIN | No |  | No | No | Because of the magnitude of the storm, one could not tell between storm water and SSO. |  | No | No | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Millbrae | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- | PG&E power failures | MH 707018 surcharged as a result of an immense amount of Inflow and Infiltration during the storm. The treatment plant was incapable of pumping this volume due to PG&E power failure through out the City. | Supervisor | Martin Crean | 2006-01-09 | 650-259-2374 | mcrean@ci.millbrae.ca.us, | MAJOR | Martin Crean | City of Millbrae | 650-259-2374 |  | 621 Magnolia Ave | Millbrae | San Mateo | 94030 |  | Pacific Gas and Electric
2579 | 14 | 2 | Millbrae | 2006-01-09 09:08 | 700 | 0 | 05-7587 | 2005-12-31 | Craig Centis | Martin Crean | Hillcrest Blvd @ Magnolia Ave | Millbrae | San Mateo | 94030 |  |  | 2005-12-31 | 6:00:00 AM | [5 empty] | RAINY WEATHER | Low | Region 2 | STORM DRAIN | No |  | No | No | Because of the magnitude of the storm, one could not determine Storm water from SSO water. |  | No | No | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Millbrae | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- | PG&E power failures | MH 314010 surcharged as a result of an immense amount of Inflow and Infiltration during the storm. The treatment plant was incapable of pumping this volume due to PG&E power failure through out the City. | Supervisor | Martin Crean | 2006-01-09 | 650-259-2374 | mcrean@ci.millbrae.ca.us, | MAJOR | Martin Crean | City of Millbrae | 650-259-2374 |  | 621 Magnolia Ave | Millbrae | San Mateo | 94030 |  | Pacific Gas and Electric
2580 | 13 | 2 | Millbrae | 2006-01-09 09:19 | 700 | 0 | 05-7587 | 2005-12-31 | Craig Centis | Martin Crean | Broadway @ Hillcrest Blvd | Millbrae | San Mateo | 94030 |  |  | 2005-12-31 | 6:00:00 AM | [5 empty] | RAINY WEATHER | Low | Region 2 | STORM DRAIN | No |  | No | No | Because of the magnitude of the storm, one could not determine Storm water from SSO water. |  | No | No | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Millbrae | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- | PG&E power failures | MH 314006 surcharged as a result of an immense amount of Inflow and Infiltration during the storm. The treatment plant was incapable of pumping this volume due to PG&E power failure through out the City. | Supervisor | Martin Crean | 2006-01-09 | 650-259-2374 | mcrean@ci.millbrae.ca.us, | MAJOR | Martin Crean | City of Millbrae | 650-259-2374 |  | 621 Magnolia Ave | Millbrae | San Mateo | 94030 |  | Pacific Gas and Electric
2581 | 12 | 2 | Millbrae | 2006-01-09 09:30 | 700 | 0 | 05-7587 | 2005-12-31 | Craig Centis | Martin Crean | La Cruz @ Broadway | Millbrae | San Mateo | 94030 |  |  | 2005-12-31 | 6:00:00 AM | [5 empty] | RAINY WEATHER | Low | Region 2 | STORM DRAIN | No |  | No | No | Because of the magnitude of the storm, one could not determine Storm water from SSO water. |  | No | No | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Millbrae | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- | PG&E power failures | MH 314002 surcharged as a result of an immense amount of Inflow and Infiltration during the storm. The treatment plant was incapable of pumping this volume due to PG&E power failure through out the City. | Supervisor | Martin Crean | 2006-01-09 | 650-259-2374 | mcrean@ci.millbrae.ca.us, | MAJOR | Martin Crean | City of Millbrae | 650-259-2374 |  | 621 Magnolia Ave | Millbrae | San Mateo | 94030 |  | Pacific Gas and Electric
2582 | 17 | 2 | Millbrae | 2006-01-09 09:39 | 2800 | 0 | 05-7587 | 2005-12-31 | Craig Centis | Martin Crean | Millbrae Ave. @ US 101 | Millbrae | San Mateo | 94030 |  |  | 2005-12-31 | 6:00:00 AM | [5 empty] | RAINY WEATHER | Low | Region 2 | STORM DRAIN | No |  | No | No | Because of the magnitude of the storm, one could not determine Storm water from SSO water. |  | No | No | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Millbrae | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- | PG&E power failure | MH 221024 surcharged as a result of an immense amount of Inflow and Infiltration during the storm. The treatment plant was incapable of pumping this volume due to PG&E power failure through out the City. | Supervisor | Martin Crean | 2006-01-09 | 650-259-2374 | mcrean@ci.millbrae.ca.us, | MAJOR | Martin Crean | City of Millbrae | 650-259-2374 |  | 621 Magnolia Ave | Millbrae | San Mateo | 94030 |  | Pacific Gas and Electric
2583 | 18 | 2 | Millbrae | 2006-01-09 09:55 | 2800 | 0 | 05-7587 | 2005-12-31 | Craig Centis | Martin Crean | Millbrae Ave. @ US 101 | Millbrae | San Mateo | 94030 |  |  | 2005-12-31 | 6:00:00 AM | [5 empty] | RAINY WEATHER | Low | Region 2 | STORM DRAIN | No |  | No | No | Because of the magnitude of the storm, one could not determine Storm water from SSO water |  | No | No | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Millbrae | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- | PG&E power failures | MH 221031 surcharged as a result of an immense amount of Inflow and Infiltration during the storm. The treatment plant was incapable of pumping this volume due to PG&E power failure through out the City | Supervisor | Martin Crean | 2006-01-09 | 650-259-2374 | mcrean@ci.millbrae.ca.us, | MAJOR | Martin Crean | City of Millbrae | 650-259-2374 |  | 621 Magnolia Ave | Millbrae | San Mateo | 94030 |  | Pacific Gas and Electric
2069 | 11 | 1 | Millbrae | 2005-10-31 08:50 | 400 | 0 |  | 2005-10-31 08:50 |  | -- | 919 Clearfield | Millbrae | San Mateo | 94030 |  |  | 2005-10-28 |  |  |  | This line will be video inspected and any necessary repairs will be completed. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Millbrae | PIPE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Martin Crean | 2005-10-31 | (650) 537-0205 | mcrean@ci.millbrae.ca.us, | MINOR
1879 | 10 | 1 | Millbrae | 2005-09-29 06:50 | 850 | 0 |  | 2005-09-29 06:50 |  | -- | 411 LOMITA | Millbrae | San Mateo | 94030 |  |  | 2005-09-28 |  |  |  | This line is on a preventative maintenance schedule. It will be video inspected and any necessary repairs will be completed. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Millbrae | PIPE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Supervisor | Martin Crean | 2005-09-29 | (650) 537-0205 | mcrean@ci.millbrae.ca.us, | MINOR
1647 | 9 | 1 | Millbrae | 2005-07-26 13:46 | 150 | 0 |  | 2005-07-26 13:46 |  | -- | 1390 El Camino Real | Millbrae | San Mateo | 94030 |  |  | 2005-07-25 |  |  |  | This line will be video inspected and any necessary repairs will be completed. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Millbrae | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Supervisor | Martin Crean | 2005-07-26 | (650) 537-0205 | mcrean@ci.millbrae.ca.us, | MINOR
1429 | 7 | 1 | Millbrae | 2005-05-19 13:33 | 500 | 0 |  | 2005-05-19 13:33 |  | -- | 63 Aura Vista | Millbrae | San Mateo | 94030 |  |  | 2005-05-17 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Millbrae | PIPE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Mike Riddell | 2005-05-19 | 650 2592375 | mcrean@ci.millbrae.ca.us, | MINOR
1401 | 6 | 1 | Millbrae | 2005-05-16 07:47 | 1 | 0 |  | 2005-05-16 07:47 |  | -- | 1250 Millbrae Ave | Millbrae | USA | 94030 |  |  | 2005-05-12 |  |  |  | Roots caused the blockage, hand rods were used to free main. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Millbrae | PIPE |  | BLOCKAGE | --Select None-- |  |  |  | Supervisor | mike Riddell | 2005-05-16 | 650 2592375 | mcrean@ci.millbrae.ca.us | MINOR
1387 | 5 | 1 | Millbrae | 2005-05-11 06:31 | 100 | 0 |  | 2005-05-11 06:31 |  | -- | 516 Barcelona | Millbrae | san Mateo | 94030 |  |  | 2005-05-10 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Millbrae | PIPE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Mike Riddell | 2005-05-11 | 650 259-2374 | tcolletti@ci.millbrae.ca.us, | MINOR
1287 | 4 | 1 | Millbrae | 2005-04-18 09:49 | 300 | 0 |  | 2005-04-18 09:49 |  | -- | 49 Via Canon | Millbrae | San Mateo | 94030 |  |  | 2005-04-18 |  |  |  | This line will be put on a preventative maintenance schedule | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | millbrae | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Martin Crean | 2005-04-18 | (650) 537-0205 | mcrean@ci.millbrae.ca.us, | MINOR
948 | 3 | 1 | Millbrae | 2005-02-02 08:33 | 150 | 0 |  | 2005-02-02 08:33 |  | -- | 823 Vista Grande - Backyard | Millbrae | San Mateo | 94030 |  |  | 2005-02-01 |  |  |  | Roots accumulated at the downstream manhole and blocked the outlet. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | millbrae | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Supervisor | Martin Crean | 2005-02-02 | (650) 259-2374 | mcrean@ci.millbrae.ca.us | MINOR
918 | 2 | 1 | Millbrae | 2005-01-26 11:45 | 900 | 0 |  | 2005-01-26 11:45 |  | -- | Approximately 800' south east of the Santa Paula/ Monterrey intersection | Millbrae | San Mateo | 94030 |  |  | 2005-01-25 |  |  |  | 14" force main got punctured while PG&E were running their auger to install an electric pole. After placing a berm around the area, the overflow was contained. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | millbrae | PIPE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Supervisor | Martin Crean | 2005-01-26 | (650) 537-0205 | mcrean@ci.millbrae.ca.us | MINOR
447 | 1 | 1 | Millbrae | 2004-12-08 16:14 | 450 | 0 |  | 2004-12-08 16:14 |  | -- | 541 Taylor | Millbrae | San Mateo | 94030 |  |  | 2004-12-08 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Millbrae | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Supervisor | Martin Crean | 2004-12-08 | (650) 537-0205 |  | MINOR
5186 | 46 | 1 | MillValley | 2007-05-01 10:48 | 200 | 0 |  | 2007-05-01 10:48 |  | -- | 400 Vista Linda Dr | Mill Valley | Marin | 94941 |  |  | 2007-04-30 |  |  |  | Broken pipe. Pipe replaced | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | PIPE |  | CAUSE UNKNOWN | -- Select One -- |  |  |  | Public Works Aide | Peggy Segale | 2007-05-01 | 415-388-4033
5184 | 45 | 1 | MillValley | 2007-05-01 09:32 | 20 | 0 |  | 2007-05-01 09:32 |  | -- | 166 Shelley Dr | Mill Valley | Marin | 94941 |  |  | 2007-04-30 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Public Works Aide | Peggy Segale | 2007-05-01 | 415-388-4033
5182 | 44 | 1 | MillValley | 2007-05-01 09:16 | 195 | 0 |  | 2007-05-01 09:16 |  | -- | 35 Bernard & Bayview Stairs | Mill Valley | Marin | 94941 |  |  | 2007-04-28 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Public Works Aide | Peggy Segale | 2007-05-01 | 415-388-4033
5180 | 43 | 1 | MillValley | 2007-05-01 09:07 | 180 | 0 |  | 2007-05-01 09:07 |  | -- | 333 Summit Avenue | Mill Valley | Marin | 94941 |  |  | 2007-04-28 |  |  |  | Off set roots | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | CAUSE UNKNOWN | -- Select One -- |  |  |  | Public Works Aide | Peggy Segale | 2007-05-01 | 415-388-4033
5178 | 42 | 1 | MillValley | 2007-05-01 08:57 | 150 | 0 |  | 2007-05-01 08:57 |  | -- | 409 Summit Avenue | Mill Valley | Marin | 94941 |  |  | 2007-04-27 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Public Works Aide | Peggy Segale | 2007-05-01 | 415-388-4033
5143 | 41 | 1 | MillValley | 2007-04-25 14:10 | 50 | 0 |  | 2007-04-25 14:10 |  | -- | 427 Summit Ave | Mill Valley | Marin | 94941 |  |  | 2007-04-25 |  |  |  | Blockage also due to grease | [5 empty] | GROUND WATER IMPACTED | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Public Works Aide | Peggy Segale | 2007-04-25 | 415-388-4033
5084 | 40 | 1 | MillValley | 2007-04-19 13:30 | 40 | 0 |  | 2007-04-19 13:30 |  | -- | 14 Eton Way | Mill Valley | Marin | 94941 |  |  | 2007-04-19 |  |  |  | Cleared w/rodder | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Public Works Aide | P. Segale | 2007-04-19 | 415-388-4033
5080 | 39 | 1 | MillValley | 2007-04-18 16:25 | 20 | 0 |  | 2007-04-18 16:25 |  | -- | 11 Locust Ave | Mill Valley | Marin | 94941 |  |  | 2007-04-12 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | Public Works Aide | P. Segale | 2007-04-18 | 415-388-4033
5078 | 38 | 1 | MillValley | 2007-04-18 16:23 | 20 | 0 |  | 2007-04-18 16:23 |  | -- | 583 Throckmorton | Mill Valley | Marin | 94941 |  |  | 2007-04-12 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | Public Works Aide | P. Segale | 2007-04-18 | 415-388-4033
5076 | 37 | 1 | MillValley | 2007-04-18 16:21 | 300 | 0 |  | 2007-04-18 16:21 |  | -- | 371 Cascade Drive | Mill Valley | Marin | 94941 |  |  | 2007-04-09 |  |  |  | water picked up with pump truck | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | P. Segale | Public Works Aide | 2007-04-18 | 415-388-4033
4862 | 36 | 1 | MillValley | 2007-03-05 09:40 | 120 | 0 |  | 2007-03-05 09:40 |  | -- | 424 W. Blithedale Ave. | Mill Valley | Marin | 94941 |  |  | 2007-03-03 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Public Works Aide | Peggy Segale | 2007-03-05 | 415-388-4033
4795 | 35 | 1 | MillValley | 2007-02-22 11:42 | 50 | 0 |  | 2007-02-22 11:42 |  | -- | 18 Buena Vista | Mill Valley | Marin | 94941 |  |  | 2007-02-22 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Public Works Aide | Peggy Segale | 2007-02-22 | 415-388-4033
4747 | 34 | 1 | MillValley | 2007-02-13 11:29 | 550 | 0 |  | 2007-02-13 11:29 |  | -- | 57 Longfellow | Mill Valley | Marin | 94941 |  |  | 2007-02-12 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Public Works Aide | Peggy Segale | 2007-02-13 | 415-388-4033
4741 | 33 | 1 | MillValley | 2007-02-13 09:32 | 30 | 0 |  | 2007-02-13 09:32 |  | -- | 77 Cascade Dr | Mill Valley | Marin | 94941 |  |  | 2007-02-12 |  |  |  | Blockage also due to paper products | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Public Works Aide | Peggy Segale | 2007-02-13 | 415-388-4033
4495 | 32 | 1 | MillValley | 2007-01-11 09:48 | 35 | 0 |  | 2007-01-11 09:48 |  | -- | Bernard Ave Stairs cross street - Bayview | Mill Valley | Marin | 94941 |  |  | 2007-01-10 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | BLOCKAGE | ROOTS |  | out of ground |  | Public Works Aide | Peggy Segale | 2007-01-11 | 415-388-4033
4463 | 31 | 1 | MillValley | 2007-01-08 09:00 | 300 | 0 |  | 2007-01-08 09:00 |  | -- | 12 Montford Ave | Mill Valley | Marin | 94941 |  |  | 2007-01-06 |  |  |  | Paper products, grease, baby wipes | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Public Works Aide | Peggy Segale | 2007-01-08 | 415-388-4033
4461 | 30 | 1 | MillValley | 2007-01-08 08:55 | 375 | 0 |  | 2007-01-08 08:55 |  | -- | Summit Ave @ Tamalpais Ave | Mill Valley | Marin | 94941 |  |  | 2007-01-05 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Public Works Aide | Peggy Segale | 2007-01-08 | 415-388-4033
4456 | 29 | 1 | MillValley | 2007-01-05 13:40 | 65 | 0 |  | 2007-01-05 13:40 |  | -- | 31 Millside Lane | Mill Valley | Marin | 94941 |  |  | 2007-01-04 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Public Works Aide | Peggy Segale | 2007-01-05 | 415-388-4033
4452 | 28 | 1 | MillValley | 2007-01-05 13:36 | 75 | 0 |  | 2007-01-05 13:36 |  | -- | 410 Summit | Mill Valley | Marin | 94941 |  |  | 2007-01-04 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Public Works Aide | Peggy Segale | 2007-01-05 | 415-388-4033
4374 | 27 | 1 | MillValley | 2006-12-20 14:36 | 30 | 0 |  | 2006-12-20 14:36 |  | -- | 389 Ethel Ave | Mill Valley | Marin | 94941 |  |  | 2006-12-20 |  |  |  | Destination also street/curb gutter & yard/land | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Public Works Aide | Peggy Segale | 2006-12-20 | 415-388-4033
4297 | 26 | 1 | MillValley | 2006-12-13 09:04 | 80 | 0 |  | 2006-12-13 09:04 |  | -- | Manor Dr @ Alvarado | Mill Valley | Marin | 94941 |  |  | 2006-12-12 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Public Works Aide | Peggy Segale | 2006-12-13 | 415-388-4033
4139 | 25 | 1 | MillValley | 2006-11-21 15:03 | 10 | 0 |  | 2006-11-21 15:03 |  | -- | 120 Shelley Drive | Mill Valley | Marin | 94941 |  |  | 2006-11-20 |  |  |  | ROOTS & PAPER PRODUCTS | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Public Works Aide | Peggy Segale | 2006-11-21 | 415-388-4033
4115 | 24 | 1 | MillValley | 2006-11-15 16:38 | 200 | 0 |  | 2006-11-15 16:38 |  | -- | 67 Molino Avenue | Mill Valley | Marin | 94941 |  |  | 2006-11-14 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Public Works Aide | Peggy Segale | 2006-11-15 | 415-388-4033 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
4110 | 23 | 1 | MillValley | 2006-11-14 11:16 | 450 | 0 |  | 2006-11-14 11:16 |  | -- | 524 Miller Avenue | Mill Valley | Marin | 94941 |  |  | 2006-11-13 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Public Works Aide | Peggy Segale | 2006-11-14 | 415-388-4033 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
4019 | 22 | 1 | MillValley | 2006-10-23 17:23 | 360 | 0 |  | 2006-10-23 17:23 |  | -- | 49 Cascade Drive | Mill Valley | Marin | 94941 |  |  | 2006-10-21 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Engineering Tech | Kimberly Wilson | 2006-10-23 | 388-4033, x118 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
4000 | 19 | 1 | MillValley | 2006-10-17 13:01 | 200 | 0 |  | 2006-10-17 13:01 |  | -- | 21 Monte Vista | Mill Valley | Marin | 94941 |  |  | 2006-10-17 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sr. Civ. Eng. | Jill Barnes (per mm) | 2006-10-17 | 415-388-4033 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
4002 | 20 | 1 | MillValley | 2006-10-17 13:13 | 420 | 0 |  | 2006-10-17 13:13 |  | -- | 5 Monte Vista | Mill Valley | Marin | 94941 |  |  | 2006-10-17 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Eng. Tech. | Kimberly Wilson | 2006-10-17 | 415-388-9112 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
4004 | 21 | 1 | MillValley | 2006-10-17 13:22 | 80 | 0 |  | 2006-10-17 13:22 |  | -- | 352 W. Blithedale | Mill Valley | Marin | 94941 |  |  | 2006-10-17 |  |  |  | Debris was "grit". | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Eng. Tech. | Kimberly Wilson (mm) | 2006-10-17 | 415-388-9112 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
3968 | 18 | 1 | MillValley | 2006-10-09 09:29 | 110 | 0 |  | 2006-10-09 09:29 |  | -- | 10 Dorset Lane | Mill Valley | Marin | 94941 |  |  | 2006-10-05 |  |  |  | Roots/Tampons | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Public Works Aide | Peggy Lee | 2006-10-09 | 415-388-4033 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
3919 | 17 | 1 | MillValley | 2006-09-25 11:03 | 35 | 0 |  | 2006-09-25 11:03 |  | -- | 106 Miller Avenue | Mill Valley | Marin | 94901 |  |  | 2006-09-25 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Public Works | Donald Peter | 2006-09-25 | 415-388-4033 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
3892 | 16 | 1 | MillValley | 2006-09-18 13:59 | 675 | 0 |  | 2006-09-18 13:59 |  | -- | 86 Molino Avenue | Mill Valley | Marin | 94941 |  |  | 2006-09-16 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sr. Civil Engineer | Jill Barnes | 2006-09-18 | 388-4033 x116 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
3884 | 15 | 1 | MillValley | 2006-09-15 10:50 | 350 | 0 |  | 2006-09-15 10:50 |  | -- | 21 Monte Vista | Mill Valley | Marin | 94941 |  |  | 2006-09-15 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sr. Civil Engineer | Jill Barnes | 2006-09-15 | 415-388-4033 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
3831 | 14 | 1 | MillValley | 2006-09-05 11:40 | 30 | 0 |  | 2006-09-05 11:40 |  | -- | 14 Glen Drive | Mill Valley | Marin | 94941 |  |  | 2006-09-04 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Public Works Aide | Peggy Lee | 2006-09-05 | 415-388-4033 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
3751 | 13 | 1 | MillValley | 2006-08-17 10:21 | 120 | 0 |  | 2006-08-17 10:21 |  | -- | 80 Cypress Ave | Mill Valley | Marin | 94941 |  |  | 2006-08-14 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sr. Civil Engineer | Jill Barnes | 2006-08-17 | 415-388-4033 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
3749 | 12 | 1 | MillValley | 2006-08-17 10:11 | 180 | 0 |  | 2006-08-17 10:11 |  | -- | 115 Marion Avenue | Mill Valley | Marin | 94941 |  |  | 2006-08-06 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sr. Civil Engineer | Jill Barnes | 2006-08-17 | 415-388-4033 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
3614 | 11 | 1 | MillValley | 2006-07-10 08:45 | 720 | 0 |  | 2006-07-10 08:45 |  | -- | 30 Shelley Drive | Mill Valley | Marin | 94941 |  |  | 2006-06-29 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Engineering Tech | Kimberly Wilson | 2006-07-10 | 415-388-4033 | kwilson@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
3619 | 10 | 2 | MillValley | 2006-07-12 17:32 | 6000 | 0 | 06-4001 | 2006-06-29 | Roto-Rooter | MillValley | 30 Shelley Drive | Mill Valley | Marin | 94941 |  |  | 2006-06-29 | 8:50:00 PM | [5 empty] | SUNNY WEATHER | Low |  | YARD/LAND | No |  | No | No | No paper matter. |  | Yes | Yes | Yes | No | No | No | No | No | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MillValley | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- | Roots & Paper Products |  | Engineering Technici | Kimberly Wilson | 2006-07-10 | 415-388-4033 | kwilson@cityofmillvalley.org, wbush@cityofmillvalley.org | MAJOR | Kimberly Wilson | MillValley | 415/388-4033 | 118 | 26 Corte Madera | Mill Valley | Marin | 94941 |  | MillValley
3541 | 7 | 1 | MillValley | 2006-06-22 14:48 | 60 | 0 |  | 2006-06-22 14:48 |  | -- | Cascade Way & Dipsea Stairs | Mill Valley | Marin | 94941 |  |  | 2006-06-17 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Sr. Civil Engineer | Jill Barnes | 2006-06-22 | 415-388-4033 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
3543 | 8 | 1 | MillValley | 2006-06-22 14:50 | 90 | 0 |  | 2006-06-22 14:50 |  | -- | 52 Longfellow Drive | Mill Valley | Marin | 94941 |  |  | 2006-04-25 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sr. Civil Engineer | Jill Barnes | 2006-06-22 | 415-388-4033 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
3545 | 9 | 1 | MillValley | 2006-06-22 14:52 | 120 | 0 |  | 2006-06-22 14:52 |  | -- | 362 Edgewood Ave | Mill Valley | Marin | 94941 |  |  | 2006-04-25 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sr. Civil Engineer | Jill Barnes | 2006-06-22 | 415-388-4033 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
2963 | 3 | 1 | MillValley | 2006-03-08 14:06 | 10 | 0 |  | 2006-03-08 14:06 |  | -- | 517 Throckmorton Cross Street Cornwall | Mill Valley | Marin | 94941 |  |  | 2006-01-14 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sr. Civil Engineer | Jill Barnes | 2006-03-08 | 415/388-4033 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
2971 | 6 | 1 | MillValley | 2006-03-08 14:25 | 0 | 0 |  | 2006-03-08 14:25 |  | -- | Safeway 1 Camino Alto cross street Miller | Mill Valley | Marin | 94941 |  |  | 2005-12-16 |  |  |  | Kirk from Roto Rooter responded and filled-out After Hour Reponse Checklist | [5 empty] | UNKNOWN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | OTHER | no spill | BLOCKAGE | GREASE |  |  |  | Sr.Civil Engineer | Jill Barnes | 2006-03-08 | 415/388-4033 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
2973 | 5 | 2 | MillValley | 2006-03-08 14:27 | 10 | 0 |  | 2006-03-08 14:27 |  | -- | 144 Corte Madera Avenue cross street Eldridge | Mill Valley | Marin | 94941 |  |  | 2005-12-13 |  |  |  | After hours Roto Rooter | [5 empty] | UNKNOWN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | CAUSE UNKNOWN | --Select None-- |  |  |  | Sr. Civil Engineer | Jill Barnes | 2006-03-08 | 415/388-4033 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
2965 | 2 | 2 | MillValley | 2006-03-08 14:08 | 200 | 0 |  | 2006-03-08 14:08 |  | -- | 13 Lyon Place cross street Corte Madera Avenue | Mill Valley | Marin | 94941 |  |  | 2005-12-10 |  |  |  | The City tried to report this spill electronically on Jan 6th 2006 but system would not accept the form. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sr. Civil Engineer | Jill Barnes | 2006-03-08 | 415/388-4033 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
2967 | 4 | 1 | MillValley | 2006-03-08 14:12 | 250 | 0 |  | 2006-03-08 14:12 |  | -- | 40 Bay View cross street Bernard | Mill Valley | Marin | 94941 |  |  | 2005-11-20 |  |  |  | The City tried to file an e-report for this spill on Jan 6, 2006 but system would not accept. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | CAUSE UNKNOWN | --Select None-- |  |  |  | Sr. Civil Engineer | Jill Barnes | 2006-03-08 | 415/388-4033 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
1225 | 1 | 1 | MillValley | 2005-03-29 14:34 | 500 | 0 |  | 2005-03-29 14:34 |  | -- | Marion Ave @ Florence Ave | Mill Valley | Marin | 94941 |  |  | 2005-03-26 |  |  |  | Roots, Paper, Diapers & Baby Wipes | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MillValley | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Superintendent | James Powell | 2005-03-29 | 415/388-4033 | jbarnes@cityofmillvalley.org, wbush@cityofmillvalley.org | MINOR
3106 | 7 | 1 | Montara | 2006-03-30 09:54 | 4750 | 0 | 061874 | 2006-03-30 | Tim Costello |  | 151 Barranca Lane | Moss Beach | San Mateo | 94038 |  |  | 2006-03-30 | 12:20:00 A | 2006-03-30 | 3:30:00 AM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | District Manager | George Irving | 2006-03-30 | (650) 728-3545 | msd@montara.com , b.ptacek@bankofamerica.com, bobptacek@earthlink.net, cduffy@dudek.com, msd@coastside.net,jack@samcleanswater.org,ldw@ldworen.net,mjferreira@aol.com,pnagengast@ci.half-moon-bay.ca.us,scott@montara.com,scott.kathey@noaa.gov,shartsell@co.sanmateo.ca.us,tony@samcleanswater.org,jeanine@hmbreview.com,ricster@sbcglobal.net | 24HR |  |  | 650-726-0124 | [6 empty] | Montara
2748 | 4 | 1 | Montara | 2006-02-01 23:48 | 5000 | 0 | 06-0706 | 2006-02-02 | George Long |  | Cypress/Airport | Moss Beach | San Mateo | 94038 |  |  | 2006-02-01 | 8:30:00 PM | 2006-02-01 | 9:30:00 PM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | District Manager | George Irving | 2006-02-02 | (650) 728-3545 | msd@montara.com , b.ptacek@bankofamerica.com, bobptacek@earthlink.net, cduffy@dudek.com, msd@coastside.net,jack@samcleanswater.org,ldw@ldworen.net,pnagengast@ci.half-moon-bay.ca.us,scott@montara.com,scott.kathey@noaa.gov,shartsell@co.sanmateo.ca.us,tony@samcleanswater.org,jeanine@hmbreview.com,ricster@sbcglobal.net | 24HR |  |  | 650-726-1557 | [6 empty] | montara
2785 | 6 | 1 | Montara | 2006-02-09 16:23 | 5000 | 0 | 06-0706 | 2006-02-02 | George Long | George Long | Airport St and Marine Blvd. | Moss Beach | San Mateo | 94038 |  |  | 2006-02-01 | 8:30:00 PM | [5 empty] | RAINY WEATHER | Low | Pacific Ocean | STORM DRAIN | Yes | SAM Posted the beach access points for precautionary purposes. Signs were removed after San Mateo County Dept. Health Services released the beach per their testing. | No | Yes | No effects apparent. |  | Yes | Yes | No | No | No | Yes | Yes | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Montara | MANHOLE |  | BLOCKAGE | DEBRIS | --Select None-- |  | SAM Staff vactored 1100 gallons Rain/Sewage on 2/2/06. | Tech Svs Supervisor | Tony Pullin | 2006-02-09 | 650-726-0124 | msd@montara.com, b.ptacek@bankofamerica.com, bobptacek@earthlink.net, cduffy@dudek.com, msd@coastside.net, jack@samcleanswater.org,ldw@ldworen.net, pnagengast@ci.half-moon-bay.ca.us, scott@montara.com, scott.kathey@noaa.gov, shartsell@co.sanmateo.ca.us, tony@samcleanswater.org, ricster@sbcglobal.net, mfraser@ci.half-moon-bay.ca.us, dgorn@sbcglobal.net | MAJOR | George Irving | Montara | 650-728-3545 |  | 8888 Cabrollo Hwy | Montara | San Mateo | 94037 | George Irving | Montara Water & Sanitary District | 650-728-3545 |  | PO Box 370131 | Montara | San Mateo | 94038
2777 | 5 | 1 | Montara | 2006-02-08 13:11 | 200 | 0 |  | 2006-02-08 13:11 |  | -- | Highway 1 at 6th Street | Montara | San Mateo | 94037 |  |  | 2006-01-30 |  |  |  | Viewed stated volume. Area indicates there was water there longer than date of SSO. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Montara | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Technical Services S | Tony Pullin | 2006-02-08 | 650-726-0124 | msd@montara.com, b.ptacek@bankofamerica.com, bobptacek@earthlink.net, cduffy@dudek.com, msd@coastside.net, jack@samcleanswater.org, ldw@ldworen.net, pnagengast@ci.half-moon-bay.ca.us, scott@montara.com, scott.kathey@noaa.gov, shartsell@co.sanmateo.ca.us, tony@samcleanswater.org, ricster@sbcglobal.net, mfraser@ci.half-moon-bay.ca.us, dgorn@sbcglobal.net | MINOR
1199 | 3 | 5 | Montara | 2005-03-17 15:08 | 1000 | 300 | 05-1636 | 2005-03-13 | John Wade | Montara | 2nd Street From Main Street to Montara State Beach | Montara | San Mateo | 94038 |  |  | 2005-03-13 | 9:00:00 AM | [5 empty] | CLOUDY WEATHER | Low | Montara State Beach | STREET/CURB & GUTTER | No |  | No | No | Spill wetted an area of about 6 feet by 20 feet on the beach |  | No | Yes | No | No | No | No | No | No | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | Montara | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- |  |  | District Manager | George Irving | 2005-03-13 | (650) 728-3545 | msd@coastside.net, jack@samcleanswater.org, tony@samcleanswater.org | MAJOR | Tony Pullin | Sewer Authority Mid Coastside | 650-726-0124 |  | 1000 N. Cabrillo Hwy. | Half Moon Bay | San Mateo | 94019 | George Irving | Montara Sanitary | 650-728-3545 |  | PO Box 370131 | Montara | San Mateo | 94038
1080 | 2 | 1 | Montara | 2005-02-24 14:06 | 900 | 0 |  | 2005-02-24 14:06 |  | -- | Harte Street at Fir Street | Montara | San Mateo | 94037 |  |  | 2005-02-09 |  |  |  | Roots caused partial blockage in mainline. Sewage seeped through cracks in mainline causing weapage at surface. | [5 empty] | NO WATER INVOLVED | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Montara | OTHER | Seeped up through ground from broken mainline | BLOCKAGE | ROOTS |  |  |  | Technical Svs Spvr | Tony Pullin | 2005-02-24 | 6507260124 | jack@samcleanswater.org, tony@samcleanswater.org | MINOR
806 | 1 | 2 | Montara | 2005-01-10 14:50 | 2410 | 0 | 04-6809 | 2004-12-28 | Tony Pullin | Montara | Harte Street at Date Street | Montara | San Mateo | 94037 | 37.53816N | 122.50519W | 2004-12-27 | 7:50:00 AM | [5 empty] | RAINY WEATHER | Low | Montara Creek | SURFACE WATER IMPACT | No |  | No | No | Entire area was flooded due to exceptionally heavy rains. Could not distinguish SSO from flood waters |  | No | No | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | Montara | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | Area received over 4 inches of rain in 24 hours. Area subject to flooding during major rain events. Station could not keep up with the excessive flows. | TechSvsSpvr | Tony Pullin | 2004-12-28 | 650-726-0124 | msd@montara.com, tony@samcleanswater.org, jack@samcleanswater.org | MAJOR | Tony Pullin | Montara | 650-726-0124 | 125 | 1000 N. Cabrillo Hwy | Half Moon Bay | San Mateo | 94019 |  | Montara
4967 | 17 | 1 | MountainViewCity | 2007-03-19 | 1500 | 1500 | 07-1785 | 2007-03-19 | Brian Brown | MountainViewCity | Intersection of Highway 237 and Maude Ave. | Mountain View | Santa Clara | 94039 |  |  | 2007-03-19 | 0.74653 | [6 empty] | Low |  | STORM DRAIN | No |  | No | No | No sign of sewage in receiving waters. Ammonia test confirmed no sewage in receiving waters. |  | Yes | Yes | Yes |  |  | Yes | Yes |  |  |  | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | GREASE | -- Select One -- |  | Approximately 1500 gal. overflowed into storm system. Two Vac Cons were used to clean and flush storm system. Recovered 9000 gal. of liquid from storm system. Tested downstream and at Stevens Creek outfall with ammonia test strips. All tests were negative. Tested Stevens Creek outfall at 0900 on 3/20. Tests were negative for ammonia. Mtn. View received heavy rain at 0900 and no further tests will be performed. | Wastewater Superviso | Mike Mulhearn | 2007-03-20 | 650-903-6270
3183 | 16 | 1 | MountainViewCity | 2006-04-14 13:48 | 180 | 0 |  | 2006-04-14 13:48 |  | -- | 505 Cyprus Point Drive | Mountain View | Santa Clara | 94039 |  |  | 2006-04-14 |  |  |  | City sewer main overflowed due to sewer main blockage. Overflow estimated to be 2-3 gpm reported at 12:50 am and cleared at 1:50 am. City storm main was cleaned and flushed with two Vac Con hydroflusher combination trucks. Overflow area was cleaned and disinfected. We were unable to test the outfall at Stevens Creek due to high creek flow from recent rains. Clean up was completed at 3:15 am. Office of Emergency Services incident # is 06-2267. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MountainViewCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Wastewater Superviso | Mike Mulhearn | 2006-04-14 | 650-903-6329 | dave.serge@ci.mtnview.ca.us, | MINOR
2479 | 15 | 1 | MountainViewCity | 2006-01-04 12:52 | 70 | 0 | 057593 | 2006-01-04 | PHILLIP H. MCNERN |  | INTERSECTION OF PHYLLIS AVE. AND PAMELA DR. | MOUNTAIN VIEW | SANTA CLARA | 94039 |  |  | 2005-12-31 | 11:55:00 A | 2005-12-31 | 12:30:00 P | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | UTILITY 3 | PHILL MCNERN | 2006-01-04 | 650-903-6270 | mike.mulhearn@ci.mtnview.ca.us, | 24HR |  |  | 650-903-6204 | [6 empty] | MountainViewCity
1850 | 11 | 1 | MountainViewCity | 2005-09-23 08:33 | 120 | 20 | 05-5525 | 2005-09-23 | Mike Mulhearn | MountainViewCity | 1772 San Luis Ave | Mountain View | Santa Clara | 94039 | 37.406350 | 122.086402 | 2005-09-22 | 9:00:00 AM | [5 empty] | SUNNY WEATHER | Low | Region 2 | STORM DRAIN | No |  | No | No | Checked Permenente Creek at outfall. No visual sign of sewage, slight sewage odor. Source control took test at outfall, upstream and downstream of outfall.I estimate sewage was leaking at 1-2 gallons a minute. There was no sign of scum or long term leakage at outfall. Source control employee had conducted a volunter creek clean up the prior Saturday in this area and no odors or debris were observed. |  | Yes | Yes | No | No | No | Yes | Yes | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MountainViewCity | OTHER | Broken sewer main over broken storm main | INFRASTRUCTURE FAILURE | --Select None-- | LEAKS OF COLLECTION SYSTEM |  | We found a broken sewer main seeping into a broken joint on a storm drain lateral. We imediatly plugged a downstream drain and flushed and cleaned storm main. We then excavated and repaired the sewer main and lateral. Both pipes have been repaired and this section of sewer main is expected to be replaced during 2005-2006 sewer replacement schedule. | Wastewater Superviso | Mike Mulhearn | 2005-09-23 | 650-903-6270 | mike.mulhearn@ci.mtnview.ca.us, | MAJOR | Mike Mulhearn | MountainViewCity | 650-903-6270 |  | 231 North Whisman Rd. | Mountain View | Santa Clara | 94039 |  | City of Mountain View
1851 | 12 | 1 | MountainViewCity | 2005-09-23 08:40 | 120 | 20 | 05-5525 | 2005-09-23 | Mike Mulhearn | MountainViewCity | 1772 San Luis Ave | Mountain View | Santa Clara | 94039 | 37.406350 | 122.086402 | 2005-09-22 | 9:00:00 AM | [5 empty] | SUNNY WEATHER | Low | Region 2 | STORM DRAIN | No |  | No | No | Checked Permenente Creek at outfall. No visual sign of sewage, slight sewage odor. Source control took test at outfall, upstream and downstream of outfall.I estimate sewage was leaking at 1-2 gallons a minute. There was no sign of scum or long term leakage at outfall. Source control employee had conducted a volunter creek clean up the prior Saturday in this area and no odors or debris were observed. |  | Yes | Yes | No | No | No | Yes | Yes | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MountainViewCity | OTHER | Rat Bait block, suspended by wire, slipped off rung and plugged the pipe. | INFRASTRUCTURE FAILURE | --Select None-- | LEAKS OF COLLECTION SYSTEM |  | We found a broken sewer main seeping into a broken joint on a storm drain lateral. We imediatly plugged a downstream drain and flushed and cleaned storm main. We then excavated and repaired the sewer main and lateral. Both pipes have been repaired and this section of sewer main is expected to be replaced during 2005-2006 sewer replacement schedule. | Wastewater Superviso | Mike Mulhearn | 2005-09-23 | 650-903-6270 | mike.mulhearn@ci.mtnview.ca.us, | MAJOR | Mike Mulhearn | MountainViewCity | 650-903-6270 |  | 231 North Whisman Rd. | Mountain View | Santa Clara | 94039 |  | City of Mountain View
1806 | 10 | 2 | MountainViewCity | 2005-09-20 09:55 | 11200 | 10000 | 05-5179 | 2005-09-06 | Mike Mulhearn | MountainViewCity | 49 Showers Drive | Mountain View | Santa Clara | 94040 | 37.403852 | -122.10375 | 2005-09-06 | 8:28:00 AM | [5 empty] | SUNNY WEATHER | Low | Region 2 | STORM DRAIN | No |  | No | No | Walked Adobe Creek and checked the outfall. There was no odors or visual signs of sewage. Testing was performed at the outfall and upstream |  | Yes | Yes | No | No | No | Yes | Yes | No | No | 2005-09-09 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MountainViewCity | MANHOLE | Cause of blockage is unknown at this time. I have asked the management company for 49 Showers Dr. to investigate the cause of the overflow. | CAUSE UNKNOWN | --Select None-- | --Select None-- |  | Private sanitary sewer m/h overflowed in complex.We were notified this morning and removed blockage to resolve overflow. We removed 20,000 gal. of water 1/2 mile downstream. Storm main has a lot of water due to upstream water extraction system. Walked Adobe Creek and sampled.Found no odors or signs of contamination | Wastewater Superviso | Mike Mulhearn | 2005-09-06 | 650-903-6270 | mike.mulhearn@ci.mtnview.ca.us, | MAJOR | Mike Mulhearn | MountainViewCity | 650-903-6270 |  | 231 North Whisman Rd. | Mountain View | Santa Clara | 94039 | Dylan Loebig | Compass Management | 408-226-3300 | 220 | 20 Great Oaks Blvd. | San Jose | Santa Clara | 95119
1756 | 9 | 1 | MountainViewCity | 2005-09-06 12:55 | 10000 | 10000 | 05-5179 | 2005-09-06 | Mike Mulhearn |  | 49 Showers Drive | Mountain View | Santa Clara | 94040 |  |  | 2005-09-05 | 9:00:00 AM | 2005-09-06 | 9:30:00 AM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Wastewater Superviso | Mike Mulhearn | 2005-09-06 | 650-903-6239 | mike.mulhearn@ci.mtnview.ca.us, | 24HR |  |  | 650-903-6270 | [6 empty] | MountainViewCity
1568 | 7 | 1 | MountainViewCity | 2005-06-27 13:47 | 800 | 0 |  | 2005-06-27 13:47 |  | -- | 1033,1050 Crestview Drive | Mountain View | Santa Clara | 94043 |  |  | 2005-06-26 |  |  |  | Sewer Main blockage caused flooding in two buildings. 1033 Crestview has minor damage to floor and flooding in a parking garage. No damage at 1050. A clean up/restoration company arrived one hour after overflow. City storm system was flushed/vacuumed with two Vac Con units. Sewage was returned to the sanitary system. The blockage was caused by a combination of grease and roots. This section of sewer main is now on a three month cleaning schedule. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MountainViewCity | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Wastewater Superviso | Mike Mulhearn | 2005-06-27 | (650)903-6270 | mike.mulhearn@ci.mtnview.ca.us, | MINOR
1566 | 6 | 1 | MountainViewCity | 2005-06-27 13:29 | 100 | 0 |  | 2005-06-27 13:29 |  | -- | 660 San Antonio Rd. | Mountain View | Santa Clara | 94043 |  |  | 2005-06-22 |  |  |  | Sewer Main stoppage caused private c/o to overflow 100 gal. into private storm system. Private system flowed to City System. Used Vac Con to flush/vacuume storm system and street sweeper to clean parking lot. All sewage returned to sanitary system. Sewer main was flushed and cleaned with rootsaw the following day. This line is now on a three month cleaning schedule. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MountainViewCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Wastewater Superviso | Mike Mulhearn | 2005-06-27 | (650)903-6270 | mike.mulhearn@ci.mtnview.ca.us, | MINOR
1540 | 5 | 1 | MountainViewCity | 2005-06-15 13:46 | 100 | 0 |  | 2005-06-15 13:46 |  | -- | Intersection of E.C.R. and El Monte Ave | Mountain View | Santa Clara | 94043 |  |  | 2005-06-11 |  |  |  | M/H overflowed spilling approximately 100 gal. into adjacent drain inlet. Crew responded with hydroflusher vacuume truck. Blockage was removed. Crew flushed and and vacuumed storm main and drain inlet. This section of sewer main will be placed on a three month cleaning schedule due to grease. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MountainViewCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Wastewater Superviso | Mike Mulhearn | 2005-06-15 | 650-903-6270 | mike.mulhearn@ci.mtnview.ca.us, | MINOR
1404 | 4 | 1 | MountainViewCity | 2005-05-16 11:31 | 100 | 0 |  | 2005-05-16 11:31 |  | -- | 800 California Street | Mountain View | Santa Clara | 94043 |  |  | 2005-05-11 |  |  |  | Main stoppage caused 15-30 to overflow from c/o on 5/11/05. 5-10 gal. entered the storm drain. Area was washed/vacuumed/cleaned. The following day while televising the lateral a c/o was found across the street that had overflowed into two storm drains. The drains and storm main were flushed and cleaned. Very little sewage was found in the storm system. I have filed this report due to the possibility the total spill exceeded 100 gal. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MountainViewCity | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Wastwwater Superviso | Mike Mulhearn | 2005-05-16 | 650-903-6270 | mike.mulhearn@ci.mtnview.ca.us, | MINOR
1336 | 3 | 1 | MountainViewCity | 2005-04-28 11:25 | 100 | 0 |  | 2005-04-28 11:25 |  | -- | 707 Continental Circle | MOUNTAIN VIEW CAL. | SANTA CLARA | 94043 |  |  | 2005-04-22 |  |  |  | SEWER MAIN OVERFLOW. DUE TO LARGE ADJACENT CONSTRUCTION PROJECT DRAINS WERE PROTECTED BY BERM. 15-30 GAL. ENTERED DI. STORM MAIN AND DRAINS WERE FLUSHED AND VACUUMED WITH HYDROFLUSHER. ON 4/25 SEWER MAIN WAS CLEANED WITH ROOT SAW AND HYDROFLUSHED. REMOVED ROOTS AND GREASE.THIS SECTION OF SS MAIN WILL BE ADDED TO 2 MONTH CLEANING SCHEDULE. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MountainViewCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | WASTEWATER SUPERVISO | MIKE MULHEARN | 2005-04-28 | 650-903-6270 | mike.mulhearn@ci.mtnview.ca.us, | MINOR
5042 | 24 | 2 | MtViewSD | 2007-03-27 | 33000 | 1200 | 07-1952 | 2007-03-27 | Dale W. Riddle | MtViewSD | oveflow occured at MH#R02017 at the end of Alan Way | Martinez | Contra Costa | 94553 |  |  | 2007-03-26 | 0.97917 |  |  | Operator Error at Pump Station |  |  |  | Low |  | SURFACE WATER IMPACT | No |  | No | Yes | No Debris,No Odors, Spill was contained to a 2 acre marsh on Central Contra Costa Sanitary District Property. |  | Yes | Yes | No |  |  | Yes | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE | Operator Error at Pump Station | BYPASS | -- Select One -- | -- Select One -- |  | The sewage discharged from MH#R02017 located at the end of Alan Way was caused by Operator error at MVSD's #2 pump station. The resulting oveflow entered a nearby 2 acre marsh owned by CCCSD. The discharge was confined to the marsh and did not reach the creek downstream. Cleanup and recovery started immediately.Sampling was preformed upstream and downstream of the impacted area. No noticeable differences were realized from the 3 samples. | District Manager | Dale W. Riddle | 2007-03-27 | 925-228-5635x2
4891 | 23 | 1 | MtViewSD | 2007-03-11 07:41 | 5 | 0 |  | 2007-03-11 07:41 |  | -- | 1101 Shell Ave | Martinez | Contra Costa | 94553 |  |  | 2007-03-01 |  |  |  | during regular sewer line maintenance activities, the home exprinced toilet backsplash,the backsplash area was contained to the bathroom and toilet area. cleaning services were called and responded within 1-2 hours for cleanup | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | CAUSE UNKNOWN | -- Select One -- |  | toilet |  | Operations Manager | Dale W. Riddle | 2007-03-11 | 925-228-5635
4848 | 22 | 1 | MtViewSD | 2007-03-01 14:43 | 50 | 0 |  | 2007-03-01 14:43 |  | -- | 313 Glenwood Ct E02004-E02001 | Martinez | Contra Costa | 94553 |  |  | 2007-02-24 |  |  |  | street area was cleaned with fresh water | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Operations Manager | Dale W. Riddle | 2007-03-01 | 925-228-5635
4654 | 21 | 2 | MtViewSD | 2007-02-01 14:56 | 30 | 0 |  | 2007-02-01 14:56 |  | -- | Muir Road between Hull Lane and Roman Way / Manhole located in planted area next to sidewalk | Martinez | Contra Costa | 94553 |  |  | 2007-01-31 |  |  |  | Recovered small portion of spill. Sand bagged storm drain flushed area with 300 gallons of water. Recovered all flush water and returned to sanitary sewer. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Senior Operator | Michael Roderick | 2007-02-01 | 925-228-5635
4519 | 20 | 1 | MtViewSD | 2007-01-16 12:43 | 200 | 0 |  | 2007-01-16 12:43 |  | -- | 1060 Palisade Dr and Melee Lane E04042-E04036 | Martinez | Contra Costa | 94553 |  |  | 2007-01-15 |  |  |  | no debris on site most soaked into dirt area. area cleaned and sanitized by restoration company 1/16/2007 | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Operation Manager | Dale Riddle | 2007-01-16 | 925-228-5635
4090 | 19 | 1 | MtViewSD | 2006-11-09 11:04 | 425 | 0 |  | 2006-11-09 11:04 |  | -- | Intersection of Pacheco Blvd and Camino Del Sol | Martinez | Contra Costa | 94553 |  |  | 2006-11-05 |  |  |  | Time of call 3:01Pm.Time of arrival 3:45Pm.Time SSO stopped 3:50Pm.Cleaned and flushed area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MtViewSD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Senior Operator | Michael Roderick | 2006-11-09 | 228-5635x17 | driddle@mvsd.org;dcontreras@mvsd.org, | MINOR
3846 | 18 | 1 | MtViewSD | 2006-09-05 16:20 | 50 | 0 |  | 2006-09-05 16:20 |  | -- | Pacheco Blvd and Shell Ave MH# P08009 | Martinez | Contra Costa | 94553 |  |  | 2006-09-05 |  |  |  | are was flushed with fresh water. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MtViewSD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Operations Manager | Dale W. Riddle | 2006-09-05 | 925-228-5635 | driddle@mvsd.org;dcontreras@mvsd.org, | MINOR
3297 | 17 | 1 | MtViewSD | 2006-05-04 13:59 | 500 | 0 |  | 2006-05-04 13:59 |  | -- | 1198 Foxhill Dr | Martinez | Contra Costa | 94553 |  |  | 2006-05-03 |  |  |  | manhole # G01077, roots caused blockage and overflow into neighboring backyard. no debris from the overflow was on site, most of the overflow soaked into the ground, minor cleanup. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MtViewSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Operations Manager | Dale W. Riddle | 2006-05-04 | 925-228-5635 | driddle@mvsd.org;dcontreras@mvsd.org, | MINOR
3016 | 16 | 1 | MtViewSD | 2006-03-16 15:56 | 250 | 0 |  | 2006-03-16 15:56 |  | -- | Manhole near 1114 Paridise Dr | Martinez | Contra Costa | 94553 |  |  | 2006-03-16 |  |  |  | Manhole overflowing approximately 2 hours @ 1.9 gallons per minute. Setup pump at down stream storm drain recovered 750 gallon of flush water. Sumped flush water to nearby manhole. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MtViewSD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Senior operator | Mike Roderick | 2006-03-16 | 2285635x17 | driddle@mvsd.org;dcontreras@mvsd.org, | MINOR
2523 | 13 | 2 | MtViewSD | 2006-01-05 15:03 | 1200 | 0 | 05-7599 | 2005-12-31 | Dale W. Riddle | MTviewSD | 1160 Plaza Dr-Garage/Basement Area | Martinez | Contra Costa | 94553 |  |  | 2005-12-31 | 8:30:00 AM | [5 empty] | RAINY WEATHER | Low |  | BUILDING/STRUCTURE | No |  | No | No | did not enter receiving waters |  | Yes | Yes | Yes | No | No | No | No | No | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MTviewSD | PIPE | homeowner sump drain | NATURAL DISASTER | --Select None-- | --Select None-- | extreme rain conditions | backup occured in homeowner's lateral, duration of backup is questionable as the homeowner did not know the start time and it had ceased by the time District's Staff arrived. 1200 gal estimated by the area of the garage and possible flow through. | Operations Manager | Dale W. Riddle | 2005-12-31 | 925-228-5635x2 | driddle@mvsd.org;dcontreras@mvsd.org, | MAJOR | Dale W. Riddle | MTviewSD | 925-228-5635 | 20 | 3800 Arthur Rd | Martinez | Contra Costa | 94553 |  | MTViewSD
2524 | 14 | 2 | MtViewSD | 2006-01-05 15:13 | 27000 | 0 | 05-7599 | 2005-12-31 | Dale W. Riddle | MTviewSD | manhole located across 197 Howe RD flowed directly to strom drainage creek | Martine CA | Contra Costa | 94553 |  |  | 2005-12-31 | 10:00:00 A | [5 empty] | RAINY WEATHER | Low | Howe Creek/Peyton Slough/Reqion 2 SF | SURFACE WATER IMPACT | No |  | No | Yes | no visible debris and negligable impact due to diluted flows |  | No | No | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MTviewSD | MANHOLE |  | NATURAL DISASTER | --Select None-- | --Select None-- | excessive rains | excessive rains caused system to backup. overflow subsided after weather conditions changed | Operations Mamanger | Dale W. Riddle | 2005-12-31 | 925-228-5635x2 | driddle@mvsd.org;dcontreras@mvsd.org, | MAJOR | Dale W. Riddle | Mtview SD | 925-228-5635 | 20 | 3800 Arthur RD | Martinez | Contra Costa | 94553 |  | MTViewSD
2528 | 15 | 3 | MtViewSD | 2006-01-05 17:06 | 176000 | 0 | 05-7599 | 2005-12-31 | Dale W. Riddle | MTviewSD | 3800 Arthur RD manhole located on plant road and treatment plant | Martinez | Contra Costa | 94553 |  |  | 2005-12-31 | 5:30:00 AM | [5 empty] | RAINY WEATHER | Low | McNabney Marsh/Moorhen Marsh/Peyton Slough/Region | SURFACE WATER IMPACT | No |  | No | Yes | no visible impact and negligible impact due to dilute flows |  | Yes | Yes | No | No | No | Yes | Yes | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | MTviewSD | MANHOLE | Treatment Plant and Storm Drain System | NATURAL DISASTER | --Select None-- | --Select None-- | excessive rain condition | Treatment Plant overload due to excissive rains for an extended period of time | Operations Manager | Dale W. Riddle | 2005-12-31 | 925-228-5635x2 | driddle@mvsd.org;dcontreras@mvsd.org, | MAJOR | Dale W. Riddle | MTviewSD | 925-228-5635 | 20 | 3800 Arthur Rd | Martinez | Contra Costa | 94553 |  | MTViewSD
2278 | 12 | 1 | MtViewSD | 2005-12-19 11:33 | 450 | 0 |  | 2005-12-19 11:33 |  | -- | 911 Palm Ave | Martinez | Contra Costa | 94553 |  |  | 2005-12-18 |  |  |  | overflow contained to yard area, mixed with rain and soaked to ground. EV-Link was called and they dispatched a cleaning service. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MtViewSD | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | Operations Manager | Dale W. Riddle | 2005-12-19 | 925-228-5635 | driddle@mvsd.org;dcontreras@mvsd.org, | MINOR
2193 | 11 | 1 | MtViewSD | 2005-11-30 13:27 | 250 | 0 |  | 2005-11-30 13:27 |  | -- | 1051 Sierra Ave | Martinez | Contra Costa | 94553 |  |  | 2005-11-23 |  |  |  | found blockage between MH#'s P09022 and P09007 Orange St and Bush St. effected area clean by contract firm EV Link. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MtViewSD | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | Operations Manager | Dale W. Riddle | 2005-11-30 | 925-228-5635*2 | driddle@mvsd.org;dcontreras@mvsd.org, | MINOR
1740 | 9 | 1 | MtViewSD | 2005-08-30 08:13 | 30 | 0 |  | 2005-08-30 08:13 |  | -- | manholes# D11-2 and D11-2a located on Denormande and Pacheco Blvd | Martinez | Contra Costa | 94553 |  |  | 2005-08-29 |  |  |  | mainline was jetted and blockage cleared, re-clean mainline on 8/30/05 | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MtViewSD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Operations Manager | Dale W. Riddle | 2005-08-30 | 925-228-5635 | driddle@mvsd.org;dcontreras@mvsd.org, | MINOR
983 | 6 | 1 | MtViewSD | 2005-02-08 09:07 | 100 | 0 |  | 2005-02-08 09:07 |  | -- | 2995 Upton Rd | Martinez | Contra Costa | 94553 |  |  | 2005-02-06 |  |  |  | Blockage located at MH#V25-3C2 located in Apartments off Center Ave. SSO at 2995 Upton Rd in yard area less than 100 gals. roots removed from manhole, SSO area cleaned | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MtViewSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SO | Dale Riddle | 2005-02-08 | 9252285635*20 | driddle@mvsd.org;dcontreras@mvsd.org | MINOR
800 | 5 | 1 | MtViewSD | 2005-01-10 10:57 | 800 | 0 |  | 2005-01-10 10:57 |  | -- | manhole near 129 Windhover Way | Martinez | Contra Costa | 94553 |  |  | 2005-01-10 |  |  |  | approxmitely 800 gallons overflowed to street surface and strom drain. the area and storm drain was flushed with 1500 gallons recycled water. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MtViewSD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SO | Dale W. Riddle | 2005-01-10 | 925-228-5635 | driddle@mvsd.org;dcontreras@mvsd.org | MINOR
766 | 4 | 1 | MtViewSD | 2005-01-05 11:06 | 1950 | 600 | 05-0077 | 2005-01-04 | David R. Contreras | Dale W. Riddle | Shell Oil Refinery | Martinez | Contra Costa | 94553 |  |  | 2005-01-04 | 3:05:00 PM | [5 empty] | CLOUDY WEATHER | Low | Peyton Slough\Peyton Watershed\Region 2 S.F. | STORM DRAIN | No |  | No | Yes | No Adverse effects noted to receiving waters. Visual observations taken, DO measerements taken,No fish kill, No odors |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | MTViewSD | MANHOLE |  | CAUSE UNKNOWN | --Select None-- | --Select None-- | possible grease blockage | Cty Mtz notified MVSD of the manhole overflowing at the Shell Oil refinery at approxmitly 3:00PM. the cause of the blockage was undeterminened. immediate access to the manhole was diffuclt due to Refinery Security and Safety concerns. overflow was stopped and cleanup began immediatly. flushed the area around the manhole with approximetly 3000 gals of raw drinking water. recovered flushwater to the nearby manhole. cleanup efforts continuing thru 1/5/2005. verbal notifaction was given to the City of Martinez Stormwater Manager notified 1/4/2005 | SO | Dale W. Riddle | 2005-01-05 | 925-228-5635 | driddle@mvsd.org;dcontreras@mvsd.org | MAJOR | David R. Contreras | MtViewSD | 925-228-5635 |  | 3800 Arthur Rd | Martinez | Contra Costa | 94553 |  | MTViewSD
691 | 3 | 1 | MtViewSD | 2004-12-30 09:26 | 750 | 0 |  | 2004-12-30 09:26 |  | -- | Manhole @ 755 Missouri St. Creek Bed | Martinez | Contra Costa | 94553 |  |  | 2004-12-29 |  |  |  | Initially 1200 gallons recovered from creek. Area cleaned then flushed and recovered 1500 gallons Back to nearby manhole. Coliform samples taken from upstream and down stream of SSO. OES #04-6882. City of martinez storm water manager contacted. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MtViewSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Operator | Michael Roderick | 2004-12-30 | 925-228-5635 | driddle@mvsd.org;dcontreras@mvsd.org | MINOR
689 | 2 | 1 | MtViewSD | 2004-12-30 09:10 | 50 | 0 |  | 2004-12-30 09:10 |  | -- | #1 Morello Heights Dr | Martinez | Contra Costa | 94553 |  |  | 2004-12-27 |  |  |  | Blockage in manhole spill contained to area around cleanout. the area was cleaned by MVSD personel | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MtViewSD | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | SO | Dale W. Riddle | 2004-12-30 | 925-228-5635 | driddle@mvsd.org;dcontreras@mvsd.org | MINOR
549 | 1 | 1 | MtViewSD | 2004-12-16 08:18 | 350 | 0 |  | 2004-12-16 08:18 |  | -- | Manhole located in front of address 888 Howe Rd | Martinez | Contra Costa | 94553 |  |  | 2004-12-14 |  |  |  | 1/3 of the overflow was captured in the storm drain. the effected street area was flushed, all recovered and flush water was pump to a nearby manhole. coliform samples were taken upstream and downstream of the stormdrain. the storm drain was then flushed with 3000 gallons reclaimed water. no visual impact on nearby open areas of the fenced creek. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | MTViewSD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Senior Operator | Dale W. Riddle | 2004-12-16 | 925-228-5635 |  | MINOR
4720 | 10 | 1 | NapaSD | 2007-02-09 10:07 | 50 | 0 |  | 2007-02-09 10:07 |  | -- | Cabot Way | Napa | Napa | 94559 |  |  | 2007-02-07 |  |  |  | Washed back into Sanitary Sewer. Minor spill, no other areas affected. | [5 empty] | NO WATER INVOLVED | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | CSW3 | Greg Dawson | 2007-02-09 | (707) 258-6000
4181 | 9 | 1 | NapaSD | 2006-12-04 10:31 | 300 | 0 |  | 2006-12-04 10:31 |  | -- | Intersection of Berks and Oxford Sts | Napa | Napa | 94558 |  |  | 2006-12-01 |  |  |  | Spill was found by NSD employees checking lines. Area drains were blocked. Sewage was vacuumed up after blockage was cleared. Storm drains were cleaned and vacuumed. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | CSMW3 | Greg Dawson | 2006-12-04 | 707-312-1593
3206 | 8 | 1 | NapaSD | 2006-04-19 18:08 | 10000 | 1200 | 06-2366 | 2006-04-19 | Greg Dawson | Greg Dawson | 1815 Silverado Trail In back of property near river | Napa | Napa | 94558 |  |  | 2006-04-19 | 10:01:00 A | [5 empty] | SUNNY WEATHER | High | Napa River | SURFACE WATER IMPACT | No |  | No | Yes | At first inspection we could see water going from the river bank and the silt trail was going down stream in a narrow band and rapidly diffusing. The silt trail was not evident after 50 ft. Tide appeared to be going out. |  | Yes | No | No | No | No | Yes | No | Yes | No | 2006-04-26 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | NapaSD | OTHER | Exact cause of Force Main Failure to still be determined. | INFRASTRUCTURE FAILURE | --Select None-- | BREAKAGE OF COLLECTION SYSTEM |  | Spill reported at 10:01, NSD response person immediatly called for extra help. Determined bypass would be needed. Tried to find ways to lessen flow going to river. Used Vacuum truck to keep level down in mains to lessen amount of overflow starting at 12:45. Pumps where shut down between 13:35 to 15:45. Bypass put into operation by 15:45. Pumps returned to normal operation after inspection of bypass showed no leaks. Cause of pipeline failure to still be determined. | Collections Wrkr 3 | Greg Dawson | 2006-04-19 | 707-258-6000 | jmerrywe@co.napa.ca.us, | MAJOR | Greg Dawson | NapaSD | (707)258-6000 | 525 | 935 Hartle Ct. | Napa | Napa | 94559 |  | Napa Sanitation District
2678 | 7 | 2 | NapaSD | 2006-01-24 13:01 | 1000000 | 100 | 2423 | 2006-01-01 | Sharleen Maglione | NapaSD | Had 30 manholes that were observed overflowing through out the City of Napa, and 400 manholes submeged under the flood waters | Napa | Napa | 94558 |  |  | 2005-12-31 | 12:57:00 P | [5 empty] | RAINING FOR SEVERAL DAYS | High |  | STORM DRAIN | No |  | No | Yes | Stormdrains, creeks and river |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | NapaSD | MANHOLE | Rain above 100 year storm event, and flooding through out the city of Napa | NATURAL DISASTER | MULTIPLE CAUSES | MULTIPLE CAUSES | Rain above 100 year storm event, and flooding through out the city of Napa |  | Collection System Ma | Gerald Merryweather | 2006-01-12 | 707-258-6000 | jmerrywe@co.napa.ca.us, | MAJOR | Gerald Merryweather | NapaSD | (707)258-6000 | 526 | 935 Hartle Ct. | Napa | Napa | 94559 |  | Napa Sanitation District
1770 | 6 | 1 | NapaSD | 2005-09-08 10:45 | 50 | 0 |  | 2005-09-08 10:45 |  | -- | Excecutive Way | Napa | Napa | 94559 |  |  | 2005-09-07 |  |  |  | NSD reclaimed Irrigation water had entered the recovery system is such a large amount that it overflowed out of the pick hole on a Manhole. Total amount was approx. 50 gallons. NSD was not notified until 9:30 a.m. on 9/8/05. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | NapaSD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | CSMW3 | Greg Dawson | 2005-09-08 | 707-258-6000 | jmerrywe@co.napa.ca.us, | MINOR
991 | 5 | 1 | NapaSD | 2005-02-09 10:36 | 600 | 0 |  | 2005-02-09 10:36 |  | -- | 3373 Browns Valley Rd | Napa | Napa | 94558 |  |  | 2005-02-08 |  |  |  | Contractor was doing air test on trenchless repair, plug was in line approx. 15 minutes, overflow started at 2 manholes and 1 clean out. Plug pulled. Flow returned to normal, area was washed down and storm drains cleaned and vacuumed. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | NapaSD | OTHER | 2 manholes and 1 clean out | BYPASS | --Select None-- |  |  |  | Collections Worker 3 | Greg Dawson | 2005-02-09 | 7073121593 | jmerrywe@co.napa.ca.us | MINOR
668 | 3 | 1 | NapaSD | 2004-12-28 16:39 | 50 | 0 |  | 2004-12-28 16:39 |  | -- | Kent St. at Between Imola Ave. and Wimbledon St. | Napa | Napa | 94558 |  |  | 2004-12-27 |  |  |  | During heavy rain event. Excessive inflow added to problem of constricted line. | [5 empty] | UNKNOWN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | NapaSD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | CW# | Greg Dawson | 2004-12-28 | 707-312-1593 | jmerrywe@co.napa.ca.us | MINOR
410 | 2 | 1 | NapaSD | 2004-12-03 18:08 | 5 | 0 |  | 2004-12-03 18:08 |  | -- | 1335 Sproul Ave. In back yard on Easement line | Napa | Napa | 94559 |  |  | 2004-12-03 |  |  |  | Baby wipes and rags hung up on turn on easement main line. Opened main line blockage and washed all overflow into sewer clean-outs. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | NapaSD | CLEAN OUT |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Coll Sys Wrkr 3 | Greg Dawson | 2004-12-03 | (707)3121593 |  | MINOR
397 | 1 | 1 | NapaSD | 2004-12-02 14:38 | 500 | 0 |  | 2004-12-02 14:38 |  | -- | 585 - 615 Stonehouse Dr. Vineyard Terrace Apartments (707)253-7529 | Napa | Napa | 94558 |  |  | 2004-12-02 |  |  |  | Main was plugged by rags. Used combination vacuum/cleaner truck to open main and wash down and vacuum entire spill. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | NapaSD | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | CMW3 | Greg Dawson | 2004-12-02 | (707)3121593 |  | MINOR
4006 | 6 | 1 | NorthSanMateo | 2006-10-17 14:34 | 750 | 0 |  | 2006-10-17 14:34 |  | -- | 333 Hickey Blv | Daly City | San Mateo | 94015 |  |  | 2006-10-16 |  |  |  | Liquid only, no solids overflowed from M.H. No sewage entered any catch basin. Crew washed down street surface and captured approx. 1000 gallons with Vac Truck. Mainline was televised and problems identified. Repairs scheduled. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | northsanmateo | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Collection System Le | Mark Pappas | 2006-10-17 | (650) 991-8200 | croyer@dalycity.org, psweetland@dalycity.org | MINOR
3447 | 5 | 1 | NorthSanMateo | 2006-06-02 11:58 | 700 | 0 |  | 2006-06-02 11:58 |  | -- | 1399 Skyline Dr | Daly City | San Mateo | 94015 |  |  | 2006-06-01 |  |  |  | Power outage in area resulted in overflow from Lift Station facility manhole.Sewage did not reach receiving waters,but samples being taken. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | northsanmateo | PUMP STATION |  | ELECTRICAL POWER FAILURE | --Select None-- |  |  |  | Leadworker | Kevin McCarthy | 2006-06-02 | (650) 991-8200 | croyer@dalycity.org, psweetland@dalycity.org | MINOR
3775 | 4 | 2 | NorthSanMateo | 2006-08-22 15:39 | 450 | 0 |  | 2006-08-22 15:39 |  | -- | 6843 Mission St | Daly City | San Mateo | 94015 |  |  | 2005-12-01 |  |  |  | Mainline had a partial plug. Sewage left from cracks in pavement, and into stormdrain. Heavy rain at the time did not allow us to capture sewage from storm drain. No solids deposited in storm drain. Televised mainline, found broken pipe, repairs made. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | northsanmateo | OTHER | Cracks In Pavement | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Collection System Le | Mark Pappas | 2005-12-06 | 650 991 8200 | croyer@dalycity.org, psweetland@dalycity.org | MINOR
2123 | 3 | 2 | NorthSanMateo | 2005-11-16 13:39 | 5600 | 2000 | 05-6608 | 2005-11-15 | Mark Pappas | NorthSanMateo | 2245 Gellert Blvd. | South San Francisco | San Mateo | 94080 | 122 | 37 | 2005-11-14 | 3:20:00 PM | [5 empty] | SUNNY WEATHER | Low | Colma Creek | STORM DRAIN | No |  | No | No | No visable signs of sewage noted during inspection |  | Yes | Yes | Yes | No | No | Yes | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | NorthSanMateo | MANHOLE |  | INFRASTRUCTURE FAILURE | --Select None-- | PUMP STATION FAILURE |  | Initial call came in at 15:20. Response crew dispatched for overflowing manhole. Additional staff called in to assist in cleanup efforts. Samples were taken and are being analyzed for coliform. The results are pending. Staff investigation concluded a series of circumstances lead to the incident. A level controller was inadvertently left in the "simulate flow" (fixed speed) mode at the District's Roundtree Lift Station following the replacement of a check valve. In addition, the wetwell's high-level alarm failed when the float that triggers the alarm became hung up. The alarm has been retested and is working. The float has been relocated to prevent similar failure in the future. | Manager of Tech Srvs | Cynthia Royer | 2005-11-15 | 650-991-8200 | croyer@dalycity.org, psweetland@dalycity.org, tpiccolotti@dalycity.org | MAJOR | Cynthia Royer | NorthSanMateo | 650-991-8200 |  | 153 Lake Merced Blvd | Daly City | San Mateo | 94015 | NorthSanMateo | northsanmateo | 650-991-8200 |  | 153 Lake Merced Blvd | Daly City | San Mateo | 94015
1780 | 2 | 1 | NorthSanMateo | 2005-09-14 14:45 | 800 | 0 |  | 2005-09-14 14:45 |  | -- | address 698, 690, 680, and 672 Niantic Ave | Daly City | San Mateo | 94015 |  |  | 2005-09-13 |  |  |  | As a result of a mainline stoppage, which occured on Westlake ave and Niantic Ave., four house garages backed up with sewage. We estimated the amount in these four garages as a combined amount of 800 gal. After the mainline stoppage was cleared, the spilled sewage drained out of the garages and into the sewer thru the garage floor drains. This left the garage floors wet with sewage. This small amount of sewage was extracted by the restoration company. At no time did the public come into contact with the sewage and the appropriate clean up measures are being implemented. At no time did this sewage reach a storm system or the receiving waters of the State Of Califronia or The United States. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | northsanmateo | OTHER | floor drains | CAUSE UNKNOWN | --Select None-- |  |  |  | Collection lead | Bob Donati | 2005-09-14 | 650 9918211 | croyer@dalycity.org, psweetland@dalycity.org | MINOR
997 | 1 | 2 | NorthSanMateo | 2005-02-09 13:55 | 2872 | 0 | 05-0753 | 2005-02-01 | Cynthia Royer | northsanmateo | 131 Price Street | Daly City | San Mateo | 94014 | 122.46 | 37.69 | 2005-01-31 | 4:40:00 PM | [5 empty] | CLOUDY WEATHER | Low | Colma Creek | STORM DRAIN | No |  | No | No | No visable signs of sewage noted during inspection |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | northsanmateo | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS | --Select None-- |  | Initial call received at 16:40 p.m. Standby crew dispatched, 5 staff members responded. Discharge flow abated at 18:45 p.m. Staff investigation concluded that blockage was caused by contractor not adhering to contract specifications to prevent debris from falling into the manhole during rehabilitation work. | Manager of Tech Srvs | Cynthia Royer | 2005-02-09 | 650-991-8200 | croyer@dalycity.org | MAJOR | Cynthia Royer | northsanmateo | 650-991-8200 |  | 153 Lake Merced Blvd | Daly City | San Mateo | 94015 | Eugene Michael Carew | Bay Pacific Pipeline Inc | 415-850-6874 |  | PO Box 1162 | Novato | Marin | 94948-1162
4939 | 32 | 2 | Novato | 2007-03-11 | 1125 | 0 | 07-1557 | 2007-03-11 | Timothy M. O'Connor | Novato | Spill occurred in front of 150 Alameda Del Prado, Novato CA | Novato | Marin | 94945 |  |  | 2007-03-11 | 0.43403 | [6 empty] | Low | Pacheco Creek | SURFACE WATER IMPACT | No |  | No | Yes | Visual inspection showed no change to water color or appearance. Fish and aquatic organisms in the spill path appeared active and unaffected. |  | Yes | No | No |  |  | Yes | Yes |  |  | 2007-03-14 | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | GREASE | -- Select One -- |  | A grease blockage in the District sewer main caused the overflow. The overflow was first noted by a passerby and reported to the district. The District responded and relieved the blockage. The overflow water went directly into a free running creek. We initiated our sampling and public notification protocol and posted the waterway. | Superintendent | Timothy M O'Connor | 2007-03-11 | 415-892-1694
4938 | 31 | 2 | Novato | 2007-03-08 | 5850 | 200 | 07-1503 | 2007-03-08 | Timothy M O'Connor | Same | 48 Capilano Dr. | Novato | Marin | 94945 |  |  | 2007-03-07 | 0.66667 | [6 empty] | Low | Arroyo San Jose | SURFACE WATER IMPACT | No |  | No | Yes | Visual inspection showed no change to water color or appearance. Fish and aquatic organisms in the spill path appeared active and unaffected. |  | Yes | Yes | No |  |  | Yes | Yes |  |  | 2007-03-09 | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | ROOTS | -- Select One -- |  | A root blockage in the District sewer main caused the overflow. The overflow was first noted on 3/7/07, appx. 1600 hrs by a local resident, but he did not report the problem until 1030 hrs, 3/8/07 for a 19.5hr duration. The District releived the blockage, cleaned the storm drain and recovered approximately 200 gallons of wastewater. The remainder went into the Arroyo San Jose which is a large, meandering impoundment used as an irrigation source for the Marin Country Club. We initiated our sampling and public notification protocol and posted the water way. This water way alternates between a free running creek and large containment ponds and has a large waterfowl population. | Superintendent | Timothy M. O'Connor | 2007-03-08 | 415-892-1694
4808 | 30 | 1 | Novato | 2007-02-23 16:10 | 750 | 0 |  | 2007-02-23 16:10 |  | -- | 400 Alameda del Prado | Novato | Marin | 94945 |  |  | 2007-02-22 |  |  |  | The overflow was determined to be caused by a grease blockage in the Districts main line. We arrived on site and releived the blockage. The manhole overflowed into a storm drain catch basin and we tracked it to an open ground discharge point where the sewage puddled. We recovered 100% of the overflow, washdown, and cleaning water. We recleaned the sewer main and will televise the main to confirm the cause of the overflow. We were notified of the overflow at 9:35am and releived the blockage at 10:00am. I estimated the overflow rate at 30 gpm for 25 minutes. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Superintendent | Timothy M. O'Connor | 2007-02-23 | 415-892-1694
4084 | 29 | 1 | Novato | 2006-11-08 14:59 | 375 | 0 |  | 2006-11-08 14:59 |  | -- | 640 Wilson St | Novato | Marin | 94945 |  |  | 2006-11-04 |  |  |  | This overflow was caused by root intrusion. We used CCTV equipment to inspect the sewer main and found several areas of sever root intrusion. We rodded the main, removed the roots and re-inspected with CCTV equipment. This section of main will be placed on a yearly preventive maintenance schedule until the pipe can be lined or replaced. We recovered approximately 90 percent of the overflow water. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Novato | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | superintendent | Timothy M. O'Connor | 2006-11-08 | 415-892-1694 | edm@novatosan.com, bevj@novatosan.com, timo@novatosan.com | MINOR
4037 | 28 | 1 | Novato | 2006-10-26 14:01 | 150 | 0 |  | 2006-10-26 14:01 |  | -- | Open space easement area at the end of Thornhill Ct. | Novato | Marin | 94945 |  |  | 2006-10-20 |  |  |  | Blockage occurred approximately 140 ft upstream from mahhole G25017 in an open space easement area. We releived the blockage using a hydro-flusher. The overflow was contained in an open space area and did not enter either a creek, storm drain, or water way. We cleaned and televised the sewer main and identified roots as the primary cause of the overflow. We have added this sewer main to the preventitive maintenance program to prevent a reoccurrance until it can be repaired or replaced. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Novato | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Timothy M. O'Connor | 2006-10-26 | 415-892-1694 | edm@novatosan.com, bevj@novatosan.com, timo@novatosan.com | MINOR
4008 | 27 | 1 | Novato | 2006-10-17 16:04 | 750 | 0 |  | 2006-10-17 16:04 |  | -- | 1537 South Novato Blvd. | Novato | Marin | 94945 |  |  | 2006-10-09 |  |  |  | The manhole that overflowed was located approximately 10 feet from a storm drain inlet. When we arrived, we releived the blockage and stopped the overflow. We located and followed the storm drain system that received the overflow to it's outfall. The entire amount of the overflow water was contained in the storm drain pipe. The outfall was dry. We flushed, cleaned and vacuumed the storm drain and recovered 100 percent of the overflow. We returned the recovered wastewater to the sanitary sewer collection system. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Novato | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Superintendent | Timothy M. O'Connor | 2006-10-17 | 415-892-1694 | edm@novatosan.com, bevj@novatosan.com, timo@novatosan.com | MINOR
3649 | 26 | 1 | Novato | 2006-07-21 17:00 | 500 | 0 |  | 2006-07-21 17:00 |  | -- | 40 Stonetree Lane | Novato | Marin | 94945 |  |  | 2006-07-20 |  |  |  | The sewage overflow occurred at manhole structure M17024. In my judgement, this overflow was caused by cement debris left in the manholes by the installing contractor. This cement created a hangup point for solidsWe used a hydrovac unit to releive the blockage and vacuum up the sewage overflow. We followed the spill evidence for approximately 1500 feet of open concrete valley gutter to a catch basin that was determined to be the furthest point the sewage reached. We found no evidence of discharge beyond this point. We recovered 100 percent of the sewage discharge and washdown water. We immediately contacted the installing contractor and directed them to remove any cement in the sewer manholes for this project. We will continue to follow up to insure the condition is fully corrected. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Novato | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Superintendent | Timothy M. O'Connor | 2006-07-21 | 415-892-1694 | edm@novatosan.com, bevj@novatosan.com, timo@novatosan.com | MINOR
3647 | 25 | 1 | Novato | 2006-07-21 15:48 | 200 | 0 |  | 2006-07-21 15:48 |  | -- | San Marin Dr. at Spinosa Way | Novato | Marin | 94945 |  |  | 2006-07-14 |  |  |  | A grease blockage occurred approximately 155 ft upstream from structure G13014. We used a hydrovac to releive the blockage and clean up the spill. The spill was contained in the dirt center median on San Marin Dr. and we recovered 100 percent of the overflow. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Novato | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Superintendent | Timothy M. O'Connor | 2006-07-21 | 415-892-1694 | edm@novatosan.com, bevj@novatosan.com, timo@novatosan.com | MINOR
3380 | 23 | 1 | Novato | 2006-05-22 16:33 | 500 | 0 |  | 2006-05-22 16:33 |  | -- | 891 Bell Marin Keys Blvd. | Novato | Marin | 94945 |  |  | 2006-05-18 |  |  |  | ON THURSDAY AT ABOUT 8:30 AM, A CONTRACTOR WORKING FOR NOVATO SANITARY DISTRICT BROKE INTO A FORCE MAIN THAT WAS ASSUMED TO BE DRY, BUT WAS STILL UNDER PRESSURE. NOVATO SANITARY DISTRICT STAFF ESTIMATED THAT APPROXIMATELY 500 GALLONS OF RAW SEWAGE WAS RELEASED. APPROXIMATELY 300 GALLONS WAS RECOVERED FROM THE STREET AND GUTTER. APPROXIMATELY 200 GALLONS OF SEWAGE ENTERED THE SOUTH LAGOON OF BEL MARIN KEYS DEVELOPMENT. A 24 HOUR REPORT WAS FILED AND THE LAGOON WATER WAS SAMPLED AT THE POINT OF ENTRY, 50 FEET ON EITHER SIDE OF THE POINT OF ENTRY, 250 FEET ON EITHER SIDE OF THE POINT OF ENTRY AND 500 FEET ON EITHER SIDE OF THE POINT OF ENTRY. SAMPLES WERE TAKEN BEFORE AND AFTER CLEANUP. NOVATO SANITARY DISTRICT CALLED IN 2 FIVE THOUSAND GALLON TANKERS AND VACUUMED TEN THOUSAND GALLONS OF WATER OUT OF THE LAGOON AT THE POINT OF ENTRY. NOVATO SANITARY DISTRICT POSTED THE AREA WITH SIGNS IN ENGLISH AND SPANISH TO NOTIFY RESIDENTS AND RECREATIONAL USERS OF THE SEWAGE SPILL. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Novato | PUMP STATION | FORCE MAIN | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Superintendent | Timothy M. OConnor | 2006-05-22 | 415-892-1694 | edm@novatosan.com, bevj@novatosan.com, timo@novatosan.com | MINOR
3408 | 24 | 2 | Novato | 2006-05-25 13:28 | 500 | 300 | 06-2979 | 2006-05-22 | Ed Mann | Novato | 891 Bel Marin Keys Blvd | Novato | Marin | 94945 | 38.04.50.9 | 122.31.33 | 2006-05-18 | 8:30:00 AM | [5 empty] | SUNNY WEATHER | Low | Bel Marin Keys, southwestern-most lagoon | SURFACE WATER IMPACT | No |  | No | Yes | Due to the nature of the lagoon and the prevailing wind conditions, the sewage spill was contained to a very small area, approximately 15ft by 15ft, in the lagoon. |  | Yes | Yes | No | No | No | Yes | Yes | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Novato | PUMP STATION | The cause of the incident was a new connection being made to a sewage force main in Bel Marin Keys Blvd. The District is constructing a new pump station on the site of an existing pump station at the subject address. The incident occurred when the District's contractor broke into the existing force main preparatory to connecting it to the discharge from the new pump station. | INFRASTRUCTURE FAILURE | --Select None-- | DAMAGE TO COLLECTION SYSTEM |  | A major portion (approximately 300 gallons) of the spilled sewage was contained within the pipe trench, and the street right-of-way by means of dirt berms, sand, and gravel bags, vacuumed up into the Districts hydro-vac units, and disposed of at the District's Ignacio Treatment Plant. The remainder or approximately 200 gallons was estimated to have flowed into the adjacent lagoon. This lagoon is the southwestern-most lagoon directly across the street from the site of the District's pump station. The lagoon is owned and operated by the Bel Marin Keys Community Services District (BMKCSD). The sewage spill entry into this lagoon was a single point entry via a street storm drain channel. Available information on the lagoon was that it is a static water body with limited and controlled water entry and exit points. Due to this nature of the lagoon and the prevailing wind conditions, the sewage spill was being contained to a very small portion of the lagoon. Based on this containment, the District immediately brought in two 5,000 gallons each, tanker trucks and siphoned approximately 10,000 gallons from this contained portion. It is estimated that most, of not all, of the 200 gallons of sewage that had gone into the lagoon was recovered in this manner. The tanker truck contents were discharged to the District's Ignacio Treatment Plant for treatment. Water quality sampling was performed immediately upon the spill into the lagoon and subsequently after the clean-up as well as for four days after the event. Testing results for the ammonia parameter indicated that upon the spill, the ammonia level was between 0.46 mg/l to 0.48 mg/l at the spill site, but after the clean-up the level was backed down to 0.03 mg/l, and has consistently stayed at the 0.03 mg/l level for the past five days. Similarly, bacteriological tests on the day of the spill and on the following day indicate a dramatic decline in the sample taken after the clean-up versus before the clean-up. Bacteriological testing was conducted for a further three days. In total, ammonia and bacteriological testing was conducted for five days. In addition, standard warning signs were posted around the site upon the spill and left there for five days. There was no evidence of a fish kill observed at any time during the cleanup and sampling activities. The BMKCSD was contacted and kept updated on the incident until it's conclusion. This report was originally filed as a short form report, tracking # 3380, sso id #23, on 05/22/2006. I contacted Johnson Lam and asked him to delete the short form report. The long form report is the correct format for this spill event. | Superintendent | Timothy M. O'Connor | 2006-05-25 | 415-892-1694 | edm@novatosan.com, bevj@novatosan.com, timo@novatosan.com | MAJOR | Ed Mann | Novato Sanitary District | 4158921694 |  | 500 Davidson Street | Novato | Marin | 94945 | Ed Mann | Novato Sanitary District | 4158921694 |  | 500 Davidson Street | Novato | Marin | 94945
3334 | 22 | 1 | Novato | 2006-05-12 17:22 | 120 | 0 |  | 2006-05-12 17:22 |  | -- | 100 Cutlass Dr. X st Redwood Dr | Novato | Marin | 94945 |  |  | 2006-05-09 |  |  |  | The sewage was contained in the storm drain catch basin. We achieved 100 percent recovery of sewage overflow and washdown water. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Novato | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Superintendent | Timothy M. O'Connor | 2006-05-12 | 415-892-1694 | edm@novatosan.com, bevj@novatosan.com, timo@novatosan.com | MINOR
3549 | 21 | 3 | Novato | 2006-06-23 08:01 | 135 | 0 |  | 2006-06-23 08:01 |  | -- | 885 Eucalyptus Ave. | Novato | Marin | 94945 |  |  | 2006-04-21 |  |  |  | Front yard area was washed dow and all wash down water, sewage, and overflow debris were 100 recovered | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Novato | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Timothy M. O'Oconnor | 2006-04-27 | 415-892-1694 | edm@novatosan.com, bevj@novatosan.com, Timo@novatosan.com | MINOR
2552 | 18 | 1 | Novato | 2006-01-06 11:09 | 525 | 0 |  | 2006-01-06 11:09 |  | -- | Intersection of Center Rd and Western Av. | Novato | Marin | 94945 |  |  | 2005-12-31 |  |  |  | This overflow occurred due to extensive flooding caused by a severe winter storm. This rain event created conditions that exceeded the capacity of our wastewater collections system. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Novato | MANHOLE |  | NATURAL DISASTER | --Select None-- |  |  |  | Superintendent | Timothy M. O'Connor | 2006-01-06 | 415-892-1694 | Timo@novatosan.com,edm@novatosan.com, bevj@novatosan.com | MINOR
2554 | 19 | 1 | Novato | 2006-01-06 11:22 | 600 | 0 |  | 2006-01-06 11:22 |  | -- | Intersection of Chase St. and Peach St. | Novato | Marin | 94945 |  |  | 2005-12-31 |  |  |  | This overflow occurred due to extensive flooding caused by a severe winter storm. This rain event created conditions that exceeded the capacity of our wastewater collections system. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Novato | MANHOLE |  | NATURAL DISASTER | --Select None-- |  |  |  | Superintendent | Timothy M. O'Connor | 2006-01-06 | 415-892-1694 | Timo@novatosan.com, edm@novatosan.com, bevj@novatosan.com | MINOR
2556 | 20 | 1 | Novato | 2006-01-06 11:31 | 945 | 0 |  | 2006-01-06 11:31 |  | -- | 71 Monte Vista | Novato | Marin | 94945 |  |  | 2005-12-31 |  |  |  | This overflow occurred due to extensive flooding caused by a severe winter storm. This rain event created conditions that exceeded the capacity of our wastewater collections system. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Novato | MANHOLE |  | NATURAL DISASTER | --Select None-- |  |  |  | Superintendent | Timothy M. O'Connor | 2006-01-06 | 415-892-1694 | Timo@novatosan.com,edm@novatosan.com, bevj@novatosan.com | MINOR
1953 | 17 | 1 | Novato | 2005-10-13 08:54 | 6000 | 0 | 05-5896 | 2005-10-13 | Edward Mann | Novato | notheast end of the old runway at hamilton airforce base | Novato | Marin | 94947 | 38.40.16 | 122.31.14 | 2005-10-12 | 12:00:00 P | [5 empty] | SUNNY WEATHER | Low |  | YARD/LAND | No |  | No | No | There was no impact on the receiving water |  | Yes | Yes | No | No | No | Yes | No | No | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Novato | OTHER | The spill was the result of a leak investigation on the Novato Sanitary District's WWTP outfall line. In repairing the leak apx. 6,000 gallons of treated effluent was leaked from the pipe. All flow was contained in the area. Please Note: this line is currently out of service and the water in the pipe was standing water only. | INFRASTRUCTURE FAILURE | --Select None-- | --Select None-- |  | The spill was the result efforts to repair a leak in the District's treated effluent outfall line. | Wastewater Facilitei | Edward M.ann | 2005-10-13 | 415.892.1694 | edm@novatosan.com, bevj@novatosan.com | MAJOR | Ed Mann | Novato Sanitary District | 4158921694 |  | 500 Davidson Street | Novato | Marin | 94945 | Ed Mann | Novato Sanitary District | 4158921694 |  | 500 Davidson Street | Novato | Marin | 94945
1692 | 16 | 1 | Novato | 2005-08-15 14:25 | 800 | 0 |  | 2005-08-15 14:25 |  | -- | 1120 7th. st. Novato | Novato | Marin | 94945 |  |  | 2005-08-15 |  |  |  | No solids were found at overflow. We used hydroflusher to clean area affected. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | novato | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Leadworker | Pascual Sandoval | 2005-08-15 | (415) 892-1694 | edm@novatosan.com, bevj@novatosan.com | MINOR
1686 | 15 | 1 | Novato | 2005-08-11 15:33 | 300 | 0 |  | 2005-08-11 15:33 |  | -- | 50 FAIRWAY DR. | Novato | Marin | 94945 |  |  | 2005-08-11 |  |  |  | Cleared stoppage and cleaned very little solids at cleanout. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | novato | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Leadworker | Pascual Sandoval | 2005-08-11 | (415) 892-1694 | edm@novatosan.com, bevj@novatosan.com | MINOR
1642 | 14 | 1 | Novato | 2005-07-25 13:34 | 500 | 0 |  | 2005-07-25 13:34 |  | -- | 445 Bel Marin Keys | Novato | Marin | 94945 |  |  | 2005-07-25 |  |  |  | An old unplugged air release on the Ignacio WWTF forcemain opened up during contact chamber cleaning and spilled Apx. 500 gallons of treated secondary effluent around the area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Novato | OTHER | Effluent Force Main | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Mr | Edward Mann | 2005-07-25 | 4158921694 | edm@novatosan.com, bevj@novatosan.com | MINOR
1545 | 13 | 1 | Novato | 2005-06-21 09:30 | 450 | 0 |  | 2005-06-21 09:30 |  | -- | 11 Garner drive. Behind address in an easement. | Novato | Marin | 94947 |  |  | 2005-06-15 |  |  |  | Sewer line is going to be chemicly treated and reduce frequency. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | novato | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Collections | Pascual Sandoval | 2005-06-21 | (415) 892-1694 | edm@novatosan.com, bevj@novatosan.com | MINOR
1489 | 12 | 1 | Novato | 2005-06-06 10:02 | 200 | 0 |  | 2005-06-06 10:02 |  | -- | #36 Partridge Dr. Easment. M.H.#F12037 | Novato | Marin | 94945 |  |  | 2005-05-30 |  |  |  | This overflow was located at approx.50ft.from Manhole #F12035 heading upstream. This line segment has been added to our maintenance schedule and will be cleaned on a six month frequency. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Novato | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | crew leader | Earl Coates | 2005-06-06 | 415-892-1694 | edm@novatosan.com, bevj@novatosan.com | MINOR
1399 | 11 | 1 | Novato | 2005-05-15 09:02 | 800 | 0 |  | 2005-05-15 09:02 |  | -- | Eastment in Hamilton. Located between State access and Martin ave. | Novato | Marin | 94945 |  |  | 2005-05-15 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Novato | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Collections | Pascual | 2005-05-15 | 415-892-1694 | edm@novatosan.com, bevj@novatosan.com | MINOR
1360 | 10 | 1 | Novato | 2005-05-04 14:43 | 275 | 0 |  | 2005-05-04 14:43 |  | -- | 21 Pinewood Lane. | Novato | Marin | 94945 |  |  | 2005-05-03 |  |  |  | This blockage was caused by root intrusion inside manhole I20050. The outlet or downstream pipe was partially blocked by the roots that had entered the manhole.All roots have been removed and all lines in this area have been cleaned. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Novato | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Leadworker | Earl Coates | 2005-05-04 | 415-892-1694 | edm@novatosan.com, bevj@novatosan.com | MINOR
1339 | 9 | 1 | Novato | 2005-04-29 12:23 | 500 | 0 |  | 2005-04-29 12:23 |  | -- | 400 Feet north of montura way on ignacio blvd. | Novato | Marin | 94945 |  |  | 2005-04-28 |  |  |  | A heavy amount of small rock and grit was removed at the downstream manhole after the stoppage was cleared. A large amount of new construction is in progress upstream from this location.50% of this spill entered a storm drain and approx. 50% was contained at the curb&gutter. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Novato | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Leadworker | Earl Coates | 2005-04-29 | 415-892-1694 | edm@novatosan.com, bevj@novatosan.com | MINOR
1135 | 8 | 1 | Novato | 2005-03-08 14:16 | 405 | 0 |  | 2005-03-08 14:16 |  | -- | Intersection of Eucalyptas st. and mendocino | Novato | Marin | 94945 |  |  | 2005-03-06 |  |  |  | Area was contained And vacced with Jet/vac machine. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Novato | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Collections II | Pascual Sandoval | 2005-03-08 | (415) 892-1694 | edm@novatosan.com, bevj@novatosan.com | MINOR
1133 | 7 | 1 | Novato | 2005-03-08 13:14 | 240 | 0 |  | 2005-03-08 13:14 |  | -- | 10 Shari ct. eastment. | Novato | Marin | 94945 |  |  | 2005-02-28 |  |  |  | Spill contained in backyard. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Novato | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Collections II | Pascual Sandoval | 2005-03-08 | (415) 892-1694 | edm@novatosan.com, bevj@novatosan.com | MINOR
781 | 6 | 1 | Novato | 2005-01-07 09:40 | 175 | 0 |  | 2005-01-07 09:40 |  | -- | 10 Palomino Drive | Novato | Marin | 94945 |  |  | 2005-01-03 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Novato | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | IS Specialist | Robin Merrill | 2005-01-07 | 415 892-1694 | edm@novatosan.com | MINOR
721 | 1 | 2 | Novato | 2005-01-03 15:04 | 5100 | 0 | 04-6800 | 2004-12-27 | Beverly James | Novato | Manhole F-14-06, on Simmons between Feliz and Benton | Novato | Marin | 94945 |  |  | 2004-12-27 | 7:30:00 AM | [5 empty] | RAINY WEATHER | Low | Novato Creek | STORM DRAIN | No |  | No | No | No visual evidence of discharge to receiving water due to high storm flows. |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | Novato | MANHOLE | 'Overflow caused by exceptionally heavy rainfall of 6.7 inches in twenty four hours. | INFLOW & INFILTRATION | --Select None-- | LEAKS OF COLLECTION SYSTEM |  | A citizen telephoned at 7:30 AM to report an overflowing manhole. District crews responded and barricaded and sandbagged the manhole. The overflow appears to have been caused by high infiltration that exceeded the capacity of a siphon under Novato Creek located about 400 feet downstream of the overflow. District crews cleaned the sewer on 12/28/04 but found no evidence of a blockage. | WWTF Mgr | E. Mann | 2004-12-27 | 4158921694 | edm@novatosan.com | MAJOR | E. Mann | Novato | 4158921694 |  | 500 Davidson Street | Novato | Marin | 94945 | E. Mann | Novato Santary District | 4158921694 |  | 500 Davidson Street | Novato | Marin | 94945
722 | 2 | 2 | Novato | 2005-01-03 15:27 | 53400 | 0 | 04-6801 | 2004-12-27 | Bev James | Novato | Manholes D15-02, D15 -036, and D15-035 at Center and Western | Novato | Marin | 94945 |  |  | 2004-12-27 | 9:30:00 AM | [5 empty] | RAINY WEATHER | Low | Novato Creek | STORM DRAIN | No |  | No | No | No visible impact |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | Novato | MANHOLE | The line downstream of the overflow was partially blocked by carpet and other construction debris that had been illegally placed in the sewer. The high flows caused by a rainfall of 6.7 inches in the 24-hour period also contributed to the overflow. | BLOCKAGE | DEBRIS | --Select None-- |  | Three manholes overflowed at the intersection of Center and Western. The overflow was caused both by carpet and construction debris that partially blocked the sewer as well as the high infiltration due to rainfall of 6.7 inches in the previous 24 hours. District crews put in barricades and sandbags and sanitized the area and cleaned the sewer line. | Manager | Beverly James | 2005-01-03 | 4158921694 | bevj@novatosan.com | MAJOR | Ed Mann | Novato Sanitary District | 4158921694 |  | 500 Davidson Street | Novato | Marin | 94945 | Ed Mann | Novato | 4158921694 |  | 500 Davidson Street | Novato | Marin | 94945
723 | 3 | 2 | Novato | 2005-01-03 15:34 | 12000 | 0 | 04-6802 | 2004-12-27 | Bev James | Novato | Manholes E-012 and E-013 at Sierra Vista & Monte Vista | Novato | Marin | 94945 |  |  | 2004-12-27 | 10:30:00 A | [5 empty] | RAINY WEATHER | Low | Novato Creek | STORM DRAIN | No |  | No | No | No visible impact |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | Novato | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | LEAKS OF COLLECTION SYSTEM |  | Two manholes overflowed at Monte Vista and Sierra Vista due to high flows caused by 6.7 inches of rain. Sewer crews cleaned downstream sewers and did not find a blockage. Sewer crews put up barricades and sandbags and cleaned and disinfected the area. | Manager | Beverly james | 2005-01-03 | 4158921694 | bevj@novatosan.com | MAJOR | Ed Mann | Novato Sanitary District | 4158921694 |  | 500 Davidson Street | Novato | Marin | 94945 | Ed Mann | Novato Sanitary District | 4158921694 |  | 500 Davidson Street | Novato | Marin | 94945
729 | 4 | 2 | Novato | 2005-01-03 15:42 | 1650 | 0 | 04-6803 | 2004-12-27 | Bev James | Novato | Chase & Peach | Novato | Marin County | 94945 |  |  | 2004-12-27 | 10:15:00 A | [5 empty] | RAINY WEATHER | Low | Novato Creek | STORM DRAIN | No |  | No | No | No visible impact |  | Yes | Yes | Yes | No | No | No | No | No | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | Novato | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | The sewer had been cleaned both upstream and downstream of the overflowing manhole just days before the event. The overflow appears to have been caused by high infiltration due to the 6.7 inches of rain within the 24-hour period. District crews sandbagged the manhole, placed barricades, and cleaned and disinfected the area. | Manager | Beverly James | 2005-01-03 | 4158921694 | bevj@novatosan.com | MAJOR | Ed Mann | Novato Sanitary District | 4158921694 |  | 500 Davidson Street | Novato | Marin | 94945 | Ed Mann | Novato Sanitary District | 4158921694 |  | 500 Davidson Street | Novato | Marin | 94945
731 | 5 | 2 | Novato | 2005-01-03 15:52 | 120000 | 0 | 04-6804 | 2004-12-27 | Bev James | Novato | On the District's treated effluent outfall at the box on the outboard levee at Hamilton Field | Novato | Marin | 94945 |  |  | 2004-12-27 | 10:30:00 A | [5 empty] | RAINY WEATHER | Low | San Pablo Bay | YARD/LAND | No |  | No | No | Did not reach receiving water |  | Yes | No | No | No | No | No | No | No | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | Novato | MANHOLE | The combination of a high tide (+6.4) and high flows caused water to backup and overflow at the District's junction box. | INFRASTRUCTURE FAILURE | --Select None-- | MULTIPLE CAUSES |  | The treated, disinfected, and dechlorinated effluent overflowed from the last effluent junction box before the bay due to the combination of a high tide (+6.4) and high flows. | Manager | Beverly James | 2005-01-03 | 4158921694 | bevj@novatosan.com | MAJOR | Ed Mann | Novato Sanitary District | 4158921694 |  | 500 Davidson Street | Novato | Marin | 94945 | Ed Mann | Novato Sanitary District | 4158921694 |  | 500 Davidson Street | Novato | Marin | 94945
5192 | 450 | 1 | Oakland | 2007-05-01 14:24 | 20 | 0 |  | 2007-05-01 14:24 |  | -- | 4128 E. 18Th. St. | oakland | alameda | 94601 |  |  | 2007-04-30 |  |  |  | Rodded m/s clear of grease, sewage was contained in homeowners basement. Cleaned affected area | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Admin. Asst. I | Kinji Wooten | 2007-05-01 | 510-615-5715
5188 | 449 | 1 | Oakland | 2007-05-01 13:40 | 25 | 0 |  | 2007-05-01 13:40 |  | -- | 9839 D St. | oakland | alameda | 94603 |  |  | 2007-04-28 |  |  |  | Sewer seeping from manhole. Rodded m/s clear fo grease stoppage and washed down street. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Admin. Asst. I | Kinji Wooten | 2007-05-01 | 510-615-5715
5165 | 448 | 1 | Oakland | 2007-04-26 15:04 | 50 | 0 |  | 2007-04-26 15:04 |  | -- | 4101 Porter st. | Oakland | Alameda | 94619 |  |  | 2007-04-24 |  |  |  | Had 195 (power roodder) rod main sewer clear of heavy roots. Washed down street area | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Admin. Asst. I | Kinji Wooten | 2007-04-26 | 510-615-5715
5162 | 447 | 1 | Oakland | 2007-04-26 14:40 | 25 | 0 |  | 2007-04-26 14:40 |  | -- | 78th Ave. & Bancroft | oakland | alameda | 94605 |  |  | 2007-04-23 |  |  |  | Found m/s plugged, rodded main clear of heavy grease stoppage, and washed down/disinfected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Admin. Assit. I | Kinji Wooten | 2007-04-26 | 510-615-5715
5156 | 446 | 1 | Oakland | 2007-04-26 11:15 | 100 | 0 |  | 2007-04-26 11:15 |  | -- | 10555 Mark St. | Oakland | Alameda | 94605 |  |  | 2007-04-22 |  |  |  | Rodded 8" main sewer on street and on easement. Cleaned out heavy grease & roots. Flushed out main, cleaned up sewage and washed down affacted area and storm drain. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Admin. Asst. I | Kinji Wooten | 2007-04-26 | 510-615-5715
5152 | 445 | 1 | Oakland | 2007-04-26 09:14 | 200 | 0 |  | 2007-04-26 09:14 |  | -- | 6000 Mauritania Ave. | Oakland | Alameda | 94605 |  |  | 2007-04-21 |  |  |  | Rodded main sewer and cleared root and grease blockage. Washed and disinfected affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2007-04-26 | 510-615-5590
5121 | 444 | 1 | Oakland | 2007-04-23 10:54 | 75 | 0 |  | 2007-04-23 10:54 |  | -- | 9 Ronada Ave. | oakland | alameda | 94611 |  |  | 2007-04-21 |  |  |  | Rodded main sewer to clear root blockage. Cleaned affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | AA I | Kinji Wooten | 2007-04-23 | 510-615-5715
5117 | 443 | 1 | Oakland | 2007-04-22 13:52 | 10 | 0 |  | 2007-04-22 13:52 |  | -- | 369 Walker Ave. | Oakland | Alameda | 94610 |  |  | 2007-04-19 |  |  |  | Rodded main sewer in rear yard on easement to clear root and grease blockage. Cleaned and disinfected affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2007-04-22 | 510-615-5590
5115 | 442 | 1 | Oakland | 2007-04-22 13:44 | 50 | 0 |  | 2007-04-22 13:44 |  | -- | 8117 Greenly Dr. | Oakland | Alameda | 94605 |  |  | 2007-04-18 |  |  |  | Hand rodded main sewer to clear heavy root blockage. Cleaned affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2007-04-22 | 510-615-5590
5113 | 441 | 1 | Oakland | 2007-04-22 13:40 | 15 | 0 |  | 2007-04-22 13:40 |  | -- | Somerset Rd. between 125 - 137 | Oakland | Alameda | 94611 |  |  | 2007-04-18 |  |  |  | Rodded main sewer from manhole upstream and could not get through with augers. Came back with mud on the augers. Need to give to construction for repair root blockage. Cleaned affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | PIPE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2007-04-22 | 510-615-5590
5111 | 440 | 1 | Oakland | 2007-04-22 13:31 | 200 | 0 |  | 2007-04-22 13:31 |  | -- | 1000 Oak St. | Oakland | Alameda | 94607 |  |  | 2007-04-18 |  |  |  | Rodded main sewer and cleared grease blockage. Cleaned and disinfected basement floor. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2007-04-22 | 510-615-5590
5108 | 438 | 1 | Oakland | 2007-04-22 13:15 | 50 | 0 |  | 2007-04-22 13:15 |  | -- | 6872 Armour Dr. | Oakland | Alameda | 94611 |  |  | 2007-04-16 |  |  |  | Hydro flushed main sewer to break blockage of gravel, roots and rags. Cleaned affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | PWA Supervisor | David Lonestar | 2007-04-22 | 510-615-5590
5106 | 437 | 1 | Oakland | 2007-04-22 09:30 | 50 | 0 |  | 2007-04-22 09:30 |  | -- | 47th Ave & Melrose Ave. | Oakland | Alameda | 94601 |  |  | 2007-04-15 |  |  |  | Power rodded main sewer to clear grease blockage. Hydro flushed main sewer to clear any loose debris. Washed and cleaned affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2007-04-22 | 510-615-5590
5099 | 431 | 1 | Oakland | 2007-04-22 08:45 | 25 | 0 |  | 2007-04-22 08:45 |  | -- | 4058 Whittle Ave. | Oakland | Alameda | 94602 |  |  | 2007-04-04 |  |  |  | Found main sewer on easement in rear plugged. Had power rodder rod main sewer from 4020 Whittle to 4069 to remove heavy roots blockage. Cleaned and disinfected affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2007-04-22 | 510-615-5590
5025 | 427 | 1 | Oakland | 2007-03-30 11:25 | 80 | 0 |  | 2007-03-30 11:25 |  | -- | 712 Franklin Street | Oakland | Alameda | 94607 |  |  | 2007-03-29 |  |  |  | Main sewer line blocked with grease between structure #64-401-47 to structure #64-401-42, sewer map sheet #183. Recovered sewage spill and returned it to collectin system, mopped and disenfected affected spill area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | BLOCKAGE | GREASE |  | FLOOR DRAIN |  | Sewer Maint. Leader | Armando Lozano | 2007-03-30 | (510)615-5566
4980 | 425 | 1 | Oakland | 2007-03-22 10:10 | 90 | 0 |  | 2007-03-22 10:10 |  | -- | 2152 mastlands Dr. | Oakland | Alameda | 94611 |  |  | 2007-03-21 |  |  |  | Rodded and flushed main sewer, also vaccum water in gutter. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Act PWA Supervisor | Kenya J. Laurie | 2007-03-22 | 510 615-5985
4978 | 424 | 1 | Oakland | 2007-03-22 09:55 | 2 | 0 |  | 2007-03-22 09:55 |  | -- | 33 Home Place East | Oakland | Alameda | 94610 |  |  | 2007-03-20 |  |  |  | Power rodded and flushed main sewer to clear root blockage. Cleaned and disinfected affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2007-03-22 | 510-615-5590
4943 | 422 | 1 | Oakland | 2007-03-15 15:39 | 2 | 0 |  | 2007-03-15 15:39 |  | -- | 2155 39th Ave. | Oakland | Alameda | 94619 |  |  | 2007-03-14 |  |  |  | Hydro-flushed main sewer to clear debris & paper blockage. Washed down affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | PWA Supervisor | David Lonestar | 2007-03-15 | 510-615-5590
4941 | 421 | 1 | Oakland | 2007-03-15 15:33 | 30 | 0 |  | 2007-03-15 15:33 |  | -- | Santa Rita & High St. | Oakland | Alameda | 94601 |  |  | 2007-03-13 |  |  |  | Rodded main sewer to clear heavy root blockage. Washed down affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2007-03-15 | 510-615-5590
4901 | 420 | 1 | Oakland | 2007-03-12 11:13 | 200 | 0 |  | 2007-03-12 11:13 |  | -- | Church St. btwn Bancroft Ave. & Foothill Ave. | Oakland | Alameda | 94605 |  |  | 2007-03-10 |  |  |  | Hydro-flushed main sewer and cleared grease blockage. Washed down affected area with the hydro-flusher. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2007-03-12 | 510-615-5590
4878 | 419 | 1 | Oakland | 2007-03-08 07:45 | 100 | 0 |  | 2007-03-08 07:45 |  | -- | 5940 Castle Drive | Oakland | Alameda | 94611 |  |  | 2007-03-05 |  |  |  | Rodded main sewer and cleared root blockage. Cleaned and washed down affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2007-03-08 | 510-615-5590
4868 | 418 | 1 | Oakland | 2007-03-06 09:02 | 5 | 0 |  | 2007-03-06 09:02 |  | -- | 3700 Dorisa Ave. | Oakland | Alameda | 94605 |  |  | 2007-03-02 |  |  |  | Rodded main sewer to clear heavy root blockage. Cleaned & washed down affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2007-03-06 | 510-615-5590
4854 | 416 | 1 | Oakland | 2007-03-03 07:58 | 20 | 0 |  | 2007-03-03 07:58 |  | -- | 66th St. & San Pablo Ave. | Oakland | Alameda | 94608 |  |  | 2007-03-01 |  |  |  | Rodded main sewer and cleared blockage of grease. Cleaned and disinfected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2007-03-03 | 615-5590
4842 | 415 | 1 | Oakland | 2007-02-28 13:06 | 30 | 0 |  | 2007-02-28 13:06 |  | -- | 8545 Skyline Blvd. | Oakland | Alameda | 94611 |  |  | 2007-02-27 |  |  |  | Rodded main sewer and cleared blockage of roots. Cleaned and disinfected affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2007-02-28 | 510-615-5590
4840 | 414 | 1 | Oakland | 2007-02-28 12:59 | 20 | 0 |  | 2007-02-28 12:59 |  | -- | Staten Ave. & Belmont | Oakland | Alameda | 94610 |  |  | 2007-02-27 |  |  |  | Rodded 8" main sewer of rags and debris from down stream manhole. Main sewer is clear and flowing. Cleaned affected area. Heavy rain washed the affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | PWA Supervisor | David Lonestar | 2007-02-28 | 510-615-5590
4838 | 413 | 1 | Oakland | 2007-02-28 12:54 | 300 | 0 |  | 2007-02-28 12:54 |  | -- | Golflinks Road - Knowland Park / Zoo | Oakland | Alameda | 94605 |  |  | 2007-02-27 |  |  |  | Hand rodded main sewer to remove heavy roots. Main sewer is open at this time. Cleaned affected area. Heavy rain washed down affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2007-02-28 | 510-615-5590
4831 | 412 | 1 | Oakland | 2007-02-27 10:56 | 75 | 0 |  | 2007-02-27 10:56 |  | -- | Melvin Road near Arcadia Ave. & Braemar Rd. | Oakland | Alameda | 94602 |  |  | 2007-02-27 |  |  |  | Rodded main sewer with 2" auger to unplug blockage. Cleaned and disinfected affected area. Heavy rain helped wash affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2007-02-27 | 510-615-5590
4817 | 411 | 1 | Oakland | 2007-02-26 11:22 | 20 | 0 |  | 2007-02-26 11:22 |  | -- | 6625 Banning Drive | Oakland | Alameda | 94611 |  |  | 2007-02-24 |  |  |  | Rodded Main Sewer and cut out roots in manhole. Cleaned and disinfected affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2007-02-26 | 510-615-5590
4806 | 409 | 1 | Oakland | 2007-02-23 14:05 | 200 | 0 |  | 2007-02-23 14:05 |  | -- | 2041 108th Avenue | Oakland | Alameda | 94603-3913 |  |  | 2007-02-22 |  |  |  | Main sewer line segment blocked with roots and grease from structure #85-208-42 to structure #85-208-43, sewer map sheet #43. Recovered all the spill back into floor drain, washed and disinfected affected spill area. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | BLOCKAGE | GREASE |  | floor drain |  | Sewer Maint. Leader | Armando Lozano | 2007-02-23 | (510)615-5566
4801 | 406 | 1 | Oakland | 2007-02-23 10:34 | 30 | 0 |  | 2007-02-23 10:34 |  | -- | 1801 Brentwood Road | Oakland | Alameda | 94602-2008 |  |  | 2007-02-22 |  |  |  | Sewer main line segment blocked with roots between structure #56-010-64 to structure #56-010-66, sewer map sheet #244. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-02-23 | (510)615-5566
4804 | 408 | 1 | Oakland | 2007-02-23 13:22 | 5 | 0 |  | 2007-02-23 13:22 |  | -- | 800 100TH AVENUE | OAKLAND | ALAMEDA | 94603-2354 |  |  | 2007-02-20 |  |  |  | MAIN SEWER LINE SEGMENT BLOCKED WITH GREASE BETWEEN STRUCTURE #85-101-50 TO STRUCTURE #85-101-51, SEWER MAP SHEET #41. RECOVERED SPILL, WASHED AND DISINFECTED AFFECTED AREA. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | BLOCKAGE | GREASE |  | FLOOR DRAIN |  | Sewer Maint. Leader | Armando Lozano | 2007-02-23 | (510)615-5566
4781 | 403 | 1 | Oakland | 2007-02-20 09:43 | 90 | 0 |  | 2007-02-20 09:43 |  | -- | 4100 Redwood Road | Oakland | Alameda | 94619-2363 |  |  | 2007-02-17 |  |  |  | Sewer main segment blocked with roots between structure #83-503-04 to structure #83-503-04 to structure #83-503-05, sewer map sheet #192, washed and vaccumed 98% of the spill from parking lot area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-02-20 | (510)615-5566
4779 | 402 | 1 | Oakland | 2007-02-20 08:56 | 90 | 0 |  | 2007-02-20 08:56 |  | -- | 6038 Snake Road | Oakland | Alameda | 94611 - 26 |  |  | 2007-02-17 |  |  |  | Main sewer line segment blocked with rocks, chicken wire and plastic bags between structure #56-210-29 to structure #56-210-26, sewer map sheet #291. Vaccumed and washed affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | VANDALISM |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-02-20 | (510)615-5566
4810 | 410 | 1 | Oakland | 2007-02-23 16:17 | 200 | 0 |  | 2007-02-23 16:17 |  | -- | 6510 Outlook Avenue | Oakland | Alameda | 94605-2194 |  |  | 2007-02-15 |  |  |  | Sewer main line segment blocked with root, sand, brick, and broken pipe between structure #84-104-C8 to structure #84-104-C7, sewer map sheet #126. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-02-23 | (510)615-5566
4772 | 401 | 1 | Oakland | 2007-02-16 09:03 | 30 | 0 |  | 2007-02-16 09:03 |  | -- | Moraga and Thornhill Drive | Oakland | Alameda | 94611-5185 |  |  | 2007-02-15 |  |  |  | Main sewer line segment blocked with roots between structure #50-308-05 to structure #50-308-06, sewer map sheet #290. Raked and disinfected affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-02-16 | (510)615-5566
4765 | 400 | 1 | Oakland | 2007-02-15 09:50 | 25 | 0 |  | 2007-02-15 09:50 |  | -- | MORAGA AVENUE AND THORNHILL DRIVE | OAKLAND | ALAMEDA | 94611-5185 |  |  | 2007-02-14 |  |  |  | Sewer main line segment blocked with roots and debris between structure #50-308-08 to structure #50-308-09, sewer map sheet #290. Cleaned and washed affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-02-15 | (510)615-5566
4745 | 396 | 1 | Oakland | 2007-02-13 11:13 | 25 | 0 |  | 2007-02-13 11:13 |  | -- | 5611 DENTON PLACE | OAKLAND | ALAMEDA | 94619-3108 |  |  | 2007-02-13 |  |  |  | Found pumps not working on automatic position, pumped wet well sewage by turning the switch to the on position, refered complaint to be repaired by the Electric Dept. Cleaned and washed affected spill area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | PUMP STATION |  | ELECTRICAL POWER FAILURE | -- Select One -- |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-02-13 | (510)615-5566
4756 | 399 | 1 | Oakland | 2007-02-14 10:17 | 500 | 0 |  | 2007-02-14 10:17 |  | -- | 54th Street and Adeline Street | Oakland | Alameda | 94609 |  |  | 2007-02-12 |  |  |  | Main sewer line blocked with grease and paper between structure #50-100-13 to structure #50-100-15, sewer map sheet #296, storm weather made it hard to recover the spill. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-02-14 | (510)615-5566
4754 | 398 | 1 | Oakland | 2007-02-14 09:58 | 20 | 0 |  | 2007-02-14 09:58 |  | -- | 6514 VALLEY VIEW ROAD | OAKLAND | ALAMEDA | 94611-123 |  |  | 2007-02-12 |  |  |  | Sewer main line segment blocked with roots between strucrure #50-395-11 to structure #50-395-10, sewer map sheet #325, cleared blockage, vaccumed and cleaned affected spill area. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-02-14 | (510)615-5566
4695 | 393 | 1 | Oakland | 2007-02-08 10:12 | 20 | 0 |  | 2007-02-08 10:12 |  | -- | 6510 Outlook Avenue | Oakland | Alameda | 94605-2194 |  |  | 2007-02-07 |  |  |  | Main sewer line broken down between structure #84-104-C8 to structure #84-104-C9, sewer map sheet #126, cleaned affected area, made construction work order for spot repair. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | INFRASTRUCTURE FAILURE | CONSTRUCTION DEBRIS |  | GROUND |  | Armando Lozano | Sewer Maint. Leader | 2007-02-08 | (510)615-5566
4693 | 392 | 1 | Oakland | 2007-02-08 09:50 | 90 | 0 |  | 2007-02-08 09:50 |  | -- | 9725 International Blvd. | Oakland | Alameda | 94603-2509 |  |  | 2007-02-07 |  |  |  | Main sewer line segment blocked with grease between structure #85-205-04 to structure #85-205-19, sewer map sheet #54, hydroflusher washed, cleaned and vaccumed all the sewage spill. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-02-08 | (510)615-5566
4674 | 391 | 1 | Oakland | 2007-02-05 10:36 | 65 | 0 |  | 2007-02-05 10:36 |  | -- | 2801 Rawson Avenue | Oakland | Alameda | 94619-3347 |  |  | 2007-02-04 |  |  |  | Main sewer line segment blocked with grease between structure segment #83-202-41 to structure #83-202-73, sewer map sheet #124. Cleaned and washed affected spill area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-02-05 | (510)615-5566
4672 | 390 | 1 | Oakland | 2007-02-05 10:25 | 25 | 0 |  | 2007-02-05 10:25 |  | -- | 7921 Hillside St. | Oakland | Alameda | 94605 |  |  | 2007-02-03 |  |  |  | Rodded M/S and cleared blockage of heavy grease. M/S is clear and flowing. Cleaned and disinfected bathroom. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2007-02-05 | 615-5590
4670 | 389 | 1 | Oakland | 2007-02-05 09:06 | 300 | 0 |  | 2007-02-05 09:06 |  | -- | 1419 & 1431 80th Ave. | Oakland | Alameda | 94603 |  |  | 2007-02-03 |  |  |  | Rodded M/S and cleared heavy grease blockage. Cleaned and Disinfected affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2007-02-03 | 615-5590
4652 | 388 | 1 | Oakland | 2007-02-01 14:51 | 20 | 0 |  | 2007-02-01 14:51 |  | -- | 98 Catron Drive | Oakland | Alameda | 94603-3551 |  |  | 2007-01-30 |  |  |  | Main sewer line segment blocked with grease between structure #86-006-69 to structure #86-006-66, sewer map sheet #25, Washed and cleaned affected spill area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-02-01 | (510)615-5566
4644 | 386 | 1 | Oakland | 2007-01-31 09:23 | 175 | 0 |  | 2007-01-31 09:23 |  | -- | 9616 Cherry Street | Oakland | Alameda | 94603-261 |  |  | 2007-01-30 |  |  |  | Main sewer line segment blocked with grease between strucrure #85-200-49 to structure #85-206-F2, Cleaned and washed affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-01-31 | (510)615-5566
4635 | 385 | 1 | Oakland | 2007-01-29 13:59 | 222 | 0 |  | 2007-01-29 13:59 |  | -- | 3888 Sequoyah Rd. | Oakland | Alameda | 94605 |  |  | 2007-01-28 |  |  |  | Main sewer line segment blocked with construction debris between structure #85-013-71 to structure #85-013-68, sewer map sheet #94. Washed and cleaned affected spill area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | INFRASTRUCTURE FAILURE | CONSTRUCTION DEBRIS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-01-29 | (510)615-5566
4633 | 384 | 1 | Oakland | 2007-01-29 13:35 | 125 | 0 |  | 2007-01-29 13:35 |  | -- | 6500 Outlook Drive | Oakland | Alameda | 94605-2128 |  |  | 2007-01-28 |  |  |  | Main sewer line segment blocked with roots and rocks between structure #84-104-C6 to structure #84-104-C8, sewer map sheet #126, cleaned and washed affected spill area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-01-29 | (510)615-5566
4631 | 383 | 1 | Oakland | 2007-01-29 13:06 | 20 | 0 |  | 2007-01-29 13:06 |  | -- | 9907 Bernhardt Drive | Oakland | Alameda | 93601 |  |  | 2007-01-26 |  |  |  | Sewer line segment blocked with grease between structure #86-003-02 to structure #86-003-01, sewer map sheet #31. Cleaned and washed affected spill area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-01-29 | (510)615-5566
4621 | 381 | 1 | Oakland | 2007-01-25 08:26 | 150 | 0 |  | 2007-01-25 08:26 |  | -- | 103th Avenue and "E" Street | Oakland | Alameda | 94603 |  |  | 2007-01-24 |  |  |  | Main sewer line segment blocked with grease between structure #85-102-08 to structure #85-102-06, sewer map sheet #42. Cleaned and flushed affected spill area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-01-25 | (510)615-5566
4617 | 380 | 1 | Oakland | 2007-01-25 08:12 | 85 | 0 |  | 2007-01-25 08:12 |  | -- | 7327 WOODROW DRIVE | OAKLAND | ALAMEDA | 94611-1436 |  |  | 2007-01-24 |  |  |  | Line segment blocked with roots between structure #56-206-08 to structure #45-206-10, sewer map sheet #301, cleaned and disenfected affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-01-25 | (510)615-5566
4610 | 379 | 1 | Oakland | 2007-01-24 10:30 | 100 | 0 |  | 2007-01-24 10:30 |  | -- | 4103 Fontain Court | Oakland | Alameda | 94605-3702 |  |  | 2007-01-23 |  |  |  | Line segment blocked with roots and grease between structure #85-500-19 to structure #85-502-01, sewer map sheet #116. Flushed and cleaned affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-01-24 | (510)615-5566
4608 | 378 | 1 | Oakland | 2007-01-24 10:12 | 25 | 0 |  | 2007-01-24 10:12 |  | -- | 2340 27th Street | Oakland | Alameda | 94601 - 13 |  |  | 2007-01-23 |  |  |  | Line segment blocked with grease between structure #52-881-15 to structure #52-891-14, sewer map sheet #253, washed affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-01-24 | (510)615-5566
4596 | 375 | 1 | Oakland | 2007-01-23 10:59 | 25 | 0 |  | 2007-01-23 10:59 |  | -- | 2626 Ivy Drive | Oakland | Alameda | 94606-2136 |  |  | 2007-01-22 |  |  |  | Line segment blocked with roots between structure #54-202-37 to structure #54-202-42, sewer map sheet #206, flushed affected spill area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-01-23 | (510)615-5566
4571 | 370 | 1 | Oakland | 2007-01-22 10:02 | 75 | 0 |  | 2007-01-22 10:02 |  | -- | 995 Glendora Avenue | Oakland | Alameda | 94602-1415 |  |  | 2007-01-21 |  |  |  | Sanitary sewer main segment blocked with roots between structure #54-315-69 to structure #54-315-71, sewer map sheet #243, recovered solid spoils and flushed creek affected area. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-01-22 | (510)615-5566
4605 | 377 | 1 | Oakland | 2007-01-24 09:45 | 20 | 0 |  | 2007-01-24 09:45 |  | -- | 995 Glendora Ave. | Oakland | Alameda | 94602-1415 |  |  | 2007-01-19 |  |  |  | Main sewer line segment blocked with roots between structure #54-315-69 to structure #54-315-71, sewer map sheet #243, cleaned and disenfected affected spill area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-01-24 | (510)615-5566
4569 | 369 | 1 | Oakland | 2007-01-22 09:40 | 50 | 0 |  | 2007-01-22 09:40 |  | -- | 12th Street and Peralta Street | Oakland | Alameda | 94607 |  |  | 2007-01-19 |  |  |  | Sanitary sewer line segment blocked with grease between structure #52-201-24 to structure #52-201-23, sewer map sheet #218, recovered spill and flushed affected area. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-01-22 | (510)615-5566
4564 | 368 | 1 | Oakland | 2007-01-20 07:49 | 75 | 0 |  | 2007-01-20 07:49 |  | -- | 2105 Mac Arthur Blvd. | Oakland | Alameda | 94602-222 |  |  | 2007-01-18 |  |  |  | Main sewer line segment blocked with grease beyween structures #56-000-43 to structure #56-010-27, sewer map sheet #208, Flushed affected area of the spill. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-01-20 | (510)615-5566
4544 | 365 | 1 | Oakland | 2007-01-18 09:04 | 25 | 0 |  | 2007-01-18 09:04 |  | -- | 6616 Outlook Avenue | Oakland | Alameda | 94619 |  |  | 2007-01-17 |  |  |  | Temporary main sewer line pulled appart, it was repaired. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | INFRASTRUCTURE FAILURE | -- Select One -- |  | Temporary main pulled appart |  | Sewer Maint. Leader | Armando Lozano | 2007-01-18 | (510)615-5566
4513 | 364 | 1 | Oakland | 2007-01-16 10:15 | 30 | 0 |  | 2007-01-16 10:15 |  | -- | 1650 96th Avenue | Oakland | Alameda | 94603-1518 |  |  | 2007-01-15 |  |  |  | Line segment between structure #85-204-A2 to structure #85-204-A3, sewer page sheet #66. Cleared line blocked with grease, washed affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-01-16 | (510)615-5566
4507 | 363 | 1 | Oakland | 2007-01-13 08:17 | 10 | 0 |  | 2007-01-13 08:17 |  | -- | 3962 Edgemoor Pl. | Oakland | Alameda | 94605-2606 |  |  | 2007-01-11 |  |  |  | Main sewer line segment blocked with an unknown blockage between structure #83-400-71 to structure #83-403-17, map pages #126/127. Cleaned and disenfected affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-01-13 | (510)615-5566
4501 | 362 | 1 | Oakland | 2007-01-11 10:56 | 50 | 0 |  | 2007-01-11 10:56 |  | -- | 3618 Dorisa Ave. | Oakland | Alameda | 94605-4921 |  |  | 2007-01-10 |  |  |  | Line segment from structure #85-013-08 to structure #85-013-10, sewer map sheet #82, was blocked with roots, flushed affectad area in street, gutter and storm inlet areas. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-01-11 | (510)615-5566
4497 | 361 | 1 | Oakland | 2007-01-11 10:45 | 15 | 0 |  | 2007-01-11 10:45 |  | -- | 2776 E.22 Street | Oakland | Alameda | 94601-1818 |  |  | 2007-01-08 |  |  |  | Main sewer line blocked with grease, flushed down affected area in street, gutter and storm inlet. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-01-11 | 510615-5566
4469 | 356 | 1 | Oakland | 2007-01-08 10:11 | 50 | 0 |  | 2007-01-08 10:11 |  | -- | 4740 Congress Ave. | Oakland | Alameda | 94601 |  |  | 2007-01-07 |  |  |  | Rodded and flushed main sewer and cleared grease blockage. Washed and vacuumed affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2007-01-08 | 615-5590
4467 | 355 | 1 | Oakland | 2007-01-08 10:01 | 1 | 0 |  | 2007-01-08 10:01 |  | -- | 3309 Glenly Rd. | Oakland | Alameda | 94605 |  |  | 2007-01-07 |  |  |  | Dye tested main sewer and sewer lateral, dye test showed clear, main sewer is clear and flowing. Possible slipline failure. Made work order and advised construction inspectors for warranty repair. Washed down affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | INFRASTRUCTURE FAILURE | -- Select One -- |  | SEEPAGE FROM GROUND |  | PWA Supervisor | David Lonestar | 2007-01-08 | 615-5590
4471 | 357 | 1 | Oakland | 2007-01-08 10:32 | 20 | 0 |  | 2007-01-08 10:32 |  | -- | 435 Capistrano Dr. | Oakland | Alameda | 94603 |  |  | 2007-01-06 |  |  |  | Rodded and flushed main sewer, cleared main sewer of heavy grease. Washed down affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2007-01-08 | 615-5590
4603 | 376 | 1 | Oakland | 2007-01-24 09:11 | 20 | 0 |  | 2007-01-24 09:11 |  | -- | 1656 33rd. Avenue | Oakland | Alameda | 94601-3018 |  |  | 2007-01-05 |  |  |  | Line segment blocked with grease between structure #80-020-29 to structure #80-021-31, sewer map sheet #133, cleaned, mopped and disenfected affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | BLOCKAGE | GREASE |  | inside room |  | Sewer Maint. Leader | Armando Lozano | 2007-01-24 | (510)615-5566
4473 | 358 | 1 | Oakland | 2007-01-08 10:42 | 50 | 0 |  | 2007-01-08 10:42 |  | -- | 128 Gravatt Dr. | Oakland | Alameda | 94705 |  |  | 2007-01-05 |  |  |  | Power rodded main sewer and cleared blockage of roots. Washed and vacuumed affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2007-01-08 | 615-5590
4465 | 354 | 1 | Oakland | 2007-01-08 09:46 | 55 | 0 |  | 2007-01-08 09:46 |  | -- | 4490 Malcolm Ave. | Oakland | Alameda | 94605 |  |  | 2007-01-05 |  |  |  | Rodded main sewer and cleared blockage of roots. Washed and vacuumed affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2007-01-08 | 615-5590
4475 | 359 | 1 | Oakland | 2007-01-08 11:03 | 60 | 0 |  | 2007-01-08 11:03 |  | -- | 2802 68th Ave. | Oakland | Alameda | 94605 |  |  | 2007-01-04 |  |  |  | Rodded main sewer and cleared main sewer of grease blockage. Washed down affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2007-01-08 | 615-5590
4588 | 372 | 1 | Oakland | 2007-01-23 09:32 | 85 | 0 |  | 2007-01-23 09:32 |  | -- | 3818 Linwood Avenue | Oakland | Alameda | 94602-1626 |  |  | 2007-01-03 |  |  |  | Sewer main line segment blocked with debris between structure #56-005-59 to structure #56-005-55, sewer map sheet #208, cleaned and disenfected affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-01-23 | (510)615-5566
4430 | 353 | 1 | Oakland | 2007-01-02 10:29 | 75 | 0 |  | 2007-01-02 10:29 |  | -- | 3726 Fruitvale Ave. | Oakland | Alameda | 94602 |  |  | 2006-12-27 |  |  |  | Rodded main sewer and broke grease blockage. The main sewer is flowing at this time. Washed down affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2007-01-02 | 615-5590
4404 | 350 | 1 | Oakland | 2006-12-27 09:09 | 30 | 0 |  | 2006-12-27 09:09 |  | -- | 86TH AVE AND INTERNATIONAL BL | OAKLAND | ALAMEDA | 94621 |  |  | 2006-12-27 |  |  |  | HYDRO FLUSHED MAIN SEWER, CLEARED GREASE STOPPAGE. WASHED DOWN AND DISINFECTED STREET AREA AND GUTTER. COULD NOT SPILLED SEWAGE BECAUSE IT HAD DRAINED AWAY IN STORM INLET. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | LEADER | GIDDENS | 2006-12-27 | 6155969
4402 | 349 | 1 | Oakland | 2006-12-27 09:05 | 30 | 0 |  | 2006-12-27 09:05 |  | -- | 86TH AVE AND INTERNATIONAL BL | OAKLAND | ALAMEDA | 94621 |  |  | 2006-12-27 |  |  |  | HYDRO FLUSHED MAIN SEWER, CLEARED GREASE STOPPAGE. WASHED DOWN AND DISINFECTED STREET AREA AND GUTTER. COULD NOT SPILLED SEWAGE BECAUSE IT HAD DRAINED AWAY IN STORM INLET. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | LEADER | GIDDENS | 2006-12-27 | 6155969
4406 | 351 | 1 | Oakland | 2006-12-27 09:39 | 75 | 0 |  | 2006-12-27 09:39 |  | -- | 3888 SEQUOYA RD | OAKLAND | ALAMEDA | 94605 |  |  | 2006-12-22 |  |  |  | FOUND M/S PLUGGED WITH CONSTRUCTION DEBRIS PUSHED INTO M/H BY CONTRACTOR WORKING ON SITE. REMOVED DEBRIS,CLEARED STOPPAGE. M/S IS FLOWING CLEAR @ THIS TIME | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | LEADER | GIDDENS | 2006-12-27 | 6155969
4408 | 352 | 1 | Oakland | 2006-12-27 09:55 | 40 | 0 |  | 2006-12-27 09:55 |  | -- | 4150 CARRINGTON ST | OAKLAND | ALAMEDA | 94601 |  |  | 2006-12-21 |  |  |  | HYDROFLUSHED M/S CLEARED GREASE STOPPAGE WASHED DOWN AREA AND DISINFECTED. RECOVERED CLEAN UP WATER FRON GUTTER AREA. | [5 empty] | GROUND WATER IMPACTED | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | LEADER | GIDDENS | 2006-12-27 | 6155969
4391 | 345 | 1 | Oakland | 2006-12-22 15:55 | 400 | 0 |  | 2006-12-22 15:55 |  | -- | 5565 Fremont St. | Oakland | Alameda | 94608 |  |  | 2006-12-21 |  |  |  | Hydro flushed main sewer and cleared stoppage of grease. Vacuumed and mopped sewage from basement. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2006-12-22 | 615-5590
4389 | 344 | 1 | Oakland | 2006-12-22 15:49 | 67 | 0 |  | 2006-12-22 15:49 |  | -- | 2400 34th Ave. | Oakland | Alameda | 94601 |  |  | 2006-12-20 |  |  |  | Power rodded main sewer on easement to clear stoppage of grease. Washed down affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2006-12-22 | 615-5590
4387 | 343 | 1 | Oakland | 2006-12-22 15:44 | 20 | 0 |  | 2006-12-22 15:44 |  | -- | 6625 Elverton Dr. | Oakland | Alameda | 94611 |  |  | 2006-12-20 |  |  |  | Rodded main sewer, and broke stoppage of heavy roots. Washed down affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-22 | 615-5590
4395 | 347 | 1 | Oakland | 2006-12-22 16:19 | 400 | 0 |  | 2006-12-22 16:19 |  | -- | 2205 40th Ave. | Oakland | Alameda | 94601 |  |  | 2006-12-18 |  |  |  | Hydro flushed main sewer and cleared grease blockage. Washed down affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2006-12-22 | 615-5590
4393 | 346 | 1 | Oakland | 2006-12-22 16:13 | 60 | 0 |  | 2006-12-22 16:13 |  | -- | 3642 Nevil St. | Oakland | Alameda | 94601 |  |  | 2006-12-18 |  |  |  | Rodded and flushed main sewer, cleared blockage of roots. Washed and vacuumed affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-22 | 615-5590
4364 | 342 | 1 | Oakland | 2006-12-18 09:43 | 50 | 0 |  | 2006-12-18 09:43 |  | -- | 3238 63rd Ave. | Oakland | Alameda | 94605 |  |  | 2006-12-17 |  |  |  | Hand rodded main sewer and cleared blockage of roots. Cleaned and disinfected affected area. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-18 | 615-5590
4362 | 341 | 1 | Oakland | 2006-12-18 09:30 | 400 | 0 |  | 2006-12-18 09:30 |  | -- | 2852 68th Ave | Oakland | Alameda | 94605 |  |  | 2006-12-17 |  |  |  | Hand rodded main sewer and cleared main sewer of heavy grease. Pumped spill back in to sewer line from basement. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2006-12-18 | 615-5590
4591 | 373 | 1 | Oakland | 2007-01-23 09:56 | 60 | 0 |  | 2007-01-23 09:56 |  | -- | 5634 Glenbrook Drive | Oakland | Alameda | 94618-172 |  |  | 2006-12-15 |  |  |  | Main sewer line segment blocked with roots between structure #50-304-17 to structure #50-304-16, sewer map sheet #312, cleaned and disenfected affected spill areas. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2007-01-23 | (510)615-5566
4321 | 337 | 1 | Oakland | 2006-12-15 09:30 | 20 | 0 |  | 2006-12-15 09:30 |  | -- | Broadway & Rockridge | Oakland | Alameda | 94618 |  |  | 2006-12-14 |  |  |  | Flushed main sewer and cleared main sewer of root blockage. Washed down affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-15 | 615-5590
4310 | 336 | 1 | Oakland | 2006-12-14 09:15 | 250 | 0 |  | 2006-12-14 09:15 |  | -- | 9777 Golf Links Rd. | Oakland | Alameda | 94605 |  |  | 2006-12-13 |  |  |  | Rodded main sewer and cleared main of heavy roots. Because of the rainy weather the receiving waters flushed the creek area. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-14 | 615-5590
4308 | 335 | 1 | Oakland | 2006-12-14 08:54 | 25 | 0 |  | 2006-12-14 08:54 |  | -- | 73 Beechwood Dr. | Oakland | Alameda | 94618 |  |  | 2006-12-13 |  |  |  | Rodded main sewer on easement and cleared root blockage. Washed and disinfected affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-14 | 615-5590
4351 | 339 | 1 | Oakland | 2006-12-16 10:22 | 75 | 0 |  | 2006-12-16 10:22 |  | -- | 69th Ave. & Snell St. | Oakland | Alameda | 94621 |  |  | 2006-12-12 |  |  |  | Flushed and cleared blockage of heavy grease. Contained spill in gutter area. Cleaned, vacuumed affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2006-12-16 | 615-5590
4349 | 338 | 1 | Oakland | 2006-12-16 10:14 | 20 | 0 |  | 2006-12-16 10:14 |  | -- | 245 17th St. | Oakland | Alameda | 94612 |  |  | 2006-12-12 |  |  |  | Rodded main sewer with 6" auger & 8" saw and cleared blockage of heavy grease. Spill was contained in parking lot area and spill drained back into main sewer once line was opened. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2006-12-16 | 615-5590
4288 | 334 | 1 | Oakland | 2006-12-12 11:33 | 75 | 0 |  | 2006-12-12 11:33 |  | -- | 9523 Cherry St. | Oakland | Alameda | 94603 |  |  | 2006-12-11 |  |  |  | Flushed main sewer to break grease blockage. Main sewer is flowing at this time. Washed and cleaned affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2006-12-12 | 615-5590
4279 | 333 | 1 | Oakland | 2006-12-11 09:21 | 20 | 0 |  | 2006-12-11 09:21 |  | -- | Winthrope St. & Shone Ave. | Oakland | Alameda | 94605 |  |  | 2006-12-10 |  |  |  | Rodded main sewer on easement and cleared main sewer of roots. Cleaned affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-11 | 615-5590
4277 | 332 | 1 | Oakland | 2006-12-11 09:13 | 100 | 0 |  | 2006-12-11 09:13 |  | -- | 6232 Wood Dr. | Oakland | Alameda | 94611 |  |  | 2006-12-08 |  |  |  | Rodded main sewer, and cleared main sewer of heavy roots. Cleaned residence with mops, buckets and wet vac. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-11 | 615-5590
4274 | 330 | 1 | Oakland | 2006-12-11 08:44 | 10 | 0 |  | 2006-12-11 08:44 |  | -- | 3926 Linwood Ave. | Oakland | Alameda | 94602 |  |  | 2006-12-08 |  |  |  | Rodded main sewer on easement and cleared root blockage. Washed and disinfected affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-11 | 615-5590
4198 | 302 | 1 | Oakland | 2006-12-05 17:06 | 100 | 0 |  | 2006-12-05 17:06 |  | -- | Snell St. & 71st Ave. | Oakland | Alameda | 94621 |  |  | 2006-12-02 |  |  |  | Rodded & flushed main sewer, main sewer is now open. Vacuumed and disinfected affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4201 | 304 | 1 | Oakland | 2006-12-05 17:26 | 10 | 0 |  | 2006-12-05 17:26 |  | -- | 9039 Thermal St. | Oakland | Alameda | 94605 |  |  | 2006-11-29 |  |  |  | Rodded main sewer, main sewer is open. cleaned and disinfected affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4213 | 310 | 1 | Oakland | 2006-12-05 18:14 | 25 | 0 |  | 2006-12-05 18:14 |  | -- | 6811 Snake Rd. | Oakland | Alameda | 94611 |  |  | 2006-11-25 |  |  |  | Made repairs to temporary sewer main in rear yard easement. Cleaned and removed solids. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | PIPE |  | INFRASTRUCTURE FAILURE | -- Select One -- |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4211 | 309 | 1 | Oakland | 2006-12-05 18:04 | 200 | 0 |  | 2006-12-05 18:04 |  | -- | 5930 Castle Dr. | Oakland | Alameda | 94611 |  |  | 2006-11-25 |  |  |  | Rodded main sewer, cleared heavy roots from line. Washed and cleaned affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4219 | 313 | 1 | Oakland | 2006-12-05 18:34 | 100 | 0 |  | 2006-12-05 18:34 |  | -- | Ascot Dr. & Mastlands Dr. | Oakland | Alameda | 94611 |  |  | 2006-11-24 |  |  |  | Flushed main sewer. Main sewer is open. Cleaned and vacuumed sewage from gutter area. Used sandbags to trap sewage. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4217 | 312 | 1 | Oakland | 2006-12-05 18:24 | 50 | 0 |  | 2006-12-05 18:24 |  | -- | 3410 Seminary Ave. | Oakland | Alameda | 94605 |  |  | 2006-11-24 |  |  |  | Rodded main sewer on easement. Rodded main sewer up stream from above location. Cleaned and washed affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4215 | 311 | 1 | Oakland | 2006-12-05 18:20 | 85 | 0 |  | 2006-12-05 18:20 |  | -- | 3431 San Pablo Ave. | Oakland | Alameda | 94608 |  |  | 2006-11-24 |  |  |  | Flushed main sewer of heavy grease and rocks. Cleaned and disinfected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4221 | 314 | 1 | Oakland | 2006-12-05 18:39 | 40 | 0 |  | 2006-12-05 18:39 |  | -- | 6165 Ascot Dr. | Oakland | Alameda | 94611 |  |  | 2006-11-22 |  |  |  | Rodded main sewer on easement. Main sewer is flowing at this time. Washed down affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4203 | 305 | 1 | Oakland | 2006-12-05 17:35 | 40 | 0 |  | 2006-12-05 17:35 |  | -- | 6789 Evergreen Ave. | Oakland | Alameda | 94611 |  |  | 2006-11-21 |  |  |  | Rodded main sewer on easement, main sewer is flowing at this time. Washed affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4205 | 306 | 1 | Oakland | 2006-12-05 17:44 | 200 | 0 |  | 2006-12-05 17:44 |  | -- | 80th Ave. & Plymouth St. (Webster Academy School) | Oakland | Alameda | 94621 |  |  | 2006-11-20 |  |  |  | Flushed main sewer, main sewer is flowing at this time. Washed down affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4209 | 308 | 1 | Oakland | 2006-12-05 17:58 | 200 | 0 |  | 2006-12-05 17:58 |  | -- | 3527 Laguna Ave. | Oakland | Alameda | 94602 |  |  | 2006-11-18 |  |  |  | Rodded & flushed main sewer, pumped spill back into collection system. Cleaned and disinfected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Suupervisor | David Lonestar | 2006-12-05 | 615-5590
4207 | 307 | 1 | Oakland | 2006-12-05 17:51 | 500 | 0 |  | 2006-12-05 17:51 |  | -- | 3521 Laguna Ave. | Oakland | Alameda | 94602 |  |  | 2006-11-18 |  |  |  | Rodded and flushed main sewer, cleared grease from line. Pumped ewage into sanitary sewer collection system. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4225 | 316 | 1 | Oakland | 2006-12-05 19:01 | 60 | 0 |  | 2006-12-05 19:01 |  | -- | 3835 Delmont Ave. | Oakland | Alameda | 94605 |  |  | 2006-11-16 |  |  |  | Rodded main sewer. Cleaned and vacuumed storm inlet. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4223 | 315 | 1 | Oakland | 2006-12-05 18:45 | 25 | 0 |  | 2006-12-05 18:45 |  | -- | MacArthur Blvd. & Laguna Ave. | Oakland | Alameda | 94602 |  |  | 2006-11-15 |  |  |  | Rodded main sewer, cleared stoppage. Washed down affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4227 | 317 | 1 | Oakland | 2006-12-05 19:07 | 20 | 0 |  | 2006-12-05 19:07 |  | -- | 10512 Creekside Circle | Oakland | Alameda | 94603 |  |  | 2006-11-13 |  |  |  | Rodded main sewer to clear grease. Washed down and vacuumed affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4230 | 319 | 1 | Oakland | 2006-12-05 19:26 | 300 | 0 |  | 2006-12-05 19:26 |  | -- | 2960 Peralta Oaks Ct. (Behind Dunsmuir House) | Oakland | Alameda | 94605 |  |  | 2006-11-09 |  |  |  | Rodded main sewer, cleared main sewer of roots. Flushed and vacuumed affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4242 | 325 | 1 | Oakland | 2006-12-05 20:09 | 10 | 0 |  | 2006-12-05 20:09 |  | -- | 2200 International Blvd. | Oakland | Alameda | 94601 |  |  | 2006-11-08 |  |  |  | Rodded main sewer to clear grease. Washed and vacuumed affected areas. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | BLOCKAGE | GREASE |  | Business Bathroom |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4232 | 320 | 1 | Oakland | 2006-12-05 19:31 | 100 | 0 |  | 2006-12-05 19:31 |  | -- | 2520 Alida St. | Oakland | Alameda | 94607 |  |  | 2006-11-08 |  |  |  | Rodded main sewer clear of roots. Cleaned affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4236 | 322 | 1 | Oakland | 2006-12-05 19:49 | 50 | 0 |  | 2006-12-05 19:49 |  | -- | 1944 90th Ave. | Oakland | Alameda | 94605 |  |  | 2006-11-07 |  |  |  | Flushed main sewer of grease. Washed and vacuumed affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4234 | 321 | 1 | Oakland | 2006-12-05 19:44 | 175 | 0 |  | 2006-12-05 19:44 |  | -- | 4029 E17th St. | Oakland | Alameda | 94601 |  |  | 2006-11-07 |  |  |  | Rodded & flushed main sewer to clear line of heavy grease and debris in two locations. Cleaned and vacuumed affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4240 | 324 | 1 | Oakland | 2006-12-05 20:03 | 300 | 0 |  | 2006-12-05 20:03 |  | -- | 4550 Heafey Rd. | Oakland | Alameda | 94605 |  |  | 2006-11-06 |  |  |  | Rodded main sewer to clear heavy grease. Washed, vacuumed and dumped 2000 gallons of water to clean affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4238 | 323 | 1 | Oakland | 2006-12-05 19:57 | 50 | 0 |  | 2006-12-05 19:57 |  | -- | 450 Heafey Rd. (By Sequoyah Country Club gate) | Oakland | Alameda | 94605 |  |  | 2006-11-06 |  |  |  | Rodded main sewer to clear roots. Washed and vacuumed affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4246 | 327 | 1 | Oakland | 2006-12-05 20:23 | 120 | 0 |  | 2006-12-05 20:23 |  | -- | 6633 Gunn Dr. | Oakland | Alameda | 94611 |  |  | 2006-11-05 |  |  |  | Rodded main sewer to clear roots. Main sewer is flowing at this time. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4244 | 326 | 1 | Oakland | 2006-12-05 20:18 | 30 | 0 |  | 2006-12-05 20:18 |  | -- | 8910 Burr St. | Oakland | Alameda | 94605 |  |  | 2006-11-05 |  |  |  | Reconnected 4" temporary sewer main. Area is being slipped lined. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | PIPE |  | CAUSE UNKNOWN | -- Select One -- |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4250 | 329 | 1 | Oakland | 2006-12-05 20:35 | 100 | 0 |  | 2006-12-05 20:35 |  | -- | 2060 Melvin Rd. | Oakland | Alameda | 94602 |  |  | 2006-11-04 |  |  |  | Rodded main sewer and cleared line of roots. Washed and vacuumed affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4248 | 328 | 1 | Oakland | 2006-12-05 20:31 | 150 | 0 |  | 2006-12-05 20:31 |  | -- | 1014 7th St. | Oakland | Alameda | 94607 |  |  | 2006-11-04 |  |  |  | Rodded main sewer easement. Washed and Cleaned affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2006-12-05 | 615-5590
4065 | 298 | 1 | Oakland | 2006-11-05 09:39 | 20 | 0 |  | 2006-11-05 09:39 |  | -- | 6788 Armour Dr. | Oakland | Alameda | 94611 |  |  | 2006-10-30 |  |  |  | Hand rodded main sewer and cleared main of heavy roots. Cleaned and disinfected affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-11-05 | (510)615-5590 | jramey@oaklandnet.com,gamirzehni@oaklandnet.com,gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
4063 | 297 | 1 | Oakland | 2006-11-05 09:32 | 50 | 0 |  | 2006-11-05 09:32 |  | -- | 1350 Mountain Blvd. | Oakland | Alameda | 94611 |  |  | 2006-10-27 |  |  |  | Power rodded main sewer line of roots. The main is clear and flowing at this time. Cleaned affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-11-05 | (510)615-5590 | jramey@oaklandnet.com, gamirzehni@oaklandnet.com,gthomas@oaklandnet.com,bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
4060 | 295 | 1 | Oakland | 2006-11-05 08:51 | 40 | 0 |  | 2006-11-05 08:51 |  | -- | 2519 Avenal Ave. | Oakland | Alameda | 94605 |  |  | 2006-10-26 |  |  |  | Power rodded main sewer and cleared sewer of heavy grease, washed and cleaned affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWA Supervisor | David Lonestar | 2006-11-05 | (510)615-5590 | gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com;gamirzehni@oaklandnet.com | MINOR
4068 | 300 | 1 | Oakland | 2006-11-05 10:07 | 20 | 0 |  | 2006-11-05 10:07 |  | -- | 40 Maiden Lane | Oakland | Alameda | 94602 |  |  | 2006-10-19 |  |  |  | Power rodded main sewer of heavy roots. Cleaned affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-11-05 | (510)615-5590 | jramey@oaklandnet.com,gamirzehni@oaklandnet.com,gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3992 | 292 | 1 | Oakland | 2006-10-16 11:18 | 10 | 0 |  | 2006-10-16 11:18 |  | -- | 297 Rishell Dr. | Oakland | Alameda | 94619 |  |  | 2006-10-15 |  |  |  | Rodded and cleared heavy root blockage. Hauled away contaminated soil and cleaned/disinfected affected area in rear yard. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-10-16 | (510)615-5590 | gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gamirzehni@oaklandnet.com, jramey@oaklandnet.com | MINOR
3994 | 293 | 1 | Oakland | 2006-10-16 11:37 | 15 | 0 |  | 2006-10-16 11:37 |  | -- | 6868 Buckingham Blvd. | Oakland | Alameda | 94705 |  |  | 2006-10-15 |  |  |  | Rodded main sewer easement and cleared heavy root blockage. uncovered buried lamphole, and disinfected/hauled away contaminated debris in affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-10-16 | (510)615-5590 | gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gamirzehni@oaklandnet.com, jramey@oaklandnet.com | MINOR
3996 | 294 | 1 | Oakland | 2006-10-16 11:44 | 10 | 0 |  | 2006-10-16 11:44 |  | -- | 6925 Balsam Way | Oakland | Alameda | 94611 |  |  | 2006-10-15 |  |  |  | Uncovered buried Manhole and removed heavy roots. Rodded and cleared blockage. Cleaned and hauled away contaminated soil. Disinfected affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-10-16 | (510)615-5590 | gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com,gamirzehni@oaklandnet.com,jramey@oaklandnet.com | MINOR
3983 | 289 | 1 | Oakland | 2006-10-15 09:50 | 60 | 0 |  | 2006-10-15 09:50 |  | -- | 3500 Mountain Blvd. | Oakland | Alameda | 94619 |  |  | 2006-10-14 |  |  |  | Rodded and cleared Main sewer of unknown stoppage. Washed affected area and vaccumed water. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | CAUSE UNKNOWN | --Select None-- |  |  |  | PWA Supervisor | David Lonestar | 2006-10-15 | (510)615-5590 | gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gamirzehni@oaklandnet.com, jramey@oaklandnet.com | MINOR
3986 | 291 | 1 | Oakland | 2006-10-15 10:14 | 90 | 0 |  | 2006-10-15 10:14 |  | -- | 5878 Broadway Terrace | Oakland | Alameda | 94618 |  |  | 2006-10-12 |  |  |  | Rodded Main Sewer and clear heavy roots. Washed, cleaned and vaccumed affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-10-15 | (510)615-5590 | gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gamirzehni@oaklandnet.com, jramey@oaklandnet.com | MINOR
3932 | 285 | 1 | Oakland | 2006-09-27 10:04 | 50 | 0 |  | 2006-09-27 10:04 |  | -- | 5714 THORNHILL DRIVE | OAKLAND | ALAMEDA | 94611-2145 |  |  | 2006-09-22 |  |  |  | LINE SEGMENT BLOCKED BETWEEN STRUCTURE #50-391-10 TO STRUCTURE #50-391-10, SEWER MAP PAGE #302, CLEARED BLOCKAGE AND CLEANED AFFECTED AREA. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SEWER MAINT LEADER | ARMANDO LOZANO | 2006-09-27 | (510)615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, jramey@oaklandnet.com, dlonestar@oaklandnet.com, gamirzheni@oaklandnet.com | MINOR
3894 | 283 | 1 | Oakland | 2006-09-19 10:54 | 65 | 0 |  | 2006-09-19 10:54 |  | -- | 1328 WELLINGTON ST | OAKLAND | ALAMEDA | 94601 |  |  | 2006-09-19 |  |  |  | FOUND M/S PLUGGED AND OVERFLOWING. RODDED MAIN AND CLEARED ROOT STOPPAGE. WASHED DOWN AND CLEANED AFFECTED AREA. RECOVERED WASH DOWN WATER | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | LEADER | GIDDENS | 2006-09-19 | 6155969 | jheredia@oaklandnet.com,gamerzihni@oaklandnet.com,gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3905 | 284 | 2 | Oakland | 2006-09-20 16:21 | 25 | 0 |  | 2006-09-20 16:21 |  | -- | 5760 CABOT RD | OAKLAND | ALAMEDA | 94611 |  |  | 2006-09-19 |  |  |  | CHECKED AND FOUND M/S PLUGGED IN STREET. RODDED M/S CLEARED UNKNOWN STOPPAGE.WASHED AND CLEANED AREA THAT WAS AFFECTED.COULD NOT CAPTURE FULL AMOUNT OF SPILL. WAS GONE WHEN WE ARRIVED. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | LEADER | GIDDENS | 2006-09-20 | 6155969 | jramey@oaklandnet.com, gamerzihni@oaklandnet.com,gthomas@oaklandnet.com,bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3888 | 282 | 1 | Oakland | 2006-09-15 14:59 | 20 | 0 |  | 2006-09-15 14:59 |  | -- | 3653 Carrington | oakland | alameda | 94602 |  |  | 2006-09-11 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | wayne guidici | 2006-09-15 | 5106155969 | gamirraehni@oaklandnet.com, gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3863 | 279 | 1 | Oakland | 2006-09-08 10:47 | 20 | 0 |  | 2006-09-08 10:47 |  | -- | 1520 COMMERNCE WAY | OAKLAND | ALAMEDA | 96602 |  |  | 2006-09-06 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | CLEAN OUT |  | CAUSE UNKNOWN | --Select None-- |  |  |  | PWS | WAYNE GUIDICI | 2006-09-08 | 5106155985 | gamirzenhi@oaklandnet.com, gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3842 | 276 | 1 | Oakland | 2006-09-05 13:53 | 60 | 0 |  | 2006-09-05 13:53 |  | -- | 56th ave and international blvd | oakland | alameda | 94621 |  |  | 2006-09-03 | [9 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | pws | wayne guidici | 2006-09-05 | 6155969 | gamirzehni@oaklandnet.com,gthimas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3839 | 274 | 1 | Oakland | 2006-09-05 13:42 | 10 | 0 |  | 2006-09-05 13:42 |  | -- | PERKINS AND BELLEVUE | OAKLAND | alameda | 94612 |  |  | 2006-08-28 | [9 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | pws | wayne guidici | 2006-09-05 | 5106155969 | gthomas@oaklandnet.com,cgamirzehni@oaklandnet.com, heredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.comas | MINOR
3801 | 272 | 1 | Oakland | 2006-08-28 10:13 | 200 | 0 |  | 2006-08-28 10:13 |  | -- | 6172 Mathieu | oakland | alameda | 94618 |  |  | 2006-08-26 |  |  |  | Sewage getting into electrial box. We will televise to see how sewage is getting into the box. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | OTHER | pge electrail box | CAUSE UNKNOWN | --Select None-- |  |  |  | pws | wayne guidici | 2006-08-28 | 5106155969 | gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gamirzehni@oaklandnet.com | MINOR
3805 | 273 | 2 | Oakland | 2006-08-28 10:31 | 20 | 0 |  | 2006-08-28 10:31 |  | -- | 1004 elbert st. | oakland | alameda | 94602 |  |  | 2006-08-24 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | waye guidici | 2006-08-28 | 5106155969 | gamirzenhi@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gthomas@oaklandnet.com | MINOR
3794 | 269 | 1 | Oakland | 2006-08-25 14:14 | 50 | 0 |  | 2006-08-25 14:14 |  | -- | 41 Fairmount Dr. | Oakland | Alameda | 94611 |  |  | 2006-08-16 |  |  |  | Rodded main sewer, opened main sewer. Hydro-flusher captured spill and clean-up area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | CAUSE UNKNOWN | MULTIPLE CAUSES |  |  |  | PWA Supervisor | David Lonestar | 2006-08-25 | (510)615-5969 | gthomas@oaklandnet.com;gamirzehni@oaklandnet.com;bsaunders@oaklandnet.com; mjneary@oaklandnet.com | MINOR
3796 | 270 | 1 | Oakland | 2006-08-25 14:22 | 10 | 0 |  | 2006-08-25 14:22 |  | -- | 805 Mandana Blvd. | Oakland | Alameda | 94610 |  |  | 2006-08-16 |  |  |  | Rodded roots in main sewer, opened main sewer. Washed and cleaned up affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-08-25 | (510)615-5969 | gthomas@oaklandnet.com;gamerzehni2oaklandnet.com; bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3798 | 271 | 1 | Oakland | 2006-08-25 14:36 | 70 | 0 |  | 2006-08-25 14:36 |  | -- | 900 Paramount Rd. (Rear of property) | Oakland | Alameda | 94610 |  |  | 2006-08-16 |  |  |  | Rodded roots easement main sewer, came across possible breakdown at 150 ft. Dye tested 900 Paramount, nothing showed. Green dye did show at 889 Paramount. Need to T.V. the main. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-08-25 | (510)615-5969 | gthomas@oaklandnet.com;gamirzehni@oaklandnet.com; bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3792 | 268 | 1 | Oakland | 2006-08-25 14:03 | 30 | 0 |  | 2006-08-25 14:03 |  | -- | 5627 Cabot Dr. | Oakland | Alameda | 94611 |  |  | 2006-08-14 |  |  |  | Rodded sewer main easement, main contained roots. Sewer main is open. Clean up at rear of residence 5627 Cabot Dr. | [5 empty] | GROUND WATER IMPACTED | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA Supervisor | David Lonestar | 2006-08-25 | (510)615-5969 | gthomas@oaklandnet.com;gamirzehni@oaklandnet.com;bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3729 | 265 | 1 | Oakland | 2006-08-14 14:56 | 10 | 0 |  | 2006-08-14 14:56 |  | -- | 1824 MOUNTAIN BL | OAKLAND | ALAMEDA | 94611 |  |  | 2006-08-13 |  |  |  | RODDED M/S CLEARED UNKNOWN STOPPAGE. WATER SOAKED INTO GROUND | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | CAUSE UNKNOWN | --Select None-- |  |  |  | LEADER | GIDDENS | 2006-08-14 | 615-5941 | jheredia@oaklandnet.com,gamerzihni@oaklandnet.com,gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3721 | 262 | 1 | Oakland | 2006-08-14 14:22 | 75 | 0 |  | 2006-08-14 14:22 |  | -- | 1132 BELLA VISTA AVE | OAKLAND | ALAMEDA | 94601 |  |  | 2006-08-12 |  |  |  | RODDEDM/S CLEARED GREASE AND DEBRIS STOPPAGE. WASHED DOWN AND RECOVERED WASH WATHE FROM STORM INLET. | [5 empty] | GROUND WATER IMPACTED | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | LEADER | GIDDENS | 2006-08-14 | 615-5969 | jheredia@oaklandnet.com, gthomas@oaklandnet..ocm,gamerzihni@oaklandnet.com,bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3723 | 263 | 1 | Oakland | 2006-08-14 14:23 | 75 | 0 |  | 2006-08-14 14:23 |  | -- | 1132 BELLA VISTA AVE | OAKLAND | ALAMEDA | 94601 |  |  | 2006-08-12 |  |  |  | RODDEDM/S CLEARED GREASE AND DEBRIS STOPPAGE. WASHED DOWN AND RECOVERED WASH WATHE FROM STORM INLET. | [5 empty] | GROUND WATER IMPACTED | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | LEADER | GIDDENS | 2006-08-14 | 615-5969 | jheredia@oaklandnet.com, gthomas@oaklandnet..com,gamerzihni@oaklandnet.com,bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3725 | 264 | 1 | Oakland | 2006-08-14 14:25 | 75 | 0 |  | 2006-08-14 14:25 |  | -- | 1132 BELLA VISTA AVE | OAKLAND | ALAMEDA | 94601 |  |  | 2006-08-12 |  |  |  | RODDEDM/S CLEARED GREASE AND DEBRIS STOPPAGE. WASHED DOWN AND RECOVERED WASH WATHE FROM STORM INLET. | [5 empty] | GROUND WATER IMPACTED | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | LEADER | GIDDENS | 2006-08-14 | 615-5969 | jheredia@oaklandnet.com,gthomas@oaklandnet.com,gamerzihni@oaklandnet.com,bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3710 | 258 | 1 | Oakland | 2006-08-10 10:34 | 30 | 0 |  | 2006-08-10 10:34 |  | -- | 5915 HAYES ST | OAKLAND | ALAMEDA | 94621 |  |  | 2006-08-10 |  |  |  | lATERAL OVERFLOWING S/S REPORT ON FILE. WASHED DOWN AREA RECOVERD WATER. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | OTHER | LATERAL | BLOCKAGE | --Select None-- |  |  |  | LEADER | GIDDENS | 2006-08-10 | 615-5941 | jheredia@oaklandnet.com,GAMIRZENHI@OAKLANDNET.COM, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3712 | 259 | 1 | Oakland | 2006-08-10 11:11 | 80 | 0 |  | 2006-08-10 11:11 |  | -- | ASCOT DRIVE & LARRY LANE | OAKLAND | ALAMEDA | 94611 |  |  | 2006-08-10 |  |  |  | WASHED DOWN AFFECTED AREA FROM A PRIOR SPILL AND VACCUMED CONTAMINATED WATER (250 GALLONS) AND DEBRIS FROM GUTTER AND STORM INLET. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | WORKER | KENYA LAURIE | 2006-08-10 | 615-5566 | jheredia@oaklandnet.com,gamirzenhi@oakland net.com bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3714 | 260 | 1 | Oakland | 2006-08-10 11:20 | 300 | 0 |  | 2006-08-10 11:20 |  | -- | 2110 MASTLANDS | OAKLAND | ALAMEDA | 94611 |  |  | 2006-08-10 |  |  |  | CLEANED DEBRIS, DISENFECTED AREA AROUND MANHOLE. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | WORKER | KENYA LAURIE | 2006-08-10 | 615-5566 | jheredia@oaklandnet.com,gamirzenhi@oaklandnet.combsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3701 | 255 | 1 | Oakland | 2006-08-08 10:42 | 50 | 0 |  | 2006-08-08 10:42 |  | -- | 96TH AVE AND SUNNYSIDE ST | OAKLAND | ALAMEDA | 94611 |  |  | 2006-08-07 |  |  |  | HYDRO FLUSHED M/S CLEARED GREASE STOPPAGE. WASHED DOWN W/ 500 GALLONS OF FRESH WATER. RECOVERED ALL OF THE SPILL AND CLEAN-UP WATER. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | LEADER | GIDDENS | 2006-08-08 | 615-5969 | jheredia@oaklandnet.com, gthomas@oaklandnet.com,gamerzihni@oaklandnet.com,bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3689 | 253 | 1 | Oakland | 2006-08-04 09:48 | 30 | 0 |  | 2006-08-04 09:48 |  | -- | 6306 Buena Vista | Oakland | Alameda | 94608 |  |  | 2006-08-04 |  |  |  | Washed down sidewalk with water and Vaccumed up sewage out of gutter area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | leader | J.R. Nicks | 2006-08-04 | 615-5969 | jheredia@oaklandnet.com,gamirzenhia@oaklandnet.com,gthomas bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3694 | 254 | 1 | Oakland | 2006-08-07 14:15 | 75 | 0 |  | 2006-08-07 14:15 |  | -- | 11035 GOLFLINKS RD | OAKLAND | ALAMEDA | 95605 |  |  | 2006-08-04 |  |  |  | Found manhole overflowing, had 195 rod and unplugged manhole full of roots. Main sewer is clear at this time. Shoveled and dug waste in yard. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SMW | LAURIE | 2006-08-07 | 615-5941 | jheredia@oaklandnet.com, gthomas@oaklandnet.com,gamerzihni@oaklandnet.com,bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3635 | 248 | 1 | Oakland | 2006-07-20 10:10 | 30 | 0 |  | 2006-07-20 10:10 |  | -- | Easement between Snake and Armour Dr and Thornhill | Oakland | Alameta | 94611 |  |  | 2006-07-19 |  |  |  | Damed Creek and vacumed up spill,Diluted the spill with 1000, Gal of water,recovered water and returned to the collection system. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | OTHER | Temp main sewer | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Leader | Nicks | 2006-07-20 | 615-5569 | jheredia@oaklandnet.com, gthomas@oaklandnet.com,gamirzehni@oaklandnet.com,bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3637 | 249 | 1 | Oakland | 2006-07-20 10:30 | 100 | 0 |  | 2006-07-20 10:30 |  | -- | 279 Elysian Fields | Oakland | ALAMEDA | 94605 |  |  | 2006-06-30 |  |  |  | Raked and Washed down, | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | leader | Nicks | 2006-07-20 | 615-5566 | jheredia@oaklandnet.com,gamirzehni@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3579 | 245 | 1 | Oakland | 2006-06-29 10:47 | 100 | 0 |  | 2006-06-29 10:47 |  | -- | COUNTRY CLUB ON HILLSIDE NEXT TO STREET | OAKLAND | ALAMEDA | 94618 |  |  | 2006-06-23 |  |  |  | HYDROFLUSHED M/S CLEARED DEBRIS STOPPAGE. WASHED DOWN AND DISINFECTED AREA. RECOVERED 25 GALLONS OF THE SPILL. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | LEADER | GIDDENS | 2006-06-29 | 615-5969 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com,gthomas@oaklandnet.com,gamirzehni@oaklandnet.co, | MINOR
3581 | 246 | 1 | Oakland | 2006-06-29 10:49 | 100 | 0 |  | 2006-06-29 10:49 |  | -- | COUNTRY CLUB ON HILLSIDE NEXT TO STREET | OAKLAND | ALAMEDA | 94618 |  |  | 2006-06-23 |  |  |  | HYDROFLUSHED M/S CLEARED DEBRIS STOPPAGE. WASHED DOWN AND DISINFECTED AREA. RECOVERED 25 GALLONS OF THE SPILL. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | LEADER | GIDDENS | 2006-06-29 | 615-5969 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com,gthomas@oaklandnet.com,gamirzehni@oaklandnet.com | MINOR
3529 | 239 | 1 | Oakland | 2006-06-21 10:45 | 10 | 0 |  | 2006-06-21 10:45 |  | -- | CLARMONT HOTEL ALVARADO AND CLAIRMONT | OAKLAND | ALAMEDA | 94705 |  |  | 2006-06-17 |  |  |  | RODDED MAIN SEWER CLEARED ROOT STOPPAGE. SPILL WAS CONTAINED ON ASPHALT INN PARKING LOT AND DRAINED BACK INTO SEWER. RODDED FROM M/H #17-408-02 TOO 17-408-03 MAP 337 | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | LEADER | GIDDENS | 2006-06-21 | 6155969 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com,gamirzehni@oaklandnet.com,gthomas@oaklandnet.com | MINOR
3531 | 240 | 1 | Oakland | 2006-06-21 11:08 | 80 | 0 |  | 2006-06-21 11:08 |  | -- | 6705 LUCILLE | OAKLAND | ALAMEDA | 94621 |  |  | 2006-06-15 |  |  |  | HYDROFLUSHED SEWER DEBRIS STOPPAGE. CLEANED UP SOLID WASTEAND WASHED DOWN GUTTER AND DISINFECTED AREA. FLUSHED FROM M/H #83-101-49 TOO 83-101-46 MAP PAGE 89. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | LEADER | GIDDENS | 2006-06-21 | 615 5969 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com,gthomas@oaklandnet.com,gamirzehni@oaklandnet.com | MINOR
3533 | 241 | 1 | Oakland | 2006-06-21 14:11 | 100 | 0 |  | 2006-06-21 14:11 |  | -- | 20TH ST AND BROADWAY | OAKLAND | ALAMEDA | 94612 |  |  | 2006-06-15 |  |  |  | RODDED M/S FROM M/H ON 20TH ST #52-302-13 TOO A BLIND CONNECTION ON BROADWAY. RECOVERED APPX. 50 GALLONS FROM GUTTER. WASHED DOWN GUTTER WITH 300 GALLONS OF FRESH WATER AND DISINFECTED AREA. MAP # 221. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | LEADER | GIDDENS | 2006-06-21 | 615-5969 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com,gamirzehni@oaklandnet.com,gthomas@oaklandnet.com | MINOR
3535 | 242 | 1 | Oakland | 2006-06-21 14:29 | 200 | 0 |  | 2006-06-21 14:29 |  | -- | 7825 SAN LEANDRO ST | OAKLAND | ALAMEDA | 94621 |  |  | 2006-06-15 |  |  |  | FLUSHED AND RODDED M/S IN STREET. CLEARED DEBRIS STOPPAGE. SPILL DRAINED BACK INTO FLOOR DRAIN IN BLDG. CLEANED AND DISINFECTED FLOOR IN BLDG. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | CLEAN OUT |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | leader | giddens | 2006-06-21 | 615-5969 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com,gthomas@oaklandnet.com,gamirzehni@oaklandnet.com | MINOR
3583 | 247 | 1 | Oakland | 2006-06-29 11:11 | 75 | 0 |  | 2006-06-29 11:11 |  | -- | 540 W MAC ARTHUR BL | OAKLAND | ALAMEDA | 94601 |  |  | 2006-06-11 |  |  |  | FLUSHED M/S CLEARED DEBRIS STOPPAGE. WASHED DOWN AND DISINFECTED GUTTER AREA. FLUSHED SPILL WITH 300 GALLONS OF WATER | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | LEADER | GIDDENS | 2006-06-29 | 615-5969 | jheredia@oaklandnet.com, gthomas@oaklandnet.com,gamirzehni@oaklandnet.com | MINOR
3441 | 235 | 1 | Oakland | 2006-05-31 13:36 | 200 | 0 |  | 2006-05-31 13:36 |  | -- | 1067 NORWOOD AVE | OAKLAND | ALAMEDA | 94611 |  |  | 2006-05-30 |  |  |  | RODDED AND FLUSHED M/S ON E/MENT CLEARED ROOT STOPPAGE.WASHED DOWN AND DISINFECTED GUTTER AREA. FLUSHED STORM DRAIN WITH 500 GALLONS OF WATER. RODDED FROM M/H #54-312-C8 TOO 54-312-L4. MAP #225. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | LEADER | GIDDENS | 2006-05-31 | 615-5969 | jheredia@oaklandnet.com, gthomas@oaklandnet.com,gamerzihni@oaklandnet.com,bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3424 | 230 | 1 | Oakland | 2006-05-30 11:03 | 100 | 0 |  | 2006-05-30 11:03 |  | -- | WEST MAC ARTHUR AND TELEGRAPH | OAKLAND | ALAMEDA | 94606 |  |  | 2006-05-27 |  |  |  | West MAC ARTHUR BL AND TELEGRAPH AVE. M/S PLUGGED WITH GREASE. HYDROFLUSHED M/S CLEARED GREASE STOPPAGE. VACCUMED OVERFLOW WATER FROM INLET. WASHED DOWN GUTTER AND DISINFECTED. FLUSHED FROM M/H #56-002-16 TO 56-002-18 MAP 268 | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | LEADER | GIDDENS | 2006-05-30 | 615-5969 | jheredia@oaklandnet.com, gthomas@oaklandnet.com,gamirzehni@oaklandnet.com,bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3426 | 231 | 1 | Oakland | 2006-05-30 11:30 | 86 | 0 |  | 2006-05-30 11:30 |  | -- | DEAD END OF MONTWOOD ON FIRE TRAIL. | OAKLAND | ALAMEDA | 94604 |  |  | 2006-05-27 |  |  |  | RODDED M/S CLEARED RAGS AND DEBRIS STOPPAGE.HAD HYDRO DUMP 1000 GALLONS OF WATER TO FLUSH CREEK. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | LEADER | GIDDENS | 2006-05-30 | 615-5969 | jheredia@oaklandnet.com, gamirzehni@oaklandnet.com,gthomas@oaklandnet.com,bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3429 | 233 | 1 | Oakland | 2006-05-30 13:07 | 100 | 0 |  | 2006-05-30 13:07 |  | -- | 5115 SADDLEBROOK DR. | OAKLAND | ALAMEDA | 94619 |  |  | 2006-05-27 |  |  |  | RODDED AND FLUSHED M/S CLEARED GREASE STOPPAGE. FUUSHED STORM LINE WITH 500 GALLONS OF FRESH WATER. FLUSHED FROM M/H #83-512-25TO 83-512-23 MAP # 176 | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | LEADER | GIDDENS | 2006-05-30 | 615-5969 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3431 | 234 | 1 | Oakland | 2006-05-30 13:16 | 5 | 0 |  | 2006-05-30 13:16 |  | -- | 4019 1/2BROOKDALE AVE | OAKLAND | ALAMEDA | 94601 |  |  | 2006-05-26 |  |  |  | HYDRO FLUSHED M/S ON NEVIL ST. CLEARED DEBRIS STOPPAGE. FLUSHED M/S FROM M/H #81-102-83 TO #81-102-84 MAP # 135 | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE | GROUND | BLOCKAGE | DEBRIS |  |  |  | LEADER | GIDDENS | 2006-05-30 | 615-5969 | jheredia@oaklandnet.com, gthomas@oaklandnet.com,gamerzihni@oaklandneet.combsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3387 | 225 | 1 | Oakland | 2006-05-23 10:44 | 95 | 0 |  | 2006-05-23 10:44 |  | -- | 1414 3RD AVE | OAKLAND | ALAMEDA | 94606 |  |  | 2006-05-19 |  |  |  | FOUND MAIN SEWER BLOCKED WITH CONCRETE. SET UP BYPASS PUMP TO ABATE THE OVERFLOW. DUG AND REPAIRED PIPE . | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | LEADER | GIDDENS | 2006-05-23 | 510-615-5941 | jheredia@oaklandnet.com, gthomas@oaklandnet.com,gamirzehni@oaklandnet.com,bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3389 | 226 | 1 | Oakland | 2006-05-23 10:56 | 85 | 0 |  | 2006-05-23 10:56 |  | -- | SKYLINE BL @ MANZANITA BL | OAKLAND | ALAMEDA | 94611 |  |  | 2006-05-15 |  |  |  | MAIN SEWERPLUGGED WITH ROOTS. RODDED MAIN CLEARED ROOT STOPPAGE. WASHED DOWN AND DISINFECTED AREA. FLUSHED STORM LINE WITH 500 GALLONS OF WATER. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | LEADER | GIDDENS | 2006-05-23 | 510-615-5985 | jheredia@oaklandnet.com, gthomas @oaklandnet.com,gamirzehni@oaklandnet.com,bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3391 | 227 | 1 | Oakland | 2006-05-23 10:59 | 85 | 0 |  | 2006-05-23 10:59 |  | -- | SKYLINE BL @ MANZANITA BL | OAKLAND | ALAMEDA | 94611 |  |  | 2006-05-15 |  |  |  | MAIN SEWERPLUGGED WITH ROOTS. RODDED MAIN CLEARED ROOT STOPPAGE. WASHED DOWN AND DISINFECTED AREA. FLUSHED STORM LINE WITH 500 GALLONS OF WATER. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | LEADER | GIDDENS | 2006-05-23 | 510-615-5985 | jheredia@oaklandnet.com, gthomas@oaklandnet.com,gamirzehni@oaklandnet.com,bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3341 | 223 | 1 | Oakland | 2006-05-15 15:36 | 48 | 0 |  | 2006-05-15 15:36 |  | -- | 1832 90TH AVE | OAKLAND | ALAMEDA | 94603 |  |  | 2006-05-13 |  |  |  | RODDED M/S CLEARED GREASSE STOPPAGE. SWEPT UP SOLIDS, WASHED DOWN AREA AND DISINFECTED AREA. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | LEADER | GIDDENS | 2006-05-15 | 510-615-5985 | jheredia@oaklandnet.com,gthomas @oaklandnet.comgamirzihni@oaklandnet.com bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3349 | 224 | 1 | Oakland | 2006-05-16 15:31 | 100 | 0 |  | 2006-05-16 15:31 |  | -- | DEAD END OF MONTWOOD ON FIRE TRAIL | OAKLAND | ALAMEDA | 94605 |  |  | 2006-05-11 |  |  |  | RODDED M/S CLEARED ROOT STOPPAGE. FLUSHED CREEK W/1000 GALLONS OF WATER. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | LEADER | GIDDENS | 2006-05-16 | 510-615-5985 | jheredia@oaklandnet.com,gamirzihni@oaklandnet.com,gthomas@oaklandntt.com bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3395 | 229 | 1 | Oakland | 2006-05-23 12:11 | 20 | 0 |  | 2006-05-23 12:11 |  | -- | 6625 banning dr | oakland | alameda | 94611 |  |  | 2006-05-09 |  |  |  | rodded m/s cleared root stoppage. washed down and disinfected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | OTHER | from ground | BLOCKAGE | ROOTS |  |  |  | leader | giddens | 2006-05-23 | 510-615-5985 | jheredia@oaklandnet.com, gthomas@oaklandnet.com,gamirzehni@oaklandnet.com,bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3393 | 228 | 1 | Oakland | 2006-05-23 11:41 | 30 | 0 |  | 2006-05-23 11:41 |  | -- | 1015 82ND AVE | OAKLAND | ALAMEDA | 94621 |  |  | 2006-05-08 |  |  |  | FOUND M/S PLUGGED WITH GREASE. RODDED M/S CLEARED GREASE STOPPAGE . HAD HYDRO FLUSH M/S AND WASH DOWN AND DISINFECT AREA | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | LEADER | GIDDENS | 2006-05-23 | 510-615-5985 | jheredia@oaklandnet.com, gthomas@oaklandnet.com,gamirzehni@oaklandnet.com,bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3322 | 221 | 1 | Oakland | 2006-05-08 15:07 | 100 | 0 |  | 2006-05-08 15:07 |  | -- | 978 40th st | OAKLAND | ALAMEDA | 94602 |  |  | 2006-05-06 |  |  |  | RODDED M/S CLEARED GREASE STOPPAGE AND REMOVED FLUSHER HOSECAVE OVER M/S.PUMPED OUT INLETAND CLEANED AND DISINFECTED IT | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | LEADER | GIDDENS | 2006-05-08 | 510-6155985 | jheredia@oaklandnet.com,GTHOMAS@OAKLANDNET.COMGAMIRgthomas@oaklandnet.comgamirzihni@oaklandnet.combsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3320 | 220 | 1 | Oakland | 2006-05-08 14:45 | 350 | 0 |  | 2006-05-08 14:45 |  | -- | 984 40th st | oakland | alameda | 94608 |  |  | 2006-05-05 |  |  |  | found m/s plugged and overflowing flushed m/s could not clear hose got stuck in m/s made work order to dig and repair. stopped overflow for the time being | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | leader | GIDDENS | 2006-05-08 | 510-615-5985 | jheredia@oaklandnet.com,GTHOMAS@oaklandnet.comgamerzihni@oakland net.com bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3293 | 213 | 1 | Oakland | 2006-05-04 09:21 | 25 | 0 |  | 2006-05-04 09:21 |  | -- | 3996 OAKMORE RD | OAKLAND | ALAMEDA | 94602 |  |  | 2006-05-04 |  |  |  | M/H OVERFLOWING FROM M/H IN REAR YARD. RODDED M/S CLEARED ROOT STOPPAGE. DISINFECTED SPILL AREA. rodded from m/h #56-004-20 too 56-004-19 map #226. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | LEADER | RON GIDDENS | 2006-05-04 | 510-615-5985 | gthomas@oaklandnet.com,gamirzehni@oaklandnet.com bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3316 | 218 | 1 | Oakland | 2006-05-08 13:38 | 10 | 0 |  | 2006-05-08 13:38 |  | -- | 2520 MONTANA ST | OAKLAND | ALAMEDA | 94602 |  |  | 2006-05-04 |  |  |  | RODDED M/S IN STREET FOUND IT CLEAR. PROBLEM WAS CLOGGED LATERAL MADE S/S REPORT. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE | COMING FROM GROUND | CAUSE UNKNOWN | --Select None-- |  |  |  | LEADER | GIDDENS | 2006-05-08 | 510-615-5985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3318 | 219 | 1 | Oakland | 2006-05-08 13:42 | 10 | 0 |  | 2006-05-08 13:42 |  | -- | 2520 MONTANA ST | OAKLAND | ALAMEDA | 94602 |  |  | 2006-05-04 |  |  |  | RODDED M/S IN STREET FOUND IT CLEAR. PROBLEM WAS CLOGGED LATERAL MADE S/S REPORT. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE | COMING FROM GROUND | CAUSE UNKNOWN | --Select None-- |  |  |  | LEADER | GIDDENS | 2006-05-08 | 510-615-5985 | jheredia@oaklandnet.com,gth0mas@oaklandnet.comgamirzehni@oaklandnet.com bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3306 | 217 | 1 | Oakland | 2006-05-04 15:27 | 100 | 0 |  | 2006-05-04 15:27 |  | -- | 2633 E27TH ST | OAKLAND | ALAMEDA | 94621 |  |  | 2006-05-01 |  |  |  | HYDRO-FLUSHED M/S CLEARED GREASE STOPPAGE WASHED DOWN AND DISINFECTED AREA. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | LEADER | GIDDENS | 2006-05-04 | 510-615-5941 | jheredia@oaklandnet.com,gthomas@oaklandnet.comgamirzehni@oaklandnet.com bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3261 | 209 | 1 | Oakland | 2006-05-02 09:32 | 20 | 0 |  | 2006-05-02 09:32 |  | -- | E15th st and derby ave | oakland | alameda | 94601 |  |  | 2006-04-30 |  |  |  | RODDED AND FLUSHED M/S CLEARED GREASE STOPPAGE. VACUUMED WATER THAT WAS ABLE TO BE RECOVERED. WASHED DOWN AND DISINFECTED AREA. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | LEADER | RON GIDDENS | 2006-05-02 | 510-615-5941 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3243 | 206 | 1 | Oakland | 2006-04-27 10:35 | 5 | 0 |  | 2006-04-27 10:35 |  | -- | 2050 clemens rd | 0akland | alameda | 94602 |  |  | 2006-04-26 |  |  |  | blockage was caused by roots and broken pipe. maintenanct crew is working to clear the blockage today. if they cant clear it we will dig and repair it . | [5 empty] | GROUND WATER IMPACTED | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | leader | Ron Giddens | 2006-04-27 | 510-615-5941 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3230 | 203 | 1 | Oakland | 2006-04-24 14:42 | 80 | 0 |  | 2006-04-24 14:42 |  | -- | 4071 Lyman Road | oakland | alameda | 94602 |  |  | 2006-04-24 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | wayne Guidici | 2006-04-24 | 5106`55969 | gthomas@oaklandnet.com,gamirzehni@oaklandnet.com,jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3249 | 207 | 1 | Oakland | 2006-04-28 11:19 | 30 | 0 |  | 2006-04-28 11:19 |  | -- | 6636 laird st | oakland | alameda | 94605 |  |  | 2006-04-24 |  |  |  | rodded sewer, could not pass 18'. made work order to repair pipe. the work was completed on 4-26-2006 | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE | main sewer (sanitary) | CAUSE UNKNOWN | --Select None-- |  |  |  | leader | Ron Giddens | 2006-04-28 | 510-615-5941 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
3264 | 210 | 1 | Oakland | 2006-05-02 10:50 | 600 | 0 |  | 2006-05-02 10:50 |  | -- | 3353 BURDECK DR | OAKLAND | ALAMEDA | 94602 |  |  | 2006-04-24 |  |  |  | RODDED M/S CLEARED ROOT STOPPAGE. WASHED DOWN AND DISINFECTED STREET | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | LEADER | RON GIDDENS | 2006-05-02 | 510-615-5941 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3266 | 211 | 1 | Oakland | 2006-05-02 14:23 | 300 | 0 |  | 2006-05-02 14:23 |  | -- | 3109 BURDECK DR | OAKLAND | ALAMEDA | 94602 |  |  | 2006-04-24 |  |  |  | RODDED M/S CLEARED ROOT STOPPAGE WASHED DOEN AND DISINFECTED STREET AND GUTTER AREA. RODDED FROM M/H #56-000-13 TO M/H 56-000-225 MAP 135 | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | LEADER | RON GIDDENS | 2006-05-02 | 510-615-5985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3228 | 202 | 1 | Oakland | 2006-04-24 14:40 | 5 | 0 |  | 2006-04-24 14:40 |  | -- | 916 - 72nd Ave. | oakland | alameda | 94603 |  |  | 2006-04-22 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | pws | wayne guidici | 2006-04-24 | 5106155969 | gthomas@oaklandnet.com,gamirzehni@oaklandnet.com,jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3232 | 204 | 1 | Oakland | 2006-04-24 14:44 | 50 | 0 |  | 2006-04-24 14:44 |  | -- | 4331 Bridge View Drive | oakland | alameda | 94602 |  |  | 2006-04-22 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | wayne guidicic | 2006-04-24 | 5106155969 | gthomes@oaklandnet.com,gamirzehni@oaklandnet.com,jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3203 | 197 | 1 | Oakland | 2006-04-19 09:44 | 400 | 0 |  | 2006-04-19 09:44 |  | -- | 882 - 41ST STREET | OAKLAND | ALAMEDA | 94609 |  |  | 2006-04-19 | [9 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | OTHER | BASEMENT | BLOCKAGE | GREASE |  |  |  | pws | wayne guidici | 2006-04-19 | 5106155969 | gthomas@oaklandnet.com,gamrzehni@oaklandnet.com,jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3225 | 200 | 1 | Oakland | 2006-04-24 14:34 | 50 | 0 |  | 2006-04-24 14:34 |  | -- | 115 Embarcadero East | oakland | alameda | 94612 |  |  | 2006-04-19 |  |  |  | Cleaned up and put back into city main. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | pws | wayne guidici | 2006-04-24 | 5106155969 | gthomas@oaklandnet.com,gamirzehni@oaklandnet.com,jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3205 | 198 | 1 | Oakland | 2006-04-19 09:55 | 220 | 0 |  | 2006-04-19 09:55 |  | -- | 1515 Market Street | Oakland | alameda | 94609 |  |  | 2006-04-18 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | pws | wayne guidici | 2006-04-19 | 5106155969 | gamirzehni@oaklandnet.com,gthomas@oaklandnet.com,jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3199 | 195 | 1 | Oakland | 2006-04-17 14:05 | 50 | 0 |  | 2006-04-17 14:05 |  | -- | 3464 66th Avenue | Oakland | Alameda | 94605 - 21 |  |  | 2006-04-16 |  |  |  | Line segment blocked with grease between structure #84-104-11 to structure #84-104-A3, map #114. Washed and recovered spill. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-04-17 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
3201 | 196 | 1 | Oakland | 2006-04-17 14:21 | 80 | 0 |  | 2006-04-17 14:21 |  | -- | 90th Avenue and Olive Street | Oakland | Alameda | 94603 |  |  | 2006-04-16 |  |  |  | Line segment blocked with grease between structure #85-211-66 to structure #85-211-67, maps #79-80. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-04-17 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
3188 | 194 | 1 | Oakland | 2006-04-17 11:47 | 50 | 0 |  | 2006-04-17 11:47 |  | -- | 1302 Holman Road | Oakland | Alameda | 94610-2543 |  |  | 2006-04-15 |  |  |  | Line segment blocked with roots between structure #54-312-F8 to structure #54-312-F9, map #225. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-04-17 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gamirzehni@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
3178 | 191 | 1 | Oakland | 2006-04-14 10:26 | 200 | 0 |  | 2006-04-14 10:26 |  | -- | 140 Montwood Way | Oakland | Alameda | 94605-5422 |  |  | 2006-04-13 |  |  |  | Line segment blocked with roots and debris between structure #85-230-71 to structure #85-230-73, map #58. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-04-14 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
3181 | 192 | 1 | Oakland | 2006-04-14 11:13 | 50 | 0 |  | 2006-04-14 11:13 |  | -- | 6217 Thornhill Drive | Oakland | Alameda | 94611-2023 |  |  | 2006-04-13 |  |  |  | Line segment blocked with roots between structure #50-392-69 to structure #50-392-67, map #315. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-04-14 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
3174 | 189 | 1 | Oakland | 2006-04-13 14:52 | 250 | 0 |  | 2006-04-13 14:52 |  | -- | 2802 68th Avenue | Oakland | Alameda | 94605-2057 |  |  | 2006-04-12 |  |  |  | Line segment blocked with grease between structure #84-103-48 to structure #84-103-47 map #114. Cleared blockage and washed affected area in street. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-04-13 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
3176 | 190 | 1 | Oakland | 2006-04-13 15:13 | 150 | 0 |  | 2006-04-13 15:13 |  | -- | 5th Street and Union Street | Oakland | Alameda | 94607 |  |  | 2006-04-12 |  |  |  | Line segment blocked with grease between structure #64-061-09 to structure #64-061-10, map #201. Cleared blockage and washed affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-04-13 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
3143 | 187 | 1 | Oakland | 2006-04-10 13:47 | 50 | 0 |  | 2006-04-10 13:47 |  | -- | 1200 Lake Shore Avenue | Oakland | Alameda | 94606-1679 |  |  | 2006-04-07 |  |  |  | Line segment blocked with grease between structure #54-010-02 to structure #54-010-12, map #185. Flushed affected area and recovered spill. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-04-10 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
3145 | 188 | 1 | Oakland | 2006-04-10 14:20 | 50 | 0 |  | 2006-04-10 14:20 |  | -- | 6623 Outlook Avenue | Oakland | Alameda | 94605-2129 |  |  | 2006-04-07 |  |  |  | Line segment blocked between structure #84-104-81 to structure #84-104-83, map #126. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-04-10 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
3134 | 185 | 1 | Oakland | 2006-04-06 10:05 | 200 | 0 |  | 2006-04-06 10:05 |  | -- | 9940 mACaRTHUR bLVE | oakland | alameda | 94603 |  |  | 2006-04-06 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | wayne gudici | 2006-04-06 | 5106155969 | gthomas@oaklandnet.com,gamirzehin@oaklandnet.com,jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3124 | 181 | 1 | Oakland | 2006-04-04 10:26 | 10 | 0 |  | 2006-04-04 10:26 |  | -- | 75TH aVE AND iNTERNATIONAL | Oakland | alameda | 94621 |  |  | 2006-04-03 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | pws | wayne guidici | 2006-04-04 | 6155969 | gthoms@oaklandnet.com,gamirzehni@oaklandnet.com,jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3126 | 182 | 1 | Oakland | 2006-04-04 10:29 | 400 | 0 |  | 2006-04-04 10:29 |  | -- | 966 - 40th streer | oakland | alameda | 9412 |  |  | 2006-04-03 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | pws | wayne guidici | 2006-04-04 | 5106155985 | gthomas@oaklandnet.com,gamirzehni@oaklandnet.com,jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3117 | 179 | 1 | Oakland | 2006-04-03 14:43 | 300 | 0 |  | 2006-04-03 14:43 |  | -- | 411 - E18th Street | oakland | alameda | 94606 |  |  | 2006-04-01 | [9 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | OTHER | toilet bowls | BLOCKAGE | GREASE |  |  |  | pws | wayne gidici | 2006-04-03 | 5106155969 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3115 | 178 | 1 | Oakland | 2006-04-03 14:37 | 70 | 0 |  | 2006-04-03 14:37 |  | -- | 1048 - 103rd Ave | oakland | alameda | 94603 |  |  | 2006-03-31 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | pws | wayne guidici | 2006-04-03 | 5106155969 | gthomas@oaklandnet.com,gamirzehni@oaklandnet.com,jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3113 | 177 | 1 | Oakland | 2006-04-03 14:34 | 10 | 0 |  | 2006-04-03 14:34 |  | -- | 10 EAST CIRCLE | OAKLANd | alameda | 94611 |  |  | 2006-03-30 |  |  |  | Temp main pulled apart. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | OTHER | temp sewer main | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | pws | wayne gudiici | 2006-04-03 | 5106155969 | gthomas@oaklandnet.com,gamirzehni@oaklandnet.com,jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3105 | 176 | 1 | Oakland | 2006-03-30 09:45 | 20 | 0 |  | 2006-03-30 09:45 |  | -- | 2801 DARNBY | OAKLAND | ALAMEDA | 94705 |  |  | 2006-03-29 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | PWS | WAYNE GUIDICI | 2006-03-30 | 5106155969 | gthomas@oaklandnet.com,aamirzehni@oaklandnet.comjheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3084 | 172 | 1 | Oakland | 2006-03-28 09:27 | 65 | 0 |  | 2006-03-28 09:27 |  | -- | e-8TH AND Park Way | oakland | alameda | 94606 |  |  | 2006-03-27 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | pws | wayne guidici | 2006-03-28 | 5106155969 | gthomas@oaklandnet.com,gamirzehni@oaklandnet.com,jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3086 | 173 | 1 | Oakland | 2006-03-28 09:32 | 50 | 0 |  | 2006-03-28 09:32 |  | -- | 4374 Terrabella Way | oakland | alameda | 94602 |  |  | 2006-03-27 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | wayne guidici | 2006-03-28 | 5106155985 | gthomas@oaklandnet.com,gmirzehni@oaklandnet.com,jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3066 | 168 | 1 | Oakland | 2006-03-27 10:37 | 100 | 0 |  | 2006-03-27 10:37 |  | -- | 1108 - 60TH aVE | OAKLAND | alameda | 94621 |  |  | 2006-03-26 |  |  |  | We were able to suck up 99% of spill. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | pws | wayne guidici | 2006-03-27 | 5106522552 | gthomas@oaklandnet.com; jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com. ;gamirzehni@oaklandnet.com | MINOR
3068 | 169 | 1 | Oakland | 2006-03-27 10:39 | 100 | 0 |  | 2006-03-27 10:39 |  | -- | 1108 - 60TH aVE | OAKLAND | alameda | 94621 |  |  | 2006-03-26 |  |  |  | We were able to suck up 99% of spill. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | pws | wayne guidici | 2006-03-27 | 5106522552 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gamirzehni@oaklandnet.com | MINOR
3072 | 171 | 1 | Oakland | 2006-03-27 10:48 | 150 | 0 |  | 2006-03-27 10:48 |  | -- | 4624 Sequoah Road | oakland | alameda | 94619 |  |  | 2006-03-25 |  |  |  | We were able to suck up 100% of spill | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | wayne guidici | 2006-03-27 | 51206155969 | gamirzehni@oaklandnet.com,gthomas@oaklandnet.com,jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3070 | 170 | 1 | Oakland | 2006-03-27 10:42 | 30 | 0 |  | 2006-03-27 10:42 |  | -- | 6616 outlook ave | oakland | alameda | 94619 |  |  | 2006-03-24 |  |  |  | Temp main pulled apart, it was repaired. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | OTHER | termp. main | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | pws | wayen guidici | 2006-03-27 | 5106155969 | gthomas@oaklandnet.com,gamirzehni@oaklandnet.com,jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
3041 | 166 | 1 | Oakland | 2006-03-20 10:59 | 30 | 0 |  | 2006-03-20 10:59 |  | -- | 48TH aVE AND cARRINGTON | OAKLAND | alameda | 94602 |  |  | 2006-03-17 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | wayne guidici | 2006-03-20 | 5106155985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gthomas@oaklandnet.com, epersons@oaklandnet.com | MINOR
3034 | 165 | 1 | Oakland | 2006-03-17 11:35 | 10 | 0 |  | 2006-03-17 11:35 |  | -- | 788 Rosemount Road | Oakland | Alameda | 94610-2330 |  |  | 2006-03-16 |  |  |  | Line segment blocked with roots between structure #34-311-29 to structure #34-311-29, map #224. Washed affected area | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-03-17 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
3020 | 163 | 1 | Oakland | 2006-03-17 09:49 | 50 | 0 |  | 2006-03-17 09:49 |  | -- | 14TH STREET AND MARKET STREET | OAKLAND | ALAMEDA | 94612 |  |  | 2006-03-13 |  |  |  | MAIN SEWER BLOCKED WITH GREASE BETWEEN STRUCTURE #52-004-29 TO STRUCTURE #52-004-31, MAP #220. CLEANED AFFECTED AREA. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWER MAINT. LEADER | ARMANDO LOZANO | 2006-03-17 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
3030 | 164 | 1 | Oakland | 2006-03-17 11:12 | 50 | 0 |  | 2006-03-17 11:12 |  | -- | #30 Lincolshire Road | Oakland | Alameda | 94618-1726 |  |  | 2006-03-13 |  |  |  | Line segment on easement blocked with roots between structure #50-305-55 to structure #50-305-62, map #312.Cleaned and disenfected affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-03-17 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gamirzehni@oaklannet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
2991 | 159 | 1 | Oakland | 2006-03-11 09:26 | 100 | 0 |  | 2006-03-11 09:26 |  | -- | 1527 80th Avenue | Oakland | Alameda | 94621-2335 |  |  | 2006-03-10 |  |  |  | Line segment blocked with roots between structure #84-000-32 to structure #80-000-35, maps #90-91. Cleared blockage, recovered spill, and washed affected gutter and sidewalk areas. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-03-11 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
2977 | 156 | 1 | Oakland | 2006-03-10 10:31 | 40 | 0 |  | 2006-03-10 10:31 |  | -- | 117 Kerwin Street | Oakland | Alameda | 94603-2041 |  |  | 2006-03-09 |  |  |  | Line segment blocked with grease between structure #86-004-29 to structure #86-004-06, maps #32-24. Cleared blockage and washed down affecrted area in yard and driveway. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-03-10 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
2989 | 158 | 1 | Oakland | 2006-03-11 09:07 | 5 | 0 |  | 2006-03-11 09:07 |  | -- | 7250 Homewood Drive | Oakland | Alameda | 94611-1413 |  |  | 2006-03-08 |  |  |  | Line segment on easement blocked with roots between structure #56-207-68 to structure #56-207-67, map #316. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-03-11 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
2950 | 154 | 1 | Oakland | 2006-03-08 10:00 | 750 | 0 |  | 2006-03-08 10:00 |  | -- | 3455 cRAND WAy | oakland | alameda | 94619 |  |  | 2006-03-07 |  |  |  | Rodded main open of Heavy Roots | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | wayne guidici | 2006-03-08 | 5106155985 | gamirzheni@oaklandnet.com, gthomes@oakland.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
2953 | 155 | 1 | Oakland | 2006-03-08 10:11 | 89 | 0 |  | 2006-03-08 10:11 |  | -- | 3275 burdeck dr | oakland | alameda | 94619 |  |  | 2006-03-07 |  |  |  | Rodded main of haevy roots and washed down gutter area | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | wayne gidici | 2006-03-08 | 5106155985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2948 | 153 | 1 | Oakland | 2006-03-07 16:01 | 20 | 0 |  | 2006-03-07 16:01 |  | -- | Keith Avenue and Broadway | Oakland | Alameda | 94628 |  |  | 2006-03-06 |  |  |  | Line segment blocked with debris between structure #50-321-15 to structure #50-321-17, map #321. Flushed and cleared blockage, washed down affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-03-07 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
2944 | 152 | 1 | Oakland | 2006-03-07 13:48 | 50 | 0 |  | 2006-03-07 13:48 |  | -- | Perkins Street and Bellevue | Oakland | Alameda | 94610 |  |  | 2006-03-04 |  |  |  | Line segment plugged with grease between structure #54-422-13 to structure #54-422-03, map #222, rodded main sewer and cleared blockage, washed down gutter and street area with 200 galons of water. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-03-07 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
2911 | 149 | 1 | Oakland | 2006-03-02 10:33 | 25 | 0 |  | 2006-03-02 10:33 |  | -- | 4168 Greenwood Avenue | Oakland | Alameda | 94602-1147 |  |  | 2006-03-02 |  |  |  | Main sewer line segment blocked with roots between structure #54-312-85 to structure #54-312-84, map #225. Cleared blockage and washed affected area with 500 galons of clean water. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-03-02 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
2931 | 150 | 2 | Oakland | 2006-03-03 14:26 | 3000 | 0 | 06-1310 | 2006-03-02 | Armando Lozano | OAKLAND | 1004 Elbert Street | Oakland | Alameda | 94602-132 |  |  | 2006-03-01 | 10:30:00 P | [5 empty] | SUNNY WEATHER | High |  | YARD/LAND | No |  | No | No | sATURATED SOIL, SEND CREW TO DO MORE CLEAN UP ON 3/3/06 |  | No | Yes | Yes | No | No | No | No | No | No | 2006-06-30 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- |  | Main sewer line on easement blocked with roots between structure #54-315-14 to structure #54-315-15, maps #226 and 225, cleaned and disenfected affected area on 3/2/06 and 3/3/06, turned main sewer to Engeenering and Design for replacement before 6/30/2006. | Sewer Maint. Leader | Armando Lozano | 2006-03-02 | 510-615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MAJOR | RONALD GIDDENS | OAKLAND SEWER DEPT. | (510)615-5566 |  | 7101 EDGEWATER DR | OAKLAND | ALAMEDA | 94621-3001 | SEWER DEPT. | OAKLAND | (510)615-5566 |  | 7101 EDGEWATER DRIVE | OAKLAND | ALAMEDA | 94621-3001
2882 | 146 | 1 | Oakland | 2006-02-27 11:31 | 99 | 0 |  | 2006-02-27 11:31 |  | -- | 10031 BERNHARDT DRIVE | OAKLAND | ALAMEDA | 94601 |  |  | 2006-02-25 |  |  |  | Main sewer line segment blocked with grease between structure #86-004-08 to structure #86-004-07, map #24. Cleared main sewer, washed solids from lawn area back into main sewer, washed down affected area in gutter and diluted spill with 500 galons of fresh water. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-02-27 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com,epersons@oaklandnet.com | MINOR
2884 | 147 | 1 | Oakland | 2006-02-27 12:20 | 75 | 0 |  | 2006-02-27 12:20 |  | -- | # 12 TIFFANY LANE | OAKLAND | ALAMEDA | 94611-1564 |  |  | 2006-02-25 |  |  |  | Main srwer line blocked with grease and paper blockage between structure #56-200-39 to structure #56-204-01, map #292.Cleared blockage, cleaned solids back to main sewer and washed and diluted spill with 500 galons of clean water. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-02-27 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
2873 | 145 | 1 | Oakland | 2006-02-24 09:34 | 75 | 0 |  | 2006-02-24 09:34 |  | -- | 6510 Outlook Avenue | Oakland | Alameda | 94605-2194 |  |  | 2006-02-23 |  |  |  | Main sewer line segment blocked with roots between structure #84-104-58 to structure #84-104-59, map #126. Cleared blockage, cleaned and disenfected affected area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-02-24 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
2856 | 143 | 1 | Oakland | 2006-02-22 08:48 | 2 | 0 |  | 2006-02-22 08:48 |  | -- | 1227 31st Avenue | Oakland | Alameda | 94601-2915 |  |  | 2006-02-21 |  |  |  | Line segment blocked with grease between structure #56-001-10 to structure #56-001-07, map #121. Cleared blockage and washed the affected area | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-02-22 | (510)615-5566 | gthomas@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, gamirzenhi@oaklandnet.com | MINOR
2838 | 141 | 1 | Oakland | 2006-02-21 10:03 | 85 | 0 |  | 2006-02-21 10:03 |  | -- | 7576 Sterling Street | Oakland | Alameda | 94605-3019 |  |  | 2006-02-19 |  |  |  | Line segment blocked with debris between structure #83-404-D4 to structure #83-404-E7, rodded main sewer easement and cleared blockage, cleaned and disenfected affected area in rear of house. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-02-21 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com, epersons@oaklandnet.com | MINOR
2835 | 140 | 1 | Oakland | 2006-02-17 10:09 | 20 | 0 |  | 2006-02-17 10:09 |  | -- | 5201 Park Blvd. | Oakland | Alameda | 94611-3328 |  |  | 2006-02-16 |  |  |  | Main sewer line blocked with roots between segment #56-006-49 to segment #56-006-48, map #259. Cleared root blockage and washed and flushed affected areas. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-02-17 | (510)615-5566 | gthomas@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, epersons@oaklandnet.com, gamirzehni@oaklandnet.com, atlaw@oaklandnet.com | MINOR
2864 | 144 | 1 | Oakland | 2006-02-22 09:25 | 65 | 0 |  | 2006-02-22 09:25 |  | -- | 2025 Manzanita Drive | Oakland | Alameda | 94611-1148 |  |  | 2006-02-16 |  |  |  | Line segment on main sewer easement blocked with roots between structure #56-206-56 to structure #56-206-99, map #316. Cleared blockage and cleaned and disenfected affected area in back yard. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-02-22 | (510)615-5566 | gthomas@oaklandnet.com, atlaw@oaklandnet.com, gamirzehni@oaklandnet.com, jheredia@oaklandnet.com, bsaunders@oaklandnet.com, epersons@oaklandnet.com | MINOR
2789 | 139 | 1 | Oakland | 2006-02-11 07:49 | 90 | 0 |  | 2006-02-11 07:49 |  | -- | 4071 LYMAN ROAD | oakland | alameda | 94602 |  |  | 2006-02-10 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | wayne guidici | 2006-02-11 | 5106155985 | gthomas@oaklandnet.com,jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2758 | 135 | 1 | Oakland | 2006-02-06 11:06 | 20 | 0 |  | 2006-02-06 11:06 |  | -- | 900 77TH Ave | oakland | alameda | 94603 |  |  | 2006-02-03 |  |  |  | Rodded main clear, washed down street | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | pws | wayne gudici | 2006-02-06 | 5106155985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2760 | 136 | 1 | Oakland | 2006-02-06 11:09 | 20 | 0 |  | 2006-02-06 11:09 |  | -- | Holy Names College at Mountain Blvd. | oakland | alameda | 94602 |  |  | 2006-02-03 |  |  |  | rodded main clear | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | wayne guidici | 2006-02-06 | 5106155985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2762 | 137 | 1 | Oakland | 2006-02-06 11:12 | 40 | 0 |  | 2006-02-06 11:12 |  | -- | 2802 Bancroft | oakland | alameda | 94621 |  |  | 2006-02-02 |  |  |  | unplugged main and washed down street | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | pws | wayne guidcic | 2006-02-06 | 51061559865 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2764 | 138 | 1 | Oakland | 2006-02-06 11:14 | 30 | 0 |  | 2006-02-06 11:14 |  | -- | 2541 Church Street | oakland | alameda | 94621 |  |  | 2006-02-02 |  |  |  | unplugged main and washed down street | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | pws | wayne gudici | 2006-02-06 | 5106155985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2672 | 119 | 1 | Oakland | 2006-01-24 09:09 | 100 | 0 |  | 2006-01-24 09:09 |  | -- | Joaquian Miller Ct and El Caminito | Oakland | Alameda | 94611 |  |  | 2006-01-23 |  |  |  | Heavy Rock in main. We will TV to see if there is a break. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | PWS | Wayne Guidici | 2006-01-24 | 510-615-5985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2676 | 121 | 1 | Oakland | 2006-01-24 09:17 | 100 | 0 |  | 2006-01-24 09:17 |  | -- | Behind 140 Montwood Way | oakland | alameda | 94605 |  |  | 2006-01-12 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | wayne guidici | 2006-01-24 | 510-615-5985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2674 | 120 | 1 | Oakland | 2006-01-24 09:14 | 150 | 0 |  | 2006-01-24 09:14 |  | -- | 2610 Mountain Blvd. | oakland | alameda | 94611 |  |  | 2006-01-11 |  |  |  | Flushed out rock in main. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | PwS | wayne guidici | 2006-01-24 | 510-615-5985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2743 | 130 | 1 | Oakland | 2006-02-01 22:39 | 200 | 0 |  | 2006-02-01 22:39 |  | -- | 82nd Avenue and Iris Avenue | Oakland | Alameda | 94621-2223 |  |  | 2005-12-31 |  |  |  | Main sewer segment blocked with unknown debris, this segment is between structure #84-005-32 and structure #84-004-03 in map #92, very heavy rain water washed affected area into storm inlet. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-02-02 | (510)615-5566 | gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, | MINOR
2753 | 134 | 1 | Oakland | 2006-02-02 09:08 | 500 | 0 |  | 2006-02-02 09:08 |  | -- | 6120 OAKDALE AVE | OAKLAND | ALAMEDA | 94605-1881 |  |  | 2005-12-29 |  |  |  | Main sewer line segment blocked with roots between structure #83-400-25 to structure #83-400-23, map #138.The main was cleared and the affected area was cleaned up. | [5 empty] | GROUND WATER IMPACTED | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-02-02 | (510)615-5566 | gthomas@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com, bsaunders@oaklandnet.com, gamirzehni@oaklandnet.com, jheredia@oaklandnet.com | MINOR
2342 | 117 | 1 | Oakland | 2005-12-28 10:42 | 120 | 0 |  | 2005-12-28 10:42 |  | -- | 58 CALVERT CT | OAKLAND | ALAMEDA | 94611 |  |  | 2005-12-22 |  |  |  | RODDED AND FLUSHED MAIN SEWER CLEARED ROOT STOPPAGE. THE SPILL SOAKED INTO THE GROUND.RETURNED SOLIDS TO SEWER DISINFECTED AREA OF SPILL. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | OTHER | LAMP HOLE | BLOCKAGE | ROOTS |  |  |  | SEWER LEADER | RON GIDDENS | 2005-12-28 | 510-615-5941 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2741 | 129 | 1 | Oakland | 2006-02-01 21:29 | 180 | 0 |  | 2006-02-01 21:29 |  | -- | 1950 Gouldin Road | Oakland | Alameda | 94611-2242 |  |  | 2005-12-21 |  |  |  | Main sewer segment between structure #50-393-B2 to structure #50-393-B7 in map #303 was blocked with roots. Hand rodded main sewer easement and cleared blockage the next day on 12/22/05 due to darkness. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-02-02 | (510)615-5566 | gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, | MINOR
2290 | 115 | 1 | Oakland | 2005-12-20 16:47 | 8000 | 0 |  | 2005-12-20 | RON GIDDENS |  | 34TH ST AND WOOD ST | 0AKLAND | ALAMEDA | 94621 |  |  | 2005-12-19 | 5:00:00 AM | 2005-12-19 | 11:00:00 A | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Acting Operations Ma | Jaime Heredia | 2005-12-20 | 510-615-5561 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | 24HR |  |  | 510-615-5985 | [6 empty] | OAKLAND
2338 | 116 | 1 | Oakland | 2005-12-27 14:45 | 8000 | 4000 | 05-7467 | 2005-12-20 | Ron Giddens | OAKLAND | 34TH STREET AND WOOD STREET | oAKland | Alameda | 94607 |  |  | 2005-12-19 | 5:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | Not detectable visually. |  | Yes | Yes | Yes | No | No | Yes | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | OAKLAND | MANHOLE | Construction debris (Concrete) looks to have come from the old Cypress Freeway rehab project. | BLOCKAGE | CONSTRUCTION DEBRIS | --Select None-- |  | Manhole overflowed out of a 36" main. | SML | Ron Giddens | 2005-12-27 | 510-615-5941 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MAJOR | Jaime Heredia | Oakland | 510-615-5822 |  | 7107 Edgewater Dr | Oakland | Alameda | 94621 |  | Contractor
2354 | 118 | 1 | Oakland | 2005-12-28 14:45 | 300 | 0 |  | 2005-12-28 14:45 |  | -- | 3162 BURDECK DR | OAKLAND | ALAMEDA | 94602 |  |  | 2005-12-18 |  |  |  | RODDDED SEWER CLEARED ROOT STOPPAGE | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | OTHER | LAMP HOLE | BLOCKAGE | ROOTS |  |  |  | SEWER LEADER | RON GIDDENS | 2005-12-28 | 510-615-5941 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2751 | 133 | 1 | Oakland | 2006-02-02 08:05 | 300 | 0 |  | 2006-02-02 08:05 |  | -- | 11271 Kerrigan Drive | Oakland | Alameda | 94605-5415 |  |  | 2005-12-12 |  |  |  | Main sewer segment blocked with roots and debris between structure #85-230-77 to structure # 85-232-29, map #58. The main sewer was cleared and the affected areas in creek were cleaned up. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Sewer Maint, Leader | Armando Lozano | 2006-02-02 | (510)615-5566 | gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, | MINOR
2747 | 132 | 1 | Oakland | 2006-02-01 23:35 | 100 | 0 |  | 2006-02-01 23:35 |  | -- | 2025 Arrowhead Drive | Oakland | Alameda | 94611-1448 |  |  | 2005-12-06 |  |  |  | Hand ropdded main sewer easement segment between structure #56-206-38 to structure #56-206-37, map #304 and cleared roots blockage. Hydro flusher crew washed down storm drain. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-02-02 | (510)615-5566 | gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, | MINOR
2202 | 112 | 1 | Oakland | 2005-12-02 10:04 | 400 | 0 |  | 2005-12-02 10:04 |  | -- | Thermal Ave. and Cherokee Ave. | Oakland | Alameda | 94623 |  |  | 2005-12-01 |  |  |  | Sewer main broke down causing a back up. HydroVac sucked up overflowing sewage. Then got main open. Emergency dig to be performed the next day. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | PWS | wayne guidici | 2005-12-02 | 5106155985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2204 | 113 | 1 | Oakland | 2005-12-02 10:07 | 150 | 0 |  | 2005-12-02 10:07 |  | -- | 9524 Thermal | Oakland | alameda | 94623 |  |  | 2005-12-01 |  |  |  | Main broken. Emergency dig to be performed in A.M. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | pes | wayne guidici | 2005-12-02 | 510-615-5985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2206 | 114 | 1 | Oakland | 2005-12-02 10:15 | 900 | 0 |  | 2005-12-02 10:15 |  | -- | 61st Ave. and Bancroft | oakland | alameda | 94605 |  |  | 2005-12-01 |  |  |  | Washed down Gutter Area | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | pws | wayne guidici | 2005-12-02 | 6155985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2182 | 111 | 1 | Oakland | 2005-11-28 14:17 | 1100 | 500 | E7bmYKBX | 2005-11-28 | Fire Alarm | Oakland | 52ND AVE. AND WENTWORTH AVE. | OAKLAND | ALAMEDA | 94602 |  |  | 2005-11-25 | 5:03:00 AM | [5 empty] | SUNNY WEATHER | High |  | STORM DRAIN | No |  | No | No | Not sure what this means? |  | Yes | Yes | Yes | No | No | Yes | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Oakland | CLEAN OUT |  | BLOCKAGE | GREASE | --Select None-- | Grease |  | pws | W. Gudicid | 2005-11-28 | 615-5985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MAJOR | W.gUIDICI | Oakland | 615-5985 |  | 7101 EDGEWATER | OAKLNAD | ALAMEDA | 94621 |  | City of Oakland
2148 | 110 | 1 | Oakland | 2005-11-21 11:00 | 300 | 0 |  | 2005-11-21 11:00 |  | -- | 3500 Mountain Blvd. | Oakland | Alameda | 94619-1627 |  |  | 2005-11-21 |  |  |  | Checked and found 8" main sewer line blocked with roots and grease blockage, rodded main sewer from wet manhole #80-010-49 to dry manhole #80-010-51; Assisted by hydro-flusher crew and vaccumed spill, flushed storm sewer lines and washed affected areas. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2005-11-21 | (510)615-5566 | wguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
2105 | 109 | 1 | Oakland | 2005-11-14 09:59 | 150 | 0 |  | 2005-11-14 09:59 |  | -- | 1388 - e-8th street | oakland | alameda | 94612 |  |  | 2005-11-12 |  |  |  | Unplugged main with Power Rodder about 350 feet up stream. 4 inch augger got stuck in main. Will have this line T.V.d. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | wayne guidici | 2005-11-14 | 5106155985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2103 | 108 | 1 | Oakland | 2005-11-14 09:56 | 100 | 0 |  | 2005-11-14 09:56 |  | -- | 8200 baldwin st. | oakland | alameda | 94621 |  |  | 2005-11-11 |  |  |  | Rodded and Flushed main clear of heavy Grease. Washed down street area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | pws | wayne gudiic | 2005-11-14 | 5106155985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2087 | 107 | 1 | Oakland | 2005-11-07 11:24 | 125 | 0 |  | 2005-11-07 11:24 |  | -- | 21st Street and Harrison | Oakland | Alameda | 94612 |  |  | 2005-11-05 |  |  |  | Rodded 24" main clear of Heavy Debris, grease and concrete in upstream Man Hole. Washed down street area with 1,000 gals of water. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | pws | Wayne Guidici | 2005-11-07 | 5106155985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2074 | 106 | 1 | Oakland | 2005-11-02 08:23 | 100 | 0 |  | 2005-11-02 08:23 |  | -- | Frank O'Ganwa Baseball Field Upper Broadway | Oalkand | Alameda | 94621 |  |  | 2005-11-01 |  |  |  | Rodded easement main sewer line with 2", 4" and 6" auger. Also used 8" Saw to clear blockage of Heavy Roots. Had Hydro Flusher wash down street and gutter area with 3,500 gallons of water. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWS | wayne guidici | 2005-11-02 | 510-615-5986 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2737 | 127 | 1 | Oakland | 2006-02-01 18:22 | 100 | 0 |  | 2006-02-01 18:22 |  | -- | Frank Ogawa ballfield at Broadway | Oakland | Alameda | 94621 |  |  | 2005-11-01 |  |  |  | Sewer main segment blocked with roots between structure #50-320-59 to structure #50-320-60, map #334, rodded and cleared blockage, also assisted by hydro flusher and washed down affected area with 500 galons of water. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-02-01 | (510)615-5566 | gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, | MINOR
2739 | 128 | 1 | Oakland | 2006-02-01 18:55 | 100 | 0 |  | 2006-02-01 18:55 |  | -- | #40 Larry Lane | Oakland | Alameda | 94611-2708 |  |  | 2005-10-11 |  |  |  | Had hydro flusher flush main sewer to clear stoppage of roots and debris. The main sewer is flowing at this time. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-02-01 | (510)615-5566 | gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, | MINOR
1926 | 105 | 1 | Oakland | 2005-10-06 15:10 | 55 | 0 |  | 2005-10-06 15:10 |  | -- | 6758 Sims | oakland | alameda | 04919 |  |  | 2005-10-05 |  |  |  | Power rodded man clear of roots. Also cleaned downstream M/H of debris | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | PWS | wayne gudici | 2005-10-06 | 5106155566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2735 | 126 | 1 | Oakland | 2006-02-01 15:25 | 100 | 0 |  | 2006-02-01 15:25 |  | -- | 103rd. Avenue and Graffian Street | Oakland | Alameda | 94621 |  |  | 2005-09-30 |  |  |  | Unplugged main sewer, washed down affected area in street and vaccumed up water and waste. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-02-01 | (510)615-5566 | gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, | MINOR
1881 | 98 | 1 | Oakland | 2005-09-29 10:18 | 100 | 0 |  | 2005-09-29 10:18 |  | -- | 4300 MOUNTAIN BLVD | OAKLAND | ALAMEDA | 94619 |  |  | 2005-09-29 |  |  |  | M/H OVERFLOWING. RODDED M/S CLEARED ROOT STOPPAGE ISSISTED BY 188. HAD HYDRO FLUSH STORM INLET TO DILUTE SPILL IN CREEK ASST184. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SEWER MAINT. WORKER | JAMES M.GRIMES | 2005-09-29 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1885 | 99 | 1 | Oakland | 2005-09-29 10:19 | 100 | 0 |  | 2005-09-29 10:19 |  | -- | 4300 MOUNTAIN BLVD | OAKLAND | ALAMEDA | 94619 |  |  | 2005-09-29 |  |  |  | M/H OVERFLOWING. RODDED M/S CLEARED ROOT STOPPAGE ISSISTED BY 188. HAD HYDRO FLUSH STORM INLET TO DILUTE SPILL IN CREEK ASST184. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SEWER MAINT. WORKER | JAMES M.GRIMES | 2005-09-29 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1887 | 100 | 1 | Oakland | 2005-09-29 10:19 | 100 | 0 |  | 2005-09-29 10:19 |  | -- | 4300 MOUNTAIN BLVD | OAKLAND | ALAMEDA | 94619 |  |  | 2005-09-29 |  |  |  | M/H OVERFLOWING. RODDED M/S CLEARED ROOT STOPPAGE ISSISTED BY 188. HAD HYDRO FLUSH STORM INLET TO DILUTE SPILL IN CREEK ASST184. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SEWER MAINT. WORKER | JAMES M.GRIMES | 2005-09-29 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1889 | 101 | 1 | Oakland | 2005-09-29 10:20 | 100 | 0 |  | 2005-09-29 10:20 |  | -- | 4300 MOUNTAIN BLVD | OAKLAND | ALAMEDA | 94619 |  |  | 2005-09-29 |  |  |  | M/H OVERFLOWING. RODDED M/S CLEARED ROOT STOPPAGE ISSISTED BY 188. HAD HYDRO FLUSH STORM INLET TO DILUTE SPILL IN CREEK ASST184. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SEWER MAINT. WORKER | JAMES M.GRIMES | 2005-09-29 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1891 | 102 | 1 | Oakland | 2005-09-29 10:21 | 100 | 0 |  | 2005-09-29 10:21 |  | -- | 4300 MOUNTAIN BLVD | OAKLAND | ALAMEDA | 94619 |  |  | 2005-09-29 |  |  |  | M/H OVERFLOWING. RODDED M/S CLEARED ROOT STOPPAGE ISSISTED BY 188. HAD HYDRO FLUSH STORM INLET TO DILUTE SPILL IN CREEK ASST184. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SEWER MAINT. WORKER | JAMES M.GRIMES | 2005-09-29 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1893 | 103 | 1 | Oakland | 2005-09-29 10:31 | 100 | 0 |  | 2005-09-29 10:31 |  | -- | 4300 MOUNTAIN BLVD | OAKLAND | ALAMEDA | 94619 |  |  | 2005-09-29 |  |  |  | M/H OVERFLOWING. RODDED M/S CLEARED ROOT STOPPAGE ISSISTED BY 188. HAD HYDRO FLUSH STORM INLET TO DILUTE SPILL IN CREEK ASST184. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SEWER MAINT. WORKER | JAMES M.GRIMES | 2005-09-29 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1895 | 104 | 1 | Oakland | 2005-09-29 10:42 | 20 | 0 |  | 2005-09-29 10:42 |  | -- | 1937 TIFFIN RD | OAKLAND | ALAMEDA | 94602 |  |  | 2005-09-29 |  |  |  | M/H OVERFLOWING. RODDED M/S CLEAR ROOT STOPPAGE TURNED OVER TO FLUSHER 193 TO WASH DOWN AND DISINFECT. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SEWER MAINT. WORKER | JAMES M. GRIMES | 2005-09-29 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1873 | 97 | 1 | Oakland | 2005-09-27 09:14 | 55 | 0 |  | 2005-09-27 09:14 |  | -- | 7283 CLAREMONT AVE | OAKLAND | ALAMEDA | 94705 |  |  | 2005-09-27 |  |  |  | MAIN SEWER PLUGGED&OVERFLOWING ON EASEMENT. RODDED MAIN SEWER ON EASEMENT CLEARED MAIN SEWER OF ROOTS. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SEWER MAINT. WORKER | JAMES M. GRIMES | 2005-09-27 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1868 | 96 | 1 | Oakland | 2005-09-26 13:04 | 15 | 0 |  | 2005-09-26 13:04 |  | -- | 82ND AVE & INTERNATIONAL BLVD | OAKLAND | ALAMEDA | 94621 |  |  | 2005-09-26 |  |  |  | RODDED M/S AND CLEARED STOPPAGE OF GREASE THE M/S IS FLOWING AT THIS TIME. ALSO FRUSHED M/S AND WASHED DOWN AREA AROUND M/H , MAP #78. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWER MAINT. WORKER | JAMES M. GRIMES | 2005-09-26 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1863 | 95 | 1 | Oakland | 2005-09-23 10:38 | 50 | 0 |  | 2005-09-23 10:38 |  | -- | 6977 PINEHAVEN RD | OAKLAND | ALAMEDA | 94611 |  |  | 2005-09-23 |  |  |  | LAMPHOLE OVERFLOWING IN STREET. HAND RODDED MAIN SEWER IN STREET CLEARED MAIN SEWER OF HEAVY ROOTS, ALSO WASHED DOWN AREA. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SEWER MAINT. WORKER | JAMES M. GRIMES | 2005-09-23 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1821 | 77 | 1 | Oakland | 2005-09-22 11:19 | 75 | 0 |  | 2005-09-22 11:19 |  | -- | 1450 FERNWOOD DR | OAKLAND | ALAMEDA | 94601 |  |  | 2005-09-22 |  |  |  | MAIN SEWER PLUGGED & OVERFLOWING. RODDED M/S OF ROOTS DEBRIS, ALSO HAD POWER RODDER TO ROD M/S WITH FULL TOOL. HAD HYDRO FLUSHER TO WASH DOWN STREET. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SEWER MAINT. WORKER | JAMES M. GRIMES | 2005-09-22 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1823 | 78 | 1 | Oakland | 2005-09-22 11:42 | 300 | 0 |  | 2005-09-22 11:42 |  | -- | 1656 33RD AVE | OAKLAND | ALAMEDA | 94601 |  |  | 2005-09-22 |  |  |  | SEWER BACKUP. RODDED AND CLEARED MAIN SEWER, VACUUMED SEWER WATER . | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWER MAINT. WORKER | JAMES M. GRIMES | 2005-09-22 | 510-615 5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1829 | 79 | 1 | Oakland | 2005-09-22 11:52 | 300 | 0 |  | 2005-09-22 11:52 |  | -- | 1656 33RD AVE | OAKLAND | ALAMEDA | 94601 |  |  | 2005-09-22 |  |  |  | SEWER BACKUP. RODDED AND CLEARED MAIN SEWER, VACUUMED SEWER WATER . | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWER MAINT. WORKER | JAMES M. GRIMES | 2005-09-22 | 510-615 5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1831 | 80 | 1 | Oakland | 2005-09-22 13:12 | 50 | 0 |  | 2005-09-22 13:12 |  | -- | MONAN ST &ZEIGLER AVE | OAKLAND | ALAMEDA | 94605 |  |  | 2005-09-22 |  |  |  | RODED M/S TO CLEAR STOPPAGE OF ROOTS. M/S IS CLEAR AT THIS TIME. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SEWER MAINT WORKER | JAMES M. GRIMES | 2005-09-22 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1861 | 94 | 1 | Oakland | 2005-09-23 10:21 | 75 | 0 |  | 2005-09-23 10:21 |  | -- | 6737 ELEVERTON DR. | OAKLAND | ALAMEDA | 94611 |  |  | 2005-09-20 |  |  |  | SEWER BACKUP. CHECKED & FOUND M/S PLUGGED OVERFLOWING FROM MANHOLE, HAND RODDED M/S IN STREET CLEARED MIN SEWER OF HEAVY ROOTS ALSO HAD POWER RODDER, ROD M/S | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SEWER MAINT. WORKER | JAMES M. GRIMES | 2005-09-07 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1786 | 67 | 1 | Oakland | 2005-09-15 13:43 | 75 | 0 |  | 2005-09-15 13:43 |  | -- | 6737 eLVERTON dR. | Oakland | alameda | 94619 |  |  | 2005-09-15 |  |  |  | Power Rodded main clear of Roots | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWS | Wayne Guidici | 2005-09-15 | 5106155985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1788 | 68 | 1 | Oakland | 2005-09-15 13:57 | 900 | 0 |  | 2005-09-15 13:57 |  | -- | 473 - 63rd Street | Oakland | alameda | 94609 |  |  | 2005-09-15 |  |  |  | Flushed and lleared main sewer in street, heavy roots, told owner we will return on 9-4-05 to rod main with Power Rodder. Home owner had emergency service restoration Inc, on site. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWA | wayne guidici | 2005-09-15 | 6155985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1784 | 66 | 1 | Oakland | 2005-09-15 10:46 | 3 | 0 |  | 2005-09-15 10:46 |  | -- | 3841 Ardley Ave | Oakland | Alameda | 94602 |  |  | 2005-09-13 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWS | wAYNE gUIDICI | 2005-09-15 | 5106155985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1794 | 71 | 1 | Oakland | 2005-09-15 14:19 | 75 | 0 |  | 2005-09-15 14:19 |  | -- | 6737 ELVERTON DR. | OAKLAND | ALAMEDA | 94611 |  |  | 2005-09-06 |  |  |  | Hand rodded main open in street and removed heavy roots. Also had Power rodder rod main with full tool. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | wayne guidici | 2005-09-15 | 6155985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1859 | 93 | 1 | Oakland | 2005-09-23 10:01 | 900 | 0 |  | 2005-09-23 10:01 |  | -- | 473 63RD STREET | OAKLAND | ALAMEDA | 94703 |  |  | 2005-09-06 |  |  |  | SEWAGE IN BASEMENT. FLUSHED AND CLEARED MAIN SEWER IN STREET, HEAVY ROOTS, ALSO RODDED M/S. HOME OWNER HAD EMERGENCY SERVICE RESTORATION INC. CLEAN SITE | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SEWER MAINT. WORKER | JAMES M. GRIMES | 2005-09-06 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1792 | 70 | 1 | Oakland | 2005-09-15 14:12 | 900 | 0 |  | 2005-09-15 14:12 |  | -- | 473 63rd Street | oakland | alameda | 94703 |  |  | 2005-09-03 |  |  |  | Sewage in basement and street. flushed and cleaned main sewer in street. Will rod with full tool on the 4th. Home owner had Emergency Service Restoration inc. on site. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWS | wayne Guidici | 2005-09-15 | 6155985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1745 | 65 | 1 | Oakland | 2005-08-31 10:35 | 10 | 0 |  | 2005-08-31 10:35 |  | -- | SAUSAL CREEK BY LEIMERY BRIDGE | OAKLAND | ALAMEDA | 94602 |  |  | 2005-08-31 |  |  |  | SEWAGE LEAK. FOUND LEAK NEXT TO M/H #56-020-07 COMING THROUGH THE GROUND, TV JR NICKS MADE THE CONST. WORK ORDER TO HAND DIG AND REPAIR M/S EASEMENT. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | SEWER MAINT WORKER | JAMES M. GRIMES | 2005-08-31 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1736 | 63 | 1 | Oakland | 2005-08-29 14:30 | 40 | 0 |  | 2005-08-29 14:30 |  | -- | 43 SLATER LANE | OAKLAND | ALAMEDA | 94705 |  |  | 2005-08-29 |  |  |  | SEWAGE COMING UP IN STREET. RODDED MAIN SEWER IN STREET BY HAND OPEN PLUGGED MAIN SEWER REMOVED VERY VERY HEAVY ROOTS FROM MAIN SEWER.ALSO HAD POWER RODDER TO ROD M/S WITH FULL TOOL THEY ALSO REMOVED HEAVY ROOTS. HAD HYDRO FLUSHER WASH DOWN STREET, WE SWEPT AND CLEANED AREA. MADE OVERFLOW REPORT. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SEWER MAINT. WORKER | JAMES M. GRIMES | 2005-08-29 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1790 | 69 | 1 | Oakland | 2005-09-15 14:06 | 75 | 0 |  | 2005-09-15 14:06 |  | -- | 50 Larry Lane | Oakland | alameda | 94611 |  |  | 2005-08-29 |  |  |  | Had 195 rod main sewer and unplug. 193 flusher did a wash down of area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Pws | Wayne Guidici | 2005-09-15 | 6155985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1857 | 92 | 1 | Oakland | 2005-09-23 09:42 | 75 | 0 |  | 2005-09-23 09:42 |  | -- | 50 LARRY LANE | OAKLAND | ALAMEDA | 94611 |  |  | 2005-08-29 |  |  |  | M/S OVERFLOWING FROM M/H. HAD POWER RODDER, ROD M/S & UNPLUG. ALSO HAD HYDRO FLUSHER WASH DOWN AREA. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SEWER MAINT. WORKER | JAMES M. GRIMES | 2005-08-29 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1849 | 89 | 1 | Oakland | 2005-09-22 15:22 | 50 | 0 |  | 2005-09-22 15:22 |  | -- | 8001 WINTHROPE ST. | OAKLAND | ALAMEDA | 94605 |  |  | 2005-08-26 |  |  |  | M/H OVERFLOWING IN FRONT HOUSE. HAD POWER RODDER TO ROD AND UNPLUG STOPPAGE OF GREASE. M/S IS CLEAR. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWER MAINT WORKER | JAMES M. GRIMES | 2005-08-26 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1853 | 90 | 1 | Oakland | 2005-09-23 09:23 | 250 | 0 |  | 2005-09-23 09:23 |  | -- | LAKESHORE AVE & MACARTHUR BLVD | OAKLAND | ALAMEDA | 94610 |  |  | 2005-08-26 |  |  |  | MANHOLE OVERFLOWING IN STREET. RODDED M/S CLEAR OF STOPPAGE ALSO WASHED DOWN STREET AND GUTTER AREA. M/S IS CLEAR AT THIS TIME WITH A GOOD FLOW. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWER MAINT WORKER | JAMES M. GRIMES | 2005-08-26 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1855 | 91 | 1 | Oakland | 2005-09-23 09:26 | 250 | 0 |  | 2005-09-23 09:26 |  | -- | LAKESHORE AVE & MACARTHUR BLVD | OAKLAND | ALAMEDA | 94610 |  |  | 2005-08-26 |  |  |  | MANHOLE OVERFLOWING IN STREET. RODDED M/S CLEAR OF STOPPAGE ALSO WASHED DOWN STREET AND GUTTER AREA. M/S IS CLEAR AT THIS TIME WITH A GOOD FLOW. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWER MAINT WORKER | JAMES M. GRIMES | 2005-08-26 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1721 | 61 | 1 | Oakland | 2005-08-25 09:38 | 85 | 0 |  | 2005-08-25 09:38 |  | -- | 40TH AVE & MERA ST | OAKLAND | ALAMEDA | 94601 |  |  | 2005-08-25 |  |  |  | MANHOLE OVERFLOWING PLUGGED MAIN. RODDED M/S CLEAR OF VERY HEAVY GREASE STOPPAGE. ALSO HAD #193 FLUSHER CREW, FLUSH AND WASH DOWN STREET AND GUTTER. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWER MAINT. WORKER | JAMES M. GRIMES | 2005-08-25 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1716 | 60 | 1 | Oakland | 2005-08-23 10:37 | 75 | 0 |  | 2005-08-23 10:37 |  | -- | 6101 LASALLE AVE | OAKLAND | ALAMEDA | 94610 |  |  | 2005-08-23 |  |  |  | MAIN SEWER OVERFLOWING. CHECKED & FOUND M/S PLUGGED & OVERFLOWING ONTO SIDEWALK HAND RODDED M/S CLEARED M/S OF VERY HEAVY GREASE. ALSO HAD #188 POWER RODDER ROD M/S WITH FULL TOOL CLEANED & WASHDOWN S/W AREA MADE OVER FLOW REPORT. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWERMAINT . WORKER | JAMES M. GRIMES | 2005-08-23 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1800 | 74 | 1 | Oakland | 2005-09-15 14:32 | 200 | 0 |  | 2005-09-15 14:32 |  | -- | 7837 Bancroft Ave | oakland | alameda | 94605 |  |  | 2005-08-23 |  |  |  | Cleared main of heavy grease in backyard. Cleaned up around spill. Will return in A.M. for futher clean up. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | pws | wayne guidici | 2005-09-15 | 6155566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1843 | 86 | 1 | Oakland | 2005-09-22 14:50 | 50 | 0 |  | 2005-09-22 14:50 |  | -- | 2465 E. 22ND ST | OAKLAND | ALAMEDA | 94601 |  |  | 2005-08-23 |  |  |  | M/H OVERFLOWING IN STREET. HAD POWER RODDER TO BREAK STOPPAGE OF GREASE & RAGS. M/S IS CLEAR. HAD HYDRO FLUSHER WASHDOWN STREET AND GUTTER. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWER MAINT. WORKER | JAMES M. GRIMES | 2005-08-23 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1845 | 87 | 1 | Oakland | 2005-09-22 14:59 | 200 | 0 |  | 2005-09-22 14:59 |  | -- | 7837 BANCROFT AVE | OAKLAND | ALAMEDA | 94605 |  |  | 2005-08-23 |  |  |  | M/H OVERFLOWING IN BACKYARD. CLEARED M/S OF GREASE, CLEANUP AROUND SPILL & M/S IS CLEAR. ALSO CLEANED CREEK. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWER MAINT. WORKER | JAMES M. GRIMES | 2005-08-23 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1847 | 88 | 1 | Oakland | 2005-09-22 15:14 | 95 | 0 |  | 2005-09-22 15:14 |  | -- | 1406 E25TH ST WAY | OAKLAND | ALAMEDA | 94606 |  |  | 2005-08-23 |  |  |  | MANHOLE OVERFLOWING IN REAR OF HOUSE. RODDED M/S CLEAR GREASE STOPPAGE. ALSO CLEANED AND WASHED DOWN AREA AROUND HOUSE, SIDEWALK 7 GUTTER AREA, ALSO VACUM UP SEWAGE. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWER MAINT WORKER | JAMES M. GRIMES | 2005-08-23 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1839 | 84 | 1 | Oakland | 2005-09-22 14:20 | 990 | 0 |  | 2005-09-22 14:20 |  | -- | BROADWAY ABOVE 6000BLOCK | OAKLAND | ALAMEDA | 94618 |  |  | 2005-08-17 |  |  |  | M/S OVERFLOWING IN GUTTER. RODDED M/S THE MAIN WAS PLUGGED WITH ROOTS, HAD FLUSHER TO VACCUM UP WATER TO KEEP FROM GOING INTO LAKE TEMESCAL. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SEWER MAINT. WORKER | JAMES M. GRIMES | 2005-08-17 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1841 | 85 | 1 | Oakland | 2005-09-22 14:41 | 20 | 0 |  | 2005-09-22 14:41 |  | -- | 94TH & OLIVE ST | OAKLAND | ALAMEDA | 94603 |  |  | 2005-08-17 |  |  |  | CHECKED FOR M/H OVERFLOWING. HAD POWER RODDER CLEAR M/S OF GREASE STOPPAGE, ALSO HAD FLUSHER TO RINSE & VACUM GUTTER AREA. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWER MAINT WORKER | JAMES M. GRIMES | 2005-08-17 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1798 | 73 | 1 | Oakland | 2005-09-15 14:28 | 20 | 0 |  | 2005-09-15 14:28 |  | -- | 82nd and International Blvd. | oakland | alameda | 94621 |  |  | 2005-08-16 |  |  |  | Power Rodded main clear of heavy grease. Also had flusher, flush out main after it plugged up again futher downstream. Washed down gutter and disinfected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | pws | wayne guidici | 2005-09-15 | 6155566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1837 | 83 | 1 | Oakland | 2005-09-22 14:05 | 20 | 0 |  | 2005-09-22 14:05 |  | -- | 82ND AVE & INTERNATIONAL BLVD | OAKLAND | ALAMEDA | 94621 |  |  | 2005-08-16 |  |  |  | MAIN SEWER PLUGGED. CHECKED & FOUND MAIN SEWER PLUGGED, RODDED M/S TO CLEAR STOPPAGE OF GREASE. ALSO HAD TO FLUSHED LINE IN PLUGGED LINE ALSO WASHEDDOWN GUTTER & DISINFECTED IN FROM OF SENIOR COMMUNITY HOME BUILDING. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWER MAINT WORKER | JAMES M. GRIMES | 2005-08-16 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2733 | 125 | 1 | Oakland | 2006-02-01 13:35 | 150 | 0 |  | 2006-02-01 13:35 |  | -- | Santa Rosa Ave. and Vernon Street | Oakland | Alameda | 94610 |  |  | 2005-08-15 |  |  |  | Rodded main sewer and cleared heavy grease stoppage, washed affected area with 500 galons of water. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-02-01 | (510)615-556 | wguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.comwguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
1796 | 72 | 1 | Oakland | 2005-09-15 14:24 | 3 | 0 |  | 2005-09-15 14:24 |  | -- | 478 Lake Park Ave | oakland | alameda | 94610 |  |  | 2005-08-12 |  |  |  | Flushed main downstream approx. 125' to clear main of grease | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | pws | wayne guidici | 2005-09-15 | 6155985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1835 | 82 | 1 | Oakland | 2005-09-22 13:50 | 3 | 0 |  | 2005-09-22 13:50 |  | -- | 478 LAKEPARK AVE | OAKLAND | ALAMEDA | 94610 |  |  | 2005-08-12 |  |  |  | SEWER BACKUP. HAD HYDRO FLUSHER CLEAR M/S OF GREASE BROCKAGE. M/S IS CLEAR. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWER MAINT. WORKER | JAMES M. GRIMES | 2005-08-12 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1833 | 81 | 1 | Oakland | 2005-09-22 13:26 | 30 | 0 |  | 2005-09-22 13:26 |  | -- | 90TH AVE & CHERRY ST | OAKLAND | ALAMEDA | 94603 |  |  | 2005-08-11 |  |  |  | M/H OVERFLOWING. RODDED M/S IN STREET TO CLEAR STOPPAGE OF GREASE. THE M/S IS FLOWINF AT THIS TIME. ALSO HAD FLUSHER WASH DOWN GUTTER AREA. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWER MAINT. WORKER | JAMES M. GRIMES | 2005-08-11 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1682 | 59 | 1 | Oakland | 2005-08-09 09:29 | 120 | 0 |  | 2005-08-09 09:29 |  | -- | 74 TH AVE & BANCROFT AVE | OAKLAND | ALAMEDA | 94605 |  |  | 2005-08-09 |  |  |  | M/H OVERFLOWING. CHECKED & FOUND M/H OVERFLOWING, POWERRODDER, RODDED M/S CLEAR UP STOPPAGE. CHECKED M/S CLEAR. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWER MAINT. WORKER | JAMES M. GRIMES | 2005-08-09 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2745 | 131 | 1 | Oakland | 2006-02-01 23:17 | 500 | 0 |  | 2006-02-01 23:17 |  | -- | 8001 Hillside Street | Oakland | Alameda | 94605-3455 |  |  | 2005-07-27 |  |  |  | Sewer line segment blocked with grease between structure #84-005-26 to structure #84-005-27, map #103. Assisted by hydro-flusher crew and cleared blockage, also vaccumed sewer water from spill. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-02-02 | (510)615-5566 | gthomas@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com, | MINOR
2729 | 124 | 1 | Oakland | 2006-02-01 11:52 | 100 | 0 |  | 2006-02-01 11:52 |  | -- | 688 Alvarado Rd. | Oakland | Alameda | 94705 |  |  | 2005-07-26 |  |  |  | Rodded main sewer and cleared light roots and heavy debris, rinsed area with 500 galons of water. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-02-01 | (510)615-5566 | wguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
1619 | 58 | 1 | Oakland | 2005-07-14 14:33 | 5 | 0 |  | 2005-07-14 14:33 |  | -- | 4223 REINHART DR. | OAKLAND | ALAMEDA | 94682 |  |  | 2005-07-14 |  |  |  | ROOTS IN MAIN SEWER. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | CAUSE UNKNOWN | ROOTS |  |  |  | LEADER | J.R. NICKS | 2005-07-14 | 615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1590 | 56 | 1 | Oakland | 2005-07-05 11:04 | 100 | 0 |  | 2005-07-05 11:04 |  | -- | 6715 LUCILLE ST. | OAKLAND | ALAMEDA | 94608 |  |  | 2005-07-05 |  |  |  | SEWAGE COMMING FROM CLEAN OUT. HYDRO FLUSHER MAIN SEWER, CLEARED STOPPAGE OF GREASE. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWER MAINT . WORKER | JAMES M. GRIMES | 2005-07-05 | 510-615-5566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
2727 | 123 | 1 | Oakland | 2006-02-01 11:30 | 200 | 0 |  | 2006-02-01 11:30 |  | -- | 20th Ave. and Sonoma Way | Oakland | Alameda | 94601 |  |  | 2005-07-02 |  |  |  | Hydro flushe main sewer and cleared grease stoppage, also flushed storm inlet with 500 galons of water. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Armando Lozano | Sewer Maint. Leader | 2006-02-01 | (510)615-5566 | wguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
2724 | 122 | 1 | Oakland | 2006-02-01 10:52 | 600 | 0 |  | 2006-02-01 10:52 |  | -- | 4100 Redwood Rd. | Oakland | Alameda | 94603 |  |  | 2005-07-01 |  |  |  | Rodded and cleared main sewer of roots and grease stoppage, washed and vaccumed sewer water from parking lot. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2006-02-01 | (510)615-5566 | wguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
1533 | 52 | 1 | Oakland | 2005-06-15 10:32 | 85 | 0 |  | 2005-06-15 10:32 |  | -- | WASHINGTON STREET BETWEEN 6TH ST. AND 7TH STREET. MAP#202 | OAKLAND | ALAMEDA | 84805 |  |  | 2005-06-15 |  |  |  | FLUSHER TRUCK WASHED DOWN SIDEWALK AND GUTTER AREA. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWER LEADER | J.R. NICKS | 2005-06-15 | 615-5941 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1536 | 54 | 1 | Oakland | 2005-06-15 10:54 | 15 | 0 |  | 2005-06-15 10:54 |  | -- | 77TH AND BANCROFT AVE | OAKLAND | ALAMEDA | 94605 |  |  | 2005-06-15 |  |  |  | MAN HOLE OVERFLOWING ONTO SIDEWALK AREA. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWER LEADER | J.R.NICKS | 2005-06-15 | 510 615-9941 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1538 | 55 | 1 | Oakland | 2005-06-15 11:02 | 20 | 0 |  | 2005-06-15 11:02 |  | -- | 8135 INTERNATIAL AVE | OAKLAND | ALAMEDA | 94605 |  |  | 2005-06-15 |  |  |  | WASHDOWN | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SEWER LEADER | J.R. NICKS | 2005-06-15 | 510 615-5941 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1493 | 47 | 1 | Oakland | 2005-06-08 11:15 | 75 | 0 |  | 2005-06-08 11:15 |  | -- | 6515 Gwin Rd | oakland | alameda | unk |  |  | 2005-06-03 | [9 empty] | GROUND WATER IMPACTED | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | leader | Giddens | 2005-06-08 | 5106155566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1495 | 48 | 1 | Oakland | 2005-06-08 12:51 | 90 | 0 |  | 2005-06-08 12:51 |  | -- | 4821 Grass valley Rd | oakland | alameda | unk |  |  | 2005-05-25 |  |  |  | washed down area | [5 empty] | GROUND WATER IMPACTED | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | leader | Giddens | 2005-06-08 | 6155566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1498 | 50 | 1 | Oakland | 2005-06-08 13:07 | 40 | 0 |  | 2005-06-08 13:07 |  | -- | 3400 calandria | oakland | alameda | unk |  |  | 2005-05-22 |  |  |  | washed down gutter | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | leader | Giddens | 2005-06-08 | 6155566 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1431 | 46 | 1 | Oakland | 2005-05-20 08:53 | 500 | 0 |  | 2005-05-20 08:53 |  | -- | 1706 Trestle Glen | Oakland | alameda | 94621 |  |  | 2005-05-17 |  |  |  | Rock and debris from contractors work upstream got into our main causing main to back up. Structure #54-310-43 to 54-310-44 Map 243 | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | OTHER | Lateral clean out | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | PWS 1 | Wayne Guidici | 2005-05-20 | 5106165985 | wguidici@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1426 | 45 | 1 | Oakland | 2005-05-17 15:00 | 90 | 0 |  | 2005-05-17 15:00 |  | -- | 1142 69th ave | oakland | alameda | 94621 |  |  | 2005-05-06 |  |  |  | main sewer line segment blocked with grease between structure #84-101-16 to structure #84-1o1-17, map #89 rodded main sewer to cleared stoppage of heavy grease. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | sewer maint. worker | james m. grimes | 2005-05-06 | {510} 615-5566 | wguidic @oaklandnet.com,ffsweiss@oaklandnet.com,epersons@0akland.com.atlaw@0aklandnet.com. | MINOR
1298 | 43 | 1 | Oakland | 2005-04-19 09:48 | 150 | 0 |  | 2005-04-19 09:48 |  | -- | 5552 Merriewood Drive | Oakland | Alameda | 94611-2133 |  |  | 2005-04-14 |  |  |  | Line segment blocked brtween structure #50-392-58 to structure #50-392-61, maps #302-303-315. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2005-04-19 | (510)615-5566 | wguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
1296 | 42 | 1 | Oakland | 2005-04-19 09:20 | 100 | 0 |  | 2005-04-19 09:20 |  | -- | 1000 Park Lane | Oakland | Alameda | 94610-1125 |  |  | 2005-04-13 |  |  |  | Line segment blocked with roots between structure #54-307-23 to structure #54-307-22, map #241. Rodded main sewer and cleared blockage. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2005-04-19 | (510)615-5566 | wguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
1294 | 41 | 1 | Oakland | 2005-04-18 15:31 | 100 | 0 |  | 2005-04-18 15:31 |  | -- | 401 Athol Avenue | Oakland | Alameda | 94606-1417 |  |  | 2005-04-12 |  |  |  | Line segment blocked with roots between structure #54-210-03 to structure #54-210-04, map #205, rodded and removed blockage. Washed affected area in gutter and street area with clean water. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Leader | Armando Lozano | 2005-04-18 | (510)615-5566 | wguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
1424 | 44 | 1 | Oakland | 2005-05-17 09:11 | 200 | 0 |  | 2005-05-17 09:11 |  | -- | 10th Street | Oakland | Alameda | 94607 |  |  | 2005-03-29 |  |  |  | Line segment between structure #64-016-01 to structure #64-016-02, map #235, blocked with debris. Washed and cleaned affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Sewer Maint. Worker | James Grimes | 2005-05-17 | (510)615-5566 | wguidici@oaklandnet.com, ffweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
1227 | 39 | 1 | Oakland | 2005-03-29 15:18 | 300 | 0 |  | 2005-03-29 15:18 |  | -- | 165 MARLOW DR | OAKLAND | ALAMEDA | 94605 |  |  | 2005-03-27 |  |  |  | MAIN SEWER LINE SEGMENT BLOCKED WITH ROOTS AND ROCKS BETWEEN STRUCTURE #85-231-E2 TO STRUCTURE #86-231-22,MAP #46.HAND RODDED EASEMENT TO CLEAR STOPPAGE OF ROOTS AND ROCKS | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE | MANHOLE | BLOCKAGE | ROOTS |  |  |  | SUPERVISOR | CHARLES BANDY | 2005-03-29 | (510)615-5566 | wguidici@oaklandnet.com,ffsweiss@oaklandnet.com,epersons@oaklandnet.com,atlaw@oaklandnet.com, | MINOR
1231 | 40 | 1 | Oakland | 2005-03-30 09:33 | 400 | 0 |  | 2005-03-30 09:33 |  | -- | 650 ALVARADO RD | OAKLAND | ALAMEDA | 94705 |  |  | 2005-03-27 |  |  |  | MAIN SEWER LINE SEGMENT BLOCKED WITH ROOTS BETWEEN STRUCTURE #81-676-97 TO STRUCTURE # 81-679-96,MAP #337.HAND RODDED FROM WET MANHOLE 65 RODS DOWNSTREAM TO CLEARED STOPPAGE OF HEAVY ROOTS. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE | LAMP-HOLE-MANHOLE | BLOCKAGE | ROOTS |  |  |  | SUPERVISOR | CHARLES BANDY | 2005-03-30 | (510)615-5566 | wguidici@oaklandnet.com,ffsweiss@oaklandnet.com,epersons@oaklandnet.com,atlaw@oaklandnet.com, | MINOR
1223 | 38 | 1 | Oakland | 2005-03-29 13:34 | 150 | 0 |  | 2005-03-29 13:34 |  | -- | 7900 NEY AVE | OAKLAND | ALAMEDA | 94605 |  |  | 2005-03-23 |  |  |  | MAIN SEWER LINE SEGMENT BLOCKED WITH GREASE BETWEEN STRUCTURE #84-112-71 TO STRUCTURE #84-112-72,MAP #103.RODDED AND CLEARED HEAVY GREASE BLOCKAGE. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE | MANHOLE | BLOCKAGE | GREASE |  |  |  | SEPERSVISOR | CHARLES BANDY | 2005-03-29 | (510)615-5566 | wguidici@oaklandnet.com,ffsweiss@oaklandnet.com,epersons@oaklandnet.com,atlaw@oaklandnet.com | MINOR
1221 | 37 | 1 | Oakland | 2005-03-29 11:39 | 150 | 0 |  | 2005-03-29 11:39 |  | -- | 7295 SARONI DR | OAKLAND | ALAMEDA | 94611 |  |  | 2005-03-16 |  |  |  | MAIN SEWER LINE SEGMENT BLOCKED WITH ROOTS BETWEEN STRUCTURE #56-200-35 TO STRUCTURE #56-200-33,MAP# 304.RODDED AND CLEARED BLOCKAGE OF ROOTS.RECOMENDED THAT THIS M/S BE TELEVISED. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE | LAMP-HOLE | BLOCKAGE | ROOTS |  |  |  | SUPERVISOR | CHARLES BANDY | 2005-03-29 | (510)615-5566 | wguidici@oaklandnet.com,ffsweiss@oaklandnet.com,epersons@oaklandnet.com,atlaw@oaklandnet.com | MINOR
1158 | 36 | 1 | Oakland | 2005-03-09 14:17 | 200 | 0 |  | 2005-03-09 14:17 |  | -- | 1125 FLEET RD | OAKLAND | ALAMEDA | 94610 |  |  | 2005-03-02 |  |  |  | LINE SEGMENT BLOCKED WITH ROOTS BETWEEN STRUCTURE #54-312-89 TO STRUCTURE #54-312-88, MAP #225, CLEARED BLOCKAGE AND WASHED AFFECTED AREA. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SUPERVISOR | CHARLES BANDY | 2005-03-09 | (510)615-5566 | wguidici@oakjlandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oakjlandnet.com | MINOR
1148 | 31 | 1 | Oakland | 2005-03-09 10:20 | 300 | 0 |  | 2005-03-09 10:20 |  | -- | 5831 ACACIA AVE | OAKLAND | ALAMEDA | 94618-1855 |  |  | 2005-02-27 |  |  |  | MAIN SEWER LINE SEGMENT BLOCKED WITH ROOTS BETWEEN STRUCTURE #50-332-55 TO STRUCTURE #50-332-57, MAP #312, RODDED AND CLEARED BLOCKAGE OF ROOTS, HOME OWNER HAD AN EMERGENCY CLEAN UP CREW ON SITE | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | supervisor | Charles Bandy | 2005-03-09 | (510)615-5566 | wguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com,atlaw@oaklandnet.com | MINOR
1156 | 35 | 1 | Oakland | 2005-03-09 14:01 | 600 | 0 |  | 2005-03-09 14:01 |  | -- | 4500 LINCOLM AVE | OAKLAND | ALAMEDA | 94602 |  |  | 2005-02-26 |  |  |  | LINE SEGMENT BLOCKED WITH DEBRIS BETWEEN STRUCURE #80-113-03 TO STRUCTURE #80-113-02.MAP#227, VACUMED DEBRIS AND WASHED DOWN AFFECTED AREA | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | SUPERVISOR | CHARLES BANDY | 2005-02-27 | (510)615-5566 | wguidici@oaklandnet.com,ffsweiss@oaklandnet.com,epersons@oaklandnet.com,atlaw@oaklandnet.com | MINOR
1152 | 33 | 1 | Oakland | 2005-03-09 11:13 | 800 | 0 |  | 2005-03-09 11:13 |  | -- | 2620 MOUNTAIN BLVD | OAKLAND | ALAMEDA | 94611-3019 |  |  | 2005-02-04 |  |  |  | MANHOLE CONE COLLAPSED BETWEEN STRUCTURES #56-111-40 TO STRUCTURE #56-111-05, MAP #244, RODDED AND FLUSHED MAIN SEWER AND CLEARED DEBRIS BLOCKAGE, MADE CONSTRUCTION WORK ORDER TO REPLACE MANHOLE | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | INFRASTRUCTURE FAILURE | DEBRIS |  |  |  | SUPERVISOR | CHARLES BANDY | 2005-03-09 | (510)615-5566 | wguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
1154 | 34 | 1 | Oakland | 2005-03-09 13:06 | 400 | 0 |  | 2005-03-09 13:06 |  | -- | 5826 AMY DR | OAKLAND | ALAMEDA | 94618 |  |  | 2005-01-28 |  |  |  | LINE SEGMENT BLOCKED WITH ROOTS BETWEEN STRUCTURE #50-353-54 TO STURCTURE # 50-353-55, MAP #301 | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | SUPERSIVOR | CHARLES BANDY | 2005-03-09 | (510)615-5566 | wguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
919 | 30 | 1 | Oakland | 2005-01-26 17:10 | 1500 | 0 | 0001 | 2005-01-26 | ARMANDO LOZANO | OAKLAND | 3340 REVERE AVE | OAKLAND | ALAMEDA | 94605-584 |  |  | 2005-01-26 | 1:53:00 AM | [5 empty] | RAINY WEATHER | High | SAN LEANDRO CREEK | GROUND WATER IMPACTED | Yes |  | No | No | HEAVY RAIN WASHED DOWN SPILL, WATER IN CREEK IS CLEAR |  | No | No | No | No | No | No | No | Yes | No | 2005-01-28 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | OAKLAND | OTHER | TOILET | BLOCKAGE | ROOTS | --Select None-- |  | Line segment blocked with roots and overflowed inside house and backyard spilling into a rear San Leandro Creek, heavy rain washed spill away, owner hired a private contractor to clean the house | Sewer Maint. Leader | Armando Lozano | 2005-01-26 | (510)615-5566 | wguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MAJOR | ELDRIDGE PERSONS | Oakland | (510)615-5566 |  | 7101 EDGEWATER DRIVE | OAKLAND | ALAMEDA | 94601 | CITY OF OAKLAND | OAKLAND | (510)615-5566 |  | 7101 EDGEWATER DR | OAKLAND | ALAMEDA | 94601
905 | 28 | 1 | Oakland | 2005-01-24 11:10 | 350 | 0 |  | 2005-01-24 11:10 |  | -- | 4347 Harbord Drive | Oakland | Alameda | 94618-2007 |  |  | 2005-01-21 |  |  |  | Line segment blocked with roots, grease and debris between structure #50-305-04 to structure #50-305-07, map #312. Vaccum, mup, cleaned and disenfected affected area in bathroom and wine room, sewer lateral is still backing up and property owner was advised to have plumber to fix problem | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | OTHER | bathroom drain | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2005-01-24 | (510)615-5566 | wguidici@oaklandnet.com, ffweiss@oaklandnet.com, epersons@oaklandnet.com,atlaw@oaklandnet.com | MINOR
913 | 29 | 1 | Oakland | 2005-01-25 13:54 | 150 | 0 |  | 2005-01-25 13:54 |  | -- | 5982 ASCOT DRIVE | OAKLAND | ALAMEDA | 94611-2705 |  |  | 2005-01-20 |  |  |  | RODDED AND FLUSHED MAIN SEWER EASEMENT BLOCKED BETWEEN STRUCTURE #56-100-38 TO STRUCTURE #56-100-35, MAP #260. CLEANED AND WASHED AFFECTED AREA IN REAR OF 5972 ASCOT DR. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2005-01-25 | (510)615-5566 | wguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
1812 | 76 | 1 | Oakland | 2005-09-20 10:53 | 300 | 0 |  | 2005-09-20 10:53 |  | -- | 1200 lakeshore drive | oakland | alameda | 94612 |  |  | 2005-01-18 |  |  |  | Flushed main clear of grease and washed down the gutter area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | pws | c bandy | 2005-09-20 | 5106155985 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
1150 | 32 | 1 | Oakland | 2005-03-09 10:49 | 300 | 0 |  | 2005-03-09 10:49 |  | -- | 1200 Lake Shore Ave | OAKLAND | ALAMEDA | 94606-1679 |  |  | 2005-01-14 |  |  |  | LINE SEGMENT BLOCKED WITH GREASE BETWEEN STRUCTURE #54-002-13 TO STRUCTURE #54-002-12,MAP #185, RODDED MAIN SEWER, CLEANED AND WASHED SPILL. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SUPERVISOR | CHARLES BANDY | 2005-03-09 | (510)6155566 | wguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
1808 | 75 | 1 | Oakland | 2005-09-20 10:42 | 200 | 0 |  | 2005-09-20 10:42 |  | -- | 4330 Mountain Blve | Oakland | alameda | 94602 |  |  | 2005-01-12 |  |  |  | Power Rodder unplugged main of haavy roots. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWS | c bandy | 2005-09-20 | 615 5941 | jheredia@oaklandnet.com, bsaunders@oaklandnet.com, mjneary@oaklandnet.com | MINOR
860 | 27 | 1 | Oakland | 2005-01-14 15:29 | 100 | 0 |  | 2005-01-14 15:29 |  | -- | 6311 HILLMONT DRIVE | OAKLAND | ALAMEDA | 94605-2240 |  |  | 2005-01-07 |  |  |  | Temporary main sewer was moved when hydro flusher was flushing the main sewer between structure #83-403-01 to structure #83-403-02, map #126, the main was extended and braced. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | OTHER | TEMPORARY LINE | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Sewer Maint. Leader | Armando Lozano | 2005-01-14 | (510)615-5566 | wguidici@oaklandnet.com, ffweiss@oaklandnet.com, epersons@oaklandnet.com,atlaw@oaklandnet.com | MINOR
804 | 25 | 1 | Oakland | 2005-01-10 14:01 | 800 | 0 |  | 2005-01-10 14:01 |  | -- | 435 CAPISTRANO DRIVE | OAKLAND | ALAMEDA | 94603-3519 |  |  | 2004-12-30 |  |  |  | Line segment blocked between structure #86-006-66 to structure #86-006-73, map #24, very heavy rain diluted and washed spill away. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2005-01-10 | (510)615-5566 | wguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
856 | 26 | 1 | Oakland | 2005-01-14 10:17 | 200 | 0 |  | 2005-01-14 10:17 |  | -- | 8065 FONTAINE STREET | OAKLAND | ALAMEDA | 94605-3638 |  |  | 2004-12-30 |  |  |  | MAIN SEWER LINE WAS SURCHARCHING DUE TO HEAVY RAIN STORM | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | Sewer Maint. Leader | Armando Lozano | 2005-01-14 | (510)615-5566 | wguidici@oaklandnet.com, ffweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
802 | 24 | 1 | Oakland | 2005-01-10 11:55 | 600 | 0 |  | 2005-01-10 11:55 |  | -- | 575 Fairmount Avenue | Oakland | Alameda | 94611-5324 |  |  | 2004-12-29 |  |  |  | Line segment blocked with debris from structure #50-502-07 to structure #50-502-07, maps #269/254, contained spill, flushed and cleaned affected area. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2005-01-10 | (510)615-5566 | wguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
673 | 23 | 1 | Oakland | 2004-12-29 09:45 | 500 | 0 |  | 2004-12-29 09:45 |  | -- | 290 ALVARADO RD | OAKLAND | ALAMEDA | 94705-1513 |  |  | 2004-12-27 |  |  |  | LINE SEGMENT BLOCKED WITH ROOTS BETWEEN STRUCTURE #17-405-32 TO STRUCTURE #17-405-33, MAP #337, WASHED DOWN AREA IN RAIN | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-29 | (510)615-5566 | wguidici@oaklandnet.com, ffweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
627 | 22 | 1 | Oakland | 2004-12-23 09:53 | 400 | 0 |  | 2004-12-23 09:53 |  | -- | 2829 99th Avenue | Oakland | Alameda | 94605-4814 |  |  | 2004-12-22 |  |  |  | Line segment blocked with roots and grease between structure #85-221-20 to structure #85-221-19, map #68. Storm inlet was plugged, main sewer problem was clear, affected area was washed and cleaned, and contaminated water was recovered. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-23 | (615-5566) | wguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
600 | 19 | 1 | Oakland | 2004-12-20 13:19 | 400 | 0 |  | 2004-12-20 13:19 |  | -- | Park Blvd. and Mountain Blvd. | Oakland | Alameda | 94606 |  |  | 2004-12-20 |  |  |  | Line segment blocked with roots and debris between structure #56-220-02 to structure #56-220-03, map #259. Washed and cleaned affected area in street. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-20 | (510)615-5566 | wguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
604 | 21 | 1 | Oakland | 2004-12-21 09:45 | 800 | 0 |  | 2004-12-21 09:45 |  | -- | GRAND AVE AND HARRISON ST | OAKLAND | ALAMEDA | 94612 |  |  | 2004-12-20 |  |  |  | LINE SEGMENT BLOCKED WITH GREASE BETWEEN STRUCTURE #52-905-06 TO STRUCTURE #52-905-11, MAP #239. RECOVERED 725 GALLONS OF THE SPILL, WASHED AND CLEANED AFFECTED AREA | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | OAKLAND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-21 | (510)615-5566 | wguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
602 | 20 | 1 | Oakland | 2004-12-20 14:00 | 400 | 0 |  | 2004-12-20 14:00 |  | -- | 4160 Whittle Avenue | Oakland | Alameda | 94602-254 |  |  | 2004-12-18 |  |  |  | Line segment blocked with roots between structure #56-010-46 to structure #56-010-47, map #227. Washed down affected area. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-20 | (510)615-5566 | wguidici@oaklandnet.com, ffsweiss@oaklandnet.com, epersons@oaklandnet.com, atlaw@oaklandnet.com | MINOR
561 | 17 | 1 | Oakland | 2004-12-16 16:20 | 150 | 0 |  | 2004-12-16 16:20 |  | -- | 4425 Carson Street | Oakland | Alameda | 94619-2954 |  |  | 2004-12-15 |  |  |  | Line segment blocked with roots between structure #83-303-25 to structure #83-303-24, cleaned affected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-16 | (510)615--5566 |  | MINOR
585 | 18 | 1 | Oakland | 2004-12-17 14:36 | 150 | 0 |  | 2004-12-17 14:36 |  | -- | #20 Stonewall Rd. | Oakland | Alameda | 94609 |  |  | 2004-12-15 |  |  |  | Line blocked with roots, cleaned spill. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-17 | (510-615-5566 | cbandy@oaklandnet.com | MINOR
525 | 10 | 1 | Oakland | 2004-12-14 10:16 | 500 | 0 |  | 2004-12-14 10:16 |  | -- | 1924 Franklin Street | Oakland | Alameda | 94612-2913 |  |  | 2004-12-14 |  |  |  | Line segment broken and collapsed between structure #52-903-21 to structure #52-903-20, map#221. Partially cleared main sewer of heavy debris, televised main sewer and recommended line for repairs. Basement and affected area in gutter and storm inlet was cleaned. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | OTHER | floor drain in basement | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-14 | (510)615-5566 |  | MINOR
529 | 12 | 1 | Oakland | 2004-12-14 10:58 | 500 | 0 |  | 2004-12-14 10:58 |  | -- | 70th Avenue and Snell | Oakland | Alameda | 94621 |  |  | 2004-12-14 |  |  |  | Line segment blocked between structure #84-101-08 to structute #84-100-17, map #77. Cleaned affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-14 | (510)615-5566 |  | MINOR
531 | 13 | 1 | Oakland | 2004-12-14 11:08 | 400 | 0 |  | 2004-12-14 11:08 |  | -- | 1924 Franklin Street | Oakland | Alameda | 94612-2913 |  |  | 2004-12-14 |  |  |  | Line segment broken and collapsed between structure #52-903-21 to structure #52-903-20, map #221. Water is being bypassed while this sewer line is being excavated and repaired by an independent contractor. Basement and affected areas were cleaned. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | OTHER | floor drain | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-14 | (510)615-5566 |  | MINOR
533 | 14 | 1 | Oakland | 2004-12-14 11:30 | 150 | 0 |  | 2004-12-14 11:30 |  | -- | 99th Avenue and Stearns Avenue | Oakland | Alameda | 94603-2520 |  |  | 2004-12-13 |  |  |  | Line segment blocked between structure #85-221-20 to structure #85-221-94, map #68. Cleaned affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-14 | (510)615-5566 |  | MINOR
536 | 15 | 1 | Oakland | 2004-12-14 13:47 | 400 | 0 |  | 2004-12-14 13:47 |  | -- | 72nd Avenue and Spencer Street | Oakland | Alameda | 94621 |  |  | 2004-12-09 |  |  |  | Line segment blocked with heavy grease from structure #84-100-21 to structure #84-102-14, map #77. Cleaned affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-14 | (510)615-5566 |  | MINOR
559 | 16 | 1 | Oakland | 2004-12-16 14:50 | 250 | 0 |  | 2004-12-16 14:50 |  | -- | 4720 Sequoyah Road | Oakland | Alameda | 94605-4655 |  |  | 2004-12-09 |  |  |  | Line segment blocked with roots between structure #85-400-73 to structure #85-400-71, cleaned affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-16 | (510)615-5566 |  | MINOR
467 | 2 | 1 | Oakland | 2004-12-09 15:51 | 120 | 0 |  | 2004-12-09 15:51 |  | -- | Saroni Drive and Homewood Drive | Oakland | Alameda | 94611 |  |  | 2004-12-06 |  |  |  | Line segment blocked and cleared of heavy roots between segment between structure #54-311-A6 to structure #54-311-A8, map #225,flushed affected area and recovered spill | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-09 | (510)615-5566 |  | MINOR
527 | 11 | 1 | Oakland | 2004-12-14 10:45 | 300 | 0 |  | 2004-12-14 10:45 |  | -- | 56th Avenue and International Street | Oakland | Alameda | 94621-4412 |  |  | 2004-12-06 |  |  |  | Line segment blocked between structure #83-200-03 to structure #83-200-01, map #99. Cleaned affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-14 | (510)615-5566 |  | MINOR
469 | 3 | 1 | Oakland | 2004-12-09 16:22 | 180 | 0 |  | 2004-12-09 16:22 |  | -- | 2020 16th Avenue | Oakland | Alameda | 94606-4016 |  |  | 2004-12-05 |  |  |  | Line segment blocked with heavy grease between structure #58-003-06 to structure #58-002-78, map #168, flushed affected area and recovered spill. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-09 | (510)615-5566 |  | MINOR
488 | 7 | 1 | Oakland | 2004-12-10 11:09 | 260 | 0 |  | 2004-12-10 11:09 |  | -- | 9098 Broadway Terrace | Oakland | Alameda | 94611-1952 |  |  | 2004-12-05 |  |  |  | Line segment on easement blocked with heavy roots between structure #50-370-21 to structure #50-370-23, map #314, washed affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-10 | (510)615-5566 |  | MINOR
521 | 8 | 1 | Oakland | 2004-12-14 09:41 | 100 | 0 |  | 2004-12-14 09:41 |  | -- | 1020 Longridge Rd. | Oakland | Alameda | 94610-2442 |  |  | 2004-12-05 |  |  |  | Line segment broken and collapsed between structure #54-311-A6 to structure #54-311-A8, main sewer was excavated and repaired, affected area was cleaned. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | INFRASTRUCTURE FAILURE | DEBRIS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-14 | (510)615-5566 |  | MINOR
523 | 9 | 1 | Oakland | 2004-12-14 09:54 | 475 | 0 |  | 2004-12-14 09:54 |  | -- | 3800 Delmont Avenue | Oakland | Alameda | 94605-2231 |  |  | 2004-12-05 |  |  |  | Emergency crew fixed temporary line between structure #83-403-01 to structure #83-403-03, map #126, ground water was flushed with 500 galons of water | [5 empty] | GROUND WATER IMPACTED | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | OTHER | Temporary main pulled appart | BLOCKAGE | --Select None-- |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-14 | (510)615-5566 |  | MINOR
464 | 1 | 1 | Oakland | 2004-12-09 15:01 | 100 | 0 |  | 2004-12-09 15:01 |  | -- | 6221 Broadway Terrace | Oakland | Alameda | 94618-2103 |  |  | 2004-12-02 |  |  |  | Line segment blocked between structure #50-343-14 to structure #50-343-15 map #313, cleared main sewer of heavy roots, flushed down affected area, vacumed and recovered spill | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | sewer maint. leader | Armando Lozano | 2004-12-09 | 510-615-5566 |  | MINOR
486 | 6 | 1 | Oakland | 2004-12-10 10:59 | 260 | 0 |  | 2004-12-10 10:59 |  | -- | 6363 Telegraph Avenue | Oakland | Alameda | 94609-1344 |  |  | 2004-12-02 |  |  |  | Line segment blocked with heavy grease between structure #50-220-22 to structure #50-220-23, map #330, after the blockage was cleared the water drain back to the sewer main,washed and disenfected the affected area in basement. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | OTHER | Floor drain | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-10 | (510)615-5566 |  | MINOR
478 | 4 | 1 | Oakland | 2004-12-10 10:31 | 100 | 0 |  | 2004-12-10 10:31 |  | -- | 14th Street and West Street | Oakland | Alameda | 94612 |  |  | 2004-12-01 |  |  |  | Line segment blocked with heavy grease between structure #52-004-31 to structure #52-004-33, map #220/ flushed main and cleared heavy grease clog, washed affected areas | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-10 | (510)615-5566 |  | MINOR
484 | 5 | 1 | Oakland | 2004-12-10 10:45 | 200 | 0 |  | 2004-12-10 10:45 |  | -- | Alvarado Road and Slater Lane | Oakland | Alameda | 94613 |  |  | 2004-12-01 |  |  |  | Line segment blocked between structure #17-405-80 to structure #17-405-79,map #337, cleaned the affected area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Oakland | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Sewer Maint. Leader | Armando Lozano | 2004-12-10 | (510_615-5566 |  | MINOR
4965 | 2 | 2 | OroLoma | 2007-03-12 | 1500 | 1500 | 07-1572 | 2007-03-12 | Lenny Rather | OroLoma | 22756 Olive Place | Hayward | Alameda | 94541 |  |  | 2007-03-11 | 0.27083 | [6 empty] | Low |  | STORM DRAIN | No |  | No | No | Cleaning crews followed the storm drain to a point that the spill did not reach, several hundred feet down stream of the spill discharge point. The storm drain was hydro-jetted and vacuumed. The spill did not reach any receiving waters. |  | Yes | Yes | No |  |  | No | No |  |  |  | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS | -- Select One -- |  |  | General Manager | Michael P. Cortez | 2007-03-12 | 510-481-6965
3906 | 1 | 2 | OroLoma | 2006-09-21 10:41 | 1562 | 1562 | 06-5529 | 2006-09-16 | Lenny Rather | Mike Cortez | 2165 & 2173 150th Avenue | San Leandro | Alameda | 94578 |  |  | 2006-09-16 | 9:00:00 AM | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | No | Not applicable. No body of water downstream or within a mile of the SSO. District attempted to cleanup the affected storm drain as much as possible on day of the SSO. Moreover, District crew returned to the site the following workday to perform more thorough cleanup and found out that SSO did not extend more than one catch basin downstream due to a hardened silt deposit accumulated at the bottom of the storm drain. |  | Yes | Yes | Yes | No | No | No | No | No | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | OroLoma | CLEAN OUT | Foreign materials accumulated in a manhole, partially blocking the flow. This created enough surcharging upstream into a defective lateral. District staff assumed a 50/50 flow split between the main and the defective lateral for about five hours. The entire SSO originated from a crack at the cleanout of the lateral at 2173 150th Avenue, eventually discharging into the driveway and curb and gutter at 2165 150th Avenue.District crew initially responding to the SSO inadvertently miscalculated the total volume at 9,300 gallons. However, after detailed evaluation, staff estimated the toal volume of spill is as follows: 50% x 200 gal/day/home x 5/24 day x 75 homes = 1,562 gallons.District staff is currently inspecting repair of the defective lateral and has instructed the homeowner to intall a backwater prevention device. | BLOCKAGE | MULTIPLE CAUSES | --Select None-- |  |  | General Manager | Michael P. Cortez | 2006-09-16 | 510-481-6965 | mcortez@oroloma.org, mcameron@oroloma.org | MAJOR | Mike Cortez | OroLoma | 510-481-6965 |  | 2655 Grant Avenue | San Lorenzo | Alameda | 94591 |  | OroLoma
5128 | 44 | 1 | Pacifica | 2007-04-24 07:51 | 50 | 0 |  | 2007-04-24 07:51 |  | -- | 800 Block of Rockaway Beach Ave. | Pacifica | San Mateo | 94044 |  |  | 2007-04-23 |  |  |  | Spill was contained in yard and vaccumed up. Area was disenfected. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Assistant Super. | Joshua Cosgrove | 2007-04-24 | 650 738-7475
5096 | 43 | 1 | Pacifica | 2007-04-20 14:37 | 60 | 0 |  | 2007-04-20 14:37 |  | -- | 1200 Block of Crespi Drive | Pacifica | San Mateo | 94044 |  |  | 2007-04-18 |  |  |  | Caused by roots and grease. Area was cleaned and disenfected. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Assistant Super. | Joshua Cosgrove | 2007-04-20 | 650 738-7475
5094 | 42 | 1 | Pacifica | 2007-04-20 14:34 | 100 | 0 |  | 2007-04-20 14:34 |  | -- | 500 block of Carmel | Pacifica | San Mateo | 94044 |  |  | 2007-04-18 |  |  |  | Area was cleaned and disenfected. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | PIPE |  | BLOCKAGE | ROOTS |  |  |  | Assistant Super. | Joshua Cosgrove | 2007-04-20 | 650 738-7475
5005 | 39 | 1 | Pacifica | 2007-03-27 07:35 | 200 | 0 |  | 2007-03-27 07:35 |  | -- | Carmel Ave | Pacifica | San Mateo | 94044 |  |  | 2007-03-27 |  |  |  | The spill area was cleaned and disinfected. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Assistant Super. | Joshua Cosgrove | 2007-03-27 | 650 738-7475
4994 | 38 | 1 | Pacifica | 2007-03-23 16:39 | 50 | 0 |  | 2007-03-23 16:39 |  | -- | Paceito Terr. | Pacifica | San Mateo | 94044 |  |  | 2007-03-23 |  |  |  | Spill area was cleaned and disinfected. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Assistant Super. | Joshua Cosgrove | 2007-03-23 | 650 738-7475
4517 | 33 | 1 | Pacifica | 2007-01-16 11:11 | 300 | 0 |  | 2007-01-16 11:11 |  | -- | 300 BLOCK PACIFIC | PACIFICA | SAN MATEO | 94044 |  |  | 2007-01-16 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | ASST SUPERINTENDENT | BRIAN MARTINEZ | 2007-01-16 | 650 738 4669
4515 | 32 | 1 | Pacifica | 2007-01-16 11:10 | 200 | 0 |  | 2007-01-16 11:10 |  | -- | GALVEZ EASEMENT | PACIFICA | SAN MATEO | 94044 |  |  | 2007-01-11 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | ASST. SUPERINTENDENT | BRIAN MARTINEZ | 2007-01-16 | 650 738 4669
4378 | 31 | 1 | Pacifica | 2006-12-21 08:22 | 40 | 0 |  | 2006-12-21 08:22 |  | -- | 200 BONITA | Pacifica | San Mateo | 94044 |  |  | 2006-12-21 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Asst. Superintendent | Brian Martinez | 2006-12-21 | 650 738 4669
4141 | 30 | 1 | Pacifica | 2006-11-21 16:24 | 50 | 0 |  | 2006-11-21 16:24 |  | -- | San Pablo Ter. (400 Block) | Pacifica | San Mateo | 94044 |  |  | 2006-11-17 |  |  |  | Did not reach any receiving waters | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Operator II | Joshua Cosgrove | 2006-11-21 | 650 738-4669
4050 | 29 | 1 | Pacifica | 2006-11-01 08:04 | 400 | 0 |  | 2006-11-01 08:04 |  | -- | 351 Carmel | Pacifica | San Mateo | 94044 |  |  | 2006-10-30 |  |  |  | Found lots of rags on auger | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | pacifica | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Operator II | Joshua Cosgrove | 2006-11-01 | 650 738-4669 | chenm@ci.pacifica.ca.us, holmess@ci.pacifica.ca.us | MINOR
3947 | 28 | 1 | Pacifica | 2006-09-29 08:01 | 200 | 0 |  | 2006-09-29 08:01 |  | -- | 315 SHORESIDE | PACIFICA | SAN MATEO | 94044 |  |  | 2006-09-27 |  |  |  | ALL SEWAGE WAS CONTAINED AND RETURNED TO SYSTEM. UNIQUE AREA WITH NO STORM DRAINS, SO WE WERE ABLE TO PUMP SEWAGE FROM PONDING AREA BACK TO SYSTEM. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pacifica | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Asst. superintendent | Brian Martinez | 2006-09-29 | 650 738 4669 | chenm@ci.pacifica.ca.us, holmess@ci.pacifica.ca.us | MINOR
3852 | 27 | 1 | Pacifica | 2006-09-07 08:34 | 10 | 0 |  | 2006-09-07 08:34 |  | -- | NATAQUA@REINA DEL MAR | Pacifica | San Mateo | 94044 |  |  | 2006-09-06 |  |  |  | Partial blockage, disinfected lawn area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pacifica | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Asst. Suparintendent | Brian Martinez | 2006-09-07 | 650 738 4669 | chenm@ci.pacifica.ca.us, holmess@ci.pacifica.ca.us | MINOR
3699 | 26 | 1 | Pacifica | 2006-08-08 08:21 | 200 | 0 |  | 2006-08-08 08:21 |  | -- | MH in front of 1450, 1459 Perez | Pacifica | san mateo | 94044 |  |  | 2006-08-07 |  |  |  | After the line was cleared roots was found in the downstream MH. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pacifica | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Operator II | Joshua Cosgrove | 2006-08-08 | 650 738-4669 | chenm@ci.pacifica.ca.us, holmess@ci.pacifica.ca.us | MINOR
3373 | 22 | 1 | Pacifica | 2006-05-22 09:47 | 20 | 0 |  | 2006-05-22 09:47 |  | -- | Sharp Park Road | Pacifica | San Mateo | 94044 |  |  | 2006-05-18 |  |  |  | Minimal spill, only wet around manhole | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pacifica | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Asst. superintendent | Brian Martinez | 2006-05-22 | 6507384669 | chenm@ci.pacifica.ca.us, holmess@ci.pacifica.ca.us | MINOR
3256 | 21 | 1 | Pacifica | 2006-05-01 07:46 | 20 | 0 |  | 2006-05-01 07:46 |  | -- | 901 OCEANA | PACIFICA | SAN MATEO | 94044 |  |  | 2006-04-29 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pacifica | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Asst. Superintendent | Brian Martinez | 2006-05-01 | 650 738 4669 | chenm@ci.pacifica.ca.us, holmess@ci.pacifica.ca.us | MINOR
3138 | 20 | 1 | Pacifica | 2006-04-10 07:21 | 28 | 0 |  | 2006-04-10 07:21 |  | -- | 1530 GRAND AVE. | PACIFICA | SAN MATEO | 94044 |  |  | 2006-04-08 | [9 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pacifica | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Asst. Superintendent | Brian Martinez | 2006-04-10 | 650 738 4669 | chenm@ci.pacifica.ca.us, holmess@ci.pacifica.ca.us | MINOR
3012 | 19 | 1 | Pacifica | 2006-03-16 08:39 | 650 | 0 |  | 2006-03-16 08:39 |  | -- | Paloma at Francisco | Pacifica | San Mateo | 94044 |  |  | 2006-03-06 |  |  |  | Found small tree branch in line. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pacifica | MANHOLE |  | BLOCKAGE | VANDALISM |  |  |  | Asst. Superintendent | Brian Martinez | 2006-03-16 | 650 738 4669 | chenm@ci.pacifica.ca.us, holmess@ci.pacifica.ca.us | MINOR
2424 | 18 | 2 | Pacifica | 2006-01-01 16:08 | 5000 | 5000 | 060022 | 2006-01-01 | Ming Chen | Pacifica | Sharp Park Golf Course | Pacifica | San Mateo | 94044 |  |  | 2005-12-31 | 1:00:00 AM | [5 empty] | RAINY WEATHER | Low |  | YARD/LAND | No |  | No | No | No changes were found. |  | Yes | Yes | Yes | No | No | No | No | No | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Pacifica | PIPE |  | INFRASTRUCTURE FAILURE | --Select None-- | --Select None-- |  | The spill occured in the Sharp Park Golf Course. Our Force Main which runs to the Calera Creek Water Recycling Plant from the Sharp Park Pump Station had a minor leak. It is sceduled to repair as soon as weather clears. On 12/31/05 01:00 am, Due to heavy rain storm, excess infiltration of rain water leaked out from the leaky force main onto golf course ground.The majority of the spill was contained and diverted to a gravity sewer main nearby. | Manager | Ming Chen | 2006-01-01 | 650-738-4668 | chenm@ci.pacifica.ca.us, holmess@ci.pacifica.ca.us | MAJOR | Ming Chen | City of Pacifica | 650 738-4668 |  | 170 Santa Maria Ave. | Pacifica | San Mateo | 94044 |  | Pacifica
2387 | 17 | 1 | Pacifica | 2005-12-30 13:28 | 700 | 0 |  | 2005-12-30 13:28 |  | -- | Sharp Park Golf Course | Pacifica | San Mateo | 94044 |  |  | 2005-12-23 |  |  |  | Our Force Main which runs to the Calera Creek Water Recycling Plant from the Sharp Park Pump Station had a minor leak. The majority of the spill was contained and diverted to a gravity sewer main nearby. The spill occured in the Sharp Park Golf Course. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pacifica | PIPE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | WWTP Operator | Joshua Cosgrove | 2005-12-30 | (650) 738-4668 | chenm@ci.pacifica.ca.us, holmess@ci.pacifica.ca.us | MINOR
2282 | 15 | 1 | Pacifica | 2005-12-19 13:50 | 850 | 0 |  | 2005-12-19 13:50 |  | -- | 300-400 Block Monterey | Pacifica | San Mateo | 94044 |  |  | 2005-12-18 |  |  |  | The main sewer in the 300-400 block of Monterey surcharged causing backups into homes located at 340,376,440 Monterey | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pacifica | OTHER | Shower drains | INFLOW & INFILTRATION | --Select None-- |  |  |  | Asst. Superintendent | Brian Martinez | 2005-12-19 | 650 738 4669 | chenm@ci.pacifica.ca.us, holmess@ci.pacifica.ca.us | MINOR
2284 | 16 | 1 | Pacifica | 2005-12-19 13:56 | 350 | 0 |  | 2005-12-19 13:56 |  | -- | 2562 Francisco Apt. # H | Pacifica | San Mateo | 94044 |  |  | 2005-12-18 |  |  |  | A storm water drainage canal surcharged in adjacent property causing the sanitary sewer to surcharge, resulting in a backup into 2562 Francisco Apt. # H. This property was also flooded by storm water from canal. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pacifica | OTHER | Shower drain | INFLOW & INFILTRATION | --Select None-- |  |  |  | Asst. Superintendent | Brian Martinez | 2005-12-19 | 650 738 4669 | chenm@ci.pacifica.ca.us, holmess@ci.pacifica.ca.us | MINOR
2229 | 14 | 3 | Pacifica | 2005-12-07 11:15 | 253331 | 0 | 05-6992 | 2005-12-05 | BRIAN MARTINEZ | Pacifica | ROCKAWAY LIFT STATION / 30 SAN MARLO | PACIFICA | SAN MATEO | 94044 |  |  | 2005-12-04 | 12:30:00 P | [5 empty] | CLOUDY WEATHER | High |  | STORM DRAIN | Yes | All of Rockaway Beach | No | Yes | SEEMS FINE TO SIGHT |  | Yes | Yes | Yes | No | No | Yes | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Pacifica | PUMP STATION |  | INFRASTRUCTURE FAILURE | --Select None-- | PUMP STATION FAILURE |  | AMOUNT SPILLED IS NOW COMPLETE | ASST. SUPERINTENDENT | BRIAN MARTINEZ | 2005-12-05 | 650-738-4669 | chenm@ci.pacifica.ca.us, holmess@ci.pacifica.ca.us | MAJOR | Ming Chen | City of Pacifica | 650 738 4668 |  | 700 COAST HWY. | PACIFICA | SAN MATEO | 94044 |  | Pacifica
1760 | 11 | 1 | Pacifica | 2005-09-07 07:20 | 100 | 0 |  | 2005-09-07 07:20 |  | -- | 407 HEATHCLIFF DR | PACIFICA | SAN MATEO | 94044 |  |  | 2005-09-02 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pacifica | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | COLLECTIONS OPERATOR | JOSHUA COSGROVE | 2005-09-07 | 650 738 4669 | chenm@ci.pacifica.ca.us, holmess@ci.pacifica.ca.us | MINOR
1724 | 9 | 1 | Pacifica | 2005-08-25 10:41 | 20 | 0 |  | 2005-08-25 10:41 |  | -- | Hwy.1 @ Seabowl Lane | Pacifica | San Mateo | 94044 |  |  | 2005-08-10 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pacifica | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Asst. superintendent | Brian martinez | 2005-08-25 | 650 738 4669 | chenm@ci.pacifica.ca.us, holmess@ci.pacifica.ca.us | MINOR
1649 | 8 | 1 | Pacifica | 2005-07-26 15:13 | 600 | 0 |  | 2005-07-26 15:13 |  | -- | GYPSY HILL EASEMENT | PACIFICA | SAN MATEO | 94044 |  |  | 2005-07-22 |  |  |  | SPILL DID NOT REACH ANY STORM INLETS. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pacifica | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | ASST. SUPERINTENDENT | BRIAN MARTINEZ | 2005-07-26 | 650 738 4669 | chenm@ci.pacifica.ca.us, holmess@ci.pacifica.ca.us | MINOR
1487 | 7 | 1 | Pacifica | 2005-06-06 08:07 | 15 | 0 |  | 2005-06-06 08:07 |  | -- | 76 Cranham ct. | Pacifica | San Mateo | 94044 |  |  | 2005-06-05 |  |  |  | A buildup of rags was blocking manhole outlet. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pacifica | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Asst. Superintendent | Brian Martinez | 2005-06-06 | 650 738 4669 | chenm@ci.pacifica.ca.us, holmess@ci.pacifica.ca.us | MINOR
1195 | 6 | 1 | Pacifica | 2005-03-17 08:24 | 300 | 0 |  | 2005-03-17 08:24 |  | -- | 1600 BLOCK HIGGINS | PACIFICA | SAN MATEO | 94044 |  |  | 2005-03-16 |  |  |  | OVERFLOWED AT MANHOLE LOCATED IN FRONT OF 1633 HIGGINS | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pacifica | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | ASST. SUPERINTENDENT | BRIAN MARTINEZ | 2005-03-17 | 650 738 4669 | chenm@ci.pacifica.ca.us, holmess@ci.pacifica.ca.us | MINOR
1097 | 4 | 1 | Pacifica | 2005-03-01 08:21 | 90 | 0 |  | 2005-03-01 08:21 |  | -- | 790 ROCKAWAY BEACH BLVD. | PACIFICA | SAN MATEO | 94044 |  |  | 2005-02-28 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pacifica | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | Asst. Superintendent | Brian Martinez | 2005-03-01 | 650 738 4669 | chenm@ci.pacifica.ca.us, holmess@ci.pacifica.ca.us | MINOR
1553 | 5 | 2 | Pacifica | 2005-06-22 09:00 | 200 | 0 |  | 2005-06-22 09:00 |  | -- | 900 Block Palmetto | PACIFICA | SAN MATEO | 94044 |  |  | 2005-02-25 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pacifica | CLEAN OUT |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | ASST SUPERINTENDENT | BRIAN MARTINEZ | 2005-03-09 | 650 738 4669 | chenm@ci.pacifica.ca.us, holmess@ci.pacifica.ca.us | MINOR
911 | 3 | 1 | Pacifica | 2005-01-25 07:49 | 520 | 0 |  | 2005-01-25 07:49 |  | -- | GRAND AVE | PACIFICA | SAN MATEO | 94044 |  |  | 2005-01-21 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pacifica | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | ASST. SUPERINTENDENT | BRIAN MARTINEZ | 2005-01-25 | 650 738 4669 | chenm@ci.pacifica.ca.us | MINOR
909 | 2 | 1 | Pacifica | 2005-01-25 07:45 | 350 | 0 |  | 2005-01-25 07:45 |  | -- | 7 HOLIDAY CT. | PACIFICA | SAN MATEO | 94044 |  |  | 2005-01-16 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pacifica | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | ASST. SUPERINTENDENT | BRIAN MARTINEZ | 2005-01-25 | 650 738 4669 | chenm@ci.pacifica.ca.us | MINOR
757 | 1 | 1 | Pacifica | 2005-01-05 08:10 | 300000 | 0 | 04-6856 | 2004-12-28 | Ming Chen | Ming Chen | 495 Linda Mar Blvd.(Linda Mar pump station). | Pacifica | San Mateo | 94044 |  |  | 2004-12-27 | 3:00:00 PM | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | Yes | Closed the entire Linda Mar Beach. | No | Yes | Some grease along the shore line. |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | pacifica | PUMP STATION | We had approximately 5” of rain fall during the storm, all within roughly a12 hour period. This amount was reported by the National Weather service correspondent to Pacifica.All incoming flows were being pumped to Treatment facility until around 4:00pm when it became apparent that the plant could not keep up with the rate of flow being pumped from lift stations. At this point we reduced the flow being pumped to the plant and began to bypass at the Linda Mar Pump station. If we did not perform this bypass we feel we would have lost all treatment capabilities at Calera Creek. | BYPASS | --Select None-- | --Select None-- |  | We had approximately 5” of rain fall during the storm, all within roughly a12 hour period. This amount was reported by the National Weather service correspondent to Pacifica. All incoming flows were being pumped to Treatment facility until around 4:00pm when it became apparent that the plant could not keep up with the rate of flow being pumped from lift stations. At this point we reduced the flow being pumped to the plant and began to bypass at the Linda Mar Pump station. If we did not perform this bypass we feel we would have lost all treatment capabilities at Calera Creek. | Utilities Manager | Ming Chen | 2005-01-05 | 650 738-4668 | chenm@ci.pacifica.ca.us | MAJOR | Ming Chen | Pacifica | 650 738-4668 |  | 170 Santa Maria Ave. | Pacifica | San Mateo | 94044 |  | City of Pacifica | 650 738-4668 |  | 170 Santa Maria Ave. | Pacifica | San Mateo | 94044
4907 | 11 | 1 | PaloAltoCity | 2007-03-13 08:51 | 204 | 0 |  | 2007-03-13 08:51 |  | -- | 324 Alma - Intersection of Alma@Everett | Palo Alto | Santa Clara | 94302 |  |  | 2007-03-03 |  |  |  | Operator could not determine the cause of blockage. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Supervisor Wastewate | Michael Haynes | 2007-03-13 | 650-496-6917
4295 | 10 | 1 | PaloAltoCity | 2006-12-13 08:51 | 250 | 0 |  | 2006-12-13 08:51 |  | -- | 3170 Porter Dr. | Palo Alto | Santa Clara | 94305 |  |  | 2006-12-12 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | CAUSE UNKNOWN | -- Select One -- |  |  |  | Supv. Wastewater Col | Michael Haynes | 2006-12-13 | 605-496-6917
4166 | 9 | 1 | PaloAltoCity | 2006-11-29 10:04 | 345 | 0 |  | 2006-11-29 10:04 |  | -- | 675 El Camino Real | Palo Alto | Santa Clara | 94303 |  |  | 2006-11-28 |  |  |  | Spill caused by grease originating from the Westin Hotel. Responding crew was able to collect 50 gallons. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supv. Wastewater Col | Michael Haynes | 2006-11-29 | 650-496-6917
4017 | 8 | 1 | PaloAltoCity | 2006-10-23 13:30 | 125 | 0 |  | 2006-10-23 13:30 |  | -- | 1748 Channing Ave Palo Alto, CA | Palo Alto | Santa Clara | 94303 |  |  | 2006-10-20 |  |  |  | call recieved at 5:31pm crew arrived at 6:21pm & contained the spill. mainline stoppage cleared at 6:40pm | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | PaloAltoCity | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Supv. Wastewater Col | Michael Haynes | 2006-10-23 | 650-496-6917 | javad.ghaffari@cityofpaloalto.org, Michael.haynes@cityofpaloalto.org | MINOR
3807 | 7 | 1 | PaloAltoCity | 2006-08-28 11:33 | 250 | 0 |  | 2006-08-28 11:33 |  | -- | 200 Block Alma Street | Palo Alto | Santa Clara | 94302 |  |  | 2006-07-15 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | PaloAltoCity | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor Wastewate | Michael Haynes | 2006-08-28 | (650) 496-6917 | javad.ghaffari@cityofpaloalto.org, Michael.haynes@cityofpaloalto.org | MINOR
2770 | 5 | 1 | PaloAltoCity | 2006-02-07 11:02 | 660 | 0 |  | 2006-02-07 11:02 |  | -- | Intersection of Ash & Portage - manhole# 049-6-1 | Palo Alto | Santa Clara | 94302 |  |  | 2006-02-03 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | PaloAltoCity | MANHOLE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Supv. Wastewater Col | Michael Haynes | 2006-02-07 | 650-496-6917 | javad.ghaffari@cityofpaloalto.org, Michael.haynes@cityofpaloalto.org | MINOR
2696 | 4 | 1 | PaloAltoCity | 2006-01-30 07:37 | 150 | 0 |  | 2006-01-30 07:37 |  | -- | 742 Melville | Palo Alto | Santa Clara | 94301 |  |  | 2006-01-28 |  |  |  | Cleanout @ 742 Melville overflowed due to a blockage in the mainline. Grease and debris was the cause of the blockage. The stoppage may have been the result of a contracted cleaning crew not vacuuming the debris from the manhole. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | PaloAltoCity | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | Supv. Wastewater Col | Michael Haynes | 2006-01-02 | 650-496-6917 | javad.ghaffari@cityofpaloalto.org, Michael.haynes@cityofpaloalto.org | MINOR
2337 | 3 | 1 | PaloAltoCity | 2005-12-27 12:15 | 600 | 0 |  | 2005-12-27 12:15 |  | -- | Palo Alto Foothills - Arastradero Preserve Palo Alto, CA | Palo Alto | Santa Clara | 94302 |  |  | 2005-12-24 |  |  |  | Spilled saturated soil in a wooded area in Arastra Preserve. Pump stations were turned off to work on the blocked manhole. | [5 empty] | NO WATER INVOLVED | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | PaloAltoCity | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supv. Wastewater Col | Michael Haynes | 2005-12-27 | 650-496-6917 | javad.ghaffari@cityofpaloalto.org, Michael.haynes@cityofpaloalto.org | MINOR
3004 | 6 | 1 | PaloAltoCity | 2006-03-14 14:58 | 600 | 0 |  | 2006-03-14 14:58 |  | -- | Arastadero Preserve | Palo Alto | Santa Clara | 94301 |  |  | 2005-12-24 |  |  |  | During the compiling of our sewer over flow data for the 2005 Annual Report, we noticed an incident that was not reported to the Regional Board within ten days of the date of the incident. On December 24, 2005, the weekend of Christmas holiday, the City of Palo Alto’s emergency standby crew received a call from Utilities dispatch to respond to an overflow in the City of Palo Alto’s Arastradero Preserve. Upon arrival, the responding crew discovered sewage overflowing from a manhole. The overflowing manhole is located on a force mainline which is pumped from a sanitary sewer lift station. SCADA information shows that the lift station pump had run for 2.7 minutes at approximately 222gpm. The approximate overflow was 600 gallons. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | PaloAltoCity | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor - Wastewa | Michael Haynes | 2005-12-24 | 650-496-6917 | javad.ghaffari@cityofpaloalto.org, Michael.haynes@cityofpaloalto.org | MINOR
2045 | 2 | 1 | PaloAltoCity | 2005-10-27 09:01 | 300 | 0 |  | 2005-10-27 09:01 |  | -- | 3350 Hanover Street, | Palo Alto | Santa Clara | 94302 |  |  | 2005-10-26 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | PaloAltoCity | MANHOLE | # 61-6-3 | BLOCKAGE | ROOTS |  |  |  | Supv. Wastewater Col | Michael Haynes | 2005-10-27 | (650) 496-6917 | javad.ghaffari@cityofpaloalto.org, Michael.haynes@cityofpaloalto.org | MINOR
1988 | 1 | 2 | PaloAltoCity | 2005-10-20 11:01 | 0 | 0 |  | 2005-10-20 11:01 |  | -- |  | Palo Alto | San Mateo | 94010 |  |  | 2005-10-19 |  |  |  | This is a test report only. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | PaloAltoCity | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | MMM | Michael Haynes | 2005-10-19 | 650-496-6917 | javad.ghaffari@cityofpaloalto.org, Michael.haynes@cityofpaloalto.org | MINOR
3156 | 25 | 1 | Petaluma | 2006-04-12 14:10 | 2400 | 0 | 06-2213 | 2006-04-12 | Imad Baiyasi | Petaluma | 1 st Street and H Street | Petaluma | Sonoma | 94952 |  |  | 2006-04-11 | 4:00:00 PM | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | Yes | Yes, no apparent problem noticed |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Associate Engineer | Imad Baiyasi | 2006-04-12 | 707-778-4582 | mban@ci.petaluma.ca.us, | MAJOR | Imad Baiyasi | Petaluma | 707-778-4582 |  | 202 N. McDowell Blvd. | Petaluma | Sonoma | 94954 |  | City of Petaluma
3157 | 26 | 1 | Petaluma | 2006-04-12 14:17 | 9000 | 0 | 06-2214 | 2006-04-12 | Imad Baiyasi | Petaluma | 831 Petaluma Blvd. South | Petaluma | Sonoma | 94952 |  |  | 2006-04-11 | 4:00:00 PM | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | Yes | Yes, no apparent problem noticed. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Associate Engineer | Imad Baiyasi | 2006-04-12 | 707-778-4582 | mban@ci.petaluma.ca.us, | MAJOR | Imad Baiyasi | Petaluma | 707-778-4582 |  | 202 N. McDowell | Petaluma | Sonoma | 94954 |  | Petaluma
2984 | 24 | 2 | Petaluma | 2006-03-10 16:36 | 7200 | 0 | 06-1247 | 2006-02-28 | Imad Baiyasi | Petaluma | 845 Petaluma Blvd. South | Petaluma | Sonoma | 94052 |  |  | 2006-02-27 | 8:00:00 AM | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | No | Yes, no apparent problem observed |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Associate Engineer | Imad Baiyasi | 2006-02-28 | 707-778-4582 | mban@ci.petaluma.ca.us, | MAJOR | Imad Baiyasi | City of Petaluma | 707-778-4582 |  | 202 N. McDowell Blvd. | Petaluma | Sonoma | 94054 |  | Petaluma
2985 | 23 | 2 | Petaluma | 2006-03-10 16:39 | 3000 | 0 | 06-1246 | 2006-02-28 | Imad Baiyasi | Petaluma | 1st. Street and H Street | Petaluma | sonoma | 94952 |  |  | 2006-02-27 | 8:30:00 AM | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | No | Yes, no apparent problem observed |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Associate Engineer | Imad Baiyasi | 2006-02-28 | 707-778-4582 | mban@ci.petaluma.ca.us, | MAJOR | Imad Baiyasi | City of Petaluma | 707-778-4582 |  | 202 N. McDowell Blvd. | Petaluma | Sonoma | 94954 |  | Petaluma
2986 | 22 | 2 | Petaluma | 2006-03-10 16:42 | 1500 | 0 | 06-1245 | 2006-02-28 | Imad Baiyasi | Petaluma | 1 st. Street and F Street | Petaluma | Sonoma | 94952 |  |  | 2006-02-27 | 8:30:00 AM | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | No | Yes, no apparent problem observed |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Associate Engineerur | Imad Baiyasi | 2006-02-28 | 707-778-4582 | mban@ci.petaluma.ca.us, | MAJOR | Imad Baiyasi | City of Petaluma | 707-778-4582 |  | 202 N. McDowell Blvd. | Petaluma | Sonoma | 94954 |  | Petaluma
3014 | 21 | 3 | Petaluma | 2006-03-16 15:27 | 15000 | 1000 | 06-0732 | 2006-02-03 | Imad Baiyasi | Petaluma | 260 Water Street North | Petaluma | Sonoma | 94952 |  |  | 2006-02-02 | 2:30:00 PM | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | Yes | No apparent effect noticed |  | Yes | Yes | No | No | No | Yes | No | Yes | No | 2006-03-16 | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Petaluma | MANHOLE |  | ELECTRICAL POWER FAILURE | --Select None-- | --Select None-- |  |  | Environmental Civil | Imad Baiyas | 2006-02-03 | 707-778-4582 | mban@ci.petaluma.ca.us, | MAJOR | Imad Baiyasi | City of Petaluma | 707-778-4582 |  | 202 N. mcDowell Blvd. | Petaluma | Sonoma | 94954 |  | Petaluma |  |  |  | Petaluma | Sonoma
2565 | 12 | 1 | Petaluma | 2006-01-06 16:00 | 2400 | 0 | 06-0100 | 2006-01-03 | Bill Spaulding | Imad Baiyasi | 1 st and H Steet | Petaluma | Sonoma | 94052 |  |  | 2006-01-02 | 10:30:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | Yes | Yes, no apparent problem |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Engineer | Imad Baiyasi | 2006-01-06 | 707-778-4582 | mban@ci.petaluma.ca.us, | MAJOR | Imad Baiyasi | Petaluma | 707-778-4582 |  | 202 N. McDowell | Petaluma | Sonoma | 94054 |  | Petaluma
2566 | 13 | 1 | Petaluma | 2006-01-06 16:05 | 7500 | 0 | 06-0101 | 2006-01-03 | Bill Spaulding | Imad Baiyasi | 825 Petaluma Blvd South | Petaluma | Sonoma | 94952 |  |  | 2006-01-02 | 10:30:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Low | Petaluma River | STORM DRAIN | No |  | No | Yes | No apparent problem |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Engineer | Imad Baiyasi | 2006-01-06 | 707-778-4582 | mban@ci.petaluma.ca.us, | MAJOR | Imad Baiyasi | Petaluma | 707-778-4582 |  | 202 N McDowell | Petaluma | Sonoma | 94054 |  | Petaluma
2569 | 16 | 1 | Petaluma | 2006-01-06 16:26 | 24000 | 0 | 06-0013 | 2006-01-01 | Bill Spaulding | Imad Baiyasi | 226 Weller Street | Petaluma | Sonoma | 94952 |  |  | 2005-12-31 | 5:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low | Petaluma River | STORM DRAIN | No |  | No | Yes | yes, no apparent problem |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Engineer | Imad Baiyasi | 2006-01-06 | 707-778-4582 | mban@ci.petaluma.ca.us, | MAJOR | Imad Baiyasi | Petaluma | 707-778-4582 |  | 202 N McDowell | Petaluma | Sonoma | 94054 |  | Petaluma
2564 | 11 | 1 | Petaluma | 2006-01-06 15:53 | 3500 | 0 | 06-0013 | 2006-01-01 | Bill Spaulding | Imad Baiyasi | 12 C Street | Petaluma | Sonoma | 94952 |  |  | 2005-12-30 | 8:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | Yes | Yes, no apparent problem |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Associate Engineer | Imad Baiyasi | 2006-01-06 | 707-778-4582 | mban@ci.petaluma.ca.us, | MAJOR | Imad Baiyasi | Petaluma | 707-778-4582 |  | 202 N McDowell | Petaluma | Sonoma | 94054 |  | City of Petaluma
2567 | 14 | 1 | Petaluma | 2006-01-06 16:14 | 38000 | 0 | 06-0013 | 2006-01-01 | Bill Spaulding | Petaluma | 825 Petaluma Blvd South | Petaluma | Sonoma | 94952 |  |  | 2005-12-30 | 8:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low | Petaluma River | STORM DRAIN | No |  | Yes | Yes | No apparent problem |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Engineer | Imad Baiyasi | 2006-01-06 | 707-778-4582 | mban@ci.petaluma.ca.us, | MAJOR | Imad Baiyasi | Petaluma | 707-778-4582 |  | 202 N. McDowell | Petaluma | Sonoma | 94954 |  | Petaluma
2568 | 15 | 1 | Petaluma | 2006-01-06 16:20 | 19000 | 0 | 06-0013 | 2006-01-01 | Bill Spaulding | Imad Baiyasi | Petaluma Blvd South and MT. View | Petaluma | Sonoma | 94952 |  |  | 2005-12-30 | 8:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | Yes | Yes, no apparent problem |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Enginner | Imad Baiyasi | 2006-01-06 | 707-778-4582 | mban@ci.petaluma.ca.us, | MAJOR | Imad Baiyasi | Petaluma | 707-778-4582 |  | 202 N. McDowell | Petaluma | Sonoma | 94954 |  | Petaluma
2570 | 17 | 1 | Petaluma | 2006-01-06 16:32 | 16800 | 0 | 06-0013 | 2006-01-01 | Bill Spaulding | Imad Baiyasi | 10 Post Street | Petaluma | Sonoma | 94952 |  |  | 2005-12-30 | 8:00:00 PM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | Yes | Yes, no apparent problem |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Engineer | Imad Baiyasi | 2006-01-06 | 707-778-4582 | mban@ci.petaluma.ca.us, | MAJOR | Imad Baiyasi | Petaluma | 707-778-4582 |  | 202 n. McDowell | Petaluma | Sonoma | 94954 |  | Petaluma
2572 | 18 | 1 | Petaluma | 2006-01-06 16:38 | 16800 | 0 | 06-0013 | 2006-01-01 | Imad Baiyasi | Imad Baiyasi | Post Steet and B Street | Petaluma | Sonoma | 94952 |  |  | 2005-12-30 | 8:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | Yes | Yes, no apparent problem |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Engineer | Imad Baiyasi | 2006-01-06 | 707-778-4582 | mban@ci.petaluma.ca.us, | MAJOR | Imad Baiyasi | Petaluma | 707-778-4582 |  | 202 N. McDowell | Petaluma | Sonoma | 94952 |  | Petaluma
2573 | 19 | 1 | Petaluma | 2006-01-06 16:43 | 12600 | 0 | 06-0013 | 2006-01-01 | Imad Baiyasi | Imad Baiyasi | 1 st Steet and H Street | Petaluma | Sonoma | 94952 |  |  | 2005-12-30 | 7:00:00 PM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | Yes | Yes | Yes, no apparent problem |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Engineer | Imad Baiyasi | 2006-01-06 | 707-778-4582 | mban@ci.petaluma.ca.us, | MAJOR | Imad Baiyasi | Petaluma | 707-778-4582 |  | 202 N. McDowell | Petaluma | Sonoma | 94952 |  | Petaluma
2574 | 20 | 1 | Petaluma | 2006-01-06 16:51 | 12600 | 0 | 06-0013 | 2006-01-01 | Imad Baiyasi | Imad Baiyasi | 1 st Street and F Street | Petaluma | Sonoma | 94952 |  |  | 2005-12-30 | 7:00:00 PM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | Yes | Yes, no apparent problem |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Engineer | Imad Baiyasi | 2006-01-06 | 707-778-4582 | mban@ci.petaluma.ca.us, | MAJOR | Imad Baiyasi | Petaluma | 707-778-4582 |  | 202 N. McDowell | Petaluma | Sonoma | 94952 |  | Petaluma
2355 | 6 | 1 | Petaluma | 2005-12-28 15:47 | 9600 | 300 | 05-7490 | 2005-12-28 | Bill Spaulding | Imad Baiyasi | 825 Petaluma BLVD South | Petaluma | Sonoma | 94952 |  |  | 2005-12-28 | 8:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low | Petaluma River | STORM DRAIN | No |  | No | Yes | Yes, no apparent problem |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Associate Civil Engi | Imad Baiyasi | 2005-12-28 | 707-778-4582 | mban@ci.petaluma.ca.us, | MAJOR | Imad Baiyasi | Petaluma | 707-778-4582 |  | 202 North McDowell Blvd | Petaluma | Sonoma | 94954 |  | City of Petaluma
2356 | 7 | 1 | Petaluma | 2005-12-28 15:56 | 2700 | 0 | 05-7494 | 2005-12-28 | Bill Spaulding | Imad Baiyasi | Post Street and B Street | Petaluma | Sonoma | 94952 |  |  | 2005-12-28 | 8:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low | Petaluma River | STORM DRAIN | No |  | No | Yes | Yes, no apparent problem |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Associate Engineer | Imad Baiyasi | 2005-12-28 | 707-778-4582 | mban@ci.petaluma.ca.us, | MAJOR | Imad Baiyasi | Petaluma | 707-778-4582 |  | 202 N. McDowell Blvd | Petaluma | Sonoma | 94954 |  | Petaluma
2357 | 8 | 1 | Petaluma | 2005-12-28 16:02 | 2700 | 0 | 5-7495 | 2005-12-28 | Bill Spaulding | Imad Baiyasi | 10 Post Street | Petaluma | Sonoma | 94952 |  |  | 2005-12-28 | 8:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low | Petaluma River | STORM DRAIN | No |  | No | Yes | Yes, no apparent problem |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Associate Engineer | Imad Baiyasi | 2005-12-28 | 707-778-4582 | mban@ci.petaluma.ca.us, | MAJOR | Imad Baiyasi | Petaluma | 707-778-4582 |  | 202 N. McDowell Blvd | Petaluma | Sonoma | 94954 |  | City of Petaluma
2358 | 9 | 1 | Petaluma | 2005-12-28 16:09 | 7200 | 0 | 05-7492 | 2005-12-28 | Bill Spaulding | Imad Baiyasi | 1 st Street and H Street | Petaluma | Sonoma | 94952 |  |  | 2005-12-28 | 8:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low | Petaluma River | STORM DRAIN | No |  | No | Yes | Yes, no apparent problem |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Associate Engineer | Imad Baiyasi | 2005-12-28 | 707-778-45482 | mban@ci.petaluma.ca.us, | MAJOR | Imad Baiyasi | Petaluma | 707-778-4582 |  | 202 N. McDowell | Petaluma | Sonoma | 94954 |  | Petaluma
2362 | 10 | 2 | Petaluma | 2005-12-28 16:21 | 300 | 0 |  | 2005-12-28 16:21 |  | -- | Mt. View and Petaluma Blvd. South | Petaluma | Sonoma | 94952 |  |  | 2005-12-28 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | Associate Engineer | Imad Baiyasi | 2005-12-28 | 707-778-4582 | mban@ci.petaluma.ca.us, | MINOR
1110 | 5 | 1 | Petaluma | 2005-03-03 16:06 | 585 | 0 |  | 2005-03-03 16:06 |  | -- | Hill Drive | Petaluma | Sonoma | 94952 |  |  | 2005-02-26 |  |  |  | Collapsed sewer main on Hill Drive. Reparis began on 2/27/05. Very small amount of overflow in heavy rain. Directed back to sewer at 8:00 AM on 2/28/05. Replacement of entire pipe is underway. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Petaluma | OTHER | Collapsed main | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Associate Engineer | Imad Baiyasi | 2005-03-03 | 707-778-4582 | mban@ci.petaluma.ca.us, | MINOR
1084 | 4 | 1 | Petaluma | 2005-02-25 09:08 | 563 | 0 |  | 2005-02-25 09:08 |  | -- | 1298 McGreger Road | Petaluma | Sonoma | 94054 |  |  | 2005-02-18 |  |  |  | Spill form 8:45 AM to 10:00 AM. No recovery. Weather rainy. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Petaluma | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Engineer | Imad Baiyasi | 2005-02-25 | 707-778-4582 | ibaiyasi@ci.petaluma.ca.us | MINOR
687 | 3 | 1 | Petaluma | 2004-12-29 15:35 | 500 | 0 |  | 2004-12-29 15:35 |  | -- | G Street and 7th | Petaluma | Sonoma | 94952 |  |  | 2004-12-27 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Petaluma | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Associate Engineer | Imad Baiyasi | 2004-12-29 | 707-778-4582 | mban@ci.petaluma.ca.us | MINOR
709 | 2 | 2 | Petaluma | 2005-01-03 12:09 | 5400 | 0 | 04-6831 | 2004-12-29 | Water Dept. | Petaluma | Petaluma Blvd. South and Mountain View | Petaluma | Sonama | 94952 |  |  | 2004-12-27 | 9:00:00 AM | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | No | No noticable impact |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Associate Engineer | Imad Baiyasi | 2004-12-29 | 707-778-4582 | mban@ci.petaluma.ca.us | MAJOR | Imad Baiyasi | Petaluma | 707-778-4582 |  | 11 English Street | Petaluma | Sonoma | 94952 |  | City of Petaluma
710 | 1 | 2 | Petaluma | 2005-01-03 12:09 | 7800 | 0 | 04-6830 | 2004-12-29 | Water Dept. | Petaluma | 1st Street and H Street | Petaluma | Sonoma | 94952 |  |  | 2004-12-27 | 9:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | No noticable impact |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | Petaluma | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Assiciate Engineer | Imad Baiyasi | 2004-12-29 | 707-778-4582 | mban@ci.petaluma.ca.us | MAJOR | Imad Baiyasi | Petaluma | 707-778-4582 |  | 11 English St. | Petaluma | Sonoma | 94952 |  | City of Petaluma
4899 | 28 | 1 | Piedmont | 2007-03-12 11:00 | 245 | 0 |  | 2007-03-12 11:00 |  | -- | 201 Highland Avenue | Piedmont | Alameda | 94611 |  |  | 2007-03-09 |  |  |  | Blockage was caused by roots and debris. The spill was contained and cleaned up. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Mrs. | Christina Acosta | 2007-03-12 | 510-420-3050
4709 | 26 | 1 | Piedmont | 2007-02-08 | 1680 | 0 | 07-0886 | 2007-02-08 | Angelo Espinosa | Piedmont | 187 St James Drive | Piedmont | Alameda | 94611 |  |  | 2007-02-07 | 0.25 | [6 empty] | Low | St James Creek | YARD/LAND | No |  | No | No | Sewage in creek water |  | Yes | Yes | No |  |  | Yes | No |  |  | 2007-02-08 | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | PIPE |  | INFRASTRUCTURE FAILURE | -- Select One -- | DAMAGE TO COLLECTION SYSTEM |  |  | Ms | Christina Acosta | 2007-02-08 | 510-420-3050
4650 | 25 | 1 | Piedmont | 2007-02-01 11:02 | 150 | 0 |  | 2007-02-01 11:02 |  | -- | 131 La Salle | Piedmont | Alameda | 94610 |  |  | 2007-02-01 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Ms | Christina Acosta | 2007-02-01 | 510-420-3050
4548 | 24 | 1 | Piedmont | 2007-01-18 09:51 | 500 | 0 |  | 2007-01-18 09:51 |  | -- | 1080 Harvard Road | Piedmont | Alameda | 94610 |  |  | 2007-01-17 | [9 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | BLOCKAGE | -- Select One -- |  | c.o. (Clean Out) |  | Ms. | Christina Acosta | 2007-01-18 | 510-420-3050
4366 | 23 | 1 | Piedmont | 2006-12-18 13:46 | 200 | 0 |  | 2006-12-18 13:46 |  | -- | 337 Wildwood Avenue | Piedmont | Alameda | 94611 |  |  | 2006-12-16 |  |  |  | Spill contained and cleaned up on front yard area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Ms. | Christina Acosta | 2006-12-18 | 510-650-3060
4302 | 22 | 1 | Piedmont | 2006-12-13 13:32 | 450 | 0 |  | 2006-12-13 13:32 |  | -- | 61 Glen Alpine | Piedmont | Alameda | 94611 |  |  | 2006-12-12 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Ms | Christina Acosta | 2006-12-13 | 510-420-3060
4300 | 21 | 1 | Piedmont | 2006-12-13 | 13500 | 0 | 067364 | 2006-12-13 | Angelo Espinosa | Piedmont | 2 Mesa Avenue/Moraga Avenue | Piedmont | Alameda | 94611 |  |  | 2006-12-12 | 0.42014 | [6 empty] | Low |  | STORM DRAIN | No |  | No | No | Unknown Location |  | Yes | No | No |  |  | No | No |  |  | 2006-12-13 | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | INFLOW & INFILTRATION | -- Select One -- | -- Select One -- |  |  | Ms | Christina Acosta | 2006-12-13 | 510-420-3063
4044 | 20 | 1 | Piedmont | 2006-10-31 15:42 | 125 | 0 |  | 2006-10-31 15:42 |  | -- | 241 Park View Avenue | Piedmont | Alameda | 94610 |  |  | 2006-10-31 |  |  |  | Blockage also caused by debris. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Piedmont | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Assistant Planner | Kevin Jackson | 2006-10-31 | 510-420-3039 | vregalado@ci.piedmont.ca.us, lrosenberg@ci.piedmont.ca.us | MINOR
4010 | 19 | 1 | Piedmont | 2006-10-19 11:11 | 10 | 0 |  | 2006-10-19 11:11 |  | -- | 145 Lexford Road | Piedmont | Alameda | 94611 |  |  | 2006-10-18 |  |  |  | Sewer overflowed out of a city cleanout downhill through ivy and back into a city manhole located about 10 Feet below over-flowing cleanout. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Piedmont | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Planning Consultant | Christina Acosta | 2006-10-19 | 510-420-3050 | vregalado@ci.piedmont.ca.us, lrosenberg@ci.piedmont.ca.us | MINOR
3809 | 18 | 1 | Piedmont | 2006-08-28 15:28 | 240 | 0 |  | 2006-08-28 15:28 |  | -- | 1067 Ranleigh Way | Piedmont | Alameda | 94610 |  |  | 2006-08-27 | [9 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Piedmont | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Assistant Planner | Kevin Jackson | 2006-08-28 | 5104203039 | vregalado@ci.piedmont.ca.us, lrosenberg@ci.piedmont.ca.us | MINOR
3668 | 17 | 1 | Piedmont | 2006-07-26 13:30 | 5 | 0 |  | 2006-07-26 13:30 |  | -- | 22 Monte Ave | Piedmont | Alameda | 94611 |  |  | 2006-07-23 |  |  |  | Emergency call back. Serviced city main line VCP 6 inch sanitary main line with hydro flusher 4 inch root saw. Ran 250 feet upstream from manhole #400, 58 to CO #06. Hit blockage at 200 feet. Cleared away roots. Will follow up with a video inspection. Weather Dry. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Piedmont | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Assistant Planner | Kevin Jackson | 2006-07-26 | 510-420-3039 | vregalado@ci.piedmont.ca.us, lrosenberg@ci.piedmont.ca.us | MINOR
3478 | 16 | 1 | Piedmont | 2006-06-09 14:06 | 400 | 0 |  | 2006-06-09 14:06 |  | -- | 201 Wildwood Avenue | Piedmont | Alameda | 94610 |  |  | 2006-06-09 |  |  |  | Sewer blockage caused by roots, rock and mud. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Piedmont | OTHER | GROUND | BLOCKAGE | ROOTS |  |  |  | Planning Assistant | Kevin Jackson | 2006-06-09 | 510-420-3039 | vregalado@ci.piedmont.ca.us, lrosenberg@ci.piedmont.ca.us | MINOR
3047 | 15 | 1 | Piedmont | 2006-03-22 16:53 | 5 | 0 |  | 2006-03-22 16:53 |  | -- | 3 Abbott Way | Piedmont | Alameda | 94618 |  |  | 2006-03-22 |  |  |  | SSO occurs only when toilet is flushed. Contained, removed and disposed of solid waste. Grey water dissipated into surrounding soil. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Piedmont | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Assistant Planner | Kevin Jackson | 2006-03-22 | 510-420-3050 | vregalado@ci.piedmont.ca.us, lrosenberg@ci.piedmont.ca.us | MINOR
2927 | 14 | 1 | Piedmont | 2006-03-03 10:40 | 450 | 0 |  | 2006-03-03 10:40 |  | -- | 147 Greenbank Avenue | Piedmont | Alameda | 94611 |  |  | 2006-03-03 | [9 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Piedmont | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Planning Technician | Sharon Lai | 2006-03-03 | 510-420-3067 | vregalado@ci.piedmont.ca.us, lrosenberg@ci.piedmont.ca.us | MINOR
2929 | 13 | 2 | Piedmont | 2006-03-03 11:38 | 3 | 0 |  | 2006-03-03 11:38 |  | -- | 6 Littlewood Drive | Piedmont | Alameda | 94611 |  |  | 2006-02-26 |  |  |  | When arrived at job site opened manhole sewer level was about 2" from the top. No sewer was coming out of manhole aponarrival. Looks like it just bouble out. Partial Blockage. Small amount of sewer was around manhole and on the side walk. No sewer went into stormdrain contained small amount of spill clened up and put away into trash bag. | [5 empty] | NO WATER INVOLVED | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Piedmont | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Planning Technician | Sharon Lai | 2006-03-01 | 510-540-3067 | vregalado@ci.piedmont.ca.us, lrosenberg@ci.piedmont.ca.us | MINOR
4725 | 27 | 1 | Piedmont | 2007-02-09 16:24 | 20 | 0 |  | 2007-02-09 16:24 |  | -- | 38 Portsmouth Road | Piedmont | Alameda | 94610 |  |  | 2006-02-21 |  |  |  | Roots and Debris were the cause of the partial blockage in City main line. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | BLOCKAGE | ROOTS |  | ground |  | Ms | Christina Acosta | 2007-02-09 | 510-420-3050
2571 | 12 | 1 | Piedmont | 2006-01-06 16:35 | 1800 | 0 | 060186 | 2006-01-06 | Bill Higgins | Kevin Jackson | 61 Glen Alpine Road | Piedmont | Alameda | 94611 |  |  | 2006-01-06 | 10:30:00 A | [5 empty] | SUNNY WEATHER | High | Indian Gulch Creek | SURFACE WATER IMPACT | No |  | No | No | Unknown |  | Yes | Yes | No | No | No | No | No | No | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Piedmont | MANHOLE | Construction by City of Oakland on main uphill from site | BLOCKAGE | DEBRIS | --Select None-- |  |  | Assistant Planner | Kevin Jackson | 2006-01-06 | 510-420-3050 | vregalado@ci.piedmont.ca.us, lrosenberg@ci.piedmont.ca.us | MAJOR | Larry Rosenberg | City of Piedmont | 510-420-3050 |  | 120 Vista Avenue | Piedmont | Alameda | 94611 | Wayne Guidici | City of Oakland Public Works | 510-615-5985 |  | 7101 Edgewater Drive, Building 4 | Oakland | Alameda | 94621
2309 | 10 | 1 | Piedmont | 2005-12-23 10:57 | 900 | 0 |  | 2005-12-23 10:57 |  | -- | Mountain Avenue at Pacific Avenue | Piedmont | Alameda | 94611 |  |  | 2005-12-22 |  |  |  | Wet Weather & Rain | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Piedmont | MANHOLE |  | FLOW CAPACITY DEFICIENCY | --Select None-- |  |  |  | Mr. | Kevin Jackson | 2005-12-23 | 510-420-3050 | vregalado@ci.piedmont.ca.us, lrosenberg@ci.piedmont.ca.us | MINOR
2311 | 11 | 1 | Piedmont | 2005-12-23 11:01 | 850 | 0 |  | 2005-12-23 11:01 |  | -- | 144 Nova Drive | Piedmont | Alameda | 94610 |  |  | 2005-12-22 |  |  |  | Wet Weather & Rain | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Piedmont | MANHOLE |  | FLOW CAPACITY DEFICIENCY | --Select None-- |  |  |  | Mr. | Kevin Jackson | 2005-12-23 | 510-420-3050 | vregalado@ci.piedmont.ca.us, lrosenberg@ci.piedmont.ca.us | MINOR
2146 | 9 | 1 | Piedmont | 2005-11-21 09:27 | 50 | 0 |  | 2005-11-21 09:27 |  | -- | 711 Blair Avenue | Piedmont | Alameda | 94611 |  |  | 2005-11-20 |  |  |  | Broken pipe. Call back 7:00 PM. Crew Jerry Dias and Ray Haguisan follow up. Video tape City Main Line. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Piedmont | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Assistant Planner | Kevin Jackson | 2005-11-21 | 510-420-3050 | vregalado@ci.piedmont.ca.us, lrosenberg@ci.piedmont.ca.us | MINOR
2096 | 8 | 1 | Piedmont | 2005-11-09 09:29 | 400 | 0 |  | 2005-11-09 09:29 |  | -- | 1080 Harvard Road | Piedmont | Alameda | 94610 |  |  | 2005-11-07 |  |  |  | Hydro flusher, service line 6-inch root. Saw 8-inch sanitary City Main, TV Inspection at a later date. Call back at 10:00PM | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Piedmont | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Planning Technician | Elizabeth Watty | 2005-11-09 | 510-420-3050 | vregalado@ci.piedmont.ca.us, lrosenberg@ci.piedmont.ca.us | MINOR
2057 | 7 | 1 | Piedmont | 2005-10-28 11:39 | 200 | 0 |  | 2005-10-28 11:39 |  | -- | 48 Lake View Avenue | Piedmont | Alameda | 94611 |  |  | 2005-10-27 |  |  |  | Blockage unknown. Video Inspection of the City Main will be done as a follow up. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Piedmont | MANHOLE |  | CAUSE UNKNOWN | --Select None-- |  |  |  | Assistant Planner | Kevin Jackson | 2005-10-28 | 510-420-3039 | vregalado@ci.piedmont.ca.us, lrosenberg@ci.piedmont.ca.us | MINOR
2041 | 6 | 1 | Piedmont | 2005-10-26 15:28 | 400 | 0 |  | 2005-10-26 15:28 |  | -- | 178 Oak Road, back yard | Piedmont | Alameda | 94610 |  |  | 2005-10-16 |  |  |  | spill also caused by grease, debris, and debris from laterals | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Piedmont | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Assistant Planner | Kevin Jackson | 2005-10-26 | 510-420-3050 | vregalado@ci.piedmont.ca.us, lrosenberg@ci.piedmont.ca.us | MINOR
796 | 5 | 1 | Piedmont | 2005-01-10 09:42 | 850 | 0 |  | 2005-01-10 09:42 |  | -- | 26 Highland Avenue | Piedmont | Alameda | 94611 |  |  | 2005-01-08 |  |  |  | Weather wet. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Piedmont | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Mr. | Larry Rosenberg | 2005-01-10 | 510-420-3050 | lajello@ci.piedmont.ca.us | MINOR
787 | 4 | 1 | Piedmont | 2005-01-07 14:02 | 800 | 0 |  | 2005-01-07 14:02 |  | -- | 253 Sandringham Road | Piedmont | Alameda | 94611 |  |  | 2005-01-06 |  |  |  | Sewer leaked out of City main line to an underground PG&E vault (checked as building/structure above). Sewage was contained and recovered from the PG&E vault and pumped back into the sanitary sewer system. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Piedmont | PIPE |  | BLOCKAGE | ROOTS |  |  |  | Mr | Larry Rosenberg | 2005-01-07 | 510-420-3050 | lajello@ci.piedmont.ca.us | MINOR
742 | 3 | 2 | Piedmont | 2005-01-04 10:32 | 150 | 0 |  | 2005-01-04 10:32 |  | -- | 1145 Ranleigh Way | Piedmont | Alameda | 94610 |  |  | 2005-01-04 |  |  |  | Weather dry. Time of call reported at 8:30 am. Blow down time 9:40 am. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Piedmont | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Mr | Larry Rosenberg | 2005-01-04 | 510-420-3050 | lajello@ci.piedmont.ca.us | MINOR
458 | 2 | 1 | Piedmont | 2004-12-09 09:12 | 800 | 0 |  | 2004-12-09 09:12 |  | -- | 201 Hillside Avenue @ Blair Avenue | Piedmont | Alameda | 94611 |  |  | 2004-12-08 |  |  |  | Heavy rain contributed to this overflow. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Piedmont | MANHOLE |  | INFLOW & INFILTRATION | MULTIPLE CAUSES |  |  |  | Sr Maint Worker | Angelo Espinosa | 2004-12-09 | 510-420-3050 |  | MINOR
4073 | 5 | 1 | Pinole | 2006-11-06 14:30 | 300 | 0 |  | 2006-11-06 14:30 |  | -- | Hazel St Lift Station - Bottom of Hazel St | Pinole | Contra Costa | 94564 |  |  | 2006-11-03 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | pinole | PUMP STATION |  | ELECTRICAL POWER FAILURE | --Select None-- |  |  |  | Maint Super | Mark Adams | 2006-11-06 | 510 724-8949 | selfers@ci.pinole.ca.us, dallison@ci.pinole.ca.us | MINOR
4025 | 4 | 1 | Pinole | 2006-10-25 09:41 | 500 | 0 |  | 2006-10-25 09:41 |  | -- | Easement. Next to Railroad tracks from Pinole Shores Development. | Pinole | Contra Costa | 94564 |  |  | 2006-10-25 |  |  |  | Maintenance access has been limited due to construction. Access capabilities have been included in construction planning for near future. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | pinole | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Maint. Supervisor | Mark Adams | 2006-10-25 | 510-724-8949 | selfers@ci.pinole.ca.us, dallison@ci.pinole.ca.us | MINOR
3547 | 3 | 1 | Pinole | 2006-06-22 15:19 | 500 | 0 |  | 2006-06-22 15:19 |  | -- | 1879 Sara Dr | Pinole | Contra Costa | 94564 |  |  | 2006-05-30 |  |  |  | The of cause is under investigation. Will assume it was grease for the time being. Records indicate the line has had routine maintenance in the past year. This is an easement line that has no past history of SSOs. A TV inspection will be performed in the near future to determine if further maintenance or repairs are required. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pinole | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Mark Adams | 2006-06-22 | 510 724-8949 | selfers@ci.pinole.ca.us, dallison@ci.pinole.ca.us | MINOR
2398 | 2 | 1 | Pinole | 2005-12-31 15:05 | 3500 | 0 | 057590 | 2005-12-31 | Pinole | Pinole | Corner of Pinon & Bayview Farm Rd | Pinole | Conrta Costa | 94564 |  |  | 2005-12-31 | 12:30:00 P | [5 empty] | RAINING FOR SEVERAL DAYS | Medium | San Pablo Bay | STORM DRAIN | No |  | No | No | Slight murkiness in stormdrai flow. Flow moving extremely fast due to rains. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Pinole | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | Contanment was not possible due to heavy rains and stormdrain flow. This section of the system has had a history of surcharging during prolonged storms and has increased recently due to I&I. Measures have been taken to have an on-site overflow storage container and pump for this purpose. | Maintenance Supervis | Mark Adams | 2005-12-31 | 510 724-8949 | selfers@ci.pinole.ca.us, mbridges@ci.pinole.ca.us | MAJOR | Mark Adams | PinoleHercules | 510 724-8949 |  | 2131 Pear St | Pinole | Contra Costa | 94564 |  | City Of Pinole | 510 724-9010 |  | 2131 Pear St | Pinole | Contra Costa | 94564
2306 | 1 | 1 | Pinole | 2005-12-22 16:35 | 750 | 0 |  | 2005-12-22 | Mark Adams |  | The corner of Bayview Farm Rd & Pinon | Pinole | Contra Costa | 94564 |  |  | 2005-12-22 | 2:55:00 AM | 2005-12-22 | 3:05:00 AM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | PW Manager | Steve Elfers | 2005-12-22 | 510-724-9010 | selfers@ci.pinole.ca.us, mbridges@ci.pinole.ca.us | 24HR |  |  | 510 724-8949 | [6 empty] | Pinole
3439 | 7 | 1 | PittsburgCity | 2006-05-31 10:17 | 7 | 0 |  | 2006-05-31 10:17 |  | -- | 3702 Railroad Avenue | Pittsburg | Contra Costa | 94565 |  |  | 2006-05-30 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | PittsburgCity | PIPE |  | FLOW CAPACITY DEFICIENCY | --Select None-- |  |  |  | Acct. Tech. | Christy Seilhan | 2006-05-31 | 925-252-4001 | Wpease@ci.pittsburg.ca.us, jfuller@ci.pittsburg.ca.us | MINOR
3291 | 3 | 2 | PittsburgCity | 2006-05-04 09:03 | 100 | 0 |  | 2006-05-04 09:03 |  | -- | 79 Hillcrest | Pittsburg | Contra Costa | 94565 |  |  | 2006-04-08 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | PittsburgCity | PIPE |  | BLOCKAGE | ROOTS |  |  |  | Acct. Tech. | Christy Seilhan | 2006-05-04 | 925-252-4001 | Wpease@ci.pittsburg.ca.us, jfuller@ci.pittsburg.ca.us | MINOR
3279 | 2 | 1 | PittsburgCity | 2006-05-04 08:34 | 50 | 0 |  | 2006-05-04 08:34 |  | -- | 1625 Ronnie Street | Pittsburg | Contra Costa | 94565 |  |  | 2006-04-02 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | PittsburgCity | PIPE |  | BLOCKAGE | GREASE |  |  |  | Acct. Technician | Christy Seilhan | 2006-05-04 | 925-252-4001 | Wpease@ci.pittsburg.ca.us, jfuller@ci.pittsburg.ca.us | MINOR
3287 | 4 | 2 | PittsburgCity | 2006-05-04 09:02 | 25 | 0 |  | 2006-05-04 09:02 |  | -- | 4242 Hillview Drive | Pittsburg | Contra Costa | 94565 |  |  | 2006-04-02 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | PittsburgCity | PIPE |  | BLOCKAGE | DEBRIS |  |  |  | Acct. Tech. | Christy Seilhan | 2006-05-04 | 925-252-4001 | Wpease@ci.pittsburg.ca.us, jfuller@ci.pittsburg.ca.us | MINOR
3289 | 5 | 2 | PittsburgCity | 2006-05-04 09:02 | 5 | 0 |  | 2006-05-04 09:02 |  | -- | 33 Barrie | Pittsburg | Contra Costa | 94565 |  |  | 2006-04-02 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | PittsburgCity | PIPE |  | BLOCKAGE | GREASE |  |  |  | Acct. Tech | Christy Seilhan | 2006-05-04 | 925-252-4001 | Wpease@ci.pittsburg.ca.us, jfuller@ci.pittsburg.ca.us | MINOR
3053 | 1 | 1 | PittsburgCity | 2006-03-23 14:32 | 75 | 0 |  | 2006-03-23 14:32 |  | -- | 595 Carpino Ave / Vincent St | Pittsburg | Contra Costa | 94565 |  |  | 2006-03-20 |  |  |  | Line was dug up and repaired on 3/23/06. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | PittsburgCity | MANHOLE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Acct. Tech. | Christy Seilhan | 2006-03-23 | 925-252-4001 | Wpease@ci.pittsburg.ca.us, jfuller@ci.pittsburg.ca.us | MINOR
4286 | 6 | 3 | Pleasanton | 2006-12-09 | 2000 | 0 | 1-800-852-7550 | 2006-12-09 | Dan Martin | Pleasanton | 3302 Prairie Drive | Pleasanton | Alameda | 94566 |  |  | 2006-12-09 | 0.40278 | [6 empty] | Low | Alamo Canal | SURFACE WATER IMPACT | No |  | No | No | No solids escaped manhole. No visual evidence of a fish kill. Water flow rate in canal removed all signs of SSO. |  | Yes | Yes | No |  |  | No | No |  |  | 2006-12-15 | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | GREASE | -- Select One -- |  |  | Chief Utility Operator | Dan Martin | 2006-12-09 | 925-931-5523
3237 | 5 | 1 | Pleasanton | 2006-04-26 08:32 | 320 | 0 |  | 2006-04-26 08:32 |  | -- | 463 Cabonia Ct. (in the street) | Pleasanton | Alameda | 94566 |  |  | 2006-04-23 |  |  |  | A 3" X 18" pneumatic sewer plug was retrieved from the MH where the blockage was accessed. We don't use that size plug. The call came in at 2:48, the overflow was stopped at 3:20. Overflow rate was estimated at 10 gpm. The storm system was jetted and vacuumed. Follow up sanitary sewer system jetting and vacuuming was also done. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pleasanton | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Lead Utilities Opera | Ken Maxwell | 2006-04-26 | (925)931-5537 | kmaxwell@ci.pleasanton.ca.us | MINOR
2164 | 4 | 1 | Pleasanton | 2005-11-22 15:23 | 790 | 0 |  | 2005-11-22 15:23 |  | -- | Junipero St. @ Tomas Way | Pleasanton | Alameda | 94566 |  |  | 2005-11-21 |  |  |  | The overflow was reported at 8:00pm. The overflow was from 2 manholes totaling 10gpm for 75 minutes, and a third manhole flowed an additional 2gpm for 20 minutes. The blockage was relieved at 9:15pm. After the blockage was relieved the street and storm system was flushed with a water hydrant with a vacuum truck downstream to collect all the wash water. We re cleaned and TV inspected the sewer main at, and upstream from the blockage site. The sewer main will be added to our monthly bad spot cleaning list and the nearby businesses will be inspected by our Source Control Inspector. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pleasanton | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Utilities Lead Oper. | Ken Maxwell | 2005-11-22 | (925)931-5537 | kmaxwell@ci.pleasanton.ca.us, | MINOR
1948 | 3 | 1 | Pleasanton | 2005-10-11 11:43 | 260 | 0 |  | 2005-10-11 11:43 |  | -- | 11920 Dublin Canyon Road | Pleasanton | Alameda | 94588 |  |  | 2005-10-08 |  |  |  | No specific debris was observed at the time the blockage was relieved. Follow up TV inspection will happen later this week because our inspection system is in for repairs. The entire overflow was contained in a parking area and reclaimed using our Vacuum combination truck. The area was then washed and the wash water collected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pleasanton | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Utility Lead Op. | Ken Maxwell | 2005-10-11 | (925)931-5537 | kmaxwell@ci.pleasanton.ca.us, | MINOR
1278 | 2 | 1 | Pleasanton | 2005-04-12 14:08 | 200 | 0 |  | 2005-04-12 14:09 |  | -- | 372 Adams Way | Pleasanton | Alameda | 94566 |  |  | 2005-04-09 |  |  |  | Blockage occured in 6" VCP sewer main as a result of construction debris from the area and roots infiltrating the pipe joints. As a result of blockage, an overflow occured inside of the home at 372 Adams Wy. City crew responed to the site and unplugged sewer main with Jetter truck. The main has been flushed and debris vacuumed out. TV Inspection and root cutting is ongoing as of 4/12/05. Clean up inside of the home was conducted by a private contractor. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Pleasanton | PIPE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Chief Oper. | Jeff Ballou | 2005-04-12 | (925) 931-5521 | jballou@ci.pleasanton.ca.us, | MINOR
1116 | 1 | 1 | Pleasanton | 2005-03-04 14:30 | 300 | 0 |  | 2005-03-04 14:30 |  | -- | 5960 Sterling Greens Circle | Pleasanton | Alameda | 94566 |  |  | 2005-03-03 |  |  |  | An inverted sewer siphon at a new development plugged with construction debris (gravel) and overflowed at the system low manhole. The overflow flowed to a drain inlet then to a stormceptor at a rate of 5 GPM. Within 30 minutes we had the vacuum truck in place collecting the sewer water. After the blockage was removed we washed the street and collected the wash water and the water from the stormceptor. We also hyrocleaned the storm pipe and collected the waste water. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | pleasanton | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Lead Operator | Ken Maxwell | 2005-03-04 | (925)931-5537 | kmaxwell@ci.pleasanton.ca.us | MINOR
4046 | 1 | 1 | PortofSanFrancisco | 2006-10-31 15:48 | 500 | 0 |  | 2006-10-31 15:48 |  | -- | Pier 96 off Cargo Way | San Francisco | CA | 94124 |  |  | 2006-10-18 |  |  |  | Most of spill was pumped to vactor truck and discharged to downstream sewer manhole. Only a small amount reached the San Francisco Bay. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | PortofSanFrancisco | PUMP STATION |  | ELECTRICAL POWER FAILURE | --Select None-- |  |  |  | Utility Specialist | John Mundy | 2006-10-31 | 415.274.0256 | John.Mundy@sfport.com, tom.carter@sfport.com, dave.rauenbeuhler@sfport.com | MINOR
4048 | 2 | 1 | PortofSanFrancisco | 2006-10-31 15:53 | 500 | 0 |  | 2006-10-31 15:53 |  | -- | Pier 96 off Cargo Way | San Francisco | CA | 94124 |  |  | 2006-10-18 |  |  |  | Most of spill was pumped to vactor truck and discharged to downstream sewer manhole. Only a small amount reached the San Francisco Bay. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | PortofSanFrancisco | PUMP STATION |  | ELECTRICAL POWER FAILURE | --Select None-- |  |  |  | Utility Specialist | John Mundy | 2006-10-31 | 415.274.0256 | John.Mundy@sfport.com, tom.carter@sfport.com, dave.rauenbeuhler@sfport.com | MINOR
3665 | 3 | 1 | Presidiotrust | 2006-07-26 09:39 | 300 | 0 |  | 2006-07-26 09:39 |  | -- | 850 MacArthur Blvd. | San Francisco | San Francisco | 94129 |  |  | 2006-07-23 |  |  |  | The spill from the manhole entered a storm drain that dumps in a concrete lined ditch. The spill was contained in the ditch and cleaned up. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Presidiotrust | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Supervisor | A. Baird | 2006-07-26 | 4155614274 | abaird@presidiotrust.gov, Abaird@presidiotrust.gov | MINOR
3627 | 2 | 1 | Presidiotrust | 2006-07-18 07:57 | 10 | 0 |  | 2006-07-18 07:57 |  | -- | 1202 Ralston Ave | San Francisco | San Francisco | 94129 |  |  | 2006-07-18 |  |  |  | Manhole overflow reported by Presidio employee. Response time was 10 minutes. Crew reported a spill of less than 10 gallons. The line was cleared and a small amount of debris was found to be the cause and removed. The overflow was cleaned up with the vac-truck and never reached the storm drain or recieving waters. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Presidiotrust | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Supervisor | A. Baird | 2006-07-18 | 415-561-4274 | Abaird@presidiotrust.gov, Abaird@presidiotrust.gov | MINOR
2235 | 1 | 1 | Presidiotrust | 2005-12-09 13:53 | 300 | 0 |  | 2005-12-09 13:53 |  | -- | Mason Street 100 yards east of bldg. 937 on walking path. | San Francisco | San Francisco | 94129 |  |  | 2005-12-04 |  |  |  | Blockage was caused by debris from public restroom. Was contained in the area of the manhole and cleaned up with vac-truck. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Presidiotrust | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Supervisor | A. Baird | 2005-12-09 | 415-561-4274 | Abaird@presidiotrust.gov, Abaird@presidiotrust.gov | MINOR
5198 | 223 | 1 | Public | 2007-05-02 23:10 | 20 | 0 |  | 2007-05-02 23:10 |  | -- | 49 Corte Dorado | Benicia | Solano | 94510 |  |  | 2007-05-02 |  |  |  | The backup/overflow was confined to the concrete slab floor of the basement. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  |  | Drake Valentine | 2007-05-02 | (707) 746-4396
5011 | 220 | 1 | Public | 2007-03-27 10:36 | 450 | 0 |  | 2007-03-27 10:36 |  | -- | BADEN AVE. & LINDEN AVE. | SOUTH SAN FRANCISCO | SAN MATEO | 94080 |  |  | 2007-03-25 |  |  |  | RECOVERED 150 GAL. WITH SAND BAGS AND SPILL SHARK GEL. WILL LOOK INTO PUTTING ON SCHEDULED MAINTENANCE. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  |  | DOUGLAS AGRESS | 2007-03-27 | 650-877-8552
4797 | 215 | 1 | Public | 2007-02-23 09:14 | 1100 | 0 |  | 2007-02-23 09:14 |  | -- | Easement area behind 620Golf Club Way | Pleasant Hill | Contra Costa | 94523 |  |  | 2007-02-22 |  |  |  | The overflow was filtered through berry bushs, ground cover etc that filtered out the solids. No measureable ammonia was detected in the creek. Blockage was a cobination of roots and rags. We recieved the sevice call at approximately 1530 hours and cleared the blockage at 1420 | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  | The overflow was filtered through berry bushs, ground cover etc that filtered out the solids. No measureable ammonia was detected in the creek. Blockage was a cobination of roots and rags. We recieved the sevice call at approximately 1530 hours and cleared the blockage at 1420 |  | Bill Echols | 2007-02-23 | (925) 229-7162
4986 | 218 | 1 | Public | 2007-03-23 09:23 | 225 | 0 |  | 2007-03-23 09:23 |  | -- | Spill on Emperor - cross street Gray Lag | Suisun City | Solano | 94585 |  |  | 2007-02-19 |  |  |  | This small SSO entered only one storm drain and was at least 95% recovered. Roto Rooter was called in and they vacuumed out one down-stream SWI and washed the street down. Public Works returned the next day and cleaned out 350ft of SWI and retrieved excess grease. There was no property damage, affected area was the gutter line. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  |  | Amanda Dum | 2007-03-23 | 707-421-7349
4668 | 206 | 1 | Public | 2007-02-02 16:29 | 800 | 0 |  | 2007-02-02 16:29 |  | -- | In the proximity of 504 Katherine St | Redwood City | San Mateo | 94062 |  |  | 2007-02-02 |  |  |  | Rags, plastic bags. Recovered approximately 500 gals of spill using Vacon (vacuum) then returned to system (info provided by on-site staff person, Paul Heavenston) | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  |  | Marilyn Harang | 2007-02-02 | 650-780-7477
4558 | 205 | 1 | Public | 2007-01-19 10:12 | 85 | 0 |  | 2007-01-19 10:12 |  | -- | 437 Rincon Ln. | ElSobrante | contra Costa County | 94806 |  |  | 2007-01-17 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  |  | Marc Raynor | 2007-01-19 | 510 222-6700
4531 | 204 | 1 | Public | 2007-01-17 10:21 | 85 | 0 |  | 2007-01-17 10:21 |  | -- | 437 Rincon ln. | ElSobrante | Contra Costa | 94806 |  |  | 2007-01-17 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  |  | Marc Raynor | 2007-01-17 | 510-222-6700
4488 | 203 | 1 | Public | 2007-01-10 16:21 | 480 | 0 |  | 2007-01-10 16:21 |  | -- | Mission Bay Site, San Francisco, California. Spill originates at temp. Sanitary Sewer pump station located at former golf driving range (located on the southern side of China Basin Channel at its western terminous). See comment section. | San Francisco | San Francisco | 94158 |  |  | 2007-01-10 |  |  |  | Spill originated at temp. SS pump station. Overflowed to a concrete surface water channel, and northwards to China Basin Channel (SF Bay). Approximately 480 gallons of spill, much of which was contained in concrete surface water channel, some of which (unknown quantity) has overflowed to China Basin Channel. Containment is currently underway. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | PUMP STATION |  | INFRASTRUCTURE FAILURE | -- Select One -- |  |  |  |  | Nicholas Loizeaux | 2007-01-10 | 510-834-4747 x
4486 | 202 | 1 | Public | 2007-01-10 08:46 | 1200 | 0 |  | 2007-01-10 08:46 |  | -- | Angel Island State Park(Immigration Station Construction Site) | Tiburon | MARIN | 94920 |  |  | 2007-01-10 |  |  |  | Spill contained on construction site,and will be pumped back into sewage system | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | PUMP STATION |  | INFLOW & INFILTRATION | -- Select One -- |  |  | Spill contained on construction site,and will be pumped back into sewage system |  | Fernando F Guzman | 2007-01-10 | 415-435-9221
4370 | 198 | 1 | Public | 2006-12-20 12:00 | 300 | 0 |  | 2006-12-20 12:00 |  | -- | 3551 East Hills Dr | San Jose | Santa Clara | 95127 |  |  | 2006-12-20 |  |  |  | Spill reported to District by property owner 0930 12/20/06. Spill first noted by property owner P.M. of 12/19/06. Originally called City of San Jose who checked main line in East Hills and reported the line was flowing unobstructed. Property is connected to main at side street, Laumer Ave. Property owner called private plumbing company who was unable to clear the line from an onsite cleanout but planned to return 12/20/06. Upon receiving the call, District Inspectors were dispatched to the site and verified a mainline stoppage in Laumer Ave. Crews were dispatched to the site to clear the stoppage, clean the subject property landscaping and a storm drain inlet which received approximately 50 gallons of the spill. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  |  | Sid Nash | 2006-12-20 | 408-255-3137
3861 | 192 | 1 | Public | 2006-09-08 09:59 | 500 | 0 |  | 2006-09-08 09:59 |  | -- | 228 24th ave | san mateo | san mateo | 94403 |  |  | 2006-09-08 |  |  |  | sanitary overflow | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | GREASE |  |  |  |  | walt dabney | 2006-09-08 | 650 522-7367 | bcorrea@cityofsanmateo | MINOR
4711 | 207 | 1 | Public | 2007-02-09 07:47 | 500 | 0 |  | 2007-02-09 07:47 |  | -- | 228 24th ave 228 24th ave | san mateo | san mateo | 94403 |  |  | 2006-09-08 |  |  |  | sanitary overflow | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  |  | walt dabney | 2007-02-09 | 650 522 7367
3848 | 191 | 1 | Public | 2006-09-06 08:56 | 100 | 0 |  | 2006-09-06 08:56 |  | -- | 1610 Mcgee | Berkeley | Alameda | 94703 |  |  | 2006-08-22 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | CLEAN OUT |  | CAUSE UNKNOWN | --Select None-- |  |  |  |  | Kevin M. Lewis | 2006-09-06 | 510 644-6620 | kel1@ci.Berkeley.ca.us | MINOR
3758 | 189 | 1 | Public | 2006-08-18 16:55 | 50 | 0 |  | 2006-08-18 16:55 |  | -- | San Pablo Ave - between 47th and 55th | Emeryville | Alameda | 94608 |  |  | 2006-08-18 |  |  |  | Grease Blockage in Oakland line on SPA backed up into private building in Emeryville. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | PIPE |  | BLOCKAGE | GREASE |  |  |  |  | Peter Schultze-Allen | 2006-08-18 | 510-596-3728 | pschultze-allen@ci.emeryville.ca.us | MINOR
3685 | 188 | 1 | Public | 2006-08-04 08:34 | 600 | 0 |  | 2006-08-04 08:34 |  | -- | 987 Tiburon Blvd. | Tiburon | Marin | 94920 |  |  | 2006-08-03 |  |  |  | Employees RA and JB responded to call out.Found manhole #323 overflowing at approx 10 gpm.Asked Roto Rooter, who were working nearby,to clean from #323 to #322. Removed roots approx 100 ft in.Estimated spill volume 600 gallons.Spill was into an open field and soaked into the land. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  |  | Tim O'Day | 2006-08-04 | 415-435-1501 | today@sani5.org | MINOR
3670 | 187 | 1 | Public | 2006-07-28 07:16 | 50 | 0 |  | 2006-07-28 07:16 |  | -- | 625 Oakdale Avenue | Corte Madera | Marin | 94976 |  |  | 2006-07-21 |  |  |  | Responded to call at 1130. Found Manhole K47 overflowing slight trickle of liquid into the curb. Placed boons and absorbent to prevent liquid entering the storm drain. Ran line and cleared blockage. T.V. camera'd line. Found roots. Called in contractor with main-line rodder to clear roots. T.V. camera'd line again. Found more roots. Called in contractor to bring bigger main-line rodder to clear remainder of roots. Will T.V. camera line again after rodding remainder of roots. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  |  | David Montero | 2006-07-28 | 415-927-5069 | dmontero@ci.corte-madera.ca.us | MINOR
3585 | 186 | 1 | Public | 2006-06-29 14:15 | 261 | 0 |  | 2006-06-29 14:15 |  | -- | 140 Lucero Way | Portola Valley | San Mateo | 94028 |  |  | 2006-06-29 |  |  |  | SSO occured in an easement between to SFR's, th eback of these residences face the Web Ranch. The sso saturated into the soil quickly. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  |  | John Simonetti | 2006-06-29 | 650-321-0384 | jsimonetti@westbaysanitary.org | MINOR
3523 | 182 | 1 | Public | 2006-06-21 08:23 | 60 | 0 |  | 2006-06-21 08:23 |  | -- | Cascade Way & Dipsea Stairs | Mill Valley | Marin | 94941 |  |  | 2006-06-17 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  |  | Jill Barnes | 2006-06-21 | 415-388-4033 | jbarnes@cityofmillvalley.org | MINOR
3492 | 180 | 1 | Public | 2006-06-16 13:49 | 300 | 0 |  | 2006-06-16 13:49 |  | -- | 44 Camino Encinas | Orinda | Contra Costa | 94563 |  |  | 2006-06-16 |  |  |  | Sewage came up through cracks in street, approximately 300 gallons reached an open culvert which flowed to a tributary to San Pablo Creek. Approximately 200 gallons was captuted and returned to the system. Follow up TV inspection will be completed within the next two buisness days | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | PIPE |  | INFRASTRUCTURE FAILURE | DEBRIS FROM LATERALS |  |  |  |  | Bill Echols | 2006-06-16 | (925)765-0183 | Roseanna@centralsan.dst.ca.us | MINOR
3458 | 178 | 1 | Public | 2006-06-06 15:37 | 500 | 0 |  | 2006-06-06 15:37 |  | -- | 1879 Sarah Dr | Pinole | Contra Costa | 94564 |  |  | 2006-05-30 |  |  |  | The source of cause is under investigation. Will assume it was grease for the time being. Records indicate line had had routine maintenance in the past year. This is an easement line that has no previous history of SSO. A TV inspection will be sceduled in the near future to detemine if any further mainteance or repairs are warranted. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | GREASE |  |  |  |  | Mark Adams | 2006-06-06 | 510 724-8949 | madams@ci.pinole.ca.us | MINOR
3405 | 177 | 1 | Public | 2006-05-24 11:02 | 300 | 0 |  | 2006-05-24 11:02 |  | -- | Camaritas Avenue and Arroyo Drive | South San Francisco | San Mateo | 94080 |  |  | 2006-05-23 |  |  |  | Recovered 200 Gal. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | GREASE |  |  |  |  | James D. Bombaci | 2006-05-24 | 650-877-8552 | jim.bombaci@ssf.net | MINOR
3377 | 176 | 1 | Public | 2006-05-22 11:29 | 50 | 0 |  | 2006-05-22 11:29 |  | -- | 8 Buckeye Drive | Belvedere | Marin | 94920 |  |  | 2006-05-17 |  |  |  | Employee RA investigated.Found evidence of prior minor spill, max 50 gallons, but no actual spill witnessed.Called Roto Rooter to clean from GB5 to GB4 to GB3. Roots removed. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  |  | Timothy O'Day | 2006-05-22 | 415-716-6371 | today@sani5.org | MINOR
3336 | 174 | 1 | Public | 2006-05-15 07:26 | 500 | 0 |  | 2006-05-15 07:26 |  | -- | 630 Baden Ave | South San Francisco | San Mateo | 94080 |  |  | 2006-05-14 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | GREASE |  |  |  |  | James D. Bombaci | 2006-05-15 | 650-877-8552 | JBombaci@ssf.net | MINOR
3326 | 173 | 1 | Public | 2006-05-09 16:56 | 100 | 0 |  | 2006-05-09 16:56 |  | -- | 1100 8th St. Sewer Lift Station | Alameda | Alameda | 94803 |  |  | 2006-04-28 |  |  |  | While cleaning the lift station wet well the operator of the Vactor truck inadvertantly opened the dump door and spilled approximately 100 gallons of sewage into the curb area of the street. He imediatly moved his truck to intercept the spill. He was able to recover the entire contents of the spill before it reached the drain inlet. The curb and gutter area was then pressure washed and sanitized. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | OTHER | Spill from Vactor Truck | BLOCKAGE | --Select None-- |  |  |  |  | Larry Strunk | 2006-05-09 | 510 747-7900 | lstrunk@ci.alameda.ca.us | MINOR
3525 | 183 | 1 | Public | 2006-06-21 08:27 | 120 | 0 |  | 2006-06-21 08:27 |  | -- | 362 Edgewood Avenue | Mill Valley | Marini | 94941 |  |  | 2006-04-25 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  |  | Jill Barnes | 2006-06-21 | 415-388-4033 | jbarnes@cityofmillvalley.org | MINOR
3527 | 184 | 1 | Public | 2006-06-21 08:39 | 90 | 0 |  | 2006-06-21 08:39 |  | -- | 52 Longfellow Dr. | Mill Valley | Marin | 94941 |  |  | 2006-04-25 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  |  | Jill Barnes | 2006-06-21 | 415-388-4033 | jbarnes@cityofmillvalley.org | MINOR
3245 | 172 | 1 | Public | 2006-04-27 15:49 | 135 | 0 |  | 2006-04-27 15:49 |  | -- | 885 Eucalyptus Ave. | Novato | Marin | 94945 |  |  | 2006-04-21 |  |  |  | Front yard area was washed down and all wash down water,sewage, and overflow debris were 100% recovered. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | GREASE |  |  |  |  | Timothy M. O'Connor | 2006-04-27 | 415-892-1694 | Timo@novatosan.com, Bevj@novatosan.com, Edm@Novatosan.com | MINOR
3165 | 170 | 1 | Public | 2006-04-13 09:34 | 4750 | 0 |  | 2006-04-13 09:34 |  | -- | Pillar Ridge Mobile Home Park | Moss Beach | San Mateo | 94038 |  |  | 2006-03-30 |  |  |  | This was erroneously reported as a Montara Water and Sanitary District SSO (24 hr. report # 3106). Report # 3106 will be updated to reflect this report. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | GREASE |  |  |  |  | Tony Pullin | 2006-04-13 | 650-726-0124 | msd@coastside.net, tony@samcleanswater.org, jack@samcleanswater.org | MINOR
2848 | 165 | 1 | Public | 2006-02-21 13:03 | 20 | 0 |  | 2006-02-21 13:03 |  | -- | 38 Portsmouth Road | Piedmont | Alameda | 94611 |  |  | 2006-02-21 |  |  |  | Partial blockage in City main line by roots and mud. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | OTHER | Ground | BLOCKAGE | DEBRIS |  |  |  |  | Sharon Lai | 2006-02-21 | 510-420-3067 | slai@ci.piedmont.ca.us | MINOR
2768 | 164 | 1 | Public | 2006-02-07 10:05 | 1200 | 0 |  | 2006-02-07 10:05 |  | -- | 140,150,170,180,190 Woodridge Rd. | Hillsborough | San Mateo | 94010 |  |  | 2006-02-03 |  |  |  | Private subdivison sewer main,that is total responsibility of the homeowners. We the Town did spot repair to keep from flowing into small creek anymore. (The private sewer main slid out.)Homeowners have been notified to get repairs going by letter that is in the mail as we speak. | [5 empty] | GROUND WATER IMPACTED | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | PIPE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  |  | TONY GERALDI | 2006-02-07 | 650 375-7507 | tgeraldi@hillsca.org | MINOR
2655 | 159 | 1 | Public | 2006-01-18 16:25 | 600 | 0 |  | 2006-01-18 16:25 |  | -- | 48 AND 56 HARLAN ST | SAN LEANDRO | ALAMEDA | 94577 |  |  | 2006-01-18 |  |  |  | We had a sewer main fail and we are now in the process of haveing an emergency point repar done on the failed section. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | OTHER | RESIDENTS BASEMENT | INFRASTRUCTURE FAILURE | GREASE |  |  |  |  | RICK ORTA | 2006-01-18 | 510-577-6058 | rorta@ci.san-leandro.ca.us | MINOR
2558 | 158 | 1 | Public | 2006-01-06 11:36 | 6000 | 0 |  | 2006-01-06 11:36 |  | -- | Intersection of Kimberly Drive and Poppyfield Way | American Canyon | Napa | 94503 |  |  | 2006-01-06 |  |  |  | Flood event on 12/31/05 overwhelmed the drainage system and the sewage system exceeded capacity due to inflow and infiltration. SSO occurred on 12/31/05. OES Control Number 06-0147 | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | NATURAL DISASTER | --Select None-- |  |  |  |  | Fred Simonson | 2006-01-06 | (707) 674-4368 | freds@ci.american-canyon.ci.us | MINOR
2458 | 154 | 1 | Public | 2006-01-03 17:33 | 270 | 0 |  | 2006-01-03 17:33 |  | -- | 168 Carlisle Way | Benicia | Solano | 94510 |  |  | 2005-12-31 |  |  |  | Power failure caused by heavy winds associated with severe storm. Crews responded by mobilizing portable emergency generator set. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | PUMP STATION |  | ELECTRICAL POWER FAILURE | --Select None-- |  |  |  |  | John Bailey | 2006-01-03 | (707) 746-4294 | jbailey@ci.benicia.ca.us | MINOR
2460 | 155 | 1 | Public | 2006-01-03 17:41 | 11625 | 0 |  | 2006-01-03 17:41 |  | -- | 111 & 113 El Bonito Way | Benicia | Solano | 94510 |  |  | 2005-12-31 |  |  |  | Exceptionally high flow due to rain induced inflow and infiltration. Severe rain storm experienced on 12/31/05 caused flows in excess of the lift stations capacity. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | PUMP STATION |  | INFLOW & INFILTRATION | --Select None-- |  |  |  |  | John Bailey | 2006-01-03 | (707) 746-4294 | jbailey@ci.benicia.ca.us | MINOR
2242 | 148 | 1 | Public | 2005-12-12 15:02 | 250 | 0 |  | 2005-12-12 15:02 |  | -- | Alameda de las Pulgas and Hwy 92 | San Mateo | San Mateo | 94403 |  |  | 2005-12-07 |  |  |  | contained wastewater, flushed area and vacuumed. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | GREASE |  |  |  |  | Bob Correa | 2005-12-12 | (650) 522-7354 | bcorrea@cityofsanmateo.org | MINOR
2244 | 149 | 1 | Public | 2005-12-12 15:12 | 100 | 0 |  | 2005-12-12 15:12 |  | -- | 1065 S. Grant St. | San Mateo | San Mateo | 94403 |  |  | 2005-12-05 |  |  |  | Contained, flushed, vacuumed and disinfected area | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | GREASE |  |  |  |  | Bob Correa | 2005-12-12 | (650) 522-7354 | bcorrea@cityof sanmateo.org | MINOR
2170 | 146 | 1 | Public | 2005-11-23 16:41 | 1000 | 0 |  | 2005-11-23 16:41 |  | -- | State Highway 29 at Sulphur Creek | SAINT HELENA | NAPA | 94574 |  |  | 2005-11-23 |  |  |  | Discharge of sewage into Sulphur Creek (surface water)from storm drain noted by City employee at 1000 this morning. Discharge to surface water ceased by 1200. Work continues as of 1640 to prevent recurrence. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | PIPE |  | BLOCKAGE | GREASE |  |  |  |  | Jonathon Goldman | 2005-11-23 | 7073121087 | jonathong@ci.st-helena.ca.us | MINOR
2152 | 144 | 1 | Public | 2005-11-22 09:57 | 200 | 0 |  | 2005-11-22 09:57 |  | -- | 401 Hillsborough blvd | Hillsborough | San Mateo | 94010 |  |  | 2005-11-21 |  |  |  | The line backed up was actually San Mateo we notified San Mateo but rodded their line at 377 Edgewood to take care of our problem | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | GREASE |  |  |  |  | Thomas Barry | 2005-11-21 | 650/375/74444 | san15rr@sbcglobal.net | MINOR
2154 | 145 | 1 | Public | 2005-11-22 10:02 | 10 | 0 |  | 2005-11-22 10:02 |  | -- | 20 Bates | Hillsborough | San Mateo | 94010 |  |  | 2005-11-21 |  |  |  | Very little spillage quick response rodded main | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | GREASE |  |  |  |  | Thomas | 2005-11-22 | 650/375/7444 | san15rr@sbcglobal.net | MINOR
2065 | 136 | 1 | Public | 2005-10-28 15:41 | 1000 | 0 |  | 2005-10-28 15:41 |  | -- | O'Keefe and Pine Lane Lift Stations | Los Altos | Santa Clara | 94022 |  |  | 2005-10-28 |  |  |  | I have become aware of at least 3 SSOs into Adobe Creek(that flows to the Bay) in Los Altos Hills and Los Altos, all greater than 1000 gallons, from these 2 poorly maintained lift stations. The city of Los Altos has responsibility for the upkeep of these pumps. I have it on good authority that the supervisor has intimidated the workers into under-reporting the volume of SSOs to avoid having to file with the OES. The city's Sewer Master Plan confirms that major repair work needs to be done on all 3 lift stations. The city has not reported any of the spills into Adobe Creek. The SSOs occurred in 2004. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | PUMP STATION |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  |  | Thomas M. Burns MD | 2005-10-28 | 1.650.492.0259 | tanddburns@sbcglobal.net | MINOR
1946 | 111 | 1 | Public | 2005-10-11 08:44 | 6000 | 0 |  | 2005-10-11 08:44 |  | -- | 2540 Olympic | San Bruno | San Mateo | 94066 |  |  | 2005-10-11 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | GREASE |  |  |  |  | Larry Smurthwaite | 2005-10-11 | 650-616-7160 | lsmurthwaite@sanbruno.ca.gov | MINOR
1952 | 113 | 1 | Public | 2005-10-12 13:24 | 100 | 0 |  | 2005-10-12 13:24 |  | -- | 40 Larry Ln. | Oakland | Alameda |  |  |  | 2005-10-11 |  |  |  | Had Hydro Flusher flush m/s to clear stoppage of rotts and debris. The ,/s is flowing at this time. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  |  | K. Moore | 2005-10-12 | 5106155566 |  | MINOR
1940 | 108 | 1 | Public | 2005-10-10 10:18 | 20 | 0 |  | 2005-10-10 10:18 |  | -- | 195 Roble Rd. | Oakland | Alameda |  |  |  | 2005-10-09 |  |  |  | Rodded m/s in street to break stoppage of roots. The m/s is flowing at this time. Washed down gutter area and storm inlet. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | OTHER | Lamp hole | BLOCKAGE | ROOTS |  |  |  |  | K. Moore | 2005-10-10 | 5106155566 |  | MINOR
1938 | 107 | 1 | Public | 2005-10-10 10:10 | 85 | 0 |  | 2005-10-10 10:10 |  | -- | 4023 E.17th Street | Oakland | Alameda |  |  |  | 2005-10-08 |  |  |  | Manhole overflowing in street. Found sewage overflowing out of cleanout. Rodded m/s broke rod had to make repairs. m/s keep plugging up down stream had to make three set up's to clear m/s of very heavy grease stoppage. Also had to return to yard and pick up Flusher to wash down street and gutter. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  |  | K. Moore | 2005-10-10 | 5106155566 |  | MINOR
1936 | 106 | 1 | Public | 2005-10-10 09:58 | 40 | 0 |  | 2005-10-10 09:58 |  | -- | 11121 Kerrigan Dr. | Oakland | Alameda |  |  |  | 2005-10-07 |  |  |  | Sewage overflowing in rear yard. Rodded m/s on easement to break stoppage of roots. Could only get a 2" auger throygh. Had #195 (Tobias)rod m/s with full size tool. The m/s is flowing at this time. Map #70 | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | PIPE | out of ground | BLOCKAGE | ROOTS |  |  |  |  | K. Moore | 2005-10-10 | 5106155566 |  | MINOR
1932 | 104 | 1 | Public | 2005-10-10 09:32 | 30 | 0 |  | 2005-10-10 09:32 |  | -- | 1969 Manzanita Dr. | oakland | alameda |  |  |  | 2005-10-06 |  |  |  | Sewer leaking on easement. Had 195 (Tobias) rod m/s to clear stoppage of heavy roots. the m/s is flowing at this time. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  |  | K. Moore | 2005-10-10 | 5106155566 |  | MINOR
1934 | 105 | 1 | Public | 2005-10-10 09:47 | 55 | 0 |  | 2005-10-10 09:47 |  | -- | 6693 Saroni Dr. | Oakland | Alameda |  |  |  | 2005-10-06 |  |  |  | Sewer water coming through cleanout near mailbox. Rodded main sewer by hand in street. Cleared blockage of heavy roots. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | CLEAN OUT | side sewer cleanout | BLOCKAGE | ROOTS |  |  |  |  | K. Moore | 2005-10-10 | 5106155566 |  | MINOR
2049 | 134 | 1 | Public | 2005-10-27 13:15 | 875 | 0 |  | 2005-10-27 13:15 |  | -- | 3341 Los Prados | San Mateo | San Mateo | 94403 |  |  | 2005-10-06 |  |  |  | Used booms to protect storm drains, wash down street, vacuumed water and disinfected. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  |  | Bob Correa | 2005-10-27 | (650) 522-7354 | bcorrea@cityofsanmateo.org | MINOR
1909 | 102 | 1 | Public | 2005-10-04 09:07 | 100 | 0 |  | 2005-10-04 09:07 |  | -- | 39 plaza drive mill valley, ca | mill valley | marin | 94941 |  |  | 2005-10-04 |  |  |  | responded to immediatly by roto rooter | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  |  | Tom Roberts | 2005-10-04 | 415 388 3696 | tomroberts7@aol.com | MINOR
1898 | 101 | 1 | Public | 2005-09-30 14:03 | 800 | 0 |  | 2005-09-30 14:03 |  | -- | 543 Appian wy. | El Sobrante | Contra Costa | 94806 |  |  | 2005-09-30 |  |  |  | WE BROKE THE STOPPAGE THEN CONTACTED E.V LINK, OUR CLEAN UP RESPONDERS, TO FACILITATE THE CLEAN UP OF THE YARD,THERE WERE NO SOLIDS JUST WATER.WE FLUSHED THE STORMDRAIN WITH CLEAN WATER. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | CLEAN OUT |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  |  | MARC RAYNOR | 2005-09-30 | 510-2223276 | mraynor@wcwd.org | MINOR
1883 | 100 | 1 | Public | 2005-09-29 10:18 | 200 | 0 |  | 2005-09-29 10:18 |  | -- | Intersection of Carson Drive and Piedra Drive. | Sunnyvale | Santa Clara | 94087 |  |  | 2005-09-28 |  |  |  | Approximatly 25-50 gallons of liquid entered the storm system through a catch basin. Leaves and dirt that were in the catch basin acted as a dam and limited the amount of liquid that entered the storm main. Crews contained the remaining liquid at the downstream manhole, vacumed out the debris in the catch basin, flushed and removed the remaining liquid in the storm sytem. The area was then treated with emzyme to disenfect/deoderize the effected area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  |  | Tony Pineda | 2005-09-29 | 408/730-7510 | tpineda@ci.sunnyvale.ca.us | MINOR
1819 | 98 | 1 | Public | 2005-09-22 11:00 | 250 | 0 |  | 2005-09-22 11:00 |  | -- | 1929 Merchant St | Crockett | Contra Costa | 94525 |  |  | 2005-09-22 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  |  | Kent Peterson | 2005-09-22 | 510-787-2992 | cvsd@earthlink.net | MINOR
1768 | 94 | 1 | Public | 2005-09-07 13:07 | 5 | 0 |  | 2005-09-07 13:07 |  | -- | Carol Dr & Delpha Dr | Napa | Napa |  |  |  | 2005-09-07 |  |  |  | Spill was flushed back into the manhole with 30 gal of water. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | GREASE |  |  |  |  | Gerald Merryweather | 2005-09-07 | 707-258-6000 | JMerrywe@co.napa.ca.us | MINOR
1383 | 62 | 1 | Public | 2005-05-10 14:10 | 10 | 0 |  | 2005-05-10 14:10 |  | -- | 135 Laphan Way (cross street, Robinson) | San Francisco | San Francisco |  |  |  | 2005-04-15 |  |  |  | From message left on sewer spill line from OES (spill #05-2282). Unknown volume, unknown cause, caused a sewage odor in soil, it is contained, no waterway involved. Original complaint called in by Lynn Yes (sp?) (public citizen) 415-713-1361. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | OTHER | unknown | CAUSE UNKNOWN | --Select None-- |  |  |  |  | Michael Chee | 2005-05-10 | 622-2333 |  | MINOR
1263 | 56 | 1 | Public | 2005-04-07 13:43 | 90 | 0 |  | 2005-04-07 13:43 |  | -- | #2 Madrono Ave | Corte Madera | Marin | 94925 |  |  | 2005-04-07 |  |  |  | Operator estimates a flow of 3gpm for approx 30 minutes. Cleared line with Vactor. Blocked storm drain with absorbent boom. We did not vactor drain in that it didn't appear to contain sewage (it was raining at the time). Cleaned line from MH#028 to MH#029 on map page 0 on the Corte Madera Sanitary Sewer map. We will monitor and schedule this line for root-cutting maintenance next week. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  |  | Kevin Kramer | 2005-04-07 | 415-927-5057 | dmontero@ci.corte-madera.ca.us | MINOR
1229 | 53 | 1 | Public | 2005-03-30 09:12 | 45 | 0 |  | 2005-03-30 09:12 |  | -- | 2514 Pfeiffer Way | Pinole | Contra Costa | 94564 |  |  | 2005-03-25 |  |  |  | Up until 6 months ago Pfeiffer Way was a privately owed street and sewer system. At the time the City took over the system the main line was flushed and deemed in good working order. The MH that was root-bound is on an easement(behind a driveway) and was not recorded on any map, hence it was never inspected. The roots were removed from the MH and the entire line is scheduled to be TV inspected this week. Any rehab or regular maintenance that is required will be implimented. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  |  | Mark Adams | 2005-03-30 | (510) 724-8949 | madams@ci.pinole.ca.us | MINOR
1215 | 52 | 1 | Public | 2005-03-24 12:08 | 100 | 0 |  | 2005-03-24 12:08 |  | -- | 344 shoreline hwy | mill valley | marin | 94941 |  |  | 2005-03-24 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | GREASE |  |  |  |  | Bob Bunce | 2005-03-24 | 415 388 6393 | bbunce@tcsd.us | MINOR
1206 | 51 | 1 | Public | 2005-03-18 14:06 | 200 | 0 |  | 2005-03-18 14:06 |  | -- | In alley behind 1023 West K Street | Benicia | Solano | 94510 |  |  | 2005-03-18 |  |  |  | There was only approximatley 50 gallons of clear water that went into the storm drain. There was no visable solids or paper at outfall. It was also raining at the time. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  |  | Rick Silva | 2005-03-18 | 707-746-4396 | rsilva@ci.benicia.ca.us | MINOR
1026 | 39 | 1 | Public | 2005-02-15 13:53 | 500 | 0 |  | 2005-02-15 13:53 |  | -- | 131 TERMINEL CT | SSF | SAN MATEO | 94080 |  |  | 2005-02-15 |  |  |  | JETTED MAIN LINE-OPENED | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | GREASE |  |  |  |  | MIKE CHARAN | 2005-02-15 | dTJ7ZjCh | MIKE CHARAN | MINOR
957 | 34 | 1 | Public | 2005-02-04 07:25 | 175 | 0 |  | 2005-02-04 07:25 |  | -- | 162 Mariner Court, | Corte Madera | Marin | 94925 |  |  | 2005-02-03 |  |  |  | Spill was between Manhole Q-12 and Q-13. The SSO was contained by an earth dam in the gutter. All materal was cleaned and removed from the street. We are having a contractor rod the main line to remove roots. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  |  | Wes Sitchler | 2005-02-04 | 415-927-5069 | Dmontero@ci.corte-madera.ca.us | MINOR
980 | 36 | 1 | Public | 2005-02-08 08:40 | 100 | 0 |  | 2005-02-08 08:40 |  | -- | 2200 Block Bryant | Palo Alto | Santa Clara | 94303 |  |  | 2005-01-18 |  |  |  | information delayed due to problem with Logon and Password. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  |  | Michael Haynes | 2005-02-08 | 650-496-6917 | michael.haynes@cityofpaloalto.org | MINOR
814 | 18 | 1 | Public | 2005-01-11 10:39 | 200 | 0 |  | 2005-01-11 10:39 |  | -- | 4330 Mountain Blvd. | Oakland | Alameda | 94621 |  |  | 2005-01-11 |  |  |  | Had power-rodder rod and unpludded main sewer of heavy roots in main sewer. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  |  | Charles Bandy | 2005-01-11 | 510-615-5941 |  | MINOR
519 | 2 | 1 | Public | 2004-12-13 17:03 | 300 | 0 |  | 2004-12-13 17:03 |  | -- | 1065 Meadowsweet Drive | Corte Madera | Marin | 94976 |  |  | 2004-12-13 |  |  |  | Spill reported by local resident. Sewage ran into earthen ditch alongside Meadowsweet Dr. then into PVC storm drain system. Storm drain system was plugged four catch basins downstream to contain the spill. Blockage was then cleared and the storm drain system was then cleaned with a Vactor truck. The earth ditch was cleaned by hand using gloves and shovels. Sewage solids material was plastic bagged and disposed of. Storm drain was flushed and Vactored with water returned to sewer main. Weather was clear and dry. Sewer main will be cleaned on Wednesday. Total clearing of line and cleanup was 4.5 hours involving a total of 8 DPW personel, not all working the whole time on the project. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  |  | David Montero | 2004-12-13 | 415-927-5091 |  | MINOR
610 | 15 | 1 | Public | 2004-12-21 14:18 | 7200 | 0 |  | 2004-12-21 14:18 |  | -- | North bound Lawrence Expy. 500 ft. North of Prospect Ave. | San Jose | Santa Clara |  |  |  | 2004-12-09 |  |  |  | Our department discovered the release coming out of the manhole in the street, but we were not responsible for it. We spent several hours trying to find the responsible party and trying to report the release. I left a voicemail message for Rich McMurty at the RWQCB on 12/9/04 and was contacted today (12/21/04) and asked to make this report on your website. I am not sure what caused the sewer blockage since it was not our department that cleared it. It was cleared by the City of San Jose. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  |  | Nicole Jakaby | 2004-12-21 | 408-494-2719 |  | MINOR
2063 | 135 | 1 | Public | 2005-10-28 14:33 | 36000 | 0 |  | 2005-10-28 14:33 |  | -- | 1530 Frontero Ave | Los Altos | Santa Clara | 94024 |  |  | 2003-02-03 |  |  |  | The City of Los Altos' revised Sewer Master Plan was just released. Two of its conclusions are that the city has a higher number of mainline stoppages and a higher number of SSOs than a number of comparators. The SSO into my home of 36,000 gallons was never reported to the RWQCB. There have been 8 SSOs on my street alone between 8/01 and 8/04. Seven of these 8 have been into homes when the city uses a high-pressure hydroflushing hose without first checking to see if there undetected root obstructions in the line. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Public | PIPE |  | BLOCKAGE | ROOTS |  |  |  |  | Thomas M. Burns MD | 2005-10-28 | 1.650.492.0259 | tanddburns@sbcglobal.net | MINOR
4946 | 29 | 1 | RedwoodCity | 2007-03-16 08:05 | 300 | 0 |  | 2007-03-16 08:05 |  | -- | Dory Lane (at Harbor Colony Dr) Redwood City | Redwood City | San Mateo | 94064 |  |  | 2007-03-15 |  |  |  | Inlet was covered when maintenance personnel first noticed slow seeping SSO however protective cover malfunctioned and wastewater flowed into inlet. No recovery was possible. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Ray Bartolo | 2007-03-16 | 650-780-7470
4829 | 28 | 1 | RedwoodCity | 2007-02-27 10:42 | 450 | 0 |  | 2007-02-27 10:42 |  | -- | Whipple Ave. & Veterans Blvd. | Redwood City | San Mateo | 94063 |  |  | 2007-02-27 |  |  |  | Storm system is currently being inspected to see if recovery can be accomplished. | [5 empty] | UNKNOWN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Ray Bartolo | 2007-02-27 | 650-780-7470
4691 | 26 | 2 | RedwoodCity | 2007-02-08 08:20 | 200 | 0 |  | 2007-02-08 08:20 |  | -- | 979 Edgewood Road | Redwood City | San Mateo | 94063 |  |  | 2007-02-07 |  |  |  | Estimated 200 Gls of overflow. Main was jetted and cleared of blockage. Area of overflow was vacuumed to clean remaining waste. Overflow area was then washed down upstream (hydrant) of spill location and vacuumed downstream to clean area. Waste water was returned back to system. There were no inlets near the affected area nor were any affected by the SSO. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Supervisor | Ray Bartolo | 2007-02-08 | 650-780-7470
4681 | 25 | 1 | RedwoodCity | 2007-02-07 08:25 | 800 | 0 |  | 2007-02-07 08:25 |  | -- | In the proximity of 504 Katherine | Redwood City | San Mateo | 94062 |  |  | 2007-02-02 |  |  |  | By request of Regional Board, this is a resubmitted report of a spill incident that took place on 2/2/07. Rags, plastic bags. Recovered approximately 500 gallons of spill using vacon jetter (vacuum) then returned back to sewer system (information provided by on site staff person Paul Heavenston. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Ray Bartolo | 2007-02-07 | 650-780-7477
5021 | 24 | 3 | RedwoodCity | 2007-02-06 | 500 | 5125 | 07-0749 | 2007-02-06 | Paul Heavenston | RedwoodCity | Seaport Blvd. / West of Chesapeake Dr. | Redwood City | San Mateo | 94063 |  |  | 2007-02-02 | 0.57292 | [6 empty] | Medium |  | SURFACE WATER IMPACT | No |  | No | No | No sign of fish kill. |  | Yes | Yes | No |  |  | No | No |  |  | 2007-02-12 | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | OTHER |  | INFRASTRUCTURE FAILURE | -- Select One -- | BREAKAGE OF COLLECTION SYSTEM | Air Release Valve |  | Supervisor | Ray Bartolo | 2007-02-06 | 650-780-7470
4552 | 22 | 1 | RedwoodCity | 2007-01-18 13:57 | 700 | 0 |  | 2007-01-18 13:57 |  | -- | Intersection of Redwood & Norman | Redwood City | San Mateo | 94063 |  |  | 2007-01-18 |  |  |  | Wastewater flowed to nearest inlet located at NW corner of Redwood & Hudson Ave. Lined creek is nearby so 700 gallons were not able to be captured or recovered. Jetter crew was able to recover estimated 50 gallons when they placed mat over nearest downstream inlet. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Public Wks Supv | Ray Bartolo | 2007-01-18 | 650-780-7470
4554 | 22 | 2 | RedwoodCity | 2007-01-18 14:05 | 700 | 0 |  | 2007-01-18 14:05 |  | -- | Intersection of Redwood & Norman | Redwood City | San Mateo | 94063 |  |  | 2007-01-18 |  |  |  | Wastewater flowed to nearest inlet located at NW corner of Redwood & Hudson Ave. Lined creek is nearby so 700 gallons were not able to be captured or recovered. Jetter crew was able to recover estimated 50 gallons when they placed mat over nearest downstream inlet. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Public Wks Supv | Ray Bartolo | 2007-01-18 | 650-780-7470
4638 | 23 | 1 | RedwoodCity | 2007-01-29 | 1500 | 0 | 07-0270 | 2007-01-29 | Ray Bartolo | RedwoodCity | MiddleField & Jefferson Ave. | Redwood City | San Mateo | 94063 |  |  | 2007-01-13 | 0.24306 | [6 empty] | High |  | SURFACE WATER IMPACT | No |  | No | No | None performed for this event. |  | Yes | Yes | No |  |  | No | No |  |  | 2007-02-09 | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | GREASE | -- Select One -- |  | This overflow was related to a previous SSO that took place on 1/13/2007. This location experienced another blockage later in the day. This SSO uses the same OES# (per OES request). There was some recovery however the amount is yet not known. | Supervisor | Ray Bartolo | 2007-01-29 | 650-780-7470
4522 | 21 | 1 | RedwoodCity | 2007-01-16 | 6000 | 6000 | 07-0270 | 2007-01-16 | Ray Bartolo | RedwoodCity | 855 Jefferson Ave. (Middlefield & Jefferson) | Redwood city | San Mateo | 94063 |  |  | 2007-01-13 | 0.44444 |  |  | Severe grease |  |  |  | Low | Redwood Creek | CAPTURED IN STORM DRAIN | Yes |  | No | No | SSO completely contained prior to pump station site. |  | Yes | Yes | No |  |  | No | No |  |  |  | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE | Severe grease | BLOCKAGE | GREASE | -- Select One -- |  | Main line blockage caused by severe grease. SSO was completely isolated to storm drain system and was not pumped out at Jefferson Ave Pump St. SSO wastewater was pumped out from storm drain system (6000 gls - 3 loads) and Storm drain pipe was plugged and flushed to clean 120 LF of pipe (500 gls). There was no discharge to state waters. | Public Works Supv | Ray Bartolo | 2007-01-16 | 650-780-7470
4058 | 20 | 2 | RedwoodCity | 2006-11-03 14:19 | 30000 | 4000 | 06-6414 | 2006-10-28 | Ray Bartolo | RedwoodCity | 990 Redwood Shores Pkwy | Redwood City | San Mateo | 94063 |  |  | 2006-10-28 | 11:30:00 A | [5 empty] | SUNNY WEATHER | High |  | SURFACE WATER IMPACT | No |  | No | Yes | There were no signs of solid waste matter, fish kill in nearby lagoon on the day of the spill (10/28/06 and again on 10/30/06. |  | Yes | Yes | No | No | No | Yes | No | Yes | No | 2006-11-07 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | RedwoodCity | PUMP STATION |  | INFRASTRUCTURE FAILURE | --Select None-- | --Select None-- |  | This release was due to what is being defined as a "glitch" in the SCADA system related to our pump station. We intend to take every corrective measure towards preventing this kind of a loss again. I am currently awaiting information from our SCADA consultant that will further provide incident information about the 10/28/06 event. We are also awaiting lab results that were taken on the incident date and another sampling taken on 10/30/06. We are also awaiting more information and a proposal from our consultant regarding additional layers of protection that may prevent this kind of an event in the future. I will be updating this report next week (week of 11/6/06). | Public Works Service | Ray Bartolo | 2006-10-28 | 650-780-7470 | rbartolo@redwoodcity.org;mharang@redwoodcity.org, lbarwacz@redwoodcity.org;mharang@redwoodcity.org | MAJOR | Ray Bartolo | City of Redwood City | 650-780-7470 |  | 1400 Broadway | Redwood city | San Mateo | 94063 | Ray Bartolo | RedwoodCity | 650-780-7470 |  | 1400 Broadway | Redwood City | San Mateo | 94063
4133 | 20 | 3 | RedwoodCity | 2006-10-28 | 30000 | 4000 | 06-6414 | 2006-10-28 | Ray Bartolo | RedwoodCity | 990 Redwood Shores Pkwy | Redwood City | San Mateo | 94063 |  |  | 2006-10-28 | 0.47917 | [6 empty] | High |  | SURFACE WATER IMPACT | No |  | No | Yes | There were no signs of solid waste matter, fish kill in nearby lagoon on the day of the spill (10/28/06 and again on 10/30/06. |  | Yes | Yes | No |  |  | Yes | No |  |  | 2006-11-07 | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | PUMP STATION |  | INFRASTRUCTURE FAILURE | -- Select One -- | -- Select One -- |  | This release was due to what is being defined as a "glitch" in the SCADA system related to our pump station. We intend to take every corrective measure towards preventing this kind of a loss again. I am currently awaiting information from our SCADA consultant that will further provide incident information about the 10/28/06 event. We are also awaiting lab results that were taken on the incident date and another sampling taken on 10/30/06. We are also awaiting more information and a proposal from our consultant regarding additional layers of protection that may prevent this kind of an event in the future. I will be updating this report next week (week of 11/6/06).Follow up (11/21/06) - Effective 11/14/06, our SCADA consultant has begun to install watchdog timers into each PLC's logic at each of our sewer lift station sites. The SCADA system will be programmed to monitor each station's timer in the event of a flatline on communications (which is what happened in this incident), the seperate timer will begin to increment to SCADA. The new system will page out an alert 10 minutes after a communications fail/malfunction takes place. I will advise and follow up to this report once this project has been completed. | Public Works Services | Ray Bartolo | 2006-10-28 | 650-780-7470
3945 | 19 | 1 | RedwoodCity | 2006-09-28 14:24 | 650 | 0 |  | 2006-09-28 14:24 |  | -- | Claremont & El Camino Real | Redwood City | San Mateo | 94063 |  |  | 2006-09-23 |  |  |  | Main sewer line cleared. Area was cleaned. Response personnel recovered 250 gallons from storm drain system. Actual release amount was 400gls. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | REDWOODCITY | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PW Supervisor | Ray Bartolo | 2006-09-28 | 650-780-7470 | rbartolo@redwoodcity.org;mharang@redwoodcity.org, lbarwacz@redwoodcity.org;mharang@redwoodcity.org | MINOR
3784 | 18 | 1 | RedwoodCity | 2006-08-24 14:33 | 750 | 0 |  | 2006-08-24 14:33 |  | -- | 848 Seminole | Redwood City | San Mateo | 94063 |  |  | 2006-08-24 |  |  |  | Maintenance crew responded to sewer manhole located at 848 Seminole. Most of wastewater was puddled around manhole at time of arrival and minimal amount flowed down to the half way point distance to nearest storm drain inlet. Downstream inlet was covered with a plastic mat at time of arrival, sewer main was immediately cleared and crew cleaned up area by watering down affected area of SSO and curb and gutter. All water that was used to wash down location was completely extracted by utilizing vactor unit. Water was then discharged back into sewer system. There was no SSO discharge into storm drain system. Strom drain system was inspected by storm drain maintenance leader. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RedwoodCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | PWS Supervisor | Ray bartolo | 2006-08-24 | 650-780-7470 | rbartolo@redwoodcity.org;mharang@redwoodcity.org, lbarwacz@redwoodcity.org;mharang@redwoodcity.org | MINOR
3814 | 17 | 2 | RedwoodCity | 2006-08-30 12:35 | 4500 | 0 | 06-5008 | 2006-08-22 | Ray Bartolo | RedwoodCity | 1628 El Camino Real (MH in sidewalk) | Redwood City | San Mateo | 94063 |  |  | 2006-08-22 | 8:30:00 AM | [5 empty] | SUNNY WEATHER | Medium |  | SURFACE WATER IMPACT | No |  | No | No | Storm maintenance personnel walked and inspected receiving creek (Eddy Lopez). Based on report, there was no sign of fish kill or waste matter in water. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | RedwoodCity | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- | Excessive grease | Following area cleanup and clearing of main line blockage, storm drain maintenance system personnel initiated a cleanup and removal of creek debris inside of receiving lined creek. The debris that was removed from creek was previously inside of creek prior to SSO. The debris included bay mud and other debris items not related to SSO. An Estimated 958 LF of lined creek was cleaned totaling roughly 20 cubic yards of mud was removed from the creek. This mud was saturated with wastewater as a result of the SSO. Following cleanup, there were no apparent and obvious signs of foul odor as there was prior to the cleanup. | Public Works Service | Ray Bartolo | 2006-08-22 | 650-780-7470 | rbartolo@redwoodcity.org;mharang@redwoodcity.org, lbarwacz@redwoodcity.org;mharang@redwoodcity.org | MAJOR | Ray Bartolo | City of Redwood City | 650-780-7470 |  | 1400 Broadway | Redwood city | San Mateo | 94063 | Ray Bartolo | RedwoodCity | 650-780-7470 |  | 1400 Broadway | Redwood City | San Mateo | 94063
3651 | 16 | 1 | RedwoodCity | 2006-07-24 12:22 | 100 | 0 |  | 2006-07-24 12:22 |  | -- | Maple & Main St. | Redwood City | San Mateo | 94063 |  |  | 2006-07-24 |  |  |  | We believe that the release was due to an offset of the sewer line that resulted in exfiltration into an abondoned storm drain line in the creek (Redwood Creek). Further CCTV inspection of the sewer main will take place on 7/25/06 to further evaluate. The hole in the abondoned storm drain line has been plugged by the contractor working on site. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RedwoodCity | PIPE | from abondoned storm drain line | BLOCKAGE | GREASE |  |  |  | public Wks Supv | Ray Bartolo | 2006-07-24 | 650-780-7470 | rbartolo@redwoodcity.org;mharang@redwoodcity.org, lbarwacz@redwoodcity.org;mharang@redwoodcity.org | MINOR
3378 | 15 | 2 | RedwoodCity | 2006-05-22 13:37 | 1000 | 0 | 06-2989 | 2006-05-18 | Ray Bartolo | REDWOODCITY | Northwest corner of Whipple Ave & Alameda De Las Pulgas | Redwood City | San Mateo | 94063 |  |  | 2006-05-18 | 11:30:00 A | [5 empty] | SUNNY WEATHER | Low |  | SURFACE WATER IMPACT | No |  | No | No | No sign of fecal matter. Also, storm drain line was plugged further downstream and 621 feet of storm drain pipe was flushed and cleaned following spill. Remaining 500 gallons of water was extracted (vactored) out of storm drain system. Also, 2 inlets and 4 strom drain manholes were inspected as well and found to have no fecal matter or odor. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | REDWOODCITY | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- |  |  | Public Works Service | Ray Bartolo | 2006-05-18 | 650-780-7470 | rbartolo@redwoodcity.org;mharang@redwoodcity.org, pingram@redwoodcity.org;mharang@redwoodcity.org | MAJOR | Ray Bartolo | City of Redwood City | 650-780-7470 |  | 1400 Broadway | Redwood city | San Mateo | 94063 | Ray Bartolo | REDWOODCITY | 650-780-7470 |  | 1400 Broadway | Redwood city | San Mateo | 94063
3303 | 14 | 6 | RedwoodCity | 2006-05-04 14:43 | 100 | 0 |  | 2006-05-04 14:43 |  | -- | 1852 El Camino Real - Redwood City | Redwood City | San Mateo | 94063 |  |  | 2006-04-19 |  |  |  | SSO final destination was curb & gutter. There was no release to storm drain system (inlet). The entire amount of spill was extracted (vactored) and returned to sewer system. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RedwoodCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Ray Bartolo | 2006-05-03 | 650-780-7470 | rbartolo@redwoodcity.org;pingram@redwoodcity.org | MINOR
3366 | 13 | 2 | RedwoodCity | 2006-05-18 14:46 | 3000 | 100 | 06-2245 | 2006-04-13 | Ray Bartolo | RedwoodCity | 990 Glennan Dr. | Redwood City | San Mateo | 94063 |  |  | 2006-04-13 | 8:15:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Medium | Stulsaft Creek | SURFACE WATER IMPACT | Yes |  | No | No | Storm drain Maintenance staff visually inspected Stulsaft creek and saw no sign of fecal matter or debris as a result of the spill. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2333 | jlam@waterboards.ca.gov | RedwoodCity | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- |  | Main line blockage and SSO occured in front of 990 Glennan Dr-Redwood City. Main line jetter responded and placed inlet covers on storm grate to minimize overflow impact. Immediately thereafter, storm drain crew arrived and inspected downstream inlets. Staff stated that storm drain flow was heavy with fresh stormwater. Five (5) storm drain manholes and one (1)inlet was inspected as well as the receiving body of water, Stulsaft creek. Based on inspection, there was no debris or fecal matter found inside of the creek. Also, main line root cutter truck was dispatched to Glennan Dr. to further clear and root cut main line - as a precausionary measure. | Supervisor | Ray Bartolo | 2006-04-13 | (650)780-7470 | jlam@waterboards.ca.gov | MAJOR | Ray Bartolo | City of Redwood City | 650-780-7470 |  | 1400 Broadway | Redwood City | San Mateo | 94063 | Ray Bartolo | REDWOOD CITY | 650-780-7470 |  | 1400 Broadway | Redwood City | San Mateo | 94063
3073 | 12 | 2 | RedwoodCity | 2006-03-27 11:29 | 4500 | 4500 | 06-1751 | 2006-03-24 | Ray Bartolo | REDWOODCITY | 898 Chestnut - on Bay Road (between Woodside Rd & Chestnut) | Redwood City | San Mateo | 94063 |  |  | 2006-03-24 | 12:30:00 P | [5 empty] | SUNNY WEATHER | Low | Redwood Creek | STORM DRAIN | No |  | No | No | Visual inspection verified that SSO did not reach creek/state waters. |  | Yes | Yes | No | No | No | No | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | REDWOODCITY | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- |  | Sewer overflow incident on 3/24/06 adjacent to 898 Chestnut. Man line was cleared at roughly 1:30pm. Mitigation/cleanup effort immediately took place. Storm Drain maintenance crews inspected 2 inlets and 3 storm drain manholes further downstream to determine location/extent of discharge. 1200 linear feet of storm drain line was inspected and cleaned. Line was plugged downstream from release point, hydro flushed then vactored out (2000 gallons of fresh water was used). Sewer main line was jetted/hydro flushed again on 3/27/06 for follow up maintenance. Storm maint crew verifies that entire SSO quantity was contained in storm drain system, extracted then discharged back into sewer system. | Public Works Service | Ray Bartolo | 2006-03-24 | 650-780-7470 | rbartolo@redwoodcity.org, pingram@redwoodcity.org | MAJOR | Ray Bartolo | City of Redwood City | 650-780-7470 |  | 1400 Broadway | Redwood City | San Mateo | 94063 | Ray Bartolo | REDWOOD CITY | 650-780-7470 |  | 1400 Broadway | Redwood City | San Mateo | 94063
3051 | 11 | 1 | RedwoodCity | 2006-03-23 09:41 | 50 | 0 |  | 2006-03-23 09:41 |  | -- | Cassia & Spring St. | Redwood City | San Mateo | 94063 |  |  | 2006-03-22 |  |  |  | Maintenance crews responded immediately. Sewer main line cleared. Storm drain crews inspected 3 inlets and determined wastewater only entered nearest one. Crews plugged storm drain line and flushed storm line then vactored out remaing water. No contact with state waters. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | REDWOODCITY | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Ray Bartolo | 2006-03-23 | 650-780-7470 | rbartolo@redwoodcity.org | MINOR
2725 | 10 | 2 | RedwoodCity | 2006-02-01 11:12 | 1500 | 50 | 06-0680 | 2006-01-31 | Ray Bartolo | REDWOODCITY | 3626 Glenwood Ave. | Redwood City | San Mateo | 94063 |  |  | 2006-01-31 | 11:30:00 A | [5 empty] | SUNNY WEATHER | Medium | Redwood Creek | STORM DRAIN | No |  | No | No | No inspection of receiving water. Most of overflow contained in strom drain line (per strom staff). Storm drain maint crews inspected downstream pipe and inlet (1000 feet downstream) and observed toilet paper in pipe. Crews plugged strom drain line at downstream location, flushed and vactored (extracted) liquid in storm drain line thus cleaning the storm drain system. Follow up maintenance (main line jetting and root cutting scheduled for 2/1/06. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | REDWOODCITY | MANHOLE | Follow up maintenance (main line jetting and root cutting) scheduled for 2/1/06 | BLOCKAGE | GREASE | --Select None-- |  |  | Public Works Service | Ray Bartolo | 2006-01-31 | 650-780-7470 | rbartolo@redwoodcity.org | MAJOR | Ray Bartolo | City of Redwood City | 650-780-7470 |  | 1400 Broadway | Redwood City | San Mateo | 94063 |  | REDWOODCITY
2706 | 9 | 1 | RedwoodCity | 2006-01-30 11:00 | 50 | 0 |  | 2006-01-30 11:00 |  | -- | 1017 Middlefield Road. (City Hall) - Redwood City | Redwood City | San Mateo | 94063 |  |  | 2006-01-19 |  |  |  | Sewer main blockage due to grease. Weather was sunny and clear. Main was immediately cleared and overflow in street was contained due to pre existing construction basin inlet socks. Overflow of wastewater out of manhole was not ongoing and only intermitten. Overflow area in street was immediately cleaned with absorbant material. On 1/21 (Sat), storm drain inlet and line was again inspected but cleaned. It was observed that there was no discharge out to the creek. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | REDWOODCITY | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Ray Bartolo | 2006-01-30 | 650-780-7470 | rbartolo@redwoodcity.org, pingram@redwoodcity.org | MINOR
2704 | 8 | 2 | RedwoodCity | 2006-01-30 10:43 | 1000 | 0 |  | 2006-01-30 10:43 |  | -- | 350 Marine Parkway - Redwood City (Redwood Shores) | Redwood City | San Mateo | 94063 |  |  | 2006-01-04 |  |  |  | Backup overflow estimated to be between 900 - 1000 gallons. This backup and office building overflowed for the second time in as many days. This backup resulted yet again in a first floor office building overflow. Again, a remediation company was called out again to clean affected areas. This backup also did not result in an overflow to creeks and/or streams. Main was again cleared. On 1/30/06, I had conversation with Johnson Lam to discuss reason for late notification (vacation). Mr. Lam recommended that this be reflected in this report. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | REDWOODCITY | PIPE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Ray Bartolo | 2006-01-30 | 650-780-7470 | rbartolo@redwoodcity.org, pingram@redwoodcity.org | MINOR
2700 | 7 | 1 | RedwoodCity | 2006-01-30 10:31 | 800 | 0 |  | 2006-01-30 10:31 |  | -- | 350 Marine Parkway / Redwood City (Commercial office building) no overflowing sewer manhole - | Redwood City | San Mateo | 94063 |  |  | 2006-01-03 |  |  |  | Sewer main line blockage was caused by grease. Overflow took place at upper lateral cleanout but primarily overflowed at the first floor of office building restroom located at 350 Marine World Parkway in Redwood Shores (Redwood City). Cleanup crew (ServiceMaster Restoration Services) was immediately requested to respond for cleaning remediation services. 700 gallons were extracted from office space and the affected areas were also sanitized. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | REDWOODCITY | OTHER | overlow source was from cleanout and office bldg | BLOCKAGE | GREASE |  |  |  | Supervisor | Ray Bartolo | 2006-01-30 | 650-780-7470 | rbartolo@redwoodcity.org, pingram@redwoodcity.org | MINOR
2080 | 6 | 1 | RedwoodCity | 2005-11-04 12:44 | 18000 | 2500 | 05-6371 | 2005-11-04 | Ray Bartolo | RedwoodCity | Overflow location was at Laurel & Hilton St, | Redwood City | San Mateo | 94063 |  |  | 2005-11-04 | 9:00:00 AM | [5 empty] | CLOUDY WEATHER | Medium |  | UNKNOWN | No |  | No | Yes | Flowed into Broadway pump station located at Woodside Road & Broadway them pumped out to receiving water at Bay Front canal. |  | Yes | Yes | No | No | No | Yes | No | Yes | No | 2005-11-18 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | RedwoodCity | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- |  | Sewer overflow incident out at Hilton & Laurel St - Redwood City (San Mateo County). Estimated 18,000 gallon overflow with estimated 2500 gallon recovery - employee responder stated that nearby resident stated that the overflow may have taken place the previous evening. Department did not receive any calls or request for service. Water samples are in the process of being taken at the following locations: 1) Broadway pump station 2)Douglas at Bay Front Canal 3)Marsh Road Tide gates (Bayside). | Public Works Supv | Ray Bartolo | 2005-11-04 | 650-780-7470 | rbartolo@redwoodcity.org, pingram@redwoodcity.org | MAJOR | Ray Bartolo | City of Redwood City | 650-780-7470 |  | 1400 Broadway | Redwood City | San Mateo | 94063 |  | redwoodcity | 650-780-7470 |  | 1400 Broadway | Redwood City | San Mateo | 94063
996 | 5 | 2 | RedwoodCity | 2005-02-09 13:45 | 3000 | 100 | 05-0756 | 2005-02-01 | Ray Bartolo | redwoodcity | 751 Canyon Road | Redwood City | San Mateo | 94063 |  |  | 2005-02-01 | 10:00:00 A | [5 empty] | SUNNY WEATHER | Medium | Redwood Creek | SURFACE WATER IMPACT | No |  | No | No | No signs of debris or any other indication of wastewater overflow. Storm Drain Maint personnel walked the entire length of creek receiving catch basin to open creek to determine extent of overflow. According to report from crew leader, there were no signs of dead or injured wildlife. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | redwoodcity | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- |  |  | Supervisor | Ray Bartolo | 2005-02-01 | 650-780-7470 | rbartolo@redwoodcity.org | MAJOR | Ray Bartolo | City of Redwood City | 650-780-7470 |  | 1400 Broadway | Redwood City | San Mateo | 94063 |  | redwoodcity | 650-780-7470 |  | 1400 Broadway | Redwood City | San Mateo | 94063
923 | 4 | 2 | RedwoodCity | 2005-01-28 11:40 | 9625 | 500 | 05-0523 | 2005-01-20 | Ray Bartolo | redwoodcity | Oak Ave & El Camino Real | Redwood City | San Mateo | 94063 |  |  | 2005-01-20 | 12:00:00 P | [5 empty] | SUNNY WEATHER | Medium |  | STORM DRAIN | No |  | No | No | No sign of odors or debris (according to Storm Drain Maint leader). Degreaser product was added to sewer manholes on Redwood Ave (upstream locations) and on El Camino Real on 1/20/05. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | redwoodcity | MANHOLE | Cause of overflow was related to main line jetting at upstream locations at 10 & 100 of Redwood Ave on previous day (1/19/05) of bloackage/overflow. | BLOCKAGE | GREASE | --Select None-- |  |  | Supervisor | Ray Bartolo | 2005-01-20 | 650-780-7470 | rbartolo@redwoodcity.org | MAJOR | Ray Bartolo | Redwood City | 650-780-7470 |  | 1400 Broadway | Redwood city | San Mateo | 94063 |  | redwoodcity | 650-780-7470 |  | 1400 Broadway | Redwood City | San Mateo | 94063
864 | 3 | 2 | RedwoodCity | 2005-01-18 10:09 | 6000 | 0 | 05-0314 | 2005-01-12 | Ray Bartolo | redwoodcity | 3640 Jefferson Ave. | Redwood City | San Mateo | 94063 |  |  | 2005-01-11 | 10:30:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | No sign of fish kill, solids or odors. Storm drain usually experiences heavy fresh water flow. Surrounding area was cleaned however crews were unable to extract wastewater from storm drain system. |  | Yes | No | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | redwoodcity | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- |  | Sewer main blockage incident located at 3640 Jefferson Ave. Wastewater flow from manhole directly into storm drain. Crews attempted to cleanup wastewater from system but were unable to due to rainy weather. | Supervisor | Ray Bartolo | 2005-01-12 | 650-780-7470 | rbartolo@redwoodcity.org | MAJOR | Ray Bartolo | City of Redwood City | 650-780-7470 |  | 1400 Broadway | Redwood City | San Mateo | 94063 |  | redwoodcity | 650-780-7470 |  | 1400 Broadway | Redwood City | San Mateo | 94063
612 | 2 | 3 | RedwoodCity | 2004-12-21 14:49 | 5000 | 0 | 04-6654 | 2004-12-19 | Ray Bartolo | redwoodcity | 1836 El Camino Real. Manhole overflowed on Oak Avenue at El Camino Real. | Redwood City | San Mateo | 94063 |  |  | 2004-12-19 | 10:35:00 A | [5 empty] | SUNNY WEATHER | Low |  | SURFACE WATER IMPACT | No |  | No | No | No signs of debris, solid waste matter or odors in Redwood Creek when inspected by storm drain maintenance crew Leader on day of overflow and on the third day after overflow. Samples have been collected and submitted to lab as a precautionary measure. Currently awaiting results. |  | Yes | Yes | No | No | No | Yes | No | Yes | No | 2004-01-07 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | redwoodcity | MANHOLE | Grease in main resulting in main line blockage. Main line will be televised to further determine cause of blockage. | BLOCKAGE | GREASE | --Select None-- |  | Catch basin is located right over boxed culvert where overflow took place thus underminning efforts to contain and remove wastewater. Main line will be televised to further determine why main line experienced a blockage. | Supervisor | Ray Bartolo | 2004-12-19 | 650-780-7470 | rbartolo@redwoodcity.org | MAJOR | Ray Bartolo | City of Redwood City | 650-780-7470 |  | 1400 Broadway | Redwood City | San Mateo | 94063 |  | redwoodcity | 650-780-7470 |  | 1400 Broadway | Redwood City | San Mateo | 94063
431 | 1 | 1 | RedwoodCity | 2004-12-08 08:32 | 500 | 0 |  | 2004-12-08 08:32 |  | -- | Sewer manhole at 121 Southgate. | Redwood City | San Mateo | 94063 |  |  | 2004-12-07 |  |  |  | Response included clearing of main line blockage by sewer crew. Also, storm drain crews responded on request to plug storm drain system and vactor out all wastewater from storm drain system. Storm drain line was flushed (jetted est 200FT)to assure no wastewater remained in storm system. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | redwoodcity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Ray Bartolo | 2004-12-08 | 650-780-7470 |  | MINOR
5126 | 14 | 1 | RichardsonBaySD | 2007-04-23 16:01 | 250 | 0 |  | 2007-04-23 16:01 |  | -- | 26 Sutter Court | Tiburon | Marin | 94941 |  |  | 2007-04-22 |  |  |  | MH TG 240.17. Reported at 1630. Roto Rooter arrived at 1715 hrs. Stoppage cleared at 1810 hrs. Spill in backyard easement due to roots/grease. Cleaned up by RBSD personnel on 4/23/07 | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Manager | Bonner Beuhler | 2007-04-23 | 415-388-1345
5088 | 13 | 1 | RichardsonBaySD | 2007-04-20 10:22 | 500 | 0 |  | 2007-04-20 10:22 |  | -- | 32 Great Circle Drive | Mill Valley | Marin | 94941 |  |  | 2007-04-16 |  |  |  | MH HP 220.03 in back yard of 32 Great Circle Drive. Partial stoppage in line due to grease, still flow in pipe to pump station wet well. Spill contained in yard. Reported to Roto Rooter at 0730 hrs, stoppage cleared with Hydrojet at 0915 hrs. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Manager | Bonner Beuhler | 2007-04-20 | 415-388-1345
4306 | 12 | 1 | RichardsonBaySD | 2006-12-14 08:24 | 400 | 0 |  | 2006-12-14 08:24 |  | -- | 125 Stewart Drive | Tiburon | Marin | 94920 |  |  | 2006-12-12 |  |  |  | Spill @ MH TG 233.01 in front of 125 Stewart Drive. Reported to Roto Rooter at 0800 hrs. Service tech arrived 0820. Spill stopped 0840. Most likely a root ball from lateral hung up at discharge mouth. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Manager | Bonner Beuhler | 2006-12-14 | 415-388-1345
3935 | 11 | 1 | RichardsonBaySD | 2006-09-27 14:03 | 500 | 0 |  | 2006-09-27 14:03 |  | -- | 594 Virginia Drive | Tiburon | Marin | 94920 |  |  | 2006-09-26 |  |  |  | Overflow from District rod hole RH TG 240.71 in backyard of 594 Virginia Drive. Reported by District staff @ 0800hrs. Called Roto Rooter, they responded to scene @ 0815 hrs. Stoppage cleared @ 0845 hrs. Added to annual cleaning program. Spill mostly contained in backyard. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RichardsonBaySD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Manager | Bonner Beuhler | 2006-09-27 | (415) 388-1345 | rbsdtg@aol.com, | MINOR
3812 | 10 | 1 | RichardsonBaySD | 2006-08-30 10:13 | 300 | 0 |  | 2006-08-30 10:13 |  | -- | 305 Trestle Glen Blvd. | Tiburon | Marin | 94941 |  |  | 2006-08-30 |  |  |  | Overflow at MH BG 224.03. Reported at 0755 hrs. by 305 Trestle Glen resident. Roto Rooter responded and cleared by 0900 hrs. Partial stoppage, some flow in downstream MH. Line serves 13 homes. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RichardsonBaySD | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Manager | Bonner Beuhler | 2006-08-30 | (415) 388-1345 | rbsdtg@aol.com, | MINOR
3591 | 9 | 1 | RichardsonBaySD | 2006-07-03 07:09 | 500 | 0 |  | 2006-07-03 07:09 |  | -- | 2 and 3 Warren Ct. MH BG 225.01 map page F3 | Tiburon | Marin | 94920 |  |  | 2006-06-28 |  |  |  | Overflow at MH BG 225.01 by resident 2 Warren Ct. 1125 hrs. MH in back of 3 Warren Ct. Cleared by Roto Rooter @ 1345 hrs. Stoppage appears to be 3/4 drain rock. Vactor and hydro lines to TV for source. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RichardsonBaySD | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Manager | Bonner Beuhler | 2006-07-03 | (415) 388-1345 | rbsdtg@aol.com, | MINOR
3120 | 8 | 1 | RichardsonBaySD | 2006-04-04 07:28 | 500 | 0 |  | 2006-04-04 07:28 |  | -- | 15 Rowley Circle | Tiburon | Marin | 94920 |  |  | 2006-04-03 |  |  |  | MH DM 225.33 in back of 15 Rowley Circle. Off-road easement, overflowing @ 0-2 GPM. Start 1530 stop 2030. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RichardsonBaySD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Manager | Bonner Beuhler | 2006-04-04 | 415.388.1345 | rbsdtg@aol.com, | MINOR
2852 | 7 | 1 | RichardsonBaySD | 2006-02-21 14:49 | 225 | 0 |  | 2006-02-21 14:49 |  | -- | 26 Sutter Ct. | Tiburon | Marin | 94920 |  |  | 2006-02-19 |  |  |  | Spill at MH TG 240.17 in backyard of 26 Sutter Ct. Spill reported at 1500 hrs. Roto Rooter arrived at 1600 hrs, cleared blockage at 1645 hrs. Grease and light roots. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RichardsonBaySD | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Manager | Bonner Beuhler | 2006-02-21 | (415) 388-1345 | rbsdtg@aol.com, | MINOR
2603 | 6 | 1 | RichardsonBaySD | 2006-01-11 11:13 | 500 | 0 |  | 2006-01-11 11:13 |  | -- | MH SW 100.11 in front of 213 E. Strawberry Drive | Mill Valley | Marin | 94941 |  |  | 2006-01-11 |  |  |  | Overflow reported at 0805 hrs. 1/11/2005. Roto Rooter responded and cleared stoppage @ 0905 hrs. Spill appeared to be approximately 5 to 8 gallons per minute. Cleaned gutter with Vactor. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RichardsonBaySD | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Manager | Bonner Beuhler | 2006-01-11 | (415) 388-1345 | rbsdtg@aol.com, | MINOR
2563 | 5 | 1 | RichardsonBaySD | 2006-01-06 14:24 | 500 | 0 |  | 2006-01-06 14:24 |  | -- | 3 Mercury Avenue | Tiburon | Marin | 94941 |  |  | 2005-12-31 |  |  |  | Lateral surchaged, some overflow from popoff valve at house clean out. 5" of rain during storm, excessive infiltration into sewer. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RichardsonBaySD | OTHER | perimeter of house, pop off valve | BLOCKAGE | --Select None-- |  |  |  | Manager | Bonner Beuhler | 2006-01-06 | (415) 388-1345 | rbsdtg@aol.com, | MINOR
2137 | 4 | 1 | RichardsonBaySD | 2005-11-17 14:16 | 750 | 0 |  | 2005-11-17 14:16 |  | -- | MH RR 260.15, MH on easement located at 104 Tiburon Blvd., Tiburon, CA 94941. | Mill Valley | CA | 94941 |  |  | 2005-11-17 |  |  |  | Call reported at 1055 hrs. Roto Rooter and RBSD staff responded. Stoppage cleared by Roto Rooter at about 1145 hrs. Overflow amount approx. 3-5 gallon per minute. Opened with small machine, rerun with HydroJet/Vactor. Spill on culvert on property edge that runs into area drain. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RichardsonBaySD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Assistant Manager | Bonner Beuhler | 2005-11-17 | (415) 388-1345 | rbsdtg@aol.com, | MINOR
1564 | 3 | 1 | RichardsonBaySD | 2005-06-27 11:17 | 500 | 0 |  | 2005-06-27 11:17 |  | -- | MH HP220.03 located in back of 32 Great Cirle Way | Mill Valley | Marin | 94941 |  |  | 2005-06-27 |  |  |  | Call received at approx. 0815 hrs. Responded, called Roto Rooter. Set up emergency pump around to stop overflow. Overflow stopped at approx. 0915 hrs. Spill appeared about 2-5 gallons per minute. Contained in planted area in back of house. Roto Rooter cleared stoppage at about 1015 hrs. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RichardsonBaySD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Asst. Manager | Bonner Beuhler | 2005-06-27 | 415-388-1345 | rbsdtg@aol.com, | MINOR
872 | 2 | 1 | RichardsonBaySD | 2005-01-19 08:12 | 850 | 0 |  | 2005-01-19 08:12 |  | -- | Rod Hole R-103 Map pg. F-5 in easement between 400 & 402 Hillary Drive | Tiburon | Marin | 94941 |  |  | 2005-01-17 |  |  |  | Spill reported 5:00 pm, Roto-Rooter arrived on scene @ 5:10 pm. Stoppage cleared @ 6:00 pm. Spill contained along flat area at bottom of lots. Roto Rooter pumped contained sewage with pump truck. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RichardsonBaySD | CLEAN OUT |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Asst. Manager | Bonner Beuhler | 2005-01-19 | 415-388-1345 | rbsdtg@aol.com, pribking@aol.com | MINOR
415 | 1 | 2 | RichardsonBaySD | 2004-12-06 10:33 | 200 | 0 |  | 2004-12-06 10:33 |  | -- | MH SW 424.09 - Map page C3. Easement in back of Blackfield Drive. | Tiburon | Marin | 94920 |  |  | 2004-12-06 |  |  |  | Stoppage caused by grease stoppage at the mouth of pipe exiting MH SW 424.09. Probed with bar. Stoppage partially cleared, then ran with blades, stoppage cleared within 5 min. of setup. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RichardsonBaySD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Assistant Mangager | Bonner Beuhler | 2004-12-06 | 415-388-2402 |  | MINOR
5030 | 69 | 1 | Richmond | 2007-04-02 16:22 | 220 | 0 |  | 2007-04-02 16:22 |  | -- | 2548 MARICOPA | RICHMOND | CONTRA COSTA | 94804 |  |  | 2007-03-29 |  |  |  | THE CITY CREW WAS NOTIFIED AT 1555 AND ON SCENE AT 1610 HOURS. THE DISCHARGE WAS STOPPED AT 1745 HOURS. THE ESTIMATED RATE OF DISCHARGE WAS 2 GPM. APPROXIMATELY 195 GALLONS OF THE OVERFLOW WAS RECOVERED AND DISCHARGED BACK INTO THE SANITARY SEWER. ADDITIONALLY, 400 GALLONS OF POTABLE WATER WAS USED TO FLUSH THE SPILL AND ALL OF IT WAS RECOVERED AND DISCHARGED INTO THE SANITARY SEWER FOR TREATMENT. THE BLOCKAGE WAS DUE TO GREASE BUILDUP ON SHOP TOWELS IN THE SANITARY SEWER PIPELINE. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | SR INDUST WASTE INSP | STEPHEN FRIDAY | 2007-04-02 | 510-412-2009
4737 | 68 | 1 | Richmond | 2007-02-12 12:03 | 450 | 0 |  | 2007-02-12 12:03 |  | -- | 500 DIMM STREET | RICHMOND | CONTRA COSTA | 94805 |  |  | 2007-02-11 |  |  |  | THE CITY SEWER CREW WAS NOTIFIED AT 0945 HRS AND ON SCENE AT 1025 HOURS. THE DISCHARGE WAS STOPPED AT 1045 HRS. ESTIMATES OF THE DURATION IS ONE HOUR AND THE RATE OF DISCHARGE 7.5 GPM. APPROXIMATELY 450 GALLONS OF SEWAGE OVERFLOWED AND 436 GALLONS OF IT WAS COLLECTED AND DISCHAREGED BACK TO THE SANITARY SEWER FOR TREATMENT AT THE POTW. APPROXIMATELY 1000 GALLONS OF FLUSH WATER WAS USED TO COMPLETE THE CLEANUP AND ALL OF IT WAS RECOVERED AND DISCHARGED INTO THE SANITARY SEWER. THE CAUSE OF THE OVERFLOW WAS DUE TO ROOTS AND SHOP TOWELS FOUND IN THE PIPE. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2007-02-12 | 510-412-2009
4524 | 67 | 1 | Richmond | 2007-01-16 14:43 | 500 | 0 |  | 2007-01-16 14:43 |  | -- | INTERSECTION OF 19TH STREET & MACDONALD AVENUE | RICHMOND | CONTRA COSTA | 94804 |  |  | 2007-01-16 |  |  |  | THE CITY RECEIVED THE REPORT AT 0810 HRS AND WAS ON SCENE AT 0830 HRS. THE BLOCKAGE WAS CLEARED AND THE SEWAGE DISCHARGE STOPPED AT 0840 HRS. THE AREA CONTAMINATED WITH THE SEWAGE WAS FLUSHED WITH CLEAN WATER & ALL THE SEWAGE AND FLUSH WATER WAS COLLECTED AND DISCHARGED INTO THE SANITARY SEWER FOR TREATMENT AT THE POTW. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2007-01-16 | 510-412-2009
4499 | 66 | 1 | Richmond | 2007-01-11 10:53 | 233 | 0 |  | 2007-01-11 10:53 |  | -- | THE INTERSECTION OF MCBRYDE AVENUE & 26TH STREET | RICHMOND | CONTRA COSTA | 94804 |  |  | 2007-01-11 |  |  |  | THE CITY WAS NOTIFIED AT 1300 HRS AND ON SCENE AT 1320 HRS. THE SSO WAS STOPPED AT 1340 HRS. ALL OF THE DISCHARGED SEWAGE WAS RECOVERED AND DISCHARGED BACK INTO THE SANITARY SEWER. THE AREA EXPOSED TO THE SEWAGE WAS FLUSHED, DISINFECTED AND VACUUMED UP. THE CLEAN-UP WATER WAS ALSO DISCHARGED INTO THE SANITARY SEWER COLLECTION SYSTEM. THE ACTIVITY IN THE AREA IS RESIDENTIAL. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SR INDTL WASTE INSPR | STEPHEN FRIDAY | 2007-01-11 | 510-412-2009
4285 | 65 | 1 | Richmond | 2006-12-11 16:08 | 160 | 0 |  | 2006-12-11 16:08 |  | -- | 438 SOUTH 20TH STREET | RICHMOND | CONTRA COSTA | 84804 |  |  | 2006-12-11 |  |  |  | THE CITY CREW WAS NOTIFIED AT 0900 HOURS AND ON SCENE AT 0930 HOURS. THE OVERFLOW WAS CONTAINED AND 200 GALLONS OF FLUSH WATER WAS USED FOR THE CLEANUP. THE TOTAL 360 GALLONS OF WASTEWATER WAS VACTORED UP AND DISCHARGED TO THE SANITARY SEWER. NO RECEIVING WATERS WEE AFFECTED. | [5 empty] | NO WATER INVOLVED | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SR INDST WASTE INPST | STEPHEN FRIDAY | 2006-12-11 | 510-412-2009
3741 | 64 | 2 | Richmond | 2006-08-15 10:57 | 0 | 0 |  | 2006-08-15 10:57 |  | -- | 417 SOUTH 35TH STREET | RICHMOND | CONTRA COSTA | 94804 |  |  | 2006-08-10 |  |  |  | THE CITY CREW RECEIVED THE REPORT AT 0950 HRS & ARRIVED ON SCENE AT 1005 HOURS. THE BLOCKAGE WAS CLEARED AT 1035 HRS. ESTIMATED DURATION & RATE OF DISCHARGE WAS 30 MINS AT 10 GPM. THE 300 GALS OF SEWAGE WAS CAPTURED IN A BERM ON CUTTING BOULEVARD & SOUTH 35TH STREET, NONE ENTERED ANY STORM DRAIN. THE IMPACTED AREA WAS FLUSHED WITH 250 GALLON OF CLEAN WATER & ALL 550 GALS WERE VACTORED UP AND DISCHARGED TO THE SANITARY SEWER. THE CITY'S INDUSTRIAL PRETREATMENT PROGRAM DISTRIBUTED FOG INFORMATION TO PROPETIES IN THE IMMEDIATE AREA. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2006-08-15 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
3695 | 63 | 2 | Richmond | 2006-08-07 14:36 | 1200 | 1200 | 06-4633 | 2006-08-03 | STEPHEN FRIDAY | Richmond | INTERSECTION OF 39TH STREET AND NEVIN AVENUE | RICHMOND | CONTRA COSTA | 94804 | 37.9364 | 122.3319 | 2006-08-03 | 9:00:00 AM | [5 empty] | SUNNY WEATHER | Low | SAN FRANCISCO BAY | STORM DRAIN | No |  | No | No | NO SEWAGE OR POLLUTANTS OBSERVED BY INSPECTION TEAM. |  | Yes | Yes | No | No | No | No | No | No | No | 2006-08-04 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Richmond | PIPE |  | BLOCKAGE | GREASE | --Select None-- |  | THE SANITARY SEWER MAIN SURCHARGED DUE TO THE GREASE BLOCKAGE, PRESSURIZING THE LINE. SEWAGE LEAKED OUT OF THE SANITARY SEWER MAIN AND INTO AN ADJACENT STORM DRAIN PIPE THAT ALSO HAD A BREACH. THE STORM LINE IS CONNECTED TO A LIFT STATION. THE POWER TO THE LIFT STATION WAS SECURED PREVENTING ANY DISCHARGE TO SAN FRANCISO BAY. BOTH THE STORM DRAIN AND SANITARY SEWER SEWER LINES ARE BEING REPAIRED AT THIS TIME WITH CAPITAL IMPROVEMENT MONEY. | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2006-08-03 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MAJOR | STEPHEN FRIDAY | CITY OF RICHMOND | 510-412-2009 |  | 1401 MARINA WAY SOUTH | RICHMOND | CONTRA COSTA | 94804 |  | City of Richmond | 510-412-2009 |  | 1401 Marina Way South | Richmond | Contra Costa | 94804
3663 | 62 | 1 | Richmond | 2006-07-25 17:22 | 0 | 0 |  | 2006-07-25 17:22 |  | -- | Seacliff Avenue & Spinnaker Way | Richmond | Contra Costa | 94801 |  |  | 2006-07-21 |  |  |  | At approx. 0500 hours there was a power outage at the Seacliff Sanitary Sewer Pump Station. The pump station overlfowed for approx. two hours at an estimated rate of 3 gpm. None of the sewage entered the storm drain or any waters of the state and all of it was vactored up for disposal at City's wastewater treatment plant. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | MANHOLE |  | ELECTRICAL POWER FAILURE | --Select None-- |  |  |  | Sr Indst Waste Inspt | Stephen Friday | 2006-07-25 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
3131 | 61 | 1 | Richmond | 2006-04-05 17:02 | 100 | 0 |  | 2006-04-05 17:02 |  | -- | 2238 KEY BOULEVARD | RICHMOND | CONTRA COSTA | 94805 |  |  | 2006-04-03 |  |  |  | CITY SEWER CREW WAS NOTIFIED AT 1530 HURS AND ON SCENE AT 1600 HOURS. THE GREASE OBSTRUCTION WAS CLEARED AND THE OVERFLOW STOPPED AT 1620 HOURS. THE DISCHARGE DURATION IS ESTIMATED AT 50 MINUTES. APPROXIMATLY 300 GALLONS DISCHARGED AND 200 GALLONS WAS VACTORED UP FOR TREATMENT AT THE POTW. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SR INDST WASTE INPST | STEPHEN FRIDAY | 2006-04-05 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
3010 | 60 | 1 | Richmond | 2006-03-15 13:28 | 500 | 0 |  | 2006-03-15 13:28 |  | -- | INTERSECTIN OF 23RD STREET AND MARICOPA AVENUE (RICHMOND HIGH SCHOOL0 | RICHMOND | CONTRA COSAT | 94804 |  |  | 2006-03-13 |  |  |  | THE CITY SEWER CREW ARRIVED ON SCENE AT 0920 HRS & THE SSO WAS REPORTED AT 0900 HRS. THE REPORTING PARTY STATED THAT THE SSO HAD OCCURRED FOR 24 HRS. IT WAS ESTIMATED THE RATE OF DISCHARGE WAS 2 GPM FOR A TOTAL OF 1800 GALS DISCHARGED. THE CREW RECOVERED AN ESTIMATED 1300 GALLONS FOR DISPOSAL AT THE POTW. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SR INDST WASTE INPST | STEPHEN FRIDAY | 2006-03-15 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
2921 | 58 | 2 | Richmond | 2006-03-03 09:37 | 175 | 0 |  | 2006-03-03 09:37 |  | -- | INTERSECTION OF SAN PABLO AVENUE & MACDONALD AVENUE | RICHMOND | CONTRA COSTA | 94801 |  |  | 2006-03-02 |  |  |  | CITY SEWER CREW ON SCENE AT 1345 HOURS AND STOPPED DISCHARGE AT 1425 HOURS. ESTIMATED RATE OF DISCHARGE WAS 5 GPM. ESTIMATE 225 GALLONS DISCHARGED & 50 WERE RECOVERED. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SR INDUST WASTE INSP | STEPHEN FRIDAY | 2006-03-03 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
2923 | 59 | 1 | Richmond | 2006-03-03 10:11 | 100 | 0 |  | 2006-03-03 10:11 |  | -- | INTERSECTION OF BRICKYARD COVE LAND, SANDPIPER SPIT & SEACLIFF DRIVE, SANITARY SEWER PUMP STATION. | RICHMOND | CONTRA COSTA | 94801 |  |  | 2006-02-28 |  |  |  | CITY SEWER CREW WAS NOTIFED AT 1100 HOURS & WAS ON SCENE AT 1115 HOURS. THE DISCHARGE WAS STOPPED AT 1130 HOURS AND A PUMP BY-PASS WAS INSTALLED WHILE PG&E RESTORED POWER TO THE PUMP STATION. THE POWER OUTAGE LASTED FOR OVER 2 HOURS AND WAS DUE TO RAIN WATER ENTERING THIER VAULT SHORTING THE SYSTEM. 300 GALLONS OF DISCHARGED SEWAGE WAS RECOVERED. THE DISCHARGE OCCURED FROM A MANHOLE UPSTREAM OF THE PUMP STATION. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | MANHOLE |  | ELECTRICAL POWER FAILURE | --Select None-- |  |  |  | SR INDUST WASTE INSP | STEPHEN FRIDAY | 2006-03-03 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
2801 | 57 | 1 | Richmond | 2006-02-14 09:16 | 20 | 0 |  | 2006-02-14 09:16 |  | -- | INTERSECTION OF 24TH STREET & ANDRADE AVENUE | RICHMOND | CONTRA COSTA | 94804 |  |  | 2006-02-09 |  |  |  | THE CITY WAS NOTIFIED @ 1000 HOURS & WAS ON SCENE AT 1010 HOURS. ESTIMATED DISCHARGE OCCURED FOR ONE HOUR @ 5 GPM FOR A TOTAL OF 300 GALLONS. ESIMATED 280 GALLONS WERE RECOVERED OFF THE STREET & ONLY 20 GALLONS ENTERED THE STORM DRAIN. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2006-02-14 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
2452 | 55 | 2 | Richmond | 2006-01-03 17:00 | 1200 | 0 | 06-0024 | 2006-01-01 | Stephen Friday | Richmond | Intersection of 39th Street & Nevin Avenue | Richmond | Contra Costa | 94804 | 37.935 | 122.332 | 2005-12-31 | 12:01:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Low | San Francisco Bay | STORM DRAIN | No |  | No | No | Overflowed sewage dissipated due to intense and long duration rain event. |  | Yes | No | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Richmond | MANHOLE |  | FLOW CAPACITY DEFICIENCY | --Select None-- | --Select None-- |  | Due to storm events occurring at back-to-back intervals with a frequency greater than normal the City's sanitary sewer collection system experienced hydrologic overloading. The rate of discharge was estimated at up to 100 gpm and the total volume discharged from infiltration and inflow stormwater (90%) and sewage (10%) was estimated at 12,000 gallons (1,200 gallons was sewage). | SR. INDUSTRIAL WASTE | STEPHEN FRIDAY | 2006-01-01 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MAJOR | Stephen Friday | City of Richmond | 510-412-2009 |  | 1401 Marina Way South | Richmond | Contra Costa | 94804 |  | Richmond | 510-412-2009 |  | 1401 Marina Way Sough | Richmond | Contra Costa | 94804
2584 | 56 | 2 | Richmond | 2006-01-09 11:30 | 505300 | 0 | 06-0024 | 2006-01-01 | Stephen Friday | richmond | Intersection of Harbour Way South & Wright Avenue | Richmond | Contra Costa | 94804 | 37.925 | 122.376 | 2005-12-31 | 12:01:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Medium | SAN FRANCISCO BAY | SURFACE WATER IMPACT | No |  | No | No | NONE OBSERVED DUE TO THE INTENSITY OF THE STORM. |  | Yes | No | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | richmond | OTHER | OVERFLOW WEIR | FLOW CAPACITY DEFICIENCY | --Select None-- | LEAKS OF COLLECTION SYSTEM |  | AFTER MANY DAYS OF RAIN THE CITY'S SANITARY SEWER COLLECTION SYSTEM WAS A CAPACITY. THE OVERFLOW WEIR IS A PUBLIC SAFETY CONVEYANCE TO PREVENT SEWAGE FROM DISCHARGING ONTO THE STREETS. 5,053,000 TOTAL DISCHARGED FROM THE WEIR ACCORDING TO THE TOTALIZER. 90% IS STORMWATER AND THE REMAINING 10% WAS RAW SEWAGE. | SR. INDUSTRIAL WASTE | STEPHEN FRIDAY | 2006-01-01 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MAJOR | STEPHEN FRIDAY | CITY OF RICHMOND | 510-412-2009 |  | 1401 MARINA WAY SOUTH | RICHMOND | CONTRA COSTA | 94804 | CITY OF RICHMOND | Richmond | 510-412-2009 |  | 1401 MARINA WAY SOUTH | RICHMOND | CONTRA COSTA | 94804
2453 | 54 | 3 | Richmond | 2006-01-03 17:02 | 3600 | 0 | 06-0024 | 2006-01-01 | Stephen Friday | Richmond | Intersection of Barrett Avenue & San Pablo Avenue | Richmond | Contra Costa | 94804 | 37.936 | 122.325 | 2005-12-31 | 12:01:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Low | San Francisco Bay | STORM DRAIN | No |  | No | No | Overflowing sewage dissipated due to intense and long duration rain event. |  | Yes | No | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Richmond | MANHOLE |  | FLOW CAPACITY DEFICIENCY | --Select None-- | --Select None-- |  | Due to storm events occurring at back-to-back intervals with a frequency greater than normal the City's sanitary sewer collection system experienced hydrologic overloading. The rate of discharge was estimated at up to 150 gpm and the total volume discharged from infiltration and inflow stormwater (90%) and sewage (10%) was estimated at 36,000 gallons (3,600 gallons was sewage). | SR. INDUSTRIAL WASTE | STEPHEN FRIDAY | 2006-01-01 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MAJOR | Stephen | Friday | 510-412-2009 |  | 1401 Marina Way South | Richmond | Contra Costa | 94804 |  | Richmond | 510-412-2009 |  | 1401 Marina Way South | Richmond | Contra Costa | 94804
4503 | 56 | 3 | Richmond | 2006-01-01 | 5053000 | 0 | 06-0024 | 2006-01-01 | Stephen Friday | Richmond | Intersection of Harbour Way South & Wright Avenue | Richmond | Contra Costa | 94804 |  |  | 2005-12-31 | 0.00069444 | [6 empty] | Medium | SAN FRANCISCO BAY | SURFACE WATER IMPACT | No |  | No | No | NONE OBSERVED DUE TO THE INTENSITY OF THE STORM. |  | Yes | No | No |  |  | No | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | OTHER |  | FLOW CAPACITY DEFICIENCY | -- Select One -- | LEAKS OF COLLECTION SYSTEM | OVERFLOW WEIR | AFTER MANY DAYS OF RAIN THE CITY'S SANITARY SEWER COLLECTION SYSTEM WAS A CAPACITY. THE OVERFLOW WEIR IS A PUBLIC SAFETY CONVEYANCE TO PREVENT SEWAGE FROM DISCHARGING ONTO THE STREETS. 5,053,000 TOTAL DISCHARGED FROM THE WEIR ACCORDING TO THE TOTALIZER. 90% IS STORMWATER AND THE REMAINING 10% WAS RAW SEWAGE. | SR. INDUSTRIAL WASTE INSPECTOR | STEPHEN FRIDAY | 2006-01-01 | 510-412-2009
2262 | 49 | 1 | Richmond | 2005-12-18 16:23 | 84000 | 24000 | 05-7279 | 2005-12-18 | Ryan Johnson |  | San Pablo and Barrett, intersection | Richmond | Contra Costa | 94805 |  |  | 2005-12-18 | 7:30:00 AM | 2005-12-18 | 2:30:00 PM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Collections system M | Ryan Johnson | 2005-12-18 | 510-412-2001 | ryan.johnson@veoliawaterna.com | 24HR |  |  | 510-412-2001 | [6 empty] | Richmond
2264 | 51 | 1 | Richmond | 2005-12-18 16:32 | 3000 | 500 | 05-7280 | 2005-12-18 | Ryan Johnson |  | 216 Western | Point Richmond | Contra Costa | 94804 |  |  | 2005-12-18 | 11:00:00 A | 2005-12-18 | 12:00:00 P | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Collections system M | Ryan Johnson | 2005-12-18 | 510-412-2001 | ryan.johnson@veoliawaterna.com | 24HR |  |  | 510-412-2001 | [6 empty] | Richmond
2279 | 53 | 1 | Richmond | 2005-12-19 11:50 | 148000 | 0 | 05-7298 | 2005-12-19 | STEPHEN FRIDAY | Richmond | INTERSECTION OF HARBOUR WAY SOUTH & WRIGHT AVENUE | RICHMOND | CONTRA COSTA | 94804 | 37.922 | -122.36 | 2005-12-18 | 6:15:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | High | SAN FRANCISCO BAY | SURFACE WATER IMPACT | No |  | No | No | NONE |  | Yes | No | No | No | No | Yes | Yes | Yes | No | 2005-12-20 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Richmond | OTHER | OVERFLOW STRUCTURE | FLOW CAPACITY DEFICIENCY | --Select None-- | --Select None-- |  | CITY WAS AWARE OF THE INCIDENT AT 16:30 HOURS ON 12/18/05 DUE TO CITY WIDE MAJOR OPERATIONAL IMPACT FROM THE LARGE AMOUNT OF RAIN IN A SHORT TIME PERIOD. READINGS WERE VERIFIED ON 12/19/05 AT OVERFLOW STRUCTURE STATIONS (2)& ONLY ONE DISHCHARGED INTO SAN FRANCISCO BAY. A TOTAL OF 1,480,000 GALLONS OF COMBINED SEWAGE WITH I&I (STORMWATER/GROUNDWATER) DISCHARGED AT A RATIO OF 10% SEWAGE TO 90% I&I. | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2005-12-19 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MAJOR | STEPHEN FRIDAY | CITY OF RICHMOND | 510-412-2009 |  | 1401 MARINA WAY SOUTH | RICHMOND | CONTRA COSTA | 94804 |  | City of Richmond | 510-412-2009 |  | 1401 Marina Way South | Richmond | Contra Costa | 94804
2272 | 52 | 2 | Richmond | 2005-12-19 11:10 | 3000 | 500 | 05-7279 | 2005-12-18 | Ryan Johnson | Richmond | 216 Western Drive | Point Richmond | Contra Costa | 94804 | 37.923 | -122.388 | 2005-12-18 | 11:00:00 A | [5 empty] | RAINY WEATHER | Low | SAN FRANCISCO BAY | STORM DRAIN | No |  | No | No | NONE |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Richmond | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- |  | OVERFLOW WAS A COMBINATION OF THE BLOCKAGE WITH THE I&I DUE TO THE HIGH AMOUNT OF RAIN DURING A SHORT PERIOD OF TIME. | Collection system Ma | Ryan Johnson | 2005-12-18 | 510-412-2001 | ryan.johnson@veoliawaterna.com | MAJOR | STEPHEN FRIDAY | CITY OF RICHMOND | 510-412-2009 |  | 1401 MARINA WAY SOUTH | RICHMOND | CONTRA COSTA | 94804 | Ryan Johnson | City of Richmond | 510-412-2009 |  | 1401 Marina Way South | Richmond | Contra Costa | 94804
4502 | 53 | 3 | Richmond | 2005-12-19 | 1480000 | 0 | 05-7298 | 2005-12-19 | STEPHEN FRIDAY | Richmond | INTERSECTION OF HARBOUR WAY SOUTH & WRIGHT AVENUE | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-12-18 | 0.26042 | [6 empty] | High | SAN FRANCISCO BAY | SURFACE WATER IMPACT | No |  | No | No | NONE |  | Yes | No | No |  |  | Yes | Yes |  |  | 2005-12-20 | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | OTHER |  | FLOW CAPACITY DEFICIENCY | -- Select One -- | -- Select One -- | OVERFLOW STRUCTURE | CITY WAS AWARE OF THE INCIDENT AT 16:30 HOURS ON 12/18/05 DUE TO CITY WIDE MAJOR OPERATIONAL IMPACT FROM THE LARGE AMOUNT OF RAIN IN A SHORT TIME PERIOD. READINGS WERE VERIFIED ON 12/19/05 AT OVERFLOW STRUCTURE STATIONS (2)& ONLY ONE DISHCHARGED INTO SAN FRANCISCO BAY. A TOTAL OF 1,480,000 GALLONS OF COMBINED SEWAGE WITH I&I (STORMWATER/GROUNDWATER) DISCHARGED AT A RATIO OF 10% SEWAGE TO 90% I&I. | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2005-12-19 | 510-412-2009
2280 | 50 | 4 | Richmond | 2005-12-19 11:51 | 8400 | 2400 | 05-7279 | 2005-12-18 | Ryan Johnson | Richmond | San Pablo and Barrett | Richmond | Contra Costa | 94805 | 37.935 | -122.325 | 2005-12-18 | 7:30:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low | SAN FRANCISCO BAY | STORM DRAIN | No |  | No | No | NONE |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | 2005-12-18 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Richmond | MANHOLE |  | FLOW CAPACITY DEFICIENCY | --Select None-- | --Select None-- |  | THE OVERFLOW WAS A RESULT OF A HIGH AMOUNT OF RAIN IN A SHORT PERIOD OF TIME. A COMBINATION OF 84,000 GALLONS OF I&I (STORMWATER/GROUNDWATER) DISCHARGED INTO SAN FRANCISCO BAY AT A RATIO OF 10% SEWAGE & 90% STORMWATER/GRONDWATER. | Collections system M | Ryan Johnson | 2005-12-18 | 510-412-2001 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MAJOR | STEPHEN FRIDAY | CITY OF RICHMOND | 510-412-2009 |  | 1401 MARINA WAY SOUTH | RICHMOND | CONTRA COSTA | 94804 |  | City of Richmond | 510-412-2009 |  | 1401 Marina Way South | Richmond | Contra Costa | 94804
2251 | 47 | 1 | Richmond | 2005-12-13 16:04 | 100 | 0 |  | 2005-12-13 16:04 |  | -- | INTERSECTION OF ORCHARD AVENUE AND SAN PABLO AVENUE | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-12-13 |  |  |  | CITY SEWER CREW NOTIFED AT 1015 HOURS AND ON SCENE AT 1020 HOURS. DISCHARGED STOPPED AT 1100 HOURS. RATE OF DISCHARGE 0.5 GALLONS PER MINUTE. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | richmond | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SR INDUST WATED INSP | STEPHEN FRIDAY | 2005-12-13 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
2261 | 48 | 2 | Richmond | 2005-12-16 12:39 | 7200 | 500 | 05-7208 | 2005-12-14 | STEPHEN FRIDAY | RICHMOND | INTERSECTION OF FLEMING AVENUE & ELLS STREET | RICHMOND | CONTRA COSTA | 94804 | 37.917 | 122.322 | 2005-12-13 | 12:30:00 A | [5 empty] | CLOUDY WEATHER | Low | SAN FRANCISCO BAY | STORM DRAIN | No |  | No | No | NO IMPACT OBSERVED IN RECEIVING WATERBODY |  | Yes | Yes | No | No | No | No | No | No | No | 2005-12-15 | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | RICHMOND | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- |  | THE AREA OF ORIGIN IS AT THE BORDER OF SEPERATE SEWER DISTRICTS (STEGE/RICHMON). WHEN STEGE REPORTED IT TO THE CITY OF RICHMOND THE CITY'S SEWER CREW WAS ON SCENE WITHIN 15 MINUTES. THEY RECOVER APPROX. 500 GALLONS & USED 500 GALLONS ON FLUSH WATER FOR THE CLEANUP WHICH WAS ALSO RECOVERED AND DISPOSED OF IN THE SANITARY SEWER. THE IPP SUBSEQUENTLY POSTED 50 GREASE DISPOSAL OUTREACH DOORHANGERS IN THE CONTRIBUTARY AREA WHICH INCLUDED A HIGH DENSITY APT. BUILDING. | SR. INDUSTRIAL WASTE | STEPHEN FRIDAY | 2005-12-14 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MAJOR | STEPHEN FRIDAY | CITY OF RICHMOND | 510-412-2009 |  | 1401 MARINA WAY SOUTH | RICHMOND | CONTRA COSTA | 94804 | UNKNOWN | CITY OF RICHMOND
2249 | 46 | 1 | Richmond | 2005-12-13 16:00 | 350 | 0 |  | 2005-12-13 16:00 |  | -- | 830 23RD STREET | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-12-12 |  |  |  | CITY SEWER CREW NOTIFIED AT 1100 HOURS & ON SCENE AT 1115. DISCHARGE STOPPED AT 1140 HOURS. eSITAMATE RATE OF DISCHARGE 1 GALLON PER MINUTE. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | richmond | OTHER | LATERAL | BLOCKAGE | GREASE |  |  |  | SR INDUST WASTE INSP | STEPHEN FRIDAY | 2005-12-13 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
2127 | 45 | 1 | Richmond | 2005-11-16 16:38 | 50 | 0 |  | 2005-11-16 16:38 |  | -- | INTERSECTION OF RHEEM AVENUE & 23RD STREET | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-11-16 |  |  |  | CITY NOTIFIED BY RPD AT 100 HRS AND SEWER CREW ON SCENE AT 1115 HRS. THE BLOCKAGE WAS CLEARD AT 1300 HOURS.RAN 320 FEET OF LINE (HYDRO HOSE). 2 HRS OF DISCHARGE OCCURED A 4 GPM ESTIMATE. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2005-11-16 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
2128 | 44 | 3 | Richmond | 2005-11-16 16:39 | 1225 | 200 | 05-6623 | 2005-11-15 | Paul Herguth | Richmond | 500 Western Drive | Richmond | Contra Costa | 94804 | 37.927 | 122.391 | 2005-11-15 | 8:00:00 AM | [5 empty] | SUNNY WEATHER | Low | SAN FRANCISCO BAY | STORM DRAIN | No |  | No | Yes | DISCHARGE DISIPATED IN TO ROCKY AREA NEAR WATER FRONT. |  | Yes | Yes | Yes | No | No | Yes | No | Yes | No | 2005-11-16 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Richmond | MANHOLE |  | BLOCKAGE | DEBRIS | --Select None-- |  | A RESIDENT IN THE AREA CONTACTED THE CITY AT APPROX. 1400 HOURS. THE CITY DISPATCHED A CREW WHEN NOTIFIED. THE AVERAGE RATE OF DISCHARGE WAS APPROX. 2.5 GPM. THE SEWER CREW BLOCKED THE DRAINAGE DITCH AND RECOVERED APPROX. 50 GALLONS. THE CITY POSTED 5 WARNING SIGNS IN THE BEACH ACCESS AREA. THE DISCHARGE DRAINED INTO AN ROCKY BEACH SURFACE AND THERE WAS NO VISIBLE PATH OF DISCHARGE INTO THE BAY. INVST TEAM DISTRIBUTED 40 GREASE DOOR HANGERS ON 11/16/05. TWO SAMPLES WERE COLLECTED ON 11/16/05 AM BETWEEN TIDES. TWO MORE WILL BE COLLECTED ON 11/17/05. | Industrial Waste Ins | Paul Herguth | 2005-11-15 | 510-412-2029 | paul_herguth@ci.richmond.ca.us | MAJOR | PAUL HERGUTH | CITY OF RICHMOND | 510-412-2029 |  | 1401 | MARINA WAY SOUTH | CONTRA COSTA | 94804 | UNKNOWN | Richmond
2024 | 43 | 2 | Richmond | 2005-10-24 14:08 | 275 | 0 |  | 2005-10-24 14:08 |  | -- | INTERSECTION OF 14TH STREE AND PENNSYLVANIA AVENUE | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-10-24 |  |  |  | CITY SEWER CREW RECEIVED THE REPORT AT 1030 HOURS AND WAS ON SCENE AT 1045 HOURS. THE BLOCKAGE WAS CELARED AT 1115 HOURS (ALL TIMES APPROXIMATE). ESTIMATED RATE OF DISCHARGE WAS 5 GPM FOR APPROX. 75 MINUTES. APPROXIMATELY 100 GALLONS REMOVED FROM STORM DRAIN AND DISPOSED OF AT POTW. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | rICHMOND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SR INDUST WASTE INSP | STEPHEN FRIDAY | 2005-10-24 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1998 | 42 | 1 | Richmond | 2005-10-21 11:20 | 100 | 0 |  | 2005-10-21 11:20 |  | -- | MONTANA STREET & EAST RICHMOND AVENUE | RICHMOND | CONTRA COSTA | 94801 |  |  | 2005-10-21 |  |  |  | CITY NOTIFIED AT 0930 HOURS & ON SCENE AT 0945 HOURS. BLOCKAGE CLEARED AT 1000 HOURS. APPROX. 80 GALLONS RECOVERED FROM STORM DRAIN AND DISPOSED OF AT POTW. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SR INDUST WASTE INSP | STEPHEN FRIDAY | 2005-10-21 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1958 | 40 | 1 | Richmond | 2005-10-13 17:15 | 900 | 0 |  | 2005-10-13 17:15 |  | -- | 601 MARINE STREET | RICHMOND | CONTRA COSTA | 94801 |  |  | 2005-10-13 | [9 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | SR INDUST WASTE INSP | STEPHEN FRIDAY | 2005-10-13 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1964 | 41 | 1 | Richmond | 2005-10-14 16:32 | 300 | 0 |  | 2005-10-14 16:32 |  | -- | BRICKYARD COVE LANE PUMP STATION | RICHMOND | CONTRA COSTA | 94801 |  |  | 2005-10-04 |  |  |  | THE PUMP STATION WAS BLOCKED WITH RAGS. ALL OF THE SEWAGE WAS VACTORED UP AND DISPOSED OF AT THE POTW. NONE ENTERED THE STORM DRAIN OR SURFACE WATERS. THE INCIDENT HAPPENED ON 10/04/05 BUT WAS ENTERED 10/14/05 DUE TO THE CHANGE OF THE FINAL DESTINATION CRITERA OF THIS REPORT FORM. IT WAS NOTED WHEN I ENTERED SSO ID # 40 (TRACK # 1958)ON 10/13/05 THERE IS NOW A "STREET/CURB & GUTTER" AS A FINAL SPILL DESTINATION. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RIchmond | MANHOLE | CAUSED BY PUMP STATION | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | SR INDUST WASTE INSP | STEPHEN FRIDAY | 2005-10-14 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1706 | 39 | 1 | Richmond | 2005-08-22 16:28 | 90 | 0 |  | 2005-08-22 16:29 |  | -- | 20TH STREET & COSTA AVENUE (INTERSECTION) | RICHMOND | CONTRA COSTA | 94801 |  |  | 2005-08-18 |  |  |  | THE CITY SEWER CREW WAS NOTIFIED BY A RESIDENT AT 1330 HOURS AND ARRIVED ON SCENE AT 1415 HOURS. THE OVERFLOW WAS STOPPED/CLEARED AT 1420 HOURS. BASED ON VISUAL OBSERVATIONS IT WAS ESTIMATED THE RATE OF DISCHARGE WAS UP 1.5 GALLONS PER MINUTE. ANY STANDING SEWAGE WAS VACTORED UP AND THE AREA DISINFECTED. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | MANHOLE |  | CAUSE UNKNOWN | --Select None-- |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2005-08-22 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1588 | 38 | 1 | Richmond | 2005-07-01 15:49 | 400 | 0 |  | 2005-07-01 15:49 |  | -- | 21ST & BISSELL AVENUE (CITY VACTOR TRUCK SEWAGE SPILL) | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-07-01 |  |  |  | AFTER REMOVING SEWAGE AND STORM WATER FROM A SBC TELEPHONE VAULT THE CITY CREW WAS DECANTING THE VACTOR TRUCK INTO A SANITARY SEWER MAINTENANCE HOLE. THE WASTEWATER SURGED OUT AT A RATE GREATER THAN EXPECTED. APPROXIMATELY 500 GALLONS WAS SPILLED AND 100 WAS RECOVERED FOR PROPER DISPOSAL. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | OTHER | VACTOR TRUCK | INFRASTRUCTURE FAILURE | MULTIPLE CAUSES |  |  |  | SR INDST WASTE INSP | STEPHEN FRIDAY | 2005-07-01 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1560 | 37 | 1 | Richmond | 2005-06-24 14:58 | 250 | 0 |  | 2005-06-24 14:58 |  | -- | 7 17th Street | Richmond | Contra Costa | 94804 |  |  | 2005-06-24 |  |  |  | Dispatch recieved call and routed it to the fire department and Veolia was called out. Fire attempted to block the flow with vermiculite. Veolia removed blockage and cleaned up the sewage and vermiculite | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Ms. | Lynne Scarpa | 2005-06-24 | 510-412-2008 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1434 | 36 | 1 | Richmond | 2005-05-20 11:35 | 300 | 0 |  | 2005-05-20 11:35 |  | -- | 425 SOUTH 36TH STREET (CROSS STREET WALL AVENUE) | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-05-19 |  |  |  | THE CITY SEWER CREW WAS NOTIFIED AT 0915 HRS AND ON SCENE AT 1000 HRS. THE BLOCKAGE WAS DUE TO A T-SHIRT IN THE CITY'S LINE. THERE WAS AN ESTIMATED 700 GALLONS OF RAW SEWAGE ON THE GROUND AND APPROX. 400 GALLONS WAS RECOVERED. THE CLEANUP WAS COMPLETED AT 1100 HRS. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | riCHMOND | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2005-05-20 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1416 | 34 | 1 | Richmond | 2005-05-16 16:21 | 140 | 0 |  | 2005-05-16 16:21 |  | -- | 36TH STREET & NEVIN AVENUE | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-05-14 |  |  |  | THE CITY RECEIVED THE CALL AT 0820 HRS AND WAS ON SCENE AT 0900 HOURS. BLOCKAGE WAS CLEARED AT 0920 HRS AND THE ESTIMATED RATE OF DISCHARGE WAS 4 GPM. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | richmond | MANHOLE |  | BLOCKAGE | VANDALISM |  |  |  | SR INDST WASTE INSPT | STEHEN FRIDAY | 2005-05-16 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1414 | 33 | 1 | Richmond | 2005-05-16 16:19 | 300 | 0 |  | 2005-05-16 16:19 |  | -- | 3500 36TH STREET | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-05-13 |  |  |  | THE CITY RECEIVED THE CALL AT 1415 HOURS, AND THE RESPONSE CREW WAS ON SCENE AT 1500 HOUR. THE BLOCKAGE WAS CLEARED AT 1525 HOURS. IT IS ESTIMATED THE RATE OF DISCHARGE WAS 4 GPM. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | richmond | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | SR INDUST WASTE INSP | STEPHEN FRIDAY | 2005-05-16 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1412 | 32 | 1 | Richmond | 2005-05-16 16:14 | 900 | 0 |  | 2005-05-16 16:14 |  | -- | Intersection of San Pablo Ave and Macdonald Ave. | Richmond | Contra Contra | 94804 |  |  | 2005-05-12 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | richmond | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Industrial Waste Ins | Paul Herguth | 2005-05-16 | 510-412-2029 | paul_herguth@ci.richmond.ca.us, steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1410 | 31 | 2 | Richmond | 2005-05-16 16:09 | 200 | 0 |  | 2005-05-16 16:09 |  | -- | 23RD STREET & MARICOPA AVENUE | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-05-11 |  |  |  | rEPORTED TO CITY AT 1930 HRS, CREW ON SCENE AT 3030 HRS. THE BLOCKAGE WAS CLEARED AT 2050 HRS. ESTIMATED RATE OF DISCHARGE WAS 2-2.5 GPM. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | richmond | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SR INDUST WASTE INSP | STEPHEN FRIDAY | 2005-05-16 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1418 | 35 | 1 | Richmond | 2005-05-16 16:26 | 180 | 0 |  | 2005-05-16 16:26 |  | -- | 3900 Block of Roosevelt Ave. | Richmond | Contra Costa | 94804 |  |  | 2005-05-10 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | richmond | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Industrial Waste Ins | Paul Herguth | 2005-05-16 | 510-412-2029 | paul_herguth@ci.richmond.ca.us, steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1368 | 30 | 1 | Richmond | 2005-05-05 15:06 | 400 | 0 |  | 2005-05-05 15:06 |  | -- | 24TH STREET & RHEEM AVENUE | RICHMOND | CONTRA COSTA | 94801 |  |  | 2005-05-04 |  |  |  | CITY SEWER CREW RVCD CALL AT 1510 HRS AND ON SCENE AT 1530 HRS. SSO STOPPED AT 1545 HRS. RAIN EVENT OCCURRING AT TIME OF OVERFLOW AND DILUTED DISCHARGE. ESTIMATED RATE OF DISCHARGE FROM MANHOLE 5 GPM. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RICHMOND | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2005-05-05 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1370 | 29 | 2 | Richmond | 2005-05-05 15:07 | 480 | 0 |  | 2005-05-05 15:07 |  | -- | 2319, 2350, 2352 MARICOPA AVENUE (CROSS STREET 23RD STREET) | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-05-04 |  |  |  | CITY SEWER CREW RCVD CALL AT 1020 HRS AND ARRIVED ON SCENE AT 1035. SSO STOPPED AT 1045 HRS. ESTIMATED RATE OF DISCHARGE 2 GPM. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RICHMOND | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2005-05-05 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1364 | 28 | 3 | Richmond | 2005-05-05 14:54 | 8700 | 50 | 05-2668 | 2005-05-04 | Paul Herguth | Richmond | 1045 Barrett Ave. Spill occurred in alley behind townhomes between Harbour Way and 12th Street. | Richmond | Contra Costa | 94804 | 37.938 | 122.38 | 2005-05-01 | 4:45:00 PM | [5 empty] | SUNNY WEATHER | Medium |  | STORM DRAIN | No |  | No | No | NONE |  | Yes | Yes | Yes | No | No | No | No | No | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | Richmond | CLEAN OUT |  | BLOCKAGE | DEBRIS | --Select None-- |  | CITY SEWER CREW RCVD RPT @ 1625 HRS AND ON SCENE AT 1630 HRS. RPTNG PARTY STATED THAT SSO HAD BEEN OCCURRING FOR APROX 3 DAYS. NO ONE IN NEIGHBORHOOD RPTD SSO UNTIL 05/03/05. ON SCENE ESTIMATE OF DISCHARGE RATE WAS 2 GPM. BLOCKAGE CLEARED AND SSO STOPPED AT 1645 HRS. | INDUSTRIAL WASTE INS | Paul Herguth | 2005-05-04 | 510-412-2029 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MAJOR | STEPHEN FRIDAY | CITY OF RICHMOND | 510-412-2009 |  | 1401 MARINA WAY SOUTH | RICHMOND | CONTRA COSTA | 94804 | CITY OF RICHMOND | CITY OF RICHMOND | 510-412-2009 |  | 1401 MARINA WAY SOUTH | RICHMOND | CONTRA COSTA | 94804
1272 | 27 | 1 | Richmond | 2005-04-08 16:42 | 600 | 0 |  | 2005-04-08 16:42 |  | -- | 1904 COSTA (CROSS STREET 19TH STREET) | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-04-08 |  |  |  | CITY SEWER CREW NOTIFIED AT 1430 HOURS AND BLOCKAGE IN MAIN CLEARD AT 1450 HOURS (DISCHARGE STOPPED). mAIN BLOCKAGEGE CAUSED PRIVATE LATERAL TO OVERFLOW. ESTIMATED RATE OF DISCHARGE 10 GPM FOR ONE HOUR. SEWAGE ENTERED STORM DRAIN AT 19TH STREET AND VISALIA AVENUE. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2005-04-08 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1208 | 26 | 1 | Richmond | 2005-03-22 10:19 | 600 | 0 |  | 2005-03-22 10:19 |  | -- | INTERSECTION OF PENNSLVANIA & 14 STREET | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-03-21 |  |  |  | CITY SEWER CREW ARRIVED ON SCENE AT 1000 HOURS. NOTIFACATION AT 0950 HOURS. CREW ESTIMATED DISCHARGE OCCURRED FOR APPROX. 1 HOUR BEFORE THEY ARRIVED, AND AT A DISCHARGE RATE OF 2 - 8 GPM, FOR AN AVG. OF 5 GPM. DISCHARGE SECURED AT 1045 HOURS. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | richmond | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2005-03-22 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1180 | 25 | 1 | Richmond | 2005-03-14 11:56 | 850 | 0 |  | 2005-03-14 11:56 |  | -- | SEACLIFF ESTATES SANITARY SEWER LIFT STATION (INTERSECTION OF SEACLIFF DRIVE & SANDY BAY COURT) | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-03-12 |  |  |  | BOTH PUMPS WERE DAMAGED AND NEED TO BE REPLACED. THE INCIDENT STARTED AT APPROX. 1600 HOURS AND ENDED AT 2000 HOURS. STANDING SEWAGE WAS VACTORED UP AND DISPOSED OF AT THE POTW. RATE OF DISCHARGE VARRIED FROM 1 TO 5 GPM. THIS PUMP STATION CAME INTO SERVICE AND WAS SIGNED OVER TO THE CITY WITHIN THE LAST YEAR. THE CITY SEWER CREW REMOVED WALL BOARD FROM THE PUMPS. THE DEVELOPMENT CONTRACTOR WILL BE BILLED FOR THE DAMAGES. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | PUMP STATION |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2005-03-14 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1114 | 24 | 1 | Richmond | 2005-03-03 19:46 | 700 | 0 |  | 2005-03-03 19:46 |  | -- | INTERSECTION OF 24TH STREET & ANDRADE AVENUE | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-02-28 |  |  |  | THE CITY SEWER CREW DROVE UP ON THE OVERFLOW AT 0800 HOURS. THERE WAS APPROXIMATELY 500 GALLONS ON THE GROUND THEY WERE ABLE TO VACTOR UP. IT WAS A HARD GREASE BLOCKAGE. THE BLOCKAGE WAS CLEARD AT 0820 HOURS. THE RATE OF DISCHARGE WHEN THEY ARRIVED ON SCENE WAS APPROX. 8-10 GPM. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2005-03-03 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1095 | 23 | 1 | Richmond | 2005-02-25 16:14 | 200 | 0 |  | 2005-02-25 16:14 |  | -- | INTERSECTION OF SOUTH 45TH AND FLORIDA AVENUE | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-02-25 |  |  |  | CITY SEWER CREW NOTIFIED AT 1030 HOURS BY THE WEST COUNTY WASTEWATER DISTRICT. THEY WERE ON SCENE AT 1045 HOURS AND STOPPED THE DISCHARGE AT 1105 HOURS. THE CAUSE OF THE BLOCKAGE WAS RAGS. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2005-02-25 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1093 | 22 | 1 | Richmond | 2005-02-25 16:08 | 240 | 0 |  | 2005-02-25 16:08 |  | -- | INTERSECTION OF ESMOND AVENUE & 23RD STREET | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-02-23 |  |  |  | CITY SEWER CREW NOTIFIED OF OVERFLOW AT 1700 HOURS AND CLEARED BOOCKAGE AT 1730 HOURS. IT IS ESTIMATED THE DISCHARGE STARTED AT 1530 HOURS AT AT RATE OF 2 GPM. THE BLOCKAGE WAS DUE TO RAGS. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2005-02-25 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1070 | 20 | 2 | Richmond | 2005-02-18 17:22 | 150 | 0 |  | 2005-02-18 17:22 |  | -- | 2811 ANDRADE AVENUE (CROSS STREET 28TH STREET) | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-02-17 |  |  |  | CITY SEWER CREW NOTIFIED AT 1800 HOURS & BLOCKAGE CLEARED AT 1930 HOURS. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RICHMOND | OTHER | CRACK IN STREET | BLOCKAGE | ROOTS |  |  |  | SR INDST WST INSPT | STEPHEN FRIDAY | 2005-02-18 | 510-412-2009 | steve_friday@ci.richmond.ca.us | MINOR
1068 | 21 | 2 | Richmond | 2005-02-18 17:21 | 120 | 0 |  | 2005-02-18 17:21 |  | -- | 5021 SEAPORT AVENUE (CROSS STREET SOUTH 51ST STREET) | RICHMOND | CONTRA COSTA | 94801 |  |  | 2005-02-16 |  |  |  | 1145 HOURS CITY SEWER CREW COMPLETED JOB. THE CITY MAIN CONTAINED RAGS. THE ABOVE GROUND STORM SEWER DRAINAGE WAS CLEANED AND DISINFECTED. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RICHMOND | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | SR INDST WST INSPT | STEPHEN FRIDAY | 2005-02-18 | 510-412-2009 | steve_friday@ci.richmond.ca.us | MINOR
1028 | 19 | 1 | Richmond | 2005-02-15 14:36 | 200 | 0 |  | 2005-02-15 14:36 |  | -- | 7 WESTERN DRIVE, RICHMOND (KELLER BEACH) | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-02-13 |  |  |  | THE OVERFLOW WAS LESS THAN 1 GPM ACCORDING CITY SEWER CREW. IT WAS REPORTED OBSERVED BY EBR PARKS ON 2/11/05 TO THEIR SUPERVISOR & THOUGHT TO BE FROM PORTABLE RESTROOMS ON SITE, AND HAD NOT REACHED A RECEIVING WATER. HOWEVER, IT WAS NOTED ON SUNDAY ENTERING THE STORMDRAIN AND REPORT TO THE CITY. EBR PARKS POSTED WARNING SIGNS AND STARTED SAMPLING FOR COLIFORM ON 2/14/05. | [5 empty] | GROUND WATER IMPACTED | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | richmond | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SR. INDUSTRIAL WASTE | STEPHEN FRIDAY | 2005-02-15 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
1010 | 18 | 2 | Richmond | 2005-02-09 15:20 | 300 | 0 |  | 2005-02-09 15:20 |  | -- | 5229 SILVA AVENUE | RICHMOND | CONTRA COSTA | 94805 |  |  | 2005-02-09 |  |  |  | CITY SEWER LINE TRANSECTS OVER PRIVATE PROPERTY IN THE AREA. THE SEWAGE ENTERED BAXTER CREEK IN MIRA VISTA PARK. A CITY PARKS EMPLOYEE NOTIFIED THE SEWER CREW OF THE INCIDENT. THE SEWER CREW DIVERTED THE DISCHARGE WHEN THEY ARRIVED ON SCENE AT 1358 HOURS AND THE BLOCKAGE WAS CLEARED AND THE DISCHARGE STOPPED AT 1445 HOURS. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SR. INDUSTRIAL WASTE | STEPHEN FRIDAY | 2005-02-09 | 510-412-2009 | steve_friday@ci.richmond.ca.us, Rich_Davidson@ci.richmond.ca.us | MINOR
946 | 17 | 1 | Richmond | 2005-02-01 18:15 | 800 | 0 |  | 2005-02-01 18:15 |  | -- | INTERSECTION OF 15TH STREET AND COSTA AVENUE | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-02-01 |  |  |  | CITY SEWER CREW RECEIVED CALL AT 2030 HRS AND ON SCENE AT 2115 HRS. BLOCAKAGE CLEARED AT 2140 HRS. DISCHARGE RATE INITIALLY 2-3 GPM. CREW WASHED DOWN AND DISINFECTED AREA, WHICH WAS ALL ABOVE GROUND DRAINAGE. SEWAGE WOULD HAVE ONLY ENTERED STORM DRAIN IF RAIN HAD OCCURRED. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RIchmond | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2005-02-01 | 510-412-2009 | STEVE_FRIDAY@CI.RICHMOND.CA.US | MINOR
993 | 16 | 2 | Richmond | 2005-02-09 12:46 | 500 | 0 |  | 2005-02-09 12:46 |  | -- | 341 SOUTH 17TH STREET | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-01-26 |  |  |  | CITY SEWER CREW NOTIFIED AT 1330 HOURS AND ON SCENE AT 1400 HOURS. OVERFLOW STOPPED WHEN CREW ARRIVED. 500 GALLONS IS AN ESTIMATE BASE ON A 2 GPM DISCHARGE RATE. BLOCKAGE CLEARED AT 1410 HOURS. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | richmond | PUMP STATION |  | BLOCKAGE | DEBRIS |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2005-01-28 | 5110-412-2009 | STEVE_FRIDAY@SBCGLOBAL.NET | MINOR
881 | 15 | 1 | Richmond | 2005-01-19 17:59 | 320 | 0 |  | 2005-01-19 17:59 |  | -- | 4333 POTRERO AVENUE (CROSS STREET 43RD STREET) | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-01-19 |  |  |  | CITY SEWER CREW NOTIFIED AT 1510 HOURS AND WAS ON SCENE AT 1540 HOURS. CREW SUPERVISOR ESTIMATED RATE OF DISCHARGE APROX. 1 GPM. RESIDENT STATED THAT DISCHARGE FROM HIS LATERAL WAS NOTICED AT APPROX. 1100 HRS. CITY SEWER CREW STOPPED DISCHARGE AT 1620 HOURS. SEWER CREW SUPERVISOR STATED THAT THE PLUGGED MAIN HAD CLEANING MAINTENANCE PERFORMED ON IT SEVERAL WEEKS EARLIER. THIS INDICATES THERE ARE MANY RESIDENTIAL CONTRIBUTIONS TO THE GREASE LOADING. THE SEWER CREW PROVIDED FOG EDUCATION HANDOUTS IN THE IMMEDIATE AREA. THE SEWAGE WAS ENTERING THE STORMDRAIN DROP INLET AT 45TH STEET AND POTRERO AVENUE. SEWER CREW CLEANED AREA & DEPARTED. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RICHMOND | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2005-01-19 | 510-412-2009 | STEVE_FRIDAY@CI.RICHMOND.CA.US | MINOR
835 | 14 | 1 | Richmond | 2005-01-12 17:18 | 500 | 0 |  | 2005-01-12 17:18 |  | -- | 35th STREET & OHIO AVENUE | Richmond | Contra Costa | 94804 |  |  | 2005-01-12 |  |  |  | CITY SEWER CREW WAS NOTIFIED OF INCIDENT AT 1520 HOURS AND ARRIVED ON SCENE AT 1530 HOURS. RESIDENT IN AREA CLAIMED OVERFLOW OCCURED FOR 5 DAYS. GREASE BLOCKAGE WAS CLEARED AT 1600 HOURS. WHEN CREW ARRIVED ON SCENE THERE WAS NO OVERFLOW IN PROGESS. AMOUNT DISCHARGED IS AND ESTIMATE BASED ON STAINING AND OBSERVATION OF WHAT ENTERED THE STORM SEWER. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RIchmond | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2005-01-12 | 510-412-2009 | STEVE_FRIDAY@CI.RICHMOND.CA.US | MINOR
837 | 13 | 2 | Richmond | 2005-01-12 17:20 | 300 | 0 |  | 2005-01-12 17:20 |  | -- | 320 SOUTH 28TH STREET (CROSS STREET MAINE AVENUE) | RICHMOND | CONTRA COSTA | 94804 |  |  | 2005-01-10 |  |  |  | THE CITY SEWER CREW REMOVED A SMALL/MINI SOCCER BALL FROM THE CITY MAIN. TWO PRIVATE CLEAN-OUTS OVERFLOWED AS A RESULT OF THE BLOCKAGE. OUR CREW WAS NOTIFIED OF THE INCIDENT AT 1610 HOURS, & ARRIVED ON SCENE AT 1620 HOURS, CLEARING THE BLOCKAGE AT 1700 HOURS (TIMES APPROXIMATE). | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | RIchmond | CLEAN OUT |  | BLOCKAGE | VANDALISM |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2005-01-12 | 510-412-2009 | STEVE_FRIDAY@CI.RICHMOND.CA.US | MINOR
755 | 12 | 1 | Richmond | 2005-01-04 17:17 | 11760 | 0 | 05-0076 | 2005-01-04 | STEPHEN FRIDAY | Richmond | 651 41ST STREET (CROSS STREET CLINTON AVENUE) | RICHMOND | CONTRA COSTA | 94804 | 37.939 | -122.3295 | 2005-01-03 | 3:10:00 PM | [5 empty] | RAINING FOR SEVERAL DAYS | Low | SAN FRANCISCO BAY | STORM DRAIN | No |  | No | No | CITY SEWER CREW ARRIVED ON SCENE AT 1530 HOURS AND CLEARED BLOCAKGE AT APPROX. 1600 HOURS. REPORTING PARTY, WHO CONTACTED THE SEWER CREW AT 1510 HOURS REPORTED THE OVERFLOW HAD BEEN OCCURING FOR APPROX 48 HOURS. DURING THIS PERIOD OF DICHARGE IT WAS RAINING AND SEWAGE WAS TRANSPORTED AND FLUSHED TO THE STORM WATER COLLECTION SYSTEM. |  | Yes | No | No | No | No | Yes | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | Richmond | MANHOLE |  | BLOCKAGE | DEBRIS | --Select None-- |  | THE LONG DURATION OF THE OVERFLOW MAY HAVE BEEN DUE TO THE ASSUMPTION IT WAS RAIN WATER SINCE THERE WERE SEVERAL STORM EVENTS AT THE SAME TIME. | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2005-01-04 | 510-412-2009 | STEVE_FRIDAY@CI.RICHMOND.CA.US | MAJOR | Stephen Friday | City of Richmond | 510-412-2009 |  | 1401 Marina Way South | Richmond | Contra Costa | 94804 |  | City of Richmond | 510-412-2009 |  | 1401 Marina Way South | Richmond | Contra Costa | 94804
702 | 11 | 1 | Richmond | 2004-12-31 15:44 | 1200 | 0 | 04-6926 | 2004-12-31 | RICHMOND | Richmond | 230 WATER STREET | RICHMOND | CONTRA COSTA | 94801 | 37.9255 | 122.3883 | 2004-12-31 | 8:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low | SAN FRANCISCO BAY | STORM DRAIN | No |  | No | No | DISINFECTED AREA. HEAVY RAINS PRIOR TO EVENT. |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | Richmond | MANHOLE |  | BLOCKAGE | DEBRIS | --Select None-- |  | DUE TO INI VELOCITIES OF WW IN COLLECTION SYSTEM AT MAXIIMUM. | SR INDUST WATE INSPT | STEPHEN FRIDAY | 2004-12-31 | 510-236-0370 | STEVE_FRIDAY@ CI.RICHMOND.CA.US | MAJOR | Stephen Friday | City of Richmond | 510-412-2009 |  | 1401 Marina Way South | Richmond | Contra Costa | 94804 | UNKNOWN | City of Richmond | 510-412-2009 |  | 1401 Marina Way South | Richmond | Contra Costa | 94804
704 | 10 | 2 | Richmond | 2005-01-01 09:33 | 700 | 0 |  | 2005-01-01 09:33 |  | -- | 603 39TH STREET (INTERSECTION OF ROOSEVELT AVENUE & 39TH STREET) | RICHMOND | CONTRA COSTA | 94804 |  |  | 2004-12-21 |  |  |  | LATERAL CAP AT SUBJECT ADDRESS/RESIDENCE BLEW OFF AS A RESULT OF THE BLOCKAGE. THE CITY'S SEWER CREW WAS NOTIFIED AT 1100 HOURS AND ARRIVED ON SCENE AT 1105 HOURS. THE SEWER MAIN BLOCKAGE WAS CLEARED AT 1115 HOURS. IT IS ESTIAMTED THE RATE OF DISCHARGE AVERAGED 5 GPM FOR APPROXIMATELY 2 HOURS. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | richmond | CLEAN OUT |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2004-12-22 | 510-412-2009 | STEVE_FRIDAY@CI.RICHMOND.CA.US | MINOR
625 | 9 | 2 | Richmond | 2004-12-22 16:53 | 225 | 0 |  | 2004-12-22 16:53 |  | -- | 736 MESA WAY (CLINTON AVENUE & MESA WAY) | RICHMOND | CONTRA COSTA | 94804 |  |  | 2004-12-17 |  |  |  | CITY SEWER CREW NOTIFIED OF INCIDENT AT 1000 HRS & ARRIVED ON SCENE AT 1020 HRS. ESTIMATE DISCHARGE TO STORMDRAIN STARTED AT 0800 HRS AND SEWER CREW CLEARED BLOACKAGE AT 1145 HRS. APPROX. RATE OF SEWAGE DISCHARGE WAS 1 GPM. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2004-12-17 | 510-412-2009 | STEVE_FRIDAY@CI.RICHMOND.CA.US | MINOR
480 | 8 | 1 | Richmond | 2004-12-10 10:39 | 400 | 0 |  | 2004-12-10 10:39 |  | -- | 144 CASTRO STREET (INTERSECTION OF CASTRO STREET AND WEST RICHMOND AVENUE) | RICHMOND | CONTRA COSTA | 94801 |  |  | 2004-12-10 |  |  |  | A 1.5 FOOT PIECE OF ASPHALT CAUSE THE OBSTRUCTION. THE ASPHAULT WAS PUSHED IN THROUGH A FAILED PIPE (SINK HOLE) CLOSE TO THE SURFACE OF THE STREET. THE CITY SEWER CREW WAS NOTIFIED AT 0800 HOURS AND WAS ON SCENE AT 0810. THE DISCHARGE WAS STOPPED AT 0930 HOURS. THEY REPLACE APPROXIMATLEY 12 FEET OF PIPELINE. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | PIPE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2004-12-10 | 510-412-2009 |  | MINOR
471 | 6 | 1 | Richmond | 2004-12-09 16:43 | 800 | 0 |  | 2004-12-09 16:43 |  | -- | 3625 MACDONALD AVENUE (INTERSECTION OF MACDONALD AVENUE & 37TH STREET) | RICHMOND | CONTRA COSTA | 94804 |  |  | 2004-12-09 |  |  |  | CITY SANITARY SEWER MAIN WAS PLUGGED WITH RAGS. DISCHARGE WAS REPORTED AT 0220 HOURS AND CITY PERSONNEL WERE ON SCENE AT 0300. THE RATE OF DISCHARGE WHEN SEWER CREW ARRIVES WAS ESTIMATED AT 5 GPM. OVERFLOW DISCHARGE WAS STOPPED AT 0330 HOURS. RAIN WASHED THE AREA CLEAN. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | richmond | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | SR INDUST WASTE INSP | STEPHEN FRIDAY | 2004-12-09 | 510-412-2009 |  | MINOR
475 | 7 | 2 | Richmond | 2004-12-09 16:55 | 360 | 0 |  | 2004-12-09 16:55 |  | -- | 320 MARINA WAY SOUTH (INTERSECTION OF MARINA WAY SOUTH & MAINE AVENUE) | RICHMOND | CONTRA COSTA | 94804 |  |  | 2004-12-09 |  |  |  | CITY SANITARY SEWER MAIN BLOCKED. CITY SEWER CREW NOTIFIED AT 1500 HOURs AND ON SCENE AT 1520 HOURS. THEY ESTIMATED THE RATE OF DISCHARGE AT 2 GPM. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | richmond | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2004-12-09 | 510-412-2009 |  | MINOR
448 | 5 | 1 | Richmond | 2004-12-08 16:16 | 1440 | 500 | 04-6416 | 2004-12-08 | STEPHEN FRIDAY | RICHMOND | 341 SOUTH 17TH STREET | RICHMOND | CONTRA COSTA | 94804 | 37.9274 | 122.353 | 2004-12-08 | 11:00:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Medium |  | BUILDING/STRUCTURE | No |  | No | No | THERE WAS PAPER AND BIOSOLIDS ACCUMULATION IN THE AREA ON PRIVATE PROPERTY. ONLY LIQUID SEWAGE LEFT THE SOURCE ADDRESS. THE SEWAGE ENTERING THE STORMWATER COLLECTION SYSTEM WAS DILLUTED BY DRAINING STORMWATER. NO FLUSHING OR DISINFECTION WAS REQUIRED. THE SUBJECT ADDRESS IS AN APARTMENT BUILDING. THERE WERE ONLY OCCUPANTS IN THE TWO UPSTAIRS UNITS. ONE APT. WAS OCCUPIED BY 2 ADULTS/3 CHILDREN & THE OTHER BY 2 ADULTS/2 CHILDREN. THE CITY PROVIDED THEM MOTEL ROOMS (3) FOR ONE NIGHT WHILE THE LOWER LEVEL OF THE APT. BUILDING IS CLEANED BY A CONTRACTOR. THE LOWER LEVEL WAS IMPACTED BY SEWAGE OVERFLOWING FROM A TOILET IN AN UNOCCUPIED APT. UNIT. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | RICHMOND | CLEAN OUT | HEAVY RAINS INFILTRATED THE CITY'S SANITARY SEWER COLLECTION SYSTEM. THE HIGH THAN NORMAL WASTEWATER VELOCITES IN THE COLLECTION SYSTEM ALLOWED RISIDUAL GREASE TO POCKET IN NARROWER INTERSECTING PIPELINES. SINCE THE CITY SANITARY SEWER COLLECTION SYSTEM WAS CHARGED WITH STORMWATER AS A RESULT OF INFILTRATION IT IS ESTIMATE THAT ONLY 50% OF THE DISCHARGED WASTEWATER WAS SEWAGE. | BLOCKAGE | GREASE | --Select None-- |  | DUE TO HEAVY RAINS INFILTRATING THE CITY'S SANTITARY SEWER COLLECTION SYSTEM, GREASE ACCUMULATED AT NARROWER PIPLINE JUNCTIONS CAUSING AN OBSTRUCTION. THE LINE PRESSURE WAS RELEIVED THROUGH A TOILET IN AN APARTMENT BUILDING. THE RESIDENTS HAD TO BE RELOCATED OVERNIGHT BY THE CITY. | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2004-12-08 | 510-412-2009 |  | MAJOR | Stephen Friday | City of Richmond | 510-412-2009 |  | 1401 Marina Way South | Richmond | Contra Costa | 94804 |  | City of Richmond | 510-412-2009 |  | 1401 Marina Way South | Richmond | Contra Costa | 94804
428 | 3 | 2 | Richmond | 2004-12-07 12:52 | 350 | 0 |  | 2004-12-07 12:52 |  | -- | 171 Harbour Way South (intersection of Harbour Way South & Florida Avenue) | Richmond | Contra Costa | 94804 |  |  | 2004-12-07 |  |  |  | The City sanitary sewer main was charged to 3/4s of its capacity due to stormwater infiltration. The rate of discharge was estimated at 10 gpm (average)from the subject manhole, for a total of 700 gallons of the 50/50 mixture or 350 gallons raw sewage. Subsequently, this mixture commingled in the curb drains contaminating an additional 2000 gallons of stormwater, and the City sewer crew vactored up approximately 1000 gallons of this mixture off the street (for treatment at the POTW). It is estimated 250 gallons or raw sewage entered Santa Fe Channel, a tributary of San Francisco Bay. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Sr Indst Waste Inspt | Stephen Friday | 2004-12-07 | 510-412-2009 |  | MINOR
482 | 4 | 3 | Richmond | 2004-12-10 10:40 | 600 | 0 |  | 2004-12-10 10:40 |  | -- | 7 17th STREET (INTERSECTION OF 17TH STREET & CHANSLOR AVENUE) | RICHMOND | CONTRA COSTA | 94804 |  |  | 2004-12-07 |  |  |  | THIS IS A RESIDENTIAL AREA @ 10 GPM FOR APPROX. ONE HOUR. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Richmond | OTHER | LAMP POLE (CITY CLEANOUT) | BLOCKAGE | GREASE |  |  |  | SR INDST WASTE INSPT | STEPHEN FRIDAY | 2004-12-08 | 510-412-2009 |  | MINOR
426 | 1 | 3 | Richmond | 2004-12-07 12:50 | 10800 | 1000 | 04-6052 | 2004-11-19 | Stephen Friday | Richmond | 601 Marine Street | Richmond | Contra Costa | 94801 | 37.9285 | 122.3936 | 2004-11-19 | 4:00:00 PM | [5 empty] | SUNNY WEATHER | Medium | San Francisco Bay | SURFACE WATER IMPACT | Yes | Keller Beach was closed for 3 days by the managing resource authority, East Bay Regional Parks. This beach is approximately 1 mile from the source & entry point into the Bay. | Yes | Yes | Spilled/discharged sewage mixed with ocean/Bay waters. The discharged sewage filtered through beach gravel prior to entering the Bay. Approximately 1000 gallons of sewage was vactored out of the manhole in an attempt to prevent discharge to the Bay with negative results. Only after the roots were cleared did the discharge cease. The manhole is approximately 30 feet from the high tide line. |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jyl@rb2.swrcb.ca.gov | Richmond | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- |  | The tree roots were rodded clear. This is a manhole at the bottom of a hill where all the biosolids in the service area collect at one point prior to entering the main line on the beach. This report was originally submitted to the RWQCBSFB on 11/29/04, by fax after several attempts on the 27th & 28th of November to file it electronically (with negative results). It was discovered another user who didn't represent the City of Richmond had been assigned this account. The City also notified East Bay Regional Parks, Contra Costa County Health, and the RWQCBSFB by phone on the day of the incident. The RWQCBSFB web site no longer lists an after hours number so the notifacation was left on voice mail. | Sr Ind. Waste Insptr | Stephen Friday | 2004-12-03 | 510-412-2009 |  | MAJOR | Stephen Friday | City of Richmond | 510-412-2009 |  | 1401 Marina Way South | Richmond | Contra Costa | 94804 |  | City of Richmond | 510-412-2009 |  | 1401 Marina Way South | Richmond | Contra Costa | 94804
5003 | 25 | 1 | Rodeo | 2007-03-26 14:24 | 100 | 0 |  | 2007-03-26 14:24 |  | -- | Intersection of Pinole Ave and 3rd Street. | Rodeo | contra costa | 94572 |  |  | 2007-03-26 |  |  |  | Cause unknown is the closest to the actual case of how the spill has occurred. The contractor is installing a new 10-inch bypass on 3rd street. The pipe is installed excepting one manhole. During the construction of the manhole, the temporary block in the upstream manhole in the new 10-inch line was leaking. The Contractor pumped the water from the manhole excavation to the curb and gutter. The District informed the contractor of this mistake and the discharge is now routed to the nearest live manhole. The contractor has cleaned up all of the spilled sewage and returend it to the collection system for treatment. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | CAUSE UNKNOWN | -- Select One -- |  | construction site dewatering |  | Engineer-Manager | Steven S. Beall | 2007-03-26 | 510-799-2970
4896 | 24 | 1 | Rodeo | 2007-03-12 08:35 | 100 | 0 |  | 2007-03-12 08:35 |  | -- | 720 Mariposa Ave | Rodeo | Contra Costa | 94572 |  |  | 2007-03-10 |  |  |  | Area cleaned and disinfected, blockage removed. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Engineer-Manager | Steven S. Beall | 2007-03-12 | 510-799-2970
4163 | 23 | 1 | Rodeo | 2006-11-28 13:14 | 100 | 0 |  | 2006-11-28 13:14 |  | -- | 835 Mariposa St | Rodeo | Contra Costa | 94572 |  |  | 2006-11-22 |  |  |  | Line cleaned and blockage removed. All downstream lines cleaned to facilitate the grease into larger lines for conveyance to treatment plant. Area cleaned and disinfected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Engineer-Manager | Steven S. Beall | 2006-11-28 | 510-799-2970
3539 | 21 | 1 | Rodeo | 2006-06-22 10:49 | 50 | 0 |  | 2006-06-22 10:49 |  | -- | Tormey Lift Station | Tormey | Contra Costa | 94572 |  |  | 2006-06-18 |  |  |  | Spill was cleaned and disinfected. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Rodeo | PUMP STATION |  | ELECTRICAL POWER FAILURE | --Select None-- |  |  |  | Engineer-Manager | Steven S. Beall | 2006-06-22 | 510-799-2970 | bealls@rodeosan.org | MINOR
3189 | 18 | 1 | Rodeo | 2006-04-17 13:35 | 3000 | 0 | 06-2297 | 2006-04-17 | Tony Brewster | Rodeo | 903 3rd Street | Rodeo | Contra Costa | 94572 |  |  | 2006-04-16 | 8:15:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | No detrimental effects observed |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Rodeo | CLEAN OUT |  | NATURAL DISASTER | --Select None-- | --Select None-- |  | The District recieved about 1-inch of rain in less then four hours. The lowest point f the collection system in this location was the clean-out. District staff frequently clean line and as result, SSO was not dur to any blockages. As no one witnesed the flow gogin from the storm drain into the creek, itis unlcear if the SSO reached the waters of the state. The District has identified this line as one of the first corrective actions for line replacement once the weather clears. The District is in the planning stages of the Rodeo Sanitary District Collection System Rehabilitation Project. The project will fund approximately $500,000 in corrective measures and I&I control and reduction. | Engineer-Manager | Steven S. Beall | 2006-04-17 | 510-799-2970 | bealls@rodeosan.org | MAJOR | Steven S. Beall | Rodeo Sanitary District | 510-799-2970 |  | 800 San Pablo Ave | Rodeo | Contra Costa | 94572 | Steven S. Beall | Rodeo Sanitary District | 510-799-2970 |  | 800 San Pablo Ave | Rodeo | Contra Costa | 94572
3191 | 19 | 1 | Rodeo | 2006-04-17 13:37 | 150 | 0 |  | 2006-04-17 13:37 |  | -- | Manhole in 3rd and Pinole | Rodeo | Contra Costa | 94572 |  |  | 2006-04-16 |  |  |  | The District received approximately 1-inch of rain in four hours. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Rodeo | MANHOLE |  | NATURAL DISASTER | --Select None-- |  |  |  | Engineer-Manager | Steven S. Beall | 2006-04-17 | 510-799-2970 | bealls@rodeosan.org | MINOR
3193 | 20 | 1 | Rodeo | 2006-04-17 13:38 | 150 | 0 |  | 2006-04-17 13:38 |  | -- | Intersection of 4th and Vaqueros. | Rodeo | Contra Costa | 94572 |  |  | 2006-04-16 |  |  |  | The District received approximately 1-inch of rain in four hours. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Rodeo | MANHOLE |  | NATURAL DISASTER | --Select None-- |  |  |  | Engineer-Manager | Steven S. Beall | 2006-04-17 | 510-799-2970 | bealls@rodeosan.org | MINOR
3136 | 17 | 1 | Rodeo | 2006-04-06 10:52 | 200 | 0 |  | 2006-04-06 10:52 |  | -- | Manhole in Mariposa Ave and California Blvd | Rodeo | Contra Costa | 94572 |  |  | 2006-03-28 |  |  |  | Diapers were found in the line. Area was claned and disinfected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Rodeo | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Engineer-Manager | Steven S. Beall | 2006-04-06 | 510-799-2970 | bealls@rodeosan.org | MINOR
2979 | 16 | 1 | Rodeo | 2006-03-10 11:21 | 500 | 0 |  | 2006-03-10 11:21 |  | -- | 907 3rd Street | Rodeo | Contra Costa | 94572 |  |  | 2006-03-09 |  |  |  | Debris in pipe was a combination of broken piece of pipe, small roots, grease build-up and diapers. Line has been cleaned once every two weeks since line was identified as a probelm spot. The District will increase the frequency of mainenance. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Rodeo | OTHER | Pop Up | BLOCKAGE | DEBRIS |  |  |  | Engineer-Manager | Steven S. Beall | 2006-03-10 | 510-799-2970 | bealls@rodeosan.org | MINOR
2472 | 11 | 2 | Rodeo | 2006-01-04 10:47 | 21000 | 0 | 06-0009 | 2006-01-01 | Steven S. Beall | Rodeo | Fourth St. and Vaqueros Ave | Rodeo | Contra Costa | 94572 |  |  | 2005-12-31 | 8:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | No impact evident. The final destination of the water emanating from the manhole was unclear. The area received over 3-inches of Rain in 12 hours. Rodeo Creek was near flood stage. Given the area of Rodeo and the multiple successive rain events, the ground was saturated and over 100,000,000 gallons of water ran off into the creek. |  | No | No | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Rodeo | MANHOLE |  | NATURAL DISASTER | --Select None-- | --Select None-- |  | The area received over 3-inches of Rain in 12 hours. Rodeo Creek was 6-inches from flooding portions of Rodeo. Given the area of Rodeo and the multiple successive rain events, the ground was saturated and over 100,000,000 gallons of water ran off into the creek. The final destination of the water emanating from the manhole was unclear. The choices above did not give an option for “unknown” if the spill entered waters of the state. It was also unclear if the spill was the result of inflow from upstream manholes. Several upstream manholes were inspected and inflow was evident. The District is about 75 percent complete with an electronic mapping and flow model of the entire collection system. The flow model, coupled with the storm data will identify trouble spots for infrastructure modification. There were six flow monitoring devices set up in the collection system. This manhole had one of them. | Engineer-Manager | Steven S. Beall | 2006-01-01 | 510-799-2970 | bealls@rodeosan.org | MAJOR | Steve Beall | RSD | 510-799-2970 |  | 800 San Pablo Ave | Rodeo | Contra Costa | 94572 |  | Rodeo Sanitary District
2473 | 12 | 2 | Rodeo | 2006-01-04 10:52 | 4500 | 0 | 06-0009 | 2006-01-01 | Steven S. Beall | Rodeo | 900 Block of Third St. | Rodeo | Contra Costa | 94572 |  |  | 2005-12-31 | 8:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | No impact evident. The final destination of the water emanating from the manhole was unclear. The area received over 3-inches of Rain in 12 hours. Rodeo Creek was near flood stage. Given the area of Rodeo and the multiple successive rain events, the ground was saturated and over 100,000,000 gallons of water ran off into the creek. |  | No | No | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Rodeo | MANHOLE |  | NATURAL DISASTER | --Select None-- | --Select None-- |  | The area received over 3-inches of Rain in 12 hours. Rodeo Creek was 6-inches from flooding portions of Rodeo. Given the area of Rodeo and the multiple successive rain events, the ground was saturated and over 100,000,000 gallons of water ran off into the creek. The final destination of the water emanating from the manhole was unclear. The choices above did not give an option for “unknown” if the spill entered waters of the state. It was also unclear if the spill was the result of inflow from upstream manholes. Several upstream manholes were inspected and inflow was evident. The District is about 75 percent complete with an electronic mapping and flow model of the entire collection system. The flow model, coupled with the storm data will identify trouble spots for infrastructure modification. There were six flow monitoring devices set up in the collection system. This manhole had one of them. | Engineer-Manager | Steven S. Beall | 2006-01-01 | 510-799-2970 | bealls@rodeosan.org | MAJOR | Steve Beall | RSD | 510-799-2970 |  | 800 San Pablo Ave | Rodeo | Conra Costa | 94572 |  | Rodeo
2476 | 13 | 2 | Rodeo | 2006-01-04 11:35 | 16500 | 0 | 06-0009 | 2006-01-01 | Steven S. Beall | Rodeo | 524 Fourth St. Toilet in basement overflowed. Water was pumped out by resident into nearest storm drain. | Rodeo | Contra Costa | 94572 |  |  | 2005-12-31 | 2:30:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | No impact evident. The final destination of the water entering the storm drain was unclear. The area received over 3-inches of Rain in 12 hours. Rodeo Creek was near flood stage. Given the area of Rodeo and the multiple successive rain events, the ground was saturated and over 100,000,000 gallons of water ran off into the creek. |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Rodeo | OTHER | Toilet in basement | NATURAL DISASTER | --Select None-- | --Select None-- |  | The area received over 3-inches of Rain in 12 hours. Rodeo Creek was 6-inches from flooding portions of Rodeo. Given the area of Rodeo and the multiple successive rain events, the ground was saturated and over 100,000,000 gallons of water ran off into the creek. The final destination of the water entering the storm drain was unclear. The choices above did not give an option for “unknown” if the spill entered waters of the state. It was also unclear if the spill was the result of inflow from upstream manholes. There were many large standing puddles of water over the manholes. The affected areas have been cleaned and disinfected. The infrastructure in the area has been modified to prevent further flooding into the home. Investigations will continue to determine if the plumbing connections will be removed. The FFEL of the basement is approx 5 feet below grade. | Engineer-Manager | Steven S. Beall | 2006-01-01 | 510-799-2970 | bealls@rodeosan.org | MAJOR | Steve Beall | RSD | 510-799-2970 |  | 800 San Pablo Ave | Rodeo | Contra Costa | 94572 |  | Rodeo
2477 | 14 | 2 | Rodeo | 2006-01-04 12:23 | 5700 | 0 | 06-0009 | 2006-01-01 | Steven S. Beall | Rodeo | 520 Fourth St. Toilet in Basement overflowed. Water was pumped out by resident into nearest storm drain. | Rodeo | Contra Costa | 94572 |  |  | 2005-12-31 | 2:30:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | No impact evident. The final destination of the water entering the strom drain was unclear. The area received over 3-inches of Rain in 12 hours. Rodeo Creek was near flood stage. Given the area of Rodeo and the multiple successive rain events, the ground was saturated and over 100,000,000 gallons of water ran off into the creek. |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Rodeo | OTHER | Toilet in Basement | NATURAL DISASTER | --Select None-- | --Select None-- |  | The area received over 3-inches of Rain in 12 hours. Rodeo Creek was 6-inches from flooding portions of Rodeo. Given the area of Rodeo and the multiple successive rain events, the ground was saturated and over 100,000,000 gallons of water ran off into the creek. The final destination of the water entering the storm drain was unclear. The choices above did not give an option for “unknown” if the spill entered waters of the state. It was also unclear if the spill was the result of inflow from upstream manholes. There were many large standing puddles of water over the manholes. The affected areas have been cleaned and disinfected. The infrastructure in the area has been modified to prevent further flooding into the home. Investigations will continue to determine if the plumbing connections will be removed. | Engineer-Manager | Steven S. Beall | 2006-01-01 | 510-799-2970 | bealls@rodeosan.org | MAJOR | Steve Beall | RSD | 510-799-2970 |  | 800 San Pablo Ave | Rodeo | Contra Costa | 94572 |  | Rodeo
2478 | 15 | 2 | Rodeo | 2006-01-04 12:30 | 1800 | 0 | 06-0009 | 2006-01-01 | Steven S. Beall | Rodeo | 201 Parker Ave. Water pumped by property owner into storm drain. | Rodeo | Contra Costa | 94572 |  |  | 2005-12-31 | 3:30:00 PM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | No impact evident. The final destination of the water entering the storm drain was unclear. The area received over 3-inches of Rain in 12 hours. Rodeo Creek was near flood stage. Given the area of Rodeo and the multiple successive rain events, the ground was saturated and over 100,000,000 gallons of water ran off into the creek. |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Rodeo | OTHER | Toilet in Bathroon | NATURAL DISASTER | --Select None-- | --Select None-- |  | The area received over 3-inches of Rain in 12 hours. Rodeo Creek was 6-inches from flooding portions of Rodeo. Given the area of Rodeo and the multiple successive rain events, the ground was saturated and over 100,000,000 gallons of water ran off into the creek. The final destination of the water entering the storm drain was unclear. The choices above did not give an option for “unknown” if the spill entered waters of the state. It was also unclear if the spill was the result of inflow from upstream manholes. The affected areas have been cleaned and disinfected. The infrastructure in the area has been modified to prevent further flooding into the property. Investigations will continue to determine if the plumbing connections will be removed. | Engineer-Manager | Steven S. Beall | 2006-01-01 | 510-799-2970 | bealls@rodeosan.org | MAJOR | Steve Beall | RSD | 510-799-2970 |  | 800 San Pablo Ave | Rodeo | Contra Costa | 94572 |  | Rodeo
2313 | 9 | 1 | Rodeo | 2005-12-23 11:38 | 400 | 0 |  | 2005-12-23 11:38 |  | -- | 927 3rd Street | Rodeo | Contra Costa | 94572 |  |  | 2005-12-21 |  |  |  | Aera cleaned and disinfected. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Rodeo | CLEAN OUT |  | BLOCKAGE | --Select None-- |  |  |  | Engineer-Manager | Steven S. Beall | 2005-12-23 | 510-799-2970 | bealls@rodeosan.org | MINOR
2315 | 10 | 1 | Rodeo | 2005-12-23 11:43 | 10 | 0 |  | 2005-12-23 11:43 |  | -- | 923 3rd Street | Rodeo | Contra Costa | 94572 |  |  | 2005-12-21 |  |  |  | Same blockage from SSO 2313. Spill confined to bathroom. Cleaning company dispatched and cleaned and disinfected affected area. Blockage unknown. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Rodeo | OTHER | Toilet | BLOCKAGE | --Select None-- |  |  |  | Engineer-Manager | Steven S. Beall | 2005-12-23 | 510-799-2970 | bealls@rodeosan.org | MINOR
1992 | 8 | 1 | Rodeo | 2005-10-20 12:47 | 25 | 0 |  | 2005-10-20 12:47 |  | -- | 1221 7th Street, backyard | Rodeo | Contra Costa | 94572 |  |  | 2005-10-19 |  |  |  | Grease and Roots were removed. This spillage/blockage was a result of the spill reported for 10/18/2005 SSO tracking number 1990 ID:7 Version:1. This location is directly downstream from the previous blockage. This line is in a steep hill and difficult to get equipment to. Staff have thoroughly cleaned the entire line and physically removed the blockage. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Rodeo | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Engineer-Manager | Steven S. Beall | 2005-10-20 | 510-799-2970 | bealls@rodeosan.org | MINOR
1990 | 7 | 1 | Rodeo | 2005-10-20 12:40 | 50 | 0 |  | 2005-10-20 12:40 |  | -- | 813 Laurel Ct, backyard | Rodeo | Contra Costa | 94572 |  |  | 2005-10-18 |  |  |  | Area cleand and disinfected. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Rodeo | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Engineer-Manager | Steven S. Beall | 2005-10-20 | 510-799-2970 | bealls@rodeosan.org | MINOR
1924 | 6 | 1 | Rodeo | 2005-10-06 11:17 | 1 | 0 |  | 2005-10-06 11:17 |  | -- | Intersection of Toulabee Rd. and California St. | Rodeo | Contra Costa | 94572 |  |  | 2005-10-05 |  |  |  | District staff found a baseball bat in the manhole, lodged in the flow line, that generated a blockage of grease. The area was cleaned and disinfected without incident. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Rodeo | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Engineer-Manager | Steven S. Beall | 2005-10-06 | 510-799-2970 | bealls@rodeosan.org | MINOR
1871 | 5 | 1 | Rodeo | 2005-09-26 14:07 | 75 | 0 |  | 2005-09-26 14:07 |  | -- | 524 4th street | rodeo | contra costa | 94572 |  |  | 2005-09-25 |  |  |  | Crime Scene Cleaners were called in to clean and disinfect the affected basement in the residence. All the sewage was cleaned without any public health issues. No further contamination remains. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Rodeo | OTHER | residential fixture | BLOCKAGE | GREASE |  |  |  | Engineer-Manager | Steven S. Beall | 2005-09-26 | 5107992970 | bealls@rodeosan.org | MINOR
1805 | 4 | 1 | Rodeo | 2005-09-19 12:48 | 25 | 0 |  | 2005-09-19 12:48 |  | -- | 842 Loral Court | Rodeo | Contra Costa | 94572 |  |  | 2005-09-17 |  |  |  | Area was cleaned and disinfected. No sewage went into storm drain. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Rodeo | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Engineer-Manager | Steven S. Beall | 2005-09-19 | 510-799-2970 | bealls@rodeosan.org | MINOR
1276 | 3 | 1 | Rodeo | 2005-04-12 13:55 | 600 | 0 |  | 2005-04-12 13:55 |  | -- | 920 Mahoney St Backyard Sewer Line | Rodeo | Contra Costa | 94572 |  |  | 2005-04-10 |  |  |  | A construction stake was driven into the backyard sewer line. It appears that this was done at least 17 years ago as the current resident has not made any improvements in the backyard on the sewer line easement (moved to residence in 1988). Upstream of this location there are approximately 15 homes that discharge into this line. The line was excavated, the broken/blocked pipe was removed and a new section of pipe was installed. The line was clean from the upstream manhole to the downstream manhole and no unusual debris was found. The storm drain line was a backyard drain and it is unclear as to the ultimate discharge point as this storm drain is believed to parallel the backyard sewer line. No records available for determination. The area was cleaned and disinfected by District staff once the repairs were made. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Rodeo | OTHER | Broken sewer line | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Engineer-Manager | Steven S. Beall | 2005-04-12 | 510-799-2970 | bealls@rodeosan.org | MINOR
1274 | 2 | 1 | Rodeo | 2005-04-11 10:03 | 25 | 0 |  | 2005-04-11 10:03 |  | -- | 755 Vaqueros | Rodeo | Contra Costa | 94572 |  |  | 2005-04-06 |  |  |  | Area of spill was cleaned. It appeared that the roots were in the homeowners lateral as well. Line was cleaned and re-checked the following day. Re-check for blockage was negative. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Rodeo | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Engineer-Manager | Steven S. Beall | 2005-04-11 | 510-799-2970 | bealls@rodeosan.org | MINOR
465 | 1 | 1 | Rodeo | 2004-12-09 15:23 | 2250 | 500 | 04-6277 | 2004-12-04 | Steven S. Beall | Rodeo | 927 3rd Street | Rodeo | Contra Costa | 94572 |  |  | 2004-12-02 | 12:00:00 P | [5 empty] | SUNNY WEATHER | Low | Rodeo Creek | STORM DRAIN | No |  | No | No | No Impact. |  | Yes | Yes | Yes | No | No | Yes | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | Rodeo | CLEAN OUT | Stray root likely from previous root control measures. | BLOCKAGE | ROOTS | --Select None-- |  | Their was a root found that created a blockage in a line that would not typically have a root blockage. Upstream of this location, vapor root control was performed during the summer. It is likely this root traveled through the system became lodged at this point. The SSO occurred from the clean out at the subject address. Sewage poured accros the sidewalk and flowed approximately 750 feet to a storm drain where it entered the Rodeo Creek. Samples were taken, 100 feet upstream, at the location and 100 feet downs stream. They were analyzed for ammonia (1.0, 0.4, 0.5 mg/L) and DO (9.4, 7.2, 6.4). No fish kills have been observed. No negative impacts have been observed. All exposed areas were vacuumed and disinfected. Any and all wash water and remaining ponding sewage was vacuumed and area disinfected. Storm drain drop inlet and pipe were vacuumed and cleaned. All contents of vacuum truck were disposed of at the Rodeo Sanitary District Wastewater Treatment Plant. | Engineer-Manager | Steven S. Beall | 2004-12-09 | 510-799-2970 |  | MAJOR | Steven S. Beall | Rodeo Sanitary District | 510-799-2970 |  | 800 San Pablo Ave | Rodeo | Contra Costa | 94572 |  | Rodeo Sanitary District | 510-799-2970 |  | 800 San Pablo Ave | Rodeo | Contra Costa | 94572
2932 | 3 | 13 | SAM | 2006-03-03 21:01 | 2000 | 2000 | 06-1106 | 2006-02-21 | Tony Pullin | SAM | Hwy 1 at Alto | El Granada | San Mateo | 94018 |  |  | 2006-02-21 | 9:39:00 AM | [5 empty] | SUNNY WEATHER | Low |  | YARD/LAND | No |  | No | No | SSO did not enter Water. |  | Yes | Yes | No | No | No | No | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SAM | PIPE |  | INFRASTRUCTURE FAILURE | --Select None-- | LEAKS OF COLLECTION SYSTEM |  | SSO was caused by a leaking force main.Staff witnessed ¡Ö 2,000 gallon SSO. Debris in area indicated SSO period was longer than witnessed and volume greater than witnessed. Contour of area contained all SSO and debris. All mess was cleaned up and soil replaced with certified clean soil. | Technical Svs Spvsr | Tony Pullin | 2006-02-21 | 650-726-0124 | msd@montara.com, bptacek@bankofamerica.com, bobptacek@earthlink.net, cduffy@dudek.com, msd@coastside.net, jack@samcleanswater.org, ldw@ldworen.net, pnagengast@ci.half-moon-bay.ca.us, scott@montara.com, scott.kathey@noaa.gov, shartsell@co.sanmateo.ca.us, tony@samcleanswater.org, ricster@sbcglobal.net, mfraser@ci.half-moon-bay.ca.us, dgorn@sbcglobal.net, deliac@comcast.net | MAJOR | Tony Pullin | Sewer Authority Mid-Coastside | 650-726-0124 | 125 | 1000 N. Cabrillo Hwy | Half Moon Bay | San Mateo | 94019 |  | SAM |  |  | 1000 N. Cabrillo Hwy | Half Moon Bay | San Mateo | 94019
805 | 1 | 2 | SAM | 2005-01-10 14:30 | 19020 | 0 | 04-6810 | 2004-12-28 | Tony Pullin | SAM | Hwy 1 adjacent to 560 Obispo Ave and Magellan at Marada. | El Granada | San Mateo | 94018 | 37.49587N | 122.46281W | 2004-12-27 | 7:00:00 AM | [5 empty] | RAINY WEATHER | Low | Pacific Ocean | SURFACE WATER IMPACT | Yes | San Mateo County Health Department warning signs were posted. | No | Yes | SSO took place during intense storm period. Wave action was also intense. Conditions made conclusion impossible. |  | Yes | No | No | No | No | Yes | Yes | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SAM | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | System was overwhelmed during an extraordinary storm event. | Tech Svs Spvsr | Tony Pullin | 2004-12-27 | 650-726-0124 | tony@samcleanswater.org, jack@samcleanswater.org | MAJOR | Tony Pullin | Sewer Authority Mid-Coastside | 650-726-0124 | 125 | 1000 N. Cabrillo Hwy | Half Moon Bay | San Mateo | 94019 |  | SAM
807 | 2 | 2 | SAM | 2005-01-10 15:35 | 83970 | 0 | 04-6811 | 2004-12-28 | Tony Pullin | SAM | Highway 1 at 16th Street | Montara | San Mateo | 94037 | 37.53433N | 122.51889W | 2004-12-27 | 10:18:00 A | [5 empty] | RAINY WEATHER | Low | Pacific Ocean | SURFACE WATER IMPACT | Yes | Posted Fitzgerald Marine Reserve as a precaution. | No | Yes | SSO Occurred during intense storm period. Entry point is a rocky surf area with large storm waves. A determination could not be made |  | No | No | No | No | No | Yes | Yes | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SAM | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | Area received over 4 inches of rain in 24 hour period. The Storm Water Retention Tank filled to capacity (430,000 gal) before SSO occurred. Staff monitored SSO for duration. | TechSvsSpvr | Tony Pullin | 2004-12-28 | 650-726-0124 | tony@samcleanswater.org, jack@samcleanswater.org | MAJOR | Tony Pullin | SAM | 650-726-0124 | 125 | 1000 N. Cabrillo Hwy | Half Moon Bay | San Mateo | 94019 |  | SAM
5053 | 19 | 1 | SanBrunoCity | 2007-04-09 10:13 | 250 | 0 |  | 2007-04-09 10:13 |  | -- | Parking lot across from 422 Mastick Ave. | San Bruno | San Mateo | 94066 |  |  | 2007-04-07 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Wastewater Field Sup | Dennis Bosch | 2007-04-09 | 650-616-7172
5020 | 18 | 1 | SanBrunoCity | 2007-03-28 14:50 | 150 | 0 |  | 2007-03-28 14:50 |  | -- | Intersection of State Highway 35 and Sharp Park Road. | San Bruno | San Mateo | 94066 |  |  | 2007-03-28 | [9 empty] | NO WATER INVOLVED | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Waste Water Field Su | Dennis Bosch | 2007-03-28 | 650-616-7161
4968 | 17 | 2 | SanBrunoCity | 2007-02-27 | 3000 | 0 | 07-1260 | 2007-02-27 | Larry Smurthwaite | SanBrunoCity | Intersection of Kains and Masson Ave. | San Bruno | San Mateo | 94066 |  |  | 2007-02-26 | 0.14583 | [6 empty] | Low |  | STORM DRAIN | No |  | No | No | There was no Visual Inspection of receiving water. |  | Yes | Yes | Yes |  |  | No | No |  |  |  | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | GREASE | -- Select One -- |  |  | Deputy Director of Public Works | Robert Howard | 2007-02-27 | 650-616-7179
4492 | 16 | 1 | SanBrunoCity | 2007-01-11 08:39 | 300 | 0 |  | 2007-01-11 08:39 |  | -- | Intersection of Santa Clara Ave. and San Antonio Ave. | San Bruno | San Mateo | 94066 |  |  | 2007-01-10 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Wastewater Field Sup | Dennis Bosch | 2007-01-11 | 650-616-7160
4267 | 15 | 1 | SanBrunoCity | 2006-12-07 16:05 | 100 | 0 |  | 2006-12-07 16:05 |  | -- | 1650 Claremont Drive | San Bruno | San Mateo | 94066 |  |  | 2006-12-06 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BYPASS | -- Select One -- |  |  |  | Wastewater Field Sup | Dennis Bosch | 2006-12-07 | 650-616-7161
3788 | 14 | 1 | SanBrunoCity | 2006-08-25 13:12 | 300 | 0 |  | 2006-08-25 13:12 |  | -- | Crystal Springs Road at Donner Ave. | San Bruno | San Mateo | 94066 |  |  | 2006-08-25 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanBrunoCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Wastewater Field Sup | Dennis Bosch | 2006-08-25 | 650-616-7160 | smunns@ci.sanbruno.ca.us, smunns@sanbruno.ca.gov | MINOR
3739 | 13 | 1 | SanBrunoCity | 2006-08-15 10:51 | 150 | 0 |  | 2006-08-15 10:51 |  | -- | Intersection of Oakmont Dr. and Olympic Dr. | San Bruno | San Mateo | 94066 |  |  | 2006-08-15 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanBrunoCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Service Manager | Larry Smurthwaite | 2006-08-15 | 06-4878 | rhoward@ci.sanbruno.ca.us, smunns@sanbruno.ca.gov | MINOR
3616 | 12 | 1 | SanBrunoCity | 2006-07-10 16:32 | 3000 | 0 | 06-4068 | 2006-07-10 | Larry Smurthwaite |  | 2480 Bennington Dr. | San Bruno | San Mateo | 94066 |  |  | 2006-07-08 | 8:19:00 AM | 2006-07-08 | 9:19:00 AM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Deputy Director of P | Robert Howard | 2006-07-10 | 650-616-7179 | rhoward@ci.sanbruno.ca.us, smunns@sanbruno.ca.gov | 24HR |  |  | 650-616-7160 | [6 empty] | SanBrunoCity
4969 | 12 | 2 | SanBrunoCity | 2006-07-10 | 3000 | 0 | 06-4068 | 2006-07-10 | Larry Smurthwaite | SanBrunoCity | 2480 Bennington Dr. | San Bruno | San Mateo | 94066 |  |  | 2006-07-08 | 0.34653 | [6 empty] | Low |  | STORM DRAIN | No |  | No | No | No visual inspection of receiving water was made |  | Yes | Yes | Yes |  |  | No | No |  |  |  | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | ROOTS | -- Select One -- |  |  | Deputy Director of Public Works | Robert Howard | 2006-07-10 | 650-616-7179
3799 | 11 | 6 | SanBrunoCity | 2006-08-25 16:07 | 276000 | 0 | 06-3783 | 2006-06-26 | Larry Smurthwaite | SanBrunoCity | Glenview Dr. @ Earl Ave (easement) 1550 Claremont Dr. | San Bruno | San Mateo | 94066 |  |  | 2006-06-24 | 11:00:00 A | [5 empty] | SUNNY WEATHER | Medium |  | STORM DRAIN | No |  | No | Yes | The majority of sewage was absorbed in the ground due to the receiving waterway being approx. 100' away from the spill origin. The spill width 3 feet downstream from the manhole was 3 feet wide. The distance of wetted surface area near the stormwater drainage was 6 inches. We assume, therefore, that 5/6th of the sewage was absorbed prior to entering into the stormwater drainage waterway. The ground that was wetted appeared to be porous and is in a wooded area. The estimated gallonage from the manhole is based on observations done at approximately 9 AM on June 26th. The spill call itself was on the City of San Bruno's Corporation Yard's voicemail and the caller called about water or a spring flowing at 11 AM on June 24th. The caller did not mention sewage and did not call Police Dispatch, though the message indicated that if there was a problem with sewage or water that Police was to be called. We are therefore approximating the flow from the manhole based on the known timeframes. We are also estimated the SSO volume based on our observations at 9 AM on Monday June 26th, which is peak morning flow time period. In determining flow from the manhole at 9AM on June 26th we used a sheet provided in a SSO report, "San Francisco Bay Area Sanitary Sewer Overflow Monitoring and Reporting Program for Sewer System Authorities" and in a subsection of that report there is a series of photos of manholes showing estimated flow volumes, titled, "Reference Sheet for Estimating Sewer Spills from Overflowing Sewer Manholes". The gpm from the manhole at 9 AM on June 26th, was therefore estimated from the visuals provided. The manhole lockdown mechanism was compromised. What remained were the two vertical mechanisms that held the crossbar, but no crossbar in evidence. On July 12th a new type of lockdown mechanism was installed and additional concrete poured around the perimeter of the manhole that experienced the SSO in order to provide additional support to the ring and cover. In addition will have automatic transfer of after hours calls to a private answering service provided with a set of questions and responses that would, if answered related to an SSO, call standby crews. |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No | 2006-06-26 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanBrunoCity | MANHOLE | Possible root intrusion due to easement location.Root intrusion unlikely cause based on downstream evidence of large rocks in blocked area of sewer line and missing lockdown mechanism that was intended to prevent removal of manhole cover. | BLOCKAGE | VANDALISM | --Select None-- | Possible root intrusion due to easement location. Root intrusion unlikely cause based on downstream evidence of large rocks in blocked area of sewer line and missing lockdown mechanism that was intended to prevent removal of manhole cover. |  | Services Manager | Larry Smurthwaite | 2006-06-26 | 06-3783 | rhoward@ci.sanbruno.ca.us | MAJOR | Larry Smurthwaite | SanBrunoCity | 650-616-7160 |  | 567 El Camino Real | San Bruno | San Mateo | 94066 |  | City of San Bruno
3480 | 9 | 1 | SanBrunoCity | 2006-06-09 14:35 | 200 | 0 |  | 2006-06-09 14:35 |  | -- | 466 San Mateo Ave. | San Bruno | San Mateo | 94066 |  |  | 2006-06-09 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanBrunoCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Wastewater Division | Dennis Bosch | 2006-06-09 | 650-616-7161 | smunns@ci.sanbruno.ca.us, smunns@sanbruno.ca.gov | MINOR
3482 | 10 | 1 | SanBrunoCity | 2006-06-09 15:13 | 600 | 0 |  | 2006-06-09 15:13 |  | -- | 2440 Bennington Drive | San Bruno | San Mateo | 94066 |  |  | 2006-06-09 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanBrunoCity | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Wastewater Field Sup | Dennis Bosch | 2006-06-09 | 650-616-7161 | smunns@ci.sanbruno.ca.us, smunns@sanbruno.ca.gov | MINOR
3466 | 8 | 1 | SanBrunoCity | 2006-06-07 08:37 | 1000 | 0 |  | 2006-06-07 08:37 |  | -- | 2150 Evergreen Dr. | San Bruno | San Mateo | 94066 |  |  | 2006-06-07 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanBrunoCity | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Services Manager | Larry Smurthwaite | 2006-06-07 | 650-616-7160 | smunns@ci.sanbruno.ca.us, smunns@sanbruno.ca.gov | MINOR
3434 | 7 | 1 | SanBrunoCity | 2006-05-31 08:26 | 300 | 0 |  | 2006-05-31 08:26 |  | -- | 424 San Mateo Ave. | San Bruno | San Mateo | 94066 |  |  | 2006-05-27 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanBrunoCity | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Services Manager | Larry Smurthwaite | 2006-05-31 | 650-616-7160 | smunns@ci.sanbruno.ca.us, smunns@sanbruno.ca.gov | MINOR
3398 | 6 | 3 | SanBrunoCity | 2006-05-23 15:34 | 3000 | 1000 | 06-0889 | 2006-02-10 | Larry Smurthwaite | SanBrunoCity | 2540 Olympic Dr. | San Bruno | San Mateo | 94066 |  |  | 2006-02-09 | 8:30:00 PM | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | No | Not able to visualize due to location |  | Yes | Yes | Yes | No | No | No | No | No | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanBrunoCity | MANHOLE |  | BLOCKAGE | --Select None-- | --Select None-- |  | This is 2nd submittal. This is a test report. | Director of Public W | Scott Munns | 2006-02-10 | 650-616-7066 | smunns@ci.sanbruno.ca.us, | MAJOR | Larry Smurthwaite | SanBrunoCity | 650-616-7160 |  | 567 El Camino Real | San Bruno | San Mateo | 94066 |  | SanBrunoCity
3396 | 5 | 2 | SanBrunoCity | 2006-05-23 15:07 | 6000 | 2000 | 06-0889 | 2006-01-01 | Larry Smurthwaite | SanBrunoCity | Pacific heights @ Highland Dr. | San Bruno | San Mateo | 94066 |  |  | 2006-01-01 | 12:53:00 P | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | No | Not able to visualize due to location |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanBrunoCity | MANHOLE |  | BLOCKAGE | --Select None-- | --Select None-- |  |  | Services Manager | Larry Smurthwaite | 2006-01-01 | 650-616-7160 | smunns@ci.sanbruno.ca.us, smunns@sanbruno.ca.gov | MAJOR | Larry Smurthwaite | SanBrunoCity | 650-616-7160 |  | 567 El Camino Real | San Bruno | San Mateo | 94066 |  | San Bruno City
1755 | 4 | 1 | SanBrunoCity | 2005-09-06 11:15 | 750 | 0 |  | 2005-09-06 11:15 |  | -- | 179 Linden (easement) | San Bruno | San Mateo | 94066 |  |  | 2005-09-06 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanBrunoCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Services Manager | Larry Smurthwaite | 2005-09-06 | 650-616-7160 | smunns@ci.sanbruno.ca.us, smunns@sanbruno.ca.gov | MINOR
1702 | 3 | 1 | SanBrunoCity | 2005-08-22 10:21 | 750 | 0 |  | 2005-08-22 10:21 |  | -- | 2450 Crestmoor Dr. | San Bruno | San Mateo | 94006 |  |  | 2005-08-22 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanBrunoCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Services Manager | Larry Smurthwaite | 2005-08-22 | 650-616-7160 | smunns@ci.sanbruno.ca.us, smunns@sanbruno.ca.gov | MINOR
1517 | 2 | 1 | SanBrunoCity | 2005-06-13 13:23 | 750 | 0 |  | 2005-06-13 13:23 |  | -- | Oakmont @ Olynpic Dr. | San Bruno | San Mateo | 94066 |  |  | 2005-06-13 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanBrunoCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Services Manager | Larry Smurthwaite | 2005-06-13 | 650-616-7168 | smunns@ci.sanbruno.ca.us, | MINOR
809 | 1 | 1 | SanBrunoCity | 2005-01-10 16:23 | 10 | 0 |  | 2005-01-10 16:23 |  | -- | Test Report Only | San Bruno | San Mateo | 94010 |  |  | 2005-01-10 |  |  |  | Test Report Only | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanBrunoCity | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Manager | Larry Smurthwaite | 2005-01-10 | 650-616-7168 | LSmurthwaite@ci.sanbruno.ca.us | MINOR
5195 | 76 | 1 | SanCarlos | 2007-05-01 15:14 | 150 | 0 |  | 2007-05-01 15:14 |  | -- | Willow Glen And Fay | SanCarlos | San Mateo | 94070 |  |  | 2007-04-27 |  |  |  | Hand rodded main to clear a paper blockage. Followed up with flushing work order and cleaned up the area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Superintendent | Paul Baker | 2007-05-01 | 650-802-4143
5150 | 75 | 1 | SanCarlos | 2007-04-26 07:56 | 20 | 0 |  | 2007-04-26 07:56 |  | -- | Alameda and Rockridge | San Carlos | San Mateo | 94070 |  |  | 2007-04-25 |  |  |  | Hand rodded main to clear grease blockage. Cleaned up area. Followed up with work order for main flushing. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Superintendent | Paul Baker | 2007-04-26 | 650-802-4143
5148 | 74 | 1 | SanCarlos | 2007-04-26 07:52 | 10 | 0 |  | 2007-04-26 07:52 |  | -- | 225 Wellington | San Carlos | San Mateo | 94070 |  |  | 2007-04-25 |  |  |  | Hand rodded main to clear root blockage. Cleaned up area. Followed up with work order to power rod main. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2007-04-26 | 650-802-4143
4984 | 69 | 1 | SanCarlos | 2007-03-23 07:48 | 375 | 0 |  | 2007-03-23 07:48 |  | -- | Bing & Bayport | San Carlos | San Mateo | 94070 |  |  | 2007-03-22 |  |  |  | Hand rodded main to clear paper blockage. Cleaned up area and used vac truck to recover all of the overflow. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Superintendent | Paul Baker | 2007-03-23 | 650 802-4143
4880 | 68 | 1 | SanCarlos | 2007-03-08 11:22 | 180 | 0 |  | 2007-03-08 11:22 |  | -- | 728 Elm Street | San Carlos | San Mateo | 94070 |  |  | 2007-03-07 |  |  |  | Flushed main to clear paper and grease blockage. Cleaned up yard planter area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Superintendent | Paul Baker | 2007-03-08 | 650-802-4143
4777 | 67 | 1 | SanCarlos | 2007-02-20 | 1125 | 375 | 07-1100 | 2007-02-20 | Paul Baker | SanCarlos | 710 Orange | San Carlos | San Mateo | 94070 |  |  | 2007-02-17 | 0.36458 | [6 empty] | Low |  | STORM DRAIN | No |  | No | No | No effect |  | Yes | Yes | Yes |  |  | No | No |  |  |  | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | DEBRIS | -- Select One -- |  | Cleared rag blockage in main with hand rods. Followed up with vac truck to flush storm main and clean up area. | Superintendent | Paul Baker | 2007-02-20 | 650-802-4140
4770 | 66 | 1 | SanCarlos | 2007-02-16 07:25 | 240 | 0 |  | 2007-02-16 07:25 |  | -- | 106 Beverly Dr. | San Carlos | San Mateo | 94070 |  |  | 2007-02-15 |  |  |  | Hand rodded main to clear paper obstruction. Followed up with vac truck to clean area and recover spill from storm system. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Superintendent | Paul Baker | 2007-02-16 | 650-802-4143
4758 | 65 | 1 | SanCarlos | 2007-02-15 08:31 | 135 | 0 |  | 2007-02-15 08:31 |  | -- | 744 Knoll Dr | San Carlos | San Mateo | 94070 |  |  | 2007-02-14 |  |  |  | Hand rodded main to clear paper blockage. Followed up with vac truck to clean up area and storm drain. Followed up with power rodding of main. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Superintendent | Paul Baker | 2007-02-15 | 650-802-4143
4706 | 64 | 1 | SanCarlos | 2007-02-08 11:53 | 100 | 0 |  | 2007-02-08 11:53 |  | -- | 710 Orange | San Carlos | San Mateo | 94070 |  |  | 2007-02-06 |  |  |  | Hydro flushed to clear blockage, cleaned up area and storm drain. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Superintendent | Paul Baker | 2007-02-08 | 650-802-4143
4629 | 62 | 1 | SanCarlos | 2007-01-29 11:10 | 300 | 0 |  | 2007-01-29 11:10 |  | -- | 2405 San Carlos Ave | San Carlos | San Mateo | 94070 |  |  | 2007-01-27 |  |  |  | Rodded main to clear root obstruction, followed up with power rodder and cleaned up area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2007-01-29 | 650 802-4140
4582 | 60 | 2 | SanCarlos | 2007-01-22 | 1125 | 0 | 07-0472 | 2007-01-22 | Paul Baker | SanCarlos | 108 Windsor | San Carlos | San Mateo | 94070 |  |  | 2007-01-21 | 0.42708 | [6 empty] | Low |  | STORM DRAIN | No |  | No | No | No effect |  | Yes | Yes | No |  |  | No | No |  |  |  | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | GREASE | -- Select One -- |  | Cleared grease and paper blockage in main with hand rods. Followed up with vac truck to flush main and clean up area. | Public Works Superintendent | Paul Baker | 2007-01-22 | 650-802-4140
4584 | 61 | 1 | SanCarlos | 2007-01-23 06:45 | 150 | 0 |  | 2007-01-23 06:45 |  | -- | 546 Alameda | San Carlos | San Mateo | 94070 |  |  | 2007-01-20 |  |  |  | Flushed main to clear grease, paper, rag blockage, flushed sewer main and storm drain to recover spillage. Cleaned up area. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Superintendent | Paul Baker | 2007-01-23 | 650-802-4143
4304 | 59 | 1 | SanCarlos | 2006-12-14 07:58 | 600 | 0 |  | 2006-12-14 07:58 |  | -- | 3375 Brittan Ave | San Carlos | San Mateo | 94070 |  |  | 2006-12-08 |  |  |  | Power rodded main to clear root blockage, Followed up with vac truck and cleaned up area. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-12-14 | 650 802-4143
4261 | 58 | 1 | SanCarlos | 2006-12-07 07:17 | 5 | 0 |  | 2006-12-07 07:17 |  | -- | 1007 Inverness | San Carlos | San Mateo | 94070 |  |  | 2006-12-03 |  |  |  | Rodded lateral to clear obstruction. Cleaned up area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-12-07 | 650-802-4143
4196 | 57 | 1 | SanCarlos | 2006-12-05 12:03 | 50 | 0 |  | 2006-12-05 12:03 |  | -- | Cranfield and San Carlos Ave | San Carlos | San MAteo | 94070 |  |  | 2006-12-01 |  |  |  | Rodded main to clear blockage, cleaned up area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-12-05 | 650-802-4143
4194 | 56 | 1 | SanCarlos | 2006-12-05 12:01 | 5 | 0 |  | 2006-12-05 12:01 |  | -- | 312 Torino | San Carlos | San Mateo | 94070 |  |  | 2006-12-01 |  |  |  | Rodded lateral to clear blockage, cleaned up area | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-12-05 | 650-802-4143
4160 | 55 | 1 | SanCarlos | 2006-11-28 08:58 | 60 | 0 |  | 2006-11-28 08:58 |  | -- | 968 Tamarack | San Carlos | San Mateo | 94070 |  |  | 2006-11-23 |  |  |  | Rodded main to clear root blockage. Followed up with vac truck for area clean up and work order to power rod main. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-11-28 | 650 802-4143
4137 | 53 | 1 | SanCarlos | 2006-11-21 14:33 | 75 | 0 |  | 2006-11-21 14:33 |  | -- | 1364 Laurel | San Carlos | San Mateo | 94070 |  |  | 2006-11-20 |  |  |  | Rodded main to clear root,towel and grease blockage. Vacuumed the debris from storm system. Followup flush work order for main. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-11-21 | 650-802-4143
4130 | 51 | 1 | SanCarlos | 2006-11-20 14:59 | 150 | 0 |  | 2006-11-20 14:59 |  | -- | 892 Bauer | San Carlos | San Mateo | 94070 |  |  | 2006-11-20 |  |  |  | Rodded main to remove root obstuction, cleaned up area. Followup work orders for main flushing and root removal from manhole. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-11-20 | 650-802-4143
4132 | 52 | 1 | SanCarlos | 2006-11-20 15:02 | 300 | 0 |  | 2006-11-20 15:02 |  | -- | Club and Lynton | San Carlos | San Mateo | 94070 |  |  | 2006-11-18 |  |  |  | Rodded main to clear paper blockage, cleaned up area | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Superintendent | Paul Baker | 2006-11-20 | 650-802-4143
4087 | 50 | 1 | SanCarlos | 2006-11-08 16:59 | 150 | 0 |  | 2006-11-08 16:59 |  | -- | 171 Madera | San Carlos | San Mateo | 94070 |  |  | 2006-11-07 |  |  |  | Hand rodded to clear blockage and followed up with power rodding of main. Cleaned up area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-11-08 | 65-802-4143 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
3988 | 49 | 1 | SanCarlos | 2006-10-16 09:10 | 10 | 0 |  | 2006-10-16 09:10 |  | -- | 737 Elm | San Carlos | San Mateo | 94070 |  |  | 2006-10-15 |  |  |  | Hand rodded lateral to clear blockage, cleaned up debris. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | Superintendent | Paul Baker | 2006-10-16 | 650-802-4143 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
3871 | 48 | 1 | SanCarlos | 2006-09-13 07:43 | 300 | 0 |  | 2006-09-13 07:43 |  | -- | El Camino and Oak | San Carlos | San Mateo | 94070 |  |  | 2006-09-12 |  |  |  | Hand rodded main to clear blockage, cleaned up street. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-09-13 | 650-802-4143 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
3766 | 47 | 1 | SanCarlos | 2006-08-21 11:28 | 250 | 0 |  | 2006-08-21 11:28 |  | -- | 66 El Camino | San Carlos | San Mateo | 94070 |  |  | 2006-08-16 |  |  |  | Hand rodded to clear blockage. cleaned up street and gutter. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Superintendent | Paul Baker | 2006-08-21 | 650-802-4143 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
3706 | 46 | 1 | SanCarlos | 2006-08-09 14:51 | 225 | 0 |  | 2006-08-09 14:51 |  | -- | San Carlos Ave and Vista | San Carlos | San Mateo | 94070 |  |  | 2006-08-08 |  |  |  | Hand rodded main to clear root and paper blockage. Cleaned up debris in gutter. Followed up with Vaccon for cleanup. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-08-09 | 650-802-4143 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
3643 | 45 | 1 | SanCarlos | 2006-07-21 10:53 | 120 | 0 |  | 2006-07-21 10:53 |  | -- | 298 Loma Road | San Carlos | San Mateo | 94070 |  |  | 2006-07-20 |  |  |  | Used hand rods to clear grease blockage and cleaned up debris in street. Followed up with work order to flush and vac main. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Siperintendent | Paul Baker | 2006-07-21 | 650-802-4143 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
3629 | 44 | 1 | SanCarlos | 2006-07-18 11:18 | 180 | 0 |  | 2006-07-18 11:18 |  | -- | 2678 San Carlos Ave | San Carlos | San Mateo | 94070 |  |  | 2006-07-17 |  |  |  | Flulshed main with Vaccon the clear blockage. Cleaned up debris with Vaccon | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Superintendent | Paul Baker | 2006-07-18 | 650-802-4143 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
3615 | 43 | 1 | SanCarlos | 2006-07-10 15:27 | 3000 | 500 | 06-4063 | 2006-07-10 | City of San Carlos | SanCarlos | Melendy and Bauer | San Carlos | San Mateo | 94070 |  |  | 2006-07-10 | 7:00:00 AM | [5 empty] | SUNNY WEATHER | Low | San Francisco Bay | STORM DRAIN | No |  | No | No | None |  | Yes | Yes | Yes | No | No | No | No | No | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- |  | Used power rodder to remove root blockage. Followed up with powersaw and vac truck to clear main and clean up debris in street and strom drain. | Superintendent | Paul Baker | 2006-07-10 | 650-802 4140 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MAJOR | Paul Baker | SanCarlos | 650-802-4143 |  | 1000 Bransten Road | San Carlos | San Mateo | 94070 |  | Ctiy of San Carlos
3571 | 42 | 1 | SanCarlos | 2006-06-28 08:54 | 135 | 0 |  | 2006-06-28 08:54 |  | -- | 245 Manor | San Carlos | San Mateo | 94070 |  |  | 2006-06-27 |  |  |  | Cleared root blockage with hand rods and followed up with power rod. Work order for video of mainline. Cleaned spill area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-06-28 | 650-802-4143 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
3551 | 41 | 1 | SanCarlos | 2006-06-23 09:07 | 225 | 0 |  | 2006-06-23 09:07 |  | -- | 17 Alta | San Carlos | San Mateo | 94070 |  |  | 2006-06-21 |  |  |  | Removed roots from inside manhole to clear problem. Cleaned up easement area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-06-23 | 650-802-4143 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
3504 | 40 | 1 | SanCarlos | 2006-06-20 07:56 | 120 | 0 |  | 2006-06-20 07:56 |  | -- | Walnut and Cherry | San Carlos | San Mateo | 94070 |  |  | 2006-06-17 |  |  |  | Cleared line with vac truck, washed down and vacuumed area of overflow. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Superintendent | Paul Baker | 2006-06-20 | 650-802-4140 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
3454 | 38 | 1 | SanCarlos | 2006-06-06 12:54 | 500 | 0 |  | 2006-06-06 12:54 |  | -- | 806 Alameda | San Carlos | San Mateo | 94070 |  |  | 2006-05-31 |  |  |  | Cleared blockage with hand rods, returned with Vacuum truck to flush lines and clean up area. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Superintendent | Paul Baker | 2006-06-06 | 650-802-4140 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
3414 | 37 | 1 | SanCarlos | 2006-05-26 10:12 | 75 | 0 |  | 2006-05-26 10:12 |  | -- | 3025 Melendy | San Carlos | San Mateo | 94070 |  |  | 2006-05-23 |  |  |  | Blockage cleared with hand rods, followed up with flushing work order and cleaned up street. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Superintendent | Paul Baker | 2006-05-26 | 650-802-4143 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
3363 | 36 | 1 | SanCarlos | 2006-05-18 08:23 | 450 | 0 |  | 2006-05-18 08:23 |  | -- | 2409 San Carlos Ave | San Carlos | San Mateo | 94070 |  |  | 2006-05-13 |  |  |  | Cleared blockage with hand rods, followed up with hydro flushing work order | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Superintendent | Paul Baker | 2006-05-18 | 650-802-4140 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
3308 | 35 | 1 | SanCarlos | 2006-05-05 09:00 | 175 | 0 |  | 2006-05-05 09:00 |  | -- | 126 Crestview Drive | San Carlos | San Mateo | 94070 |  |  | 2006-05-04 |  |  |  | Lower Crestview pump station failed due to power outage. Station back in service and area cleaned up. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | ELECTRICAL POWER FAILURE | --Select None-- |  |  |  | Superintendent | Paul Baker | 2006-05-05 | 650 802-4143 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
3122 | 34 | 1 | SanCarlos | 2006-04-04 08:21 | 300 | 0 |  | 2006-04-04 08:21 |  | -- | 680 Dartmouth Ave | San Carlos | San Mateo | 94070 |  |  | 2006-04-03 |  |  |  | Hand rodded main to clear root and towel blockage. Followed up with power rod work order. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Superintendent | Paul Baker | 2006-04-04 | 650 802-4140 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
3082 | 33 | 1 | SanCarlos | 2006-03-28 08:41 | 150 | 0 |  | 2006-03-28 08:41 |  | -- | 116 Wycombe | San Carlos | San Mateo | 94070 |  |  | 2006-03-27 |  |  |  | Hand rodded to clear root blockage. Work order for power rodder folow-up. Cleaned up area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-03-28 | 650-802-4140 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
3080 | 32 | 1 | SanCarlos | 2006-03-28 08:37 | 450 | 0 |  | 2006-03-28 08:37 |  | -- | 116 Wycombe | San Carlos | San Mateo | 94070 |  |  | 2006-03-26 |  |  |  | Hand rodded main to clear, Work order to follow-up with power rodder. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-03-28 | 650-802-4140 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
3078 | 31 | 1 | SanCarlos | 2006-03-28 08:16 | 475 | 0 |  | 2006-03-28 08:16 |  | -- | 156 Exbourne | San Carlos | San Mateo | 94070 |  |  | 2006-03-25 |  |  |  | Hand rodded main to clear. Work order for power rodder follow-up. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-03-28 | 650-802-4140 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
2998 | 30 | 1 | SanCarlos | 2006-03-13 11:16 | 450 | 0 |  | 2006-03-13 11:16 |  | -- | Walnut and Olive | San Carlos | San Mateo | 94070 |  |  | 2006-03-12 |  |  |  | Hand rodded to clear blockage, cleaned up area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Superintendent | Paul Baker | 2006-03-13 | 650-802-4140 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
2876 | 29 | 1 | SanCarlos | 2006-02-27 07:19 | 450 | 0 |  | 2006-02-27 07:19 |  | -- | 2052 San Carlos Ave | San Carlos | San Mateo | 94070 |  |  | 2006-02-24 |  |  |  | Hand rodded to clear root and rag obstruction. Cleaned up area and followed up with hydro flush work order. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-02-27 | 650 802-4143 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
2867 | 28 | 1 | SanCarlos | 2006-02-23 13:44 | 375 | 0 |  | 2006-02-23 13:44 |  | -- | 422 Clifton | San Carlos | San Mateo | 94070 |  |  | 2006-02-23 |  |  |  | Hand rodded to clear root blockage. Followed up with Hydro flush and TV of main. Cleaned up debris in area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-02-23 | 650 802-4140 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
2806 | 27 | 1 | SanCarlos | 2006-02-14 12:03 | 135 | 0 |  | 2006-02-14 12:03 |  | -- | 164 Arundel Road | San Carlos | San Mateo | 94070 |  |  | 2006-02-09 |  |  |  | Hand rodded main to clear root and grease obstruction. Cleaned up area and created work order for power rod of main. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-02-14 | 650 802-4143 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
2661 | 26 | 1 | SanCarlos | 2006-01-19 08:05 | 240 | 0 |  | 2006-01-19 08:05 |  | -- | Eaton & Stanford | San Carlos | San Mateo | 94070 |  |  | 2006-01-16 |  |  |  | HAnd rodded to clear main, cleaned up area. Followed up with hydro flush of main. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Superintendent | Paul Baker | 2006-01-19 | 650-802-4140 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
2659 | 25 | 1 | SanCarlos | 2006-01-19 08:01 | 300 | 0 |  | 2006-01-19 08:01 |  | -- | 187 Exeter | San Carlos | San Mateo | 94070 |  |  | 2006-01-09 |  |  |  | Rodded main line to clear, cleaned up debris in street. Followed up with power rodder. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-01-19 | 650-802-4140 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
2614 | 24 | 1 | SanCarlos | 2006-01-12 08:51 | 170 | 0 |  | 2006-01-12 08:51 |  | -- | 95 Curtis Ct. | San Carlos | San Mateo | 94070 |  |  | 2006-01-06 |  |  |  | Hand rodded main to clear root blockage. Cleaned debris from area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-01-12 | 650-802-4140 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
2612 | 23 | 1 | SanCarlos | 2006-01-12 08:48 | 135 | 0 |  | 2006-01-12 08:48 |  | -- | 2731 San Carlos Ave | San Carlos | San Mateo | 94070 |  |  | 2006-01-05 |  |  |  | Hand rodded main to clear root and Towel obstruction. Followed up with hydroflush to clear main. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-01-12 | 650-802-4140 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
2610 | 22 | 1 | SanCarlos | 2006-01-12 08:42 | 150 | 0 |  | 2006-01-12 08:42 |  | -- | San Carlos Ave and Cranfield | San Carlos | San Mateo | 94070 |  |  | 2006-01-04 |  |  |  | 6" fitting broke on forced sewer main in access vault. Shut down pumps and repaired fiting. Cleaned up debris in gutter. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | PIPE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Superintendent | Paul Baker | 2006-01-12 | 650-802-4140 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
2561 | 21 | 1 | SanCarlos | 2006-01-06 13:57 | 200 | 0 |  | 2006-01-06 13:57 |  | -- | Melendy & Torino | San Carlos | San Mateo | 94070 |  |  | 2005-12-28 |  |  |  | Rodded main to clear root obstruction. Cleaned up street. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2006-01-06 | 650-802-4140 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
2329 | 20 | 1 | SanCarlos | 2005-12-23 15:08 | 125 | 0 |  | 2005-12-23 15:08 |  | -- | 2007 Saint Francis | San Carlos | San Mateo | 94070 |  |  | 2005-12-22 |  |  |  | Rodded main line to clear paper blockage. Cleaned up and disinfected street and yard. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Superintendent | Paul Baker | 2005-12-23 | 650-802 4140 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
1977 | 19 | 1 | SanCarlos | 2005-10-17 13:42 | 275 | 0 |  | 2005-10-17 13:42 |  | -- | 1660 Prospect | San Carlos | San Mateo | 94070 |  |  | 2005-10-16 |  |  |  | removed roots with hand rods, cleaned up area. Follow-up work order for power rodding. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2005-10-17 | 650-802-4143 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
1903 | 18 | 1 | SanCarlos | 2005-10-03 08:56 | 200 | 0 |  | 2005-10-03 08:56 |  | -- | 769 Walnut | San Carlos | San Mateo | 94070 |  |  | 2005-10-01 |  |  |  | Cleaned up area, created work order to power rod main. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Spuerintendent | Paul Baker | 2005-10-03 | 650 802-4140 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
1751 | 17 | 1 | SanCarlos | 2005-09-06 09:38 | 450 | 0 |  | 2005-09-06 09:38 |  | -- | 106 Beverly | San Carlos | San Mateo | 94070 |  |  | 2005-09-01 |  |  |  | Cleared blockage with vac truck and recovered 50 gal. of the overflow. Follow-up with work order for video of main. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Superintendent | Paul Baker | 2005-09-06 | 650-802-4140 | pbaker@cityofsancarlos.org, pmokhtari@cityofsancarlos.org | MINOR
1595 | 16 | 1 | SanCarlos | 2005-07-06 07:50 | 50 | 0 |  | 2005-07-06 07:50 |  | -- | 118 Crestview | San Carlos | San Mateo | 94070 |  |  | 2005-07-04 |  |  |  | Power outage caused sewer pump shutdown. Cleaned up entire spill | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | ELECTRICAL POWER FAILURE | --Select None-- |  |  |  | Superintendent | Paul Baker | 2005-07-06 | 650-802-4140 | pbaker@cityofsancarlos.org | MINOR
1527 | 14 | 1 | SanCarlos | 2005-06-14 14:11 | 50 | 0 |  | 2005-06-14 14:11 |  | -- | 815 Regent | San Carlos | San Mateo | 94070 |  |  | 2005-06-13 |  |  |  | Rodded main to clear root blockage. Video inspection for possible replacement. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2005-06-14 | 650-802-4143 | pbaker@cityofsancarlos.org | MINOR
1525 | 13 | 1 | SanCarlos | 2005-06-14 14:08 | 750 | 0 |  | 2005-06-14 14:08 |  | -- | San Carlos Ave and Walnut | San Carlos | San Mateo | 94070 |  |  | 2005-06-12 |  |  |  | Rodded main to clear blockage | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Superintendent | Paul Baker | 2005-06-14 | 650-802-4143 | pbaker@cityofsancarlos.org | MINOR
1531 | 15 | 2 | SanCarlos | 2005-06-14 14:50 | 750 | 0 |  | 2005-06-14 14:50 |  | -- | 2705 Victoria Manor | San Carlos | San Mateo | 94070 |  |  | 2005-06-06 |  |  |  | Rodded main to remove blockage. Followed up with flushing as maintenance. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Superintendent | Paul Baker | 2005-06-14 | 650-802-4143 | pbaker@cityofsancarlos.org | MINOR
1385 | 12 | 1 | SanCarlos | 2005-05-10 14:20 | 60 | 0 |  | 2005-05-10 14:20 |  | -- | 1720 Belmont Ave | San Carlos | San Mateo | 94070 |  |  | 2005-05-09 |  |  |  | Hand rodded main to clear, Work order for folowup hydro flushing | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Superintendent | Paul Baker | 2005-05-10 | 650-802-4140 | pbaker@cityofsancarlos.org | MINOR
1379 | 11 | 1 | SanCarlos | 2005-05-09 15:39 | 500 | 0 |  | 2005-05-09 15:39 |  | -- | 320 Torino | San Carlos | San Mateo | 94070 |  |  | 2005-05-03 |  |  |  | Power rodded main to clear root obstruction. Cleaned up 150 gal of debris from storm gutter. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2005-05-09 | 650-802-4143 | parviz.mokhtari@ci.san-carlos.ca.us, | MINOR
1374 | 10 | 1 | SanCarlos | 2005-05-06 16:26 | 40 | 0 |  | 2005-05-06 16:26 |  | -- | 1340 Alameda de las pulgas | San Carlos | San Mateo | 94070 |  |  | 2005-04-29 |  |  |  | Hand rodded to clear blockage, Cleaned up 10 gal of the spill. Work order to power rod main and Work order to flush as well. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2005-05-06 | 650-802-4143 | pbaker@cityofsancarlos.org | MINOR
1332 | 9 | 1 | SanCarlos | 2005-04-26 14:58 | 600 | 0 |  | 2005-04-26 14:58 |  | -- | Tamarack and Birch | San Carlos | San Mateo | 94070 |  |  | 2005-04-25 |  |  |  | Rodded main to clear blockage. Work order to hydro flush main. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Superintendent | Paul Baker | 2005-04-26 | 650-802-4143 | pbaker@cityofsancarlos.org | MINOR
1328 | 8 | 1 | SanCarlos | 2005-04-25 15:36 | 900 | 0 |  | 2005-04-25 15:36 |  | -- | Manor & Madera | San Carlos | San Mateo | 94070 |  |  | 2005-04-22 |  |  |  | Rodded main to clear. Power rodded to remove roots. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2005-04-25 | 650-802-4143 | parviz.mokhtari@ci.san-carlos.ca.us, | MINOR
1317 | 6 | 1 | SanCarlos | 2005-04-22 15:25 | 15 | 0 |  | 2005-04-22 15:25 |  | -- | 1091 Sunset | San Carlos | San Mateo | 94070 |  |  | 2005-04-21 |  |  |  | Rodded main to clear. Work order to follow up with another rodding. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Superintendent | Paul Baker | 2005-04-22 | 650-802-4143 | pbaker@cityofsancarlos.org | MINOR
1321 | 7 | 1 | SanCarlos | 2005-04-25 09:57 | 675 | 0 |  | 2005-04-25 09:57 |  | -- | 32 Coronado | San Carlos | San Mateo | 94070 |  |  | 2005-04-21 |  |  |  | Rodded main to clear blockage, Work order to follow up with power rodding of main. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2005-04-25 | 650-802-4143 | pbaker@cityofsancarlos.org | MINOR
1219 | 5 | 1 | SanCarlos | 2005-03-28 13:51 | 225 | 0 |  | 2005-03-28 13:51 |  | -- | Elm and Oak | San Carlos | San Mateo | 94070 |  |  | 2005-03-27 |  |  |  | Blockage cleared, work order created for hydro cleaning. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Superintendent | Paul Baker | 2005-03-28 | 650 802-4143 | pbaker@cityofsancarlos.org | MINOR
1160 | 4 | 1 | SanCarlos | 2005-03-10 12:48 | 900 | 0 |  | 2005-03-10 12:48 |  | -- | 3343 Brittan Ave | San Carlos | San Mateo | 94070 |  |  | 2005-03-08 |  |  |  | Rodded line, line clear. Cleaned up area | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Superintendent | Paul Baker | 2005-03-10 | 650 802 4143 | pbaker@cityofsancarlos.org | MINOR
976 | 3 | 1 | SanCarlos | 2005-02-07 13:55 | 1200 | 0 | 05-0849 | 2005-02-07 | Paul Baker | Paul Baker | 1251 Crestview Drive | San Carlos | San Mateo | 94070 |  |  | 2005-02-02 | 7:30:00 PM | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | No | No effect |  | Yes | Yes | Yes | No | No | No | No | No | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- |  | Main in easement. overflow due to roots. Clean up minimal due to inaccesible area, waste in storm easement. Flushed to break roots. Follow-up with power rodding and additional flushing. Main put on future replacement list. | Superintendent | Paul Baker | 2005-02-07 | (650) 802-4143 | pbaker@cityofsancarlos.org | MAJOR | Paul Baker | SanCarlos | (650) 802-4140 |  | 1000 Bransten Rd | San Carlos | San Mateo | 94070 |  | City of San Carlos |  |  | 1000 Bransten Road | San Carlos | San Mateo | 94070
943 | 2 | 1 | SanCarlos | 2005-02-01 13:48 | 500 | 0 |  | 2005-02-01 13:48 |  | -- | 310 Phelps Road | San Carlos | San Mateo | 94070 |  |  | 2005-01-30 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanCarlos | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Paul Baker | 2005-02-01 | (650) 802-4143 | pbaker@cityofsancarlos.org | MINOR
5173 | 133 | 1 | SanJoseCity | 2007-04-27 13:23 | 200 | 0 |  | 2007-04-27 13:23 |  | -- | 4541 Renaissance Drive/Tasman Drive (easement) | San Jose | Santa Clara | 95134 |  |  | 2007-04-24 |  |  |  | Blocked off catch basin, cleared blockage and vactored and cleaned up SSO. Returned all sewage to sanitary main. No waterways were affected. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2007-04-27 | (408) 277-3058
5171 | 132 | 1 | SanJoseCity | 2007-04-27 13:19 | 200 | 0 |  | 2007-04-27 13:19 |  | -- | Friar Way and Lockhaven Way | San Jose | Santa Clara | 95129 |  |  | 2007-04-19 |  |  |  | SSO confined to street, curb and gutter. After main cleared, vactored and cleaned up area and returned SSO into sanitary sewer manhole. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip lee | 2007-04-27 | (408) 277-3058
5092 | 131 | 1 | SanJoseCity | 2007-04-20 12:26 | 400 | 0 |  | 2007-04-20 12:26 |  | -- | 7174 Wooded lake @ Leyland Park | San Jose | Santa Clara | 95120 |  |  | 2007-04-16 |  |  |  | SSO occured on private property in an easement. SSO confined to yard. No waterways were affected. SSO cleaned up and vactored and returned to sanitary system. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2007-04-20 | (408) 277-3058
5090 | 130 | 1 | SanJoseCity | 2007-04-20 12:24 | 100 | 0 |  | 2007-04-20 12:24 |  | -- | 485 Willard Ave @ Willard Garden Court | San Jose | Santa Clara | 95126 |  |  | 2007-04-16 |  |  |  | SSO confined to street, curb and gutter. No waterways were affected. Vactored up after blockage cleared and returned to sanitary system. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2007-04-20 | (408) 277-3058
5056 | 129 | 1 | SanJoseCity | 2007-04-13 09:56 | 300 | 0 |  | 2007-04-13 09:56 |  | -- | 11th & Williams St. | San Jose | Santa Clara | 95112 |  |  | 2007-04-09 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2007-04-13 | (408) 277-3058
4992 | 128 | 1 | SanJoseCity | 2007-03-23 14:28 | 100 | 0 |  | 2007-03-23 14:28 |  | -- | 1829 Anne Way @ Leigh Avenue | San Jose | Santa Clara | 95124 |  |  | 2007-03-21 |  |  |  | SSO confined to street, curb and gutter. Vactored SSO and returned to sanitary system after blockage cleared. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2007-03-23 | (408) 277-3058
4963 | 127 | 1 | SanJoseCity | 2007-03-19 13:34 | 100 | 0 |  | 2007-03-19 13:34 |  | -- | 340 Northlake / Stevens Creek | San Jose | Santa Clara | 95117 |  |  | 2007-03-19 |  |  |  | SSO confined to street, curb and gutter. SSO vactored up and returned to sanitary manhole. No waterways affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2007-03-19 | (408) 277-3058
4961 | 126 | 1 | SanJoseCity | 2007-03-19 13:32 | 100 | 0 |  | 2007-03-19 13:32 |  | -- | College Drive / Fruitdale | San Jose | Santa Clara | 95128 |  |  | 2007-03-15 |  |  |  | SSO confined to street, curb and gutter. Vactored up and returned to sanitary manhole. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2007-03-19 | (408) 277-3058
4886 | 125 | 1 | SanJoseCity | 2007-03-08 13:49 | 100 | 0 |  | 2007-03-08 13:49 |  | -- | 3230 Moorpark & Eden Avenue | San Jose | Santa Clara | 95117 |  |  | 2007-03-07 |  |  |  | SSO confined to street, curb and gutter. Blockage cleared and SSO returned to sanitary system. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2007-03-08 | (408) 277-3058
4884 | 124 | 1 | SanJoseCity | 2007-03-08 13:47 | 100 | 0 |  | 2007-03-08 13:47 |  | -- | Clover and Williams | San Jose | Santa Clara | 95128 |  |  | 2007-03-06 |  |  |  | Catch basin was sandbagged (blocked); SSO vactored and returned to sanitary system after blockage cleared. No waterways were affected. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2007-03-08 | (408) 277-3058
4882 | 123 | 1 | SanJoseCity | 2007-03-08 13:45 | 100 | 0 |  | 2007-03-08 13:45 |  | -- | Baywood & Williams | San Jose | Santa Clara | 95128 |  |  | 2007-03-06 |  |  |  | Catch basin was sandbagged; SSO vactored and returned to sanitary system after blockage was cleared. No waterways were affected. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2007-03-08 | (408) 277-3058
4852 | 121 | 1 | SanJoseCity | 2007-03-02 14:27 | 100 | 0 |  | 2007-03-02 14:27 |  | -- | 5535 Purdue Place @ Blossom Hill Road | San Jose | Santa Clara | 95118 |  |  | 2007-02-28 |  |  |  | SSO confined to street, curb and gutter. Vactored up curbline and returned to sanitary system. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2007-03-02 | (408) 277-3058
4871 | 122 | 1 | SanJoseCity | 2007-03-06 09:53 | 100 | 0 |  | 2007-03-06 09:53 |  | -- | 5278 Herbert Dr @ Hershner Dr | San Jose | Santa Clara | 95124 |  |  | 2007-02-24 |  |  |  | SSO confined to street, curb and gutter. Washed down street with clean water and vactored up; returned to sanitary system. No water ways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2007-03-06 | (408) 277-3058
4774 | 120 | 1 | SanJoseCity | 2007-02-16 09:15 | 200 | 0 |  | 2007-02-16 09:15 |  | -- | 5974 Burchell Avenue @ Medallion Drive | San Jose | Santa Clara | 95120 |  |  | 2007-02-14 |  |  |  | SSO confined to street, curb and gutter. Vactored up SSO after blockage cleared; returned to sanitary system. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Asscoiate Engineer | Philip Lee | 2007-02-16 | (408) 277-3058
4708 | 119 | 1 | SanJoseCity | 2007-02-08 14:41 | 100 | 0 |  | 2007-02-08 14:41 |  | -- | San Pedro St. @ Hedding St. | San Jose | Santa Clara | 95110 |  |  | 2007-02-06 |  |  |  | SSO confined to street, curb & gutter. No waterways were affected. SSO returned to sanitary system after sewer main was cleared. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Asscoaite Engineer | Philip Lee | 2007-02-08 | (408) 277-3058
4685 | 118 | 1 | SanJoseCity | 2007-02-07 11:30 | 150 | 0 |  | 2007-02-07 11:30 |  | -- | Mission Greens Drive @ Britt Way | San Jose | Santa Clara | 95148 |  |  | 2007-02-03 |  |  |  | SSO confined to street, curb and gutter. No waterways were affected. SSO returned to sanitary main after being vactored up. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2007-02-07 | (408) 277-3058
4683 | 117 | 1 | SanJoseCity | 2007-02-07 11:28 | 600 | 0 |  | 2007-02-07 11:28 |  | -- | 747 Boulder Dr @ Claitor Way | San Jose | Santa Clara | 95132 |  |  | 2007-02-03 |  |  |  | Dammed up catch basin and removed SSO with vactor after main was repaired. No waterways were affected. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | PIPE |  | INFRASTRUCTURE FAILURE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2007-02-07 | (408) 277-3058
4657 | 116 | 1 | SanJoseCity | 2007-02-02 08:41 | 500 | 0 |  | 2007-02-02 08:41 |  | -- | Wall St @ Weber St | San Jose | Santa Clara | 95111 |  |  | 2007-02-01 |  |  |  | Plugged off storm drain to contain SSO; Flushed with clean water and vactored up after blockage cleared. Returned sewage back into sanitary system. No water ways were affected. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2007-02-02 | (408) 277-3058
4521 | 115 | 1 | SanJoseCity | 2007-01-16 13:07 | 500 | 0 |  | 2007-01-16 13:07 |  | -- | McLellan Ave. @ Edwards St. | San Jose | Santa Clara | 95110 |  |  | 2007-01-11 |  |  |  | Dammed up SSO in Catch Basin; vactored up SSO from catch basin, street, curb and gutter after main cleared. SSO returned to sanitary system. No waterways were affected. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Associate Engineer | Philip Lee | 2007-01-16 | (408) 277-3058
4448 | 114 | 1 | SanJoseCity | 2007-01-04 10:08 | 100 | 0 |  | 2007-01-04 10:08 |  | -- | 1277 Leigh @ Stokes | San Jose | Santa Clara | 95126 |  |  | 2007-01-03 |  |  |  | SSO confined to street, curb and gutter. SSO vactored up and returned to sanitary system after blockage was cleared. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2007-01-04 | (408) 277-3058
4446 | 113 | 1 | SanJoseCity | 2007-01-04 10:06 | 100 | 0 |  | 2007-01-04 10:06 |  | -- | 1060 Owsley @ Clemence | San Jose | Santa Clara | 95122 |  |  | 2007-01-03 |  |  |  | SSO confined to street, curb and gutter. Vactored up SSO after blockage cleared; returned to sanitary system. No waterways were affected | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2007-01-04 | (408) 277-3058
4444 | 112 | 1 | SanJoseCity | 2007-01-04 10:03 | 100 | 0 |  | 2007-01-04 10:03 |  | -- | 1547 Padres @ Arada Ct | San Jose | Santa Clara | 95125 |  |  | 2006-12-29 |  |  |  | SSO confined to street, curb and gutter. Vactored up SSO after blockage was cleared; returned to sanitary system. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Asscoate Engineer | Philip Lee | 2007-01-04 | (408) 277-3058
4383 | 110 | 1 | SanJoseCity | 2006-12-22 09:09 | 225 | 0 |  | 2006-12-22 09:09 |  | -- | Via Encinitas / Guidehall | San Jose | Santa Clara | 95132 |  |  | 2006-12-21 |  |  |  | SSO confined to street, curb and gutter. SSO vactored up and returned to sanitary main after blockage cleared. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2006-12-22 | (408) 277-3058
4372 | 109 | 1 | SanJoseCity | 2006-12-20 14:13 | 300 | 0 |  | 2006-12-20 14:13 |  | -- | 88 Madden Avenue @ Jackson Avenue | San Jose | Santa Clara | 95116 |  |  | 2006-12-19 |  |  |  | Blockage/damage due to contractor damaging a manhole. SSO was confined to sreet, curb and gutter. Contractor repaired damaged manhole; vactored up SSO and returned to sanitary manhole. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | INFRASTRUCTURE FAILURE | CONSTRUCTION DEBRIS |  |  |  | Associate Engineer | Philip Lee | 2006-12-20 | (408) 277-3058
4319 | 108 | 1 | SanJoseCity | 2006-12-14 14:02 | 150 | 0 |  | 2006-12-14 14:02 |  | -- | 2889 Granite Creek Place | San Jose | Santa Clara | 95127 |  |  | 2006-12-13 |  |  |  | Grease in lateral caused SSO in street, curb & gutter. No waterways were affected. SSO cleared and returned to sanitary system. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-12-14 | (408) 277-3058
4317 | 107 | 1 | SanJoseCity | 2006-12-14 13:59 | 100 | 0 |  | 2006-12-14 13:59 |  | -- | 2425 S. Bascom Avenue @ San Carlos | San Jose | Santa Clara | 95130 |  |  | 2006-12-12 |  |  |  | SSO occurred on private property's lateral/cleanout. A private plumber was called to clear lateral and perform cleanup on private property. No waterways were affected. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2006-12-14 | (408) 277-3058
4315 | 106 | 1 | SanJoseCity | 2006-12-14 13:56 | 100 | 0 |  | 2006-12-14 13:56 |  | -- | 1795 Lancaster Drive @ Ross | San Jose | Santa Clara | 95124 |  |  | 2006-12-12 |  |  |  | SSO confined to street, curb and gutter. Blockage cleared; vactored up SSO and returned to sanitary system. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2006-12-14 | (408) 277-3058
4313 | 105 | 1 | SanJoseCity | 2006-12-14 13:54 | 100 | 0 |  | 2006-12-14 13:54 |  | -- | Dry Creek Road @ Bascom Avenue | San Jose | Santa Clara | 95125 |  |  | 2006-12-12 |  |  |  | Sandbagged/blocked off storm catch basin; cleared blockage; vactored up SSO from catch basin, street, curb and gutter; returned SSO in sanitary system. No waterways were affected. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2006-12-14 | (408) 277-3058
4258 | 102 | 1 | SanJoseCity | 2006-12-06 11:06 | 200 | 0 |  | 2006-12-06 11:06 |  | -- | Helmsley @ Summerview Drive | San Jose | Santa Clara | 95132 |  |  | 2006-12-04 |  |  |  | SSO confined to street, curb and gutter. SSO returned to sanitary system after blockage cleared. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-12-06 | (408) 277-3058
4256 | 101 | 1 | SanJoseCity | 2006-12-06 11:04 | 100 | 0 |  | 2006-12-06 11:04 |  | -- | 2445 S. Bascom @ Dry Creek Road | San Jose | Santa Clara | 95125 |  |  | 2006-12-04 |  |  |  | SSO confined to street curb and gutter. SSO vactored up and returned to sanitary system after blockage was cleared. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-12-06 | (408) 277-3058
4282 | 103 | 1 | SanJoseCity | 2006-12-11 09:53 | 100 | 0 |  | 2006-12-11 09:53 |  | -- | 1048 Vista Oaks @ Bayo Vista | San Jose | Santa Clara | 95132 |  |  | 2006-12-03 |  |  |  | SSO confined to area around manhole and in flower bed on private yard. No waterways were affected. SSO vactored and returned to sanitary system after blockage cleared. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2006-12-11 | (408) 277-3058
4291 | 104 | 1 | SanJoseCity | 2006-12-12 13:28 | 630 | 0 |  | 2006-12-12 13:28 |  | -- | 3288 Spreckles Avenue and State Street | San Jose | Santa Clara | 95002 |  |  | 2006-11-30 |  |  |  | Broken sewer main resulted in SSO. SSO contained in yard area of pump station. No waterways were affected. SSO pumped into wetwell; sewer main repaired. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | INFRASTRUCTURE FAILURE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2006-12-12 | (408) 277-3058
4177 | 99 | 1 | SanJoseCity | 2006-12-04 09:39 | 200 | 0 |  | 2006-12-04 09:39 |  | -- | Gillis @ Littman | San Jose | Santa Clara | 95120 |  |  | 2006-11-27 |  |  |  | Dammed up CB; flushed with clean water and vactored out. Returned to sanitary system after blockage cleared. No waterways were affected. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2006-12-04 | (408) 277-3058
4175 | 98 | 1 | SanJoseCity | 2006-12-04 09:35 | 200 | 0 |  | 2006-12-04 09:35 |  | -- | Bird Ave @ Willow Glen Way | San Jose | Santa Clara | 95125 |  |  | 2006-11-27 |  |  |  | SSO confined to street curb and gutter. No waterways were affected. Vactored up sewage water from curb and returned to sanitary system after blockage was cleared. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2006-12-04 | (408) 277-3058
4170 | 97 | 1 | SanJoseCity | 2006-11-29 14:27 | 100 | 0 |  | 2006-11-29 14:27 |  | -- | 602 Drake @ Virginia | San Jose | Santa Clara | 95125 |  |  | 2006-11-25 |  |  |  | SSO confined to street, curb and gutter. No waterways were affected. Cleared blockage, vactored up and returned to sanitary system. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-11-29 | (408) 277-3058
4168 | 96 | 1 | SanJoseCity | 2006-11-29 14:25 | 400 | 0 |  | 2006-11-29 14:25 |  | -- | 1595 Sierraville @ Crator | San Jose | Santa Clara | 95132 |  |  | 2006-11-25 |  |  |  | SSO confined to street, curb and gutter. No waterways were affected. Cleared blockage; vactored and returned to sanitary main. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-11-29 | (408) 277-3058
4254 | 100 | 1 | SanJoseCity | 2006-12-06 11:01 | 600 | 0 |  | 2006-12-06 11:01 |  | -- | 3130 Zanker Road @ Montague (Lockheed) | San Jose | Santa Clara | 95134 |  |  | 2006-11-22 |  |  |  | SSO occurred in the parking lot of Lockheed. City of San Jose maintenance personnel were denied access for cleanup purposes. SSO cleared and disposed of by Lockheed contractors. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Associate Engineer | Philip Lee | 2006-12-06 | (408) 277-3058
4135 | 95 | 1 | SanJoseCity | 2006-11-21 13:38 | 200 | 0 |  | 2006-11-21 13:38 |  | -- | 2472 Clyda @ Dobern | San Jose | Santa Clara | 95116 |  |  | 2006-11-19 |  |  |  | Dammed up catch basin; cleared blockage; vactored up catch basin, street, curb and gutter. SSO was returned to sanitary system after cleanup. No waterways were affected. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-11-21 | (408) 277-3058
4128 | 94 | 1 | SanJoseCity | 2006-11-20 14:18 | 100 | 0 |  | 2006-11-20 14:18 |  | -- | 357 Richfield Dr @ Albany | San Jose | Santa Clara | 95129 |  |  | 2006-11-17 |  |  |  | SSO confined to carport on private property. Vactored up and returned to sanitary system after main was cleared. No waterways were affected. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2006-11-20 | (408) 277-3058
4126 | 93 | 1 | SanJoseCity | 2006-11-20 14:16 | 200 | 0 |  | 2006-11-20 14:16 |  | -- | 415 Fenton St @ Lucian Avenue | San Jose | Santa Clara | 95127 |  |  | 2006-11-16 |  |  |  | SSO confined to street, curb and gutter. Vactored up and returned to sanitary system after blockage cleared. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | -- Select One -- |  |  |  | Associate Engineer | Philip Lee | 2006-11-20 | (408) 277-3058
4094 | 92 | 1 | SanJoseCity | 2006-11-09 13:55 | 100 | 0 |  | 2006-11-09 13:55 |  | -- | 377 S. First Street @ San Carlos Street | San Jose | Santa Clara | 95113 |  |  | 2006-11-08 |  |  |  | Catch basin was dammed and then vactored out. No waterways were affected. Vactored and returned to sanitary manhole. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Associate Engineer | Philip Lee | 2006-11-09 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
4092 | 91 | 1 | SanJoseCity | 2006-11-09 13:52 | 200 | 0 |  | 2006-11-09 13:52 |  | -- | Brete Harte @ Via Valiente | San Jose | Santa Clara | 95120 |  |  | 2006-11-07 |  |  |  | SSO confined to street, curb and gutter. Storm drains were blocked off with sandbags. No waterways were affected. SSO vactored and returned to sanitary sewer manhole. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Associate Engineer | Philip Lee | 2006-11-09 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
4057 | 90 | 1 | SanJoseCity | 2006-11-02 14:41 | 200 | 0 |  | 2006-11-02 14:41 |  | -- | Stockton Avenue/Santa Clara St/White St | San Jose | Santa Clara | 95126 |  |  | 2006-10-29 |  |  |  | Plugged up catch basin; used a vactor to cleanup catch basin, street, curb and gutter. no waterways were affected. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Associate Engineer | Philip Lee | 2006-11-02 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
4055 | 89 | 1 | SanJoseCity | 2006-11-02 14:39 | 200 | 0 |  | 2006-11-02 14:39 |  | -- | 7166 Via Corona @ Via Blanca | San Jose | Santa Clara | 95139 |  |  | 2006-10-27 |  |  |  | Bermed curb and gutter area; vactored up sewage water from curb and gutter; washed down area with clean water and then vactored up and returned to sanitary manhole. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-11-02 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
4035 | 88 | 1 | SanJoseCity | 2006-10-26 13:46 | 200 | 0 |  | 2006-10-26 13:46 |  | -- | 930 Gretchen @ Williams | San Jose | Santa Clara | 95117 |  |  | 2006-10-24 |  |  |  | Plugged catch basin; vactored/cleaned catch basin, street, curb and gutter. Returned SSO to sanitary manhole. No waterways were affected. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-10-26 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
4031 | 86 | 1 | SanJoseCity | 2006-10-26 13:40 | 200 | 0 |  | 2006-10-26 13:40 |  | -- | 1015 Craig Dr @ Miller | San Jose | Santa Clara | 95129 |  |  | 2006-10-22 |  |  |  | Plugged catch basin; cleaned and vactored up SSO from catch basin, street, curb and gutter. No waterways were affected. SSO returned to sanitary manhole. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-10-26 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
4033 | 87 | 1 | SanJoseCity | 2006-10-26 13:44 | 100 | 0 |  | 2006-10-26 13:44 |  | -- | 6674 Bret Harte @ Heathfield | San Jose | Santa Clara | 95120 |  |  | 2006-10-22 |  |  |  | SSO confined to street, curb and gutter. After blockage cleared, vactored/washed curb and gutter and returned to sanitary manhole. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-10-26 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
4029 | 85 | 1 | SanJoseCity | 2006-10-26 13:38 | 150 | 0 |  | 2006-10-26 13:38 |  | -- | 1614 Alum Rock @ 33rd St. | San Jose | Santa Clara | 95116 |  |  | 2006-10-20 |  |  |  | SSO confined to street, curb and gutter. SSO vactored up and returned to manhole after blockage cleared. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Associate Engineer | Philip Lee | 2006-10-26 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
4015 | 84 | 1 | SanJoseCity | 2006-10-20 13:50 | 100 | 0 |  | 2006-10-20 13:50 |  | -- | 5609 Blossom Hill @ Camden | San Jose | Santa Clara | 95124 |  |  | 2006-10-16 |  |  |  | SSO confined to street curb & gutter. Vactor crew cleaned up SSO and returned to sanitary manhole. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-10-20 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
3960 | 82 | 1 | SanJoseCity | 2006-10-03 12:45 | 100 | 0 |  | 2006-10-03 12:45 |  | -- | Bascom & Camden Avenues | San Jose | Santa Clara | 95130 |  |  | 2006-09-28 |  |  |  | Captured liquid SSO in storm catch basin; vactored up and reintroduced back into sanitary manhole. No water ways were affected. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-10-03 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
3822 | 81 | 1 | SanJoseCity | 2006-09-01 09:31 | 100 | 0 |  | 2006-09-01 09:31 |  | -- | 1640 Brookvale Dr x Prospect Road | San Jose | Santa Clara | 95129 |  |  | 2006-08-29 |  |  |  | No waterways were affected. SSO confined to street curb & gutter. SSO vactored and returned to sanitary system after main was cleared. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-09-01 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
3773 | 80 | 1 | SanJoseCity | 2006-08-22 13:25 | 300 | 0 |  | 2006-08-22 13:25 |  | -- | 6168 Paso Los Cerritos @ Meridian | San Jose | Santa Clara | 95120 |  |  | 2006-08-18 |  |  |  | SSO confined to street curb and gutter. No waterways were affected. Bermed/sandbagged area to prevent SSO from entering storm drain; vactored from street and put back into manhole after plug cleared. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Associate Engineer | Philip Lee | 2006-08-22 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
3753 | 79 | 1 | SanJoseCity | 2006-08-17 10:56 | 450 | 0 |  | 2006-08-17 10:56 |  | -- | 2254 Luz Ave | San Jose | Santa Clara | 95116 |  |  | 2006-08-10 |  |  |  | No waterways were affected. SSO confined to street curb and gutter. SSO vactored and returned to sanitary system after plug was cleared. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Associate Engineer | Philip Lee | 2006-08-17 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
3593 | 78 | 1 | SanJoseCity | 2006-07-03 10:31 | 100 | 0 |  | 2006-07-03 10:31 |  | -- | 1377 Vinci Park Way/Seville Way | San Jose | Santa Clara | 95131 |  |  | 2006-07-02 |  |  |  | No waterways were affected. Used HP to clear blockage; vactored up sso from sidewalk and street area and returned to sanitary syste. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-07-03 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
3556 | 76 | 1 | SanJoseCity | 2006-06-26 14:03 | 900 | 0 |  | 2006-06-26 14:03 |  | -- | 177 Gramercy | San Jose | Santa Clara | 95116 |  |  | 2006-06-24 |  |  |  | No water ways were affected. Catch basin was plugged; blockage cleared; SSO vactored from catch basin, street, curb & gutter. SSO returned to sanitary sewer main after blockage cleared. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-06-26 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
3563 | 77 | 1 | SanJoseCity | 2006-06-27 13:08 | 640 | 0 |  | 2006-06-27 13:08 |  | -- | Montelena Drive @ Florence Park Drive | San Jose | Santa Clara | 95135 |  |  | 2006-06-24 |  |  |  | No waterways were impacted. Plugged catch basin; cleared blockage; vactored up sso from catch basin, street, curb and gutter. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-06-27 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
3519 | 73 | 1 | SanJoseCity | 2006-06-20 13:29 | 400 | 0 |  | 2006-06-20 13:29 |  | -- | 2814 Joseph Av @ Angela Ct | San Jose | Santa Clara | 95124 |  |  | 2006-06-18 |  |  |  | Plug in sewer main caused cleanout at 2814 Joseph Ave. to overflow. No waterways were affected. SSO was vactored up after plug was cleared. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-06-20 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
3474 | 71 | 1 | SanJoseCity | 2006-06-09 13:17 | 120 | 0 |  | 2006-06-09 13:17 |  | -- | 2947 Murtha @ Farringdon | San Jose | Santa Clara | 95127 |  |  | 2006-06-08 |  |  |  | No waterways were affected. Vactored up SSO after blockage was cleared and returned back into manhole/sanitary system. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-06-09 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
3476 | 72 | 1 | SanJoseCity | 2006-06-09 13:19 | 130 | 0 |  | 2006-06-09 13:19 |  | -- | The Villages Parkway @ Ashley Way | San Jose | Santa Clara | 95135 |  |  | 2006-06-08 |  |  |  | No waterways affected. Vactored up SSO and returned to sanitary system after blockage cleared. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-06-09 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
3436 | 69 | 1 | SanJoseCity | 2006-05-31 09:19 | 350 | 0 |  | 2006-05-31 09:19 |  | -- | Mueller Avenue @ N. Capitol Avenue | San Jose | Santa Clara | 95127 |  |  | 2006-05-26 |  |  |  | SSO was confined to street, curb and gutter. Blockage was cleared with HP; no waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Asscoate Engineer | Philip Lee | 2006-05-31 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
3470 | 70 | 1 | SanJoseCity | 2006-06-08 12:29 | 500 | 0 |  | 2006-06-08 12:29 |  | -- | 2065 Los Gatos Almaden @ Union | San Jose | Santa Clara | 95124 |  |  | 2006-05-24 |  |  |  | This is a late submittal. SSO confined to yard behind health facility and was caused by excessive debris such as paper towels and food products. Originally thought to be solely a private matter; however, further investigation shows that a plug in the City main may have contributed to the SSO. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Associate Engineer | Philip Lee | 2006-06-08 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
3400 | 67 | 1 | SanJoseCity | 2006-05-23 20:18 | 4800 | 0 | 06-3099 | 2006-05-23 | Mike Roderick |  | BlackPool Ct @ Country Club Pkwy | San Jose | Santa Clara | 95133 |  |  | 2006-05-22 | 6:50:00 PM | 2006-05-22 | 8:10:00 PM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Senior Maint. Worker | Mike Roderick | 2006-05-23 | 408-277-5509 | mike.roderick@sanjoseca.gov, Mitchell_Barron,Lisa@sanjoseca.gov | 24HR |  |  | 4082775509 | [6 empty] | SanJoseCity
3403 | 68 | 3 | SanJoseCity | 2006-05-24 08:36 | 4800 | 0 | 06-3099 | 2006-05-24 | Mike Roderick | SanJoseCity | Black Pool Ct at Country Club Pkwy | San Jose | Santa Clara | 95133 |  |  | 2006-05-22 | 6:50:00 PM | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | No | This is a test report only (by Johnson Lam). |  | No | No | No | No | No | No | No | No | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanJoseCity | MANHOLE |  | BLOCKAGE | --Select None-- | --Select None-- |  | Test report only. | Associate Engineer | Philip Lee | 2006-05-24 | 408-277-5509 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov;mike.roderick@sanjoseca.gov | MAJOR | Mike Roderick | SanJoseCity | 408-277-5509 |  | 2000 E. Santa Clara Street | San Jose | Santa Clara | 95133 |  | SanJoseCity
3345 | 65 | 1 | SanJoseCity | 2006-05-16 11:14 | 100 | 0 |  | 2006-05-16 11:14 |  | -- | Cambrianna Drive @ Browning Avenue | San Jose | Santa Clara | 95124 |  |  | 2006-05-16 |  |  |  | Cleared sewer main with HP. Reintroduced SSO back into manhole. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-05-16 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
3347 | 66 | 1 | SanJoseCity | 2006-05-16 11:17 | 900 | 0 |  | 2006-05-16 11:17 |  | -- | Coyote Road @ Nicole Court | San Jose | Santa Clara | 95111 |  |  | 2006-05-14 |  |  |  | Sandbagged catch basin, cleared sewer main with HP and vactored up SSO. No waterways were affected. Location will be put on preventive maintenance list. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-05-16 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
3208 | 64 | 1 | SanJoseCity | 2006-04-20 11:19 | 750 | 0 |  | 2006-04-20 11:19 |  | -- | Williams Road/Opal Drive | San Jose | Santa Clara | 95117 |  |  | 2006-04-15 |  |  |  | No waterways were affected. SSO confined to street, curb & gutter. Vactored SSO and returned to manhole after plug was cleared. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-04-20 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
3059 | 63 | 1 | SanJoseCity | 2006-03-24 13:55 | 200 | 0 |  | 2006-03-24 13:55 |  | -- | D'Amico/White Road | San Jose | Santa Clara | 95148 |  |  | 2006-03-18 |  |  |  | SSO confined to street, curb & gutter and sidewalk park strip area. Used High Pressure cleaning to clear plug and returned SSO into manhole. No waterways or inlets were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-03-24 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
3032 | 62 | 1 | SanJoseCity | 2006-03-17 11:15 | 150 | 0 |  | 2006-03-17 11:15 |  | -- | 4517 Lobos Ave/Skyway | San Jose | Santa clara | 95111 |  |  | 2006-03-14 |  |  |  | No waterways or inlets were affected. Blockage cleared with HP and returned to sanitary manhole. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-03-17 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
3024 | 60 | 1 | SanJoseCity | 2006-03-17 11:09 | 100 | 0 |  | 2006-03-17 11:09 |  | -- | Ferrington/Chiltern | San Jose | Santa Clara | 95127 |  |  | 2006-03-11 |  |  |  | Cleared blockage and returned sewage into sanitary manhole. No waterways or inlets were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-03-17 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
3026 | 61 | 1 | SanJoseCity | 2006-03-17 11:12 | 100 | 0 |  | 2006-03-17 11:12 |  | -- | Checkers/McKee | San Jose | Santa Clara | 95133 |  |  | 2006-03-11 |  |  |  | Street, curb and gutter and part of sidewalk area affected by SSO. Blockage cleared and sso returned to sanitary manhole. No waterways or inlets affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-03-17 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
2955 | 58 | 1 | SanJoseCity | 2006-03-08 13:27 | 150 | 0 |  | 2006-03-08 13:27 |  | -- | 1742 Chaney Road @ Rochelle | San Jose | Santa Clara | 95124 |  |  | 2006-03-04 |  |  |  | No surface waters were affected. SSO reintroduced into manhole after main was cleared with high pressure cleaning. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-03-08 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
2957 | 59 | 1 | SanJoseCity | 2006-03-08 13:30 | 750 | 0 |  | 2006-03-08 13:30 |  | -- | S. White Road @ Story Road | San Jose | Santa Clara | 95127 |  |  | 2006-03-04 |  |  |  | No surface waterways were affected. Cleared main with high pressure cleaning and reintroduced SSO back into sanitary manhole. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-03-08 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
2892 | 57 | 1 | SanJoseCity | 2006-02-28 09:54 | 100 | 0 |  | 2006-02-28 09:54 |  | -- | Coyote Road @ Snow Drive | San Jose | Santa Clara | 95111 |  |  | 2006-02-23 |  |  |  | Used HP to clear blockage. No waterways were affected. Returned SSO to sanitary main/manhole after it was cleared. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-02-28 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
3485 | 53 | 3 | SanJoseCity | 2006-06-13 11:13 | 51000 | 40000 | 06-1076 | 2006-02-20 | Phyllis Schulz | SanJoseCity | San Tomas Expwy @ Saratoga Ave | Santa Clara | Santa Clara | 95117 |  |  | 2006-02-19 | 4:09:00 PM | [5 empty] | SUNNY WEATHER | Medium |  | SURFACE WATER IMPACT | No |  | No | No | No solid debris, santiary water slight grey film on surface. Volume of SSO revised due to discussions with the City of Santa Clara Superintendant John Peterson. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- |  | NOTE: Pictures will be sent when we receive them from Santa Clara Fire Dept. and the Santa Clara Water District. VOLUME: Approximately 51000 gallons RATE OF FLOW: 250 gallons per minute DURATION: 3.5 hours SURFACE BODY WATER IMPACTED: San Tomas Creek RESPONDING AGENCIES: • The City of Santa Clara; John Peterson, Sanitary Sewer Superintendent; 408 615-2062 • The City of Santa Clara; Greg Phillips, Fire Dept. 408 615-4933 • The City of Santa Clara; Mark Pullin, Utility Crew Supervisor; 408 615-2060 • Santa Clara Valley Water District; Dale Jacques, Assoc. Engineer 408 265-2607 X 2637 CAUSE OF SPILL: Grease in main sanitary line CLEAN UP ACTIONS: • Located and unplugged the main • Flushed the catch basin (Santa Clara Fire Department) • Vactored, vacuumed up the grease from the sanitary manhole • Built sandbag damn for containment • Pumped waste water into the sanitary main located N/S of Walsh Ave. above the creek • Removed the sandbags from the creek • Notified the Regional Water Board, OES Control # 06-1076 • Advised the Dept. of Fish and Game (No visible fish kill) High Pressure unit reported to the site to give relief to the plugged main. After the main was cleared the grease was vacuumed up from the sanitary manhole. The catch basin was washed down with clear water. Sand bags were placed in the creek; building a damn to contain the liquid wastewater. Approximately 40,000 gallons of the liquid wastewater was then pumped from the creek into the nearby sanitary main. After pumping for 3.5 hours we removed the sand bags to the concrete platform. The next day the sandbags were hauled away from the site. The original report stated the rate of flow to be 1000 gallons per minute however after looking at the reference sheet for estimating Sewer spills provided by BACWA, it was determined to be 250 gallons per minute. John Peterson of the City of Santa Clara also agreed upon this change. A meeting is being scheduled with the City of Santa Clara and the City of San Jose to determine who is responsible for the maintenance of this siphon. If it is determined that this area is the responsibility of the City of San Jose it will be put on to a routine cleaning cycle. | Maintenance Supervis | Phyllis Schulz | 2006-02-20 | 408-998-6183 | phyllis.schulz@ sanjoseca.gov, phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MAJOR | Mike Roderick | SanJoseCity | 408-277-5509 |  | 2000 E. Santa Clara Street | San Jose | Santa Clara | 95133 |  | SanJoseCity
2858 | 54 | 1 | SanJoseCity | 2006-02-22 08:59 | 750 | 0 |  | 2006-02-22 08:59 |  | -- | Ridgetree Way and Jennifer Way | San Jose | Santa Clara | 95131 |  |  | 2006-02-18 |  |  |  | No waterways/catch basins were affected. Plug was cleared and all SSO was introduced back into the manhole. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-02-22 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
2860 | 55 | 1 | SanJoseCity | 2006-02-22 09:02 | 150 | 0 |  | 2006-02-22 09:02 |  | -- | 1973 Geneva St/Jennifer Way | San Jose | Santa Clara | 95124 |  |  | 2006-02-18 |  |  |  | Minor sewage overflow, no waterways/catch basins affected. Plug cleared and sso reintroduced back into manhole. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-02-22 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
2862 | 56 | 1 | SanJoseCity | 2006-02-22 09:05 | 750 | 0 |  | 2006-02-22 09:05 |  | -- | 2776 Twin Oaks Ln/Craigwood | San Jose | Santa Clara | 95127 |  |  | 2006-02-18 |  |  |  | No waterways affected. SSO returned to manhole after plug/blockage was cleared. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-02-22 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
2833 | 52 | 1 | SanJoseCity | 2006-02-17 09:02 | 600 | 0 |  | 2006-02-17 09:02 |  | -- | Collomia Court @ Branham Lane | San Jose | Santa Clara | 95111 |  |  | 2006-02-15 |  |  |  | SSO captured in storm drain. Storm drained plugged and vactored out; then returned to sanitary main after blockage was cleared. No surface/state waterways were affected. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-02-17 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
2810 | 51 | 1 | SanJoseCity | 2006-02-14 14:57 | 100 | 0 |  | 2006-02-14 14:57 |  | -- | 7115 Wooded Lake @ Leyland Park Drive | San Jose | Santa Clara | 95120 |  |  | 2006-02-09 |  |  |  | Main located in easement in back of property on Wooded Lake. After plug was cleared, sso was vactored up and disposed of back into sanitary main. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Associate Engineer | Philip Lee | 2006-02-14 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
2439 | 50 | 1 | SanJoseCity | 2006-01-03 11:25 | 600 | 0 |  | 2006-01-03 11:25 |  | -- | 218 Checkers @ McKee | San Jose | Santa Clara | 95116 |  |  | 2005-12-27 |  |  |  | Manhole overflowed due to plug in main. SSO confined to street, curb & gutter; no waterways were affected. SSO vactored and reintroduced back into manhole after plug was cleared. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2006-01-03 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
2286 | 47 | 1 | SanJoseCity | 2005-12-19 14:44 | 100 | 0 |  | 2005-12-19 14:44 |  | -- | 1259 Park Avenue @ Martin Ave | San Jose | Santa Clara | 95126 |  |  | 2005-12-15 |  |  |  | Broken lateral resulted in SSO. SSO confined to sidewalk, curb and gutter. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | OTHER | Private Lateral | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Associate Engineer | Philip Lee | 2005-12-19 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
2288 | 48 | 1 | SanJoseCity | 2005-12-19 14:47 | 200 | 0 |  | 2005-12-19 14:47 |  | -- | Shriver Avenue @ Shriver Court | San Jose | Santa Clara | 95132 |  |  | 2005-12-13 |  |  |  | Heavy grease resulted in blockage of main. SSO confined to sidewalk curb & gutter. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-12-19 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
2237 | 46 | 1 | SanJoseCity | 2005-12-12 11:02 | 200 | 0 |  | 2005-12-12 11:02 |  | -- | Capitol Avenue @ Wilbur Avenue | San Jose | Santa Clara | 95127 |  |  | 2005-12-08 |  |  |  | Plug in main caused SSO. SSO was contained in street, curb & gutter and storm catch basin. Catch basin was vactored out after plug in main removed. No waterways were affected. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-12-12 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
2231 | 44 | 1 | SanJoseCity | 2005-12-07 13:07 | 300 | 0 |  | 2005-12-07 13:07 |  | -- | Landess Avenue @ Ashwood Lane | San Jose | Santa Clara | 95132 |  |  | 2005-12-05 |  |  |  | Plugged sewer main caused SSO around manhole. No waterways were affected. Plug cleared and sewage reintroduced into manhole. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Associate Engineer | Philip Lee | 2005-12-07 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
2233 | 45 | 1 | SanJoseCity | 2005-12-07 13:10 | 900 | 0 |  | 2005-12-07 13:10 |  | -- | Oxbow Court and Rosswood Avenue | San Jose | Santa Clara | 95124 |  |  | 2005-12-02 |  |  |  | Plugged main caused SSO in court. Plug cleared and SSO washed back into manhole. Sewer line segment will be put on preventive maintenance cleaning cycle. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Associate Engineer | Philip Lee | 2005-12-07 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
2189 | 43 | 1 | SanJoseCity | 2005-11-29 14:16 | 200 | 0 |  | 2005-11-29 14:16 |  | -- | 252 Mahoney Avenue @ East Hills drive | San Jose | Santa Clara | 95127 |  |  | 2005-11-28 |  |  |  | SSO confined to street, curb & gutter. Cleared plug (will return to power rod and remove roots) and reintroduce SSO back into manhole. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Associate Engineer | Philip Lee | 2005-11-29 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
2116 | 42 | 1 | SanJoseCity | 2005-11-15 14:34 | 100 | 0 |  | 2005-11-15 14:34 |  | -- | 6920 Westmoor Way @ Long Fellow Drive | San Jose | Santa Clara | 95129 |  |  | 2005-11-11 |  |  |  | SSO confined to street, curb and gutter, no waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Associate Engineer | Philip Lee | 2005-11-15 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
2016 | 40 | 1 | SanJoseCity | 2005-10-24 12:46 | 300 | 0 |  | 2005-10-24 12:46 |  | -- | 2158 Camden Avenue @ S. Bascom Avenue | San Jose | Santa Clara | 95124 |  |  | 2005-10-20 |  |  |  | SSO was confined to street curb and gutter. No waterways were affected. Main was cleared and sewage was reintroduced back into manhole. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-10-24 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
2018 | 41 | 1 | SanJoseCity | 2005-10-24 12:50 | 200 | 0 |  | 2005-10-24 12:50 |  | -- | 622 Gaundabert Lane @ Chynoweth Avenue | San Jose | Santa Clara | 95136 |  |  | 2005-10-20 |  |  |  | SSO was from a private cleanout. No water ways were affected. SSO was cleaned up from front yard of residence. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | CLEAN OUT |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Associate Engineer | Philip Lee | 2005-10-24 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
1905 | 39 | 1 | SanJoseCity | 2005-10-03 09:40 | 100 | 0 |  | 2005-10-03 09:40 |  | -- | Westmont Avenue / Quito Road | San Jose | Santa Clara | 95130 |  |  | 2005-09-29 |  |  |  | SSO confined to street curb and gutter. Construction pump failed/plugged, resulting in SSO. No waterways or catch basins were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Associate Engineer | Philip Lee | 2005-10-03 | (408) 277-3058 | phil.lee@sanjoseca.gov, jim.helmer@sanjoseca.gov | MINOR
1738 | 38 | 1 | SanJoseCity | 2005-08-29 14:49 | 150 | 0 |  | 2005-08-29 14:49 |  | -- | 19027 Greystone Lane x Briana Court | San Jose | Santa Clara | 95120 |  |  | 2005-08-27 |  |  |  | SSO contained on private property in a dirt area. No homes were affected and no bodies of water were affected. Plugged main was cleared and sso was reintroduced back into manhole. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-08-29 | (408) 277-3058 | phil.lee@sanjoseca.gov, | MINOR
1679 | 37 | 1 | SanJoseCity | 2005-08-08 14:05 | 500 | 0 |  | 2005-08-08 14:05 |  | -- | Penitencia Creek Road @ Toyon Avenue | San Jose | Santa Clara | 95133 |  |  | 2005-08-04 |  |  |  | No waterways were affected. SSO confined to street, curb and gutter. HP cleared main and SSO was reintroduced back into manhole. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-08-08 | (408) 277-3058 | phil.lee@sanjoseca.gov, | MINOR
1672 | 36 | 1 | SanJoseCity | 2005-08-03 11:56 | 1900 | 1900 | not available | 2005-08-03 | Lisa Mitchell-Barron |  | 1620 Whitton Ave c/s King Rd NOTE: Waterways not affected. Private basement flooded | San Jose | Santa Clara | 95116 |  |  | 2005-08-02 | 12:24:00 P | 2005-08-02 | 2:00:00 PM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Acting Maintenance S | Lisa Mitchell-Barron | 2005-08-03 | 408-277-5509 | Lisa.Mitchell_Barron@sanjoseca.gov, | 24HR |  |  | 408-277-5509 | [6 empty] | SanJoseCity
1661 | 35 | 1 | SanJoseCity | 2005-07-29 14:36 | 300 | 0 |  | 2005-07-29 14:36 |  | -- | Bolero Drive @ Continental Drive | San Jose | Santa Clara | 95133 |  |  | 2005-07-28 |  |  |  | No water ways affected. SSO was confined to street, curb and gutter. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-07-29 | (408) 277-3058 | phil.lee@sanjoseca.gov, | MINOR
1631 | 33 | 1 | SanJoseCity | 2005-07-20 14:50 | 600 | 0 |  | 2005-07-20 14:50 |  | -- | 2047 Willester Av @ Union Av | San Jose | Santa Clara | 95124 |  |  | 2005-07-18 |  |  |  | No waterways affected. SSO contained in street, curb and gutter and reintroduced into manhole after blockage cleared. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE | Environmental Services is presently investigating cause; however, preliminary findings indicating possible illegal dumping of liquid toilet deodorant. | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-07-20 | (408) 277-3058 | phil.lee@sanjoseca.gov, | MINOR
1598 | 32 | 2 | SanJoseCity | 2005-07-06 14:02 | 2500 | 2500 | 05-3872 | 2005-06-28 | Pete Cruz | SanJoseCity | Remillard Court @ Story Road into Coyote Creek | San Jose | Santa Clara | 95122 |  |  | 2005-06-28 | 3:30:00 PM | [5 empty] | SUNNY WEATHER | Low | Coyote Creek | SURFACE WATER IMPACT | No |  | No | Yes | Blue water caused by liquid toilet deodorant. Fish in creek appeared not to be affected. |  | Yes | Yes | No | No | No | Yes | No | No | No | 2005-07-31 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SanJoseCity | OTHER | Environmental Services is presently investigating cause; however, preliminary findings indicating possible illegal dumping of liquid toilet deodorant. | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Maintenance Supervis | Lisa Barron | 2005-06-29 | 408-277-5509 | lisa.mitchellbarron@sanjoseca.gov, | MAJOR | Lisa Barron | City of San Jose | (408) 277-5509 |  | 1404 Mabury Road | San Jose | Santa Clara | 95133 |  | SanJoseCity
1576 | 31 | 1 | SanJoseCity | 2005-06-29 09:54 | 300 | 0 |  | 2005-06-29 09:54 |  | -- | 845 Clearview Dr. @ Bowcheff Dr. | San Jose | Santa Clara | 95133 |  |  | 2005-06-24 |  |  |  | Rags and grease were recovered from main. SSO confined to street curb and gutter. No water ways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-06-29 | (408) 277-3058 | phil.lee@sanjoseca.gov, | MINOR
1477 | 30 | 1 | SanJoseCity | 2005-06-02 09:55 | 500 | 0 |  | 2005-06-02 09:55 |  | -- | 1837 Little Orchard | San Jose | Santa Clara | 95125 |  |  | 2005-06-01 |  |  |  | SSO confined to street curb, gutter and driveway. SSO reintroduced back into manhole after main cleared. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-06-02 | (408) 277-3058 | phil.lee@sanjoseca.gov, | MINOR
1471 | 27 | 1 | SanJoseCity | 2005-06-01 13:52 | 350 | 0 |  | 2005-06-01 13:52 |  | -- | Peacock Gap @ Crothers Road | San Jose | Santa Clara | 95127 |  |  | 2005-05-31 |  |  |  | No waterways were affected. 2x4 was removed from manhole downstream. This contributed to blockage. SSO was vactored and reintroduced back into manhole after blockage removed. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Associate Engineer | Philip Lee | 2005-06-01 | (408) 277-3058 | phil.lee@sanjoseca.gov, | MINOR
1473 | 28 | 1 | SanJoseCity | 2005-06-02 09:47 | 100 | 0 |  | 2005-06-02 09:47 |  | -- | Gaton Drive @ Hamilton Avenue | San Jose | Santa Clara | 95125 |  |  | 2005-05-31 |  |  |  | SSO contained in street curb and gutter. Main cleared and SSO reintroduced back into manhole. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-06-02 | (408) 277-3058 | phil.lee@sanjoseca.gov, | MINOR
1475 | 29 | 1 | SanJoseCity | 2005-06-02 09:51 | 125 | 0 |  | 2005-06-02 09:51 |  | -- | 1512 English Drive @ Lyle Dr | San Jose | Santa Clara | 95129 |  |  | 2005-05-31 |  |  |  | SSO confined to street curb and gutter. SSO reintroduced into manhole after main was cleared with HP. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-06-02 | (408) 277-3058 | phil.lee@sanjoseca.gov, | MINOR
1457 | 26 | 1 | SanJoseCity | 2005-05-26 09:58 | 100 | 0 |  | 2005-05-26 09:58 |  | -- | 15360 Union Avenue @ Rosswood | San Jose | Santa Clara | 95124 |  |  | 2005-05-25 |  |  |  | Vactor truck vaccuumed up sewage and debris. SSO liquid was reintroduced back into manhole after plug cleared. No waterways or catch basins were affected. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-05-26 | (408) 277-3058 | phil.lee@sanjoseca.gov, | MINOR
1451 | 25 | 1 | SanJoseCity | 2005-05-24 13:19 | 900 | 0 |  | 2005-05-24 13:19 |  | -- | 1628 Hostetter Road | San Jose | Santa Clara | 95131 |  |  | 2005-05-23 |  |  |  | SSO caused by a broken lateral. SSO was contained within the parking strip and street curb and gutter. SSO vactored up and returned to nearest manhole. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | OTHER | Broken Lateral | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Associate Engineer | Philip Lee | 2005-05-24 | (408) 277-3058 | phil.lee@sanjoseca.gov, | MINOR
1439 | 24 | 1 | SanJoseCity | 2005-05-20 15:09 | 500 | 0 |  | 2005-05-20 15:09 |  | -- | 1835 Anne Way @ Leigh Avenue | San Jose | Santa Clara | 95124 |  |  | 2005-05-18 |  |  |  | Sewage contained in catch basin and vactored out after plug removed from main line. No waterways were affected. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-05-20 | (408) 277-3058 | phil.lee@sanjoseca.gov, | MINOR
1357 | 23 | 1 | SanJoseCity | 2005-05-04 10:08 | 600 | 0 |  | 2005-05-04 10:08 |  | -- | 7121 Echo Loop @ Echo Valley | San Jose | Santa Clara | 95120 |  |  | 2005-05-03 |  |  |  | HP cleared blockage and SSO reintroduced back into manhole. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-05-04 | (408) 277-3058 | phil.lee@sanjoseca.gov, | MINOR
1355 | 22 | 1 | SanJoseCity | 2005-05-04 10:02 | 450 | 0 |  | 2005-05-04 10:02 |  | -- | 908 College Drive | San Jose | Santa Clara | 95128 |  |  | 2005-04-25 |  |  |  | Used HP to clear blockage; SSO contained in street curb and gutter and reintroduced back into manhole. No waterways were affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-05-04 | (408) 277-3058 | phil.lee@sanjoseca.gov, | MINOR
1309 | 20 | 1 | SanJoseCity | 2005-04-22 09:53 | 100 | 0 |  | 2005-04-22 09:53 |  | -- | Riverrun Drive and Capitol Avenue | San Jose | Santa Clara | 95127 |  |  | 2005-04-19 |  |  |  | SSO contained in street, curb and gutter. Plug removed and sewage reintroduced back into manhole. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-04-22 | (408) 277-3058 | phil.lee@sanjoseca.gov, | MINOR
1311 | 21 | 1 | SanJoseCity | 2005-04-22 09:57 | 275 | 0 |  | 2005-04-22 09:57 |  | -- | Perie Lane @ Dorel Drive | San Jose | Santa Clara | 95132 |  |  | 2005-04-19 |  |  |  | SSO cleared with backhoe. Sewer main will be videoed to assess seriousness of root invasion. Preventive maintenance will then be determined. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Associate Engineer | Philip Lee | 2005-04-22 | (408) 277-3058 | phil.lee@sanjoseca.gov, | MINOR
1233 | 19 | 1 | SanJoseCity | 2005-03-30 14:08 | 100 | 0 |  | 2005-03-30 14:08 |  | -- | Branham Lane @ Lawson Court | San Jose | Santa Clara | 95118 |  |  | 2005-03-28 |  |  |  | Plugged main was HPed; sewer water was washed down and reintroduced back into manhole. No waterway was affected. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-03-30 | (408) 277-3058 | phil.lee@sanjoseca.gov, | MINOR
1204 | 18 | 1 | SanJoseCity | 2005-03-18 10:57 | 400 | 0 |  | 2005-03-18 10:57 |  | -- | Vista Park Dr @ Capitol Expressway | San Jose | Santa Clara | 95136 |  |  | 2005-03-16 |  |  |  | SSO was contained in street curb and gutter. After blockage was cleared, SSO was reintroduced back into manhole. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-03-18 | (408) 277-3058 | phil.lee@sanjoseca.gov, | MINOR
1169 | 17 | 1 | SanJoseCity | 2005-03-11 14:36 | 120 | 0 |  | 2005-03-11 14:36 |  | -- | Yerba Buena Road @ Hurstglen Way | San Jose | Santa Clara | 95121 |  |  | 2005-03-09 |  |  |  | Blockage was cleared with an HP; sewage then reintroduced back into manhole. Sewage never reached catchbasin or any other waterway. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-03-11 | (408) 277-3058 | phil.lee@sanjoseca.gov, | MINOR
1018 | 16 | 1 | SanJoseCity | 2005-02-11 11:19 | 200 | 0 |  | 2005-02-11 11:19 |  | -- | Montgomery Place and Gerdts Drive | San Jose | Santa Clara | 95135 |  |  | 2005-02-10 |  |  |  | After blockage was cleared by HP; sewage and cleanup water was introduced back into manhole. SSO never entered storm drain or any other waterways. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-02-11 | 408-277-3058 | phil.lee@sanjoseca.gov, | MINOR
941 | 15 | 1 | SanJoseCity | 2005-02-01 11:38 | 500 | 0 |  | 2005-02-01 11:38 |  | -- | 2411 Greengate Dr @ Capitol Ave | San Jose | Santa Clara | 95132 |  |  | 2005-01-31 |  |  |  | High pressured main to clear plug. Flushed street curb and gutter with hydrant water and reintroduced back into manhole. SSO never entered catch basin or waterways. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-02-01 | (408) 277-3058 | phil.lee@sanjoseca.gov | MINOR
895 | 14 | 1 | SanJoseCity | 2005-01-21 14:46 | 100 | 0 |  | 2005-01-21 14:46 |  | -- | 2824 Garden Avenue @ Lewis Road | San Jose | Santa Clara | 95111 |  |  | 2005-01-20 |  |  |  | Cleared blockage with HP and reintroduced overflow back into manhole. Sewage was confined to street curb and gutter and never reached the storm catch basins. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-01-21 | (408) 277-3058 | phil.lee@sanjoseca.gov | MINOR
870 | 13 | 1 | SanJoseCity | 2005-01-18 15:04 | 400 | 0 |  | 2005-01-18 15:04 |  | -- | Sabal Drive @ Leisure Court | San Jose | Santa Clara | 95132 |  |  | 2005-01-12 |  |  |  | SSO confined to street curb and gutter. Sewage was reintroduced back into manhole after blockage was cleared. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-01-18 | (408) 277-3058 | phil.lee@sanjoseca.gov | MINOR
858 | 11 | 2 | SanJoseCity | 2005-01-14 14:31 | 2820 | 0 | 05-0361 | 2005-01-13 | Ernie Espitia | SanJoseCity | Squeri Drive @ Cedar Flat Court Babb Creek | San Jose | Santa Clara | 95127 |  |  | 2005-01-11 | 5:00:00 PM | [5 empty] | SUNNY WEATHER | Low | Babb Creek | SURFACE WATER IMPACT | No |  | No | Yes | Murky and odorous at entry into creek. Rapid creek flow cleared water approximately 800 feet downstream. |  | Yes | Yes | No | No | No | No | No | Yes | No | 2005-01-28 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SanJoseCity | MANHOLE | Possible break in sanitary sewer main. Will be verified through scheduled video. | INFRASTRUCTURE FAILURE | --Select None-- | BREAKAGE OF COLLECTION SYSTEM | Possible break in sanitary sewer main. Will be verified through scheduled video. | DOT received original complaint of sewer odor at 17:00 on 1/11/2005; however, initial investigation did not disclose location of overflow. SSO location was discovered under marshy area at 12:00 on 1/13/2005. SSO was contained at 16:00 on 1/13/2005. DOT feels that there is probably a break in the main. A video has been scheduled to verify this. | Maintenance Supervi | Ernie Espitia | 2005-01-14 | (408) 277-5509 | phil.lee@sanjoseca.gov | MAJOR | Ernie Espitia | City of San Jose, DOT | (408) 277-5509 |  | 1404 Mabury Road | San Jose | Santa Clara | 95133 |  | SanJoseCity
831 | 10 | 1 | SanJoseCity | 2005-01-12 14:44 | 100 | 0 |  | 2005-01-12 14:44 |  | -- | 306 Ryegate Court @ Educational Park Drive | San Jose | Santa Clara | 95133 |  |  | 2005-01-10 |  |  |  | Cleared blockage, washed down area around manhole and reintroduced all sewage and clean water back into manhole. Sewage was contained in street curb and gutter. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-01-12 | (408) 277-3058 | phil.lee@sanjoseca.gov | MINOR
868 | 12 | 1 | SanJoseCity | 2005-01-18 15:01 | 100 | 0 |  | 2005-01-18 15:01 |  | -- | 4587 Student Lane @ Castro Drive | San Jose | Santa Clara | 95130 |  |  | 2005-01-10 |  |  |  | Sewage contained in street curb and gutter. Sewage reintroduced back into manhole after plug cleared. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-01-18 | (408) 277-3058 | phil.lee@sanjoseca.gov | MINOR
798 | 9 | 1 | SanJoseCity | 2005-01-10 10:43 | 300 | 0 |  | 2005-01-10 10:43 |  | -- | 2667 Sand Point Drive @ Quimby Road | San Jose | Santa Clara | 95148 |  |  | 2005-01-06 |  |  |  | Cleared main with HP. All sewage contained in street curb and gutter. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2005-01-10 | (408) 277-3058 | phil.lee@sanjoseca.gov | MINOR
754 | 8 | 1 | SanJoseCity | 2005-01-04 15:26 | 3000 | 0 |  | 2005-01-04 15:26 |  | -- | Winchester Blvd @ Williams Road | San Jose | Santa Clara | 95117 |  |  | 2004-12-30 |  |  |  | All sewage was captured in the storm drain and vactored out. Cleaned Curb and gutter after main was cleared. Sewage never reached any waterways. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Associate Engineer | Philip Lee | 2005-01-04 | (408) 277-3058 | phil.lee@sanjoseca.gov | MINOR
752 | 7 | 1 | SanJoseCity | 2005-01-04 15:25 | 100 | 0 |  | 2005-01-04 15:25 |  | -- | Simpson Way @ Dry Creek Road | San Jose | Santa Clara | 95125 |  |  | 2004-12-28 |  |  |  | Sewage was contained in curb and gutter and reintroduced back into manhole after main was cleared. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Associate Engineer | Philip Lee | 2005-01-04 | (408)277-3058 | phil.lee@sanjoseca.gov | MINOR
555 | 3 | 1 | SanJoseCity | 2004-12-16 10:22 | 100 | 0 |  | 2004-12-16 10:22 |  | -- | 2921 Castleton Drive/S. White Road | San Jose | Santa Clara | 95148 |  |  | 2004-12-15 |  |  |  | Sewage contained in street curb and gutter and reintroduced back into manhole after blockage was cleared. Sewage never entered storm catch basin. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2004-12-16 | (408) 277-3058 |  | MINOR
553 | 2 | 1 | SanJoseCity | 2004-12-16 10:12 | 100 | 0 |  | 2004-12-16 10:13 |  | -- | 1733 Oldtree Court | San Jose | Santa Clara | 95131 |  |  | 2004-12-14 |  |  |  | Sewage was contained in street curb and gutter and introduced back into manhole after blockage was cleared. Sewage never reached waterways. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2004-12-16 | (408) 277-3058 |  | MINOR
543 | 1 | 1 | SanJoseCity | 2004-12-15 08:48 | 200 | 0 |  | 2004-12-15 08:48 |  | -- | 3084 Quinto Way @ Foxworthy Ave | San Jose | Santa Clara | 95124 |  |  | 2004-12-11 |  |  |  | Spill was contained in the curb and gutter. It was then vactored up and dumped back into sanitary main after the main was cleared. Sewage never reached the storm catch basins. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2004-12-15 | (408) 277-3058 |  | MINOR
583 | 4 | 1 | SanJoseCity | 2004-12-17 13:57 | 25 | 0 |  | 2004-12-17 13:57 |  | -- | Lawrence Expressway @ Lassen Avenue | San Jose | Santa Clara | 95129 |  |  | 2004-12-09 |  |  |  | Cleared main with HP and flushed sewage back into manhole. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanJoseCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Associate Engineer | Philip Lee | 2004-12-17 | (408) 277-3058 | phil.lee@sanjoseca.gov | MINOR
4333 | 5 | 1 | SanLeandro | 2006-12-15 11:09 | 750 | 0 |  | 2006-12-15 11:09 |  | -- | 3000 Davis St. | San | Leandro | 94002 |  |  | 2006-12-12 |  |  |  | Operator error, valve left open. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | INFRASTRUCTURE FAILURE | -- Select One -- |  | holding basin |  | WPC Manager | Dean Wilson | 2006-12-14 | 510-577-3434
3917 | 4 | 1 | SanLeandro | 2006-09-25 08:42 | 200 | 0 |  | 2006-09-25 08:42 |  | -- | 14488 Wicks Blvd | San Leandro | Alameda | 94577 |  |  | 2006-09-25 |  |  |  | The Coka Cola plant that is connected upstream of the sso had a valve failure on their water treatment system and were pumping out the system to repair the valve. So they were discharging higher than normal volume for a fairly sustained period. This matches up with the LS SCADA data and is certainly a contributor to the surcharge condition on the gravity line.the pump station pumped over capacity of what the gravity line can handle due to the longer than normal duration of discharge coming into the lift station. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanLeandro | MANHOLE |  | FLOW CAPACITY DEFICIENCY | --Select None-- |  |  |  | St Maint Wkr III | Rick Orta | 2006-09-25 | 510-577-6058 | rorta@ci.san-leandro.ca.us, dwilson@ci.san-leandro.ca.us | MINOR
2692 | 3 | 2 | SanLeandro | 2006-01-27 13:25 | 6000 | 3000 | 06-0593 | 2006-01-26 | Rick Orta | SanLeandro | 1201 Sadelin Ave | San Leandro | Alameda | 94577 |  |  | 2006-01-26 | 7:30:00 AM | [5 empty] | SUNNY WEATHER | Low | San Leandro Creek | STORM DRAIN | No |  | No | No | Could not visualy inspect recieving water but water from storm drain was clear, odorless and without solids |  | Yes | Yes | Yes | No | No | No | No | Yes | No | 2006-01-30 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanLeandro | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- |  | SSO occured aproximatley six miles east of S.F Bay. | Water Pollution Cont | Dean Wilson | 2006-01-26 | 510-577-3434 | rorta@ci.san-leandro.ca.us, dwilson@ci.san-leandro.ca.us | MAJOR | Rick Orta | City Of San Leandro | 510-577-3434 |  | 3000 Davis St | San Leandro | Alameda | 94577 |  | SanLeandro
2670 | 2 | 1 | SanLeandro | 2006-01-24 07:38 | 600 | 0 |  | 2006-01-24 07:38 |  | -- | 48 & 56 Harlan St Pipe segment Upstream M/H 108+10 to Downstream M/H 108+09 | San Leandro | Alameda | 94577 |  |  | 2006-01-18 |  |  |  | Main line failure 2' east of M/H 108+09 causing two basements to overflow 300 gal each we were able to hydro jet main line enough to relieve the blokage. The 600 gal discharge was returned to the system.We have scheduled an emergency point repair wich will start on 1/20/2006 Friday morning. The contractor will repair the collapse as well as replace M/H 108+09 & M/H 108+10 | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanLeandro | OTHER | two residents basements | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Collections Lead | Rick Orta | 2006-01-24 | 510-577-6058 | rorta@ci.san-leandro.ca.us, dwilson@ci.san-leandro.ca.us | MINOR
930 | 1 | 1 | SanLeandro | 2005-01-31 11:51 | 300 | 0 |  | 2005-01-31 11:51 |  | -- | 2960 MERCED ST | San Leandro | Alameda | 94577 |  |  | 2005-01-31 |  |  |  | Cause af blockage due to bad offset in pipe. Pipe slated for point repair in 2004/05 Fiscal Year Merced lift station Project. Area incident ocured has been washed down and deoderized. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanLeandro | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Collection Lead | RICK ORTA | 2005-01-31 | 510-577-5068 | rorta@ci.san-leandro.ca.us | MINOR
5124 | 47 | 1 | SanMateo | 2007-04-23 | 1375 | 1500 | 07-2479 | 2007-04-23 | eric morkve | SanMateo | Barriolhet&Edgewood | San Mateo | San Mateo | 94403 |  |  | 2007-04-21 | 0.39583 | [6 empty] | Medium |  | STORM DRAIN | Yes |  | No | Yes | contained in storm drains |  | Yes | Yes | Yes |  |  | Yes | No |  |  |  | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | ROOTS | -- Select One -- |  | sanitary over flow | lead | walt dabney | 2007-04-23 | 650 522-7367
5016 | 46 | 1 | SanMateo | 2007-03-28 | 1300 | 0 | 07-1964 | 2007-03-28 | walt dabney | SanMateo | 1130 yew street | san mateo | san mateo | 94403 |  |  | 2007-03-26 | 0.38889 | [6 empty] | Medium |  | STORM DRAIN | Yes |  | Yes | No | yes |  | Yes | Yes | Yes |  |  | No | No |  |  | 2007-03-26 | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | ANIMAL CARCASS | -- Select One -- |  | sanitary overflow | lead | walt dabney | 2007-03-28 | 650-522-7367
4937 | 45 | 1 | SanMateo | 2007-03-15 13:22 | 125 | 0 |  | 2007-03-15 13:22 |  | -- | Ocidental/Clark | San Mateo | S M | 94403 |  |  | 2007-03-15 | [9 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Lead Worker | Steve Camilleri | 2007-03-15 | 650-522-7350
4933 | 44 | 1 | SanMateo | 2007-03-15 13:16 | 300 | 0 |  | 2007-03-15 13:16 |  | -- | Tulane ct/Tulane | San Mateo | SanMateo | 94403 |  |  | 2007-03-15 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Lead worker | Steve Camilleri | 2007-03-15 | 650-522-7350
4793 | 43 | 1 | SanMateo | 2007-02-22 11:15 | 500 | 0 |  | 2007-02-22 11:15 |  | -- | 31st&alameda | san mateo | san mateo | 94403 |  |  | 2007-02-22 |  |  |  | sanitary overflow | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | lead | walt dabney | 2007-02-22 | 650 522-7367
4791 | 42 | 1 | SanMateo | 2007-02-22 11:12 | 500 | 0 |  | 2007-02-22 11:12 |  | -- | 31st&alameda | san mateo | san mateo | 94403 |  |  | 2007-02-22 |  |  |  | sanitary overflow | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | lead | walt dabney | 2007-02-22 | 650 522-7367
3930 | 40 | 1 | SanMateo | 2006-09-26 13:27 | 875 | 0 |  | 2006-09-26 13:27 |  | -- | 2019 Parrot | san mateo | san mateo | 04403 |  |  | 2006-09-26 |  |  |  | sanitary overflow | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanMateo | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | lead | walt dabney | 2006-09-26 | 650-5227367 | bob correa@ci.sanmateo.ca.us, | MINOR
4743 | 41 | 1 | SanMateo | 2007-02-13 10:25 | 500 | 0 |  | 2007-02-13 10:25 |  | -- | 228 24th ave | san mateo | san mateo | 94403 |  |  | 2006-09-08 |  |  |  | sanitary overflow | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | supervisor | walt dabney | 2007-02-13 | 650 522 7367
3827 | 38 | 1 | SanMateo | 2006-09-05 11:04 | 500 | 0 |  | 2006-09-05 11:04 |  | -- | 205 west 39th ave | san mateo | san mateo | 94403 |  |  | 2006-09-05 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanMateo | OTHER | storm drain | INFRASTRUCTURE FAILURE | VANDALISM |  |  |  | lead | walt dabney | 2006-09-05 | 650 522 7367 | karmendy@ci.sanmateo.ca.us, | MINOR
3829 | 39 | 1 | SanMateo | 2006-09-05 11:19 | 450 | 0 |  | 2006-09-05 11:19 |  | -- | 221north el camino real | san mateo | san mateo | 94403 |  |  | 2006-09-05 |  |  |  | sanitary overflow | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanMateo | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | lead | walt dabney | 2006-09-05 | 650 522-7367 | bcorrea@cityofsanmateo.org, | MINOR
3756 | 37 | 2 | SanMateo | 2006-08-18 14:58 | 8250 | 6000 | 06-4941 | 2006-08-18 | park dept | SanMateo | fathom dr&mariners island | san mateo | san mateo | 94403 |  |  | 2006-08-18 | 10:00:00 A | [5 empty] | SUNNY WEATHER | Low |  | CAPTURED IN STORM DRAIN | Yes | posted on lagoon | No | Yes | No impact of flow into lagoon |  | Yes | Yes | Yes | No | No | Yes | No | Yes | No | 2006-08-24 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanMateo | MANHOLE |  | INFRASTRUCTURE FAILURE | --Select None-- | LEAKS OF COLLECTION SYSTEM | air relief valve | air relief valve failure | lead | steve camilleri | 2006-08-18 | 650 823-8325 | bcorrea@cityofsanmateo.org | MAJOR | Bob Correa | SanMateo | 650-522-7354 |  | 1949 Pacific Blvd | San Mateo | San Mateo | 94403 | CITY OF SAN MATEO | PUBLIC WORKS | 650-522-7354 |  | 1949 PACIFIC BLVD | SAN MATEO | SAN MATEO | 94403
3055 | 36 | 1 | SanMateo | 2006-03-23 16:42 | 650 | 0 |  | 2006-03-23 16:42 |  | -- | 72 Oak Valley | San Mateo | San Mateo | 94402 |  |  | 2006-03-22 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanMateo | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | secretary | Sandy Russell | 2006-03-23 | 650.522.7347 | srussell@cityofsanmateo | MINOR
2951 | 35 | 1 | SanMateo | 2006-03-08 10:06 | 1800 | 900 | 06-1425 | 2006-03-08 | allenda | SanMateo | 2051 south norfolk | san mateo | san mateo | 94403 |  |  | 2006-03-06 | 10:25:00 A | [5 empty] | RAINY WEATHER | Medium |  | STORM DRAIN | No |  | No | No | 19th channal booms |  | Yes | Yes | Yes | No | No | Yes | Yes | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanMateo | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES | LEAKS OF COLLECTION SYSTEM |  | sanitary overflow | lead | walt dabney | 2006-03-08 | 650 522-7367 | karmendy@ci.sanmateo.ca.us, | MAJOR | Bob Correa | SanMateo | 650-522-7354 |  | 1949 Pacific Blvd | San Mateo | San Mateo | 94403 | CITY OF SAN MATEO | PUBLIC WORKS | 650-522-7354 |  | 1949 PACIFIC BLVD | SAN MATEO | SAN MATEO | 94403
2830 | 33 | 2 | SanMateo | 2006-02-16 15:49 | 305 | 0 |  | 2006-02-16 15:49 |  | -- | Curtiss Street and East 38th Ave | SanMateo | SanMateo | 94403 |  |  | 2006-01-09 |  |  |  | Please delete #'s 2824 & #2828 - incorrect date on both. Correct incident date is 1-9-2006. Thank You. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanMateo | MANHOLE |  | CAUSE UNKNOWN | --Select None-- |  |  |  | PW Supervisor | Bob Correa | 2006-02-16 | (650) 522-7354 | bcorrea@cityofsanmateo.org | MINOR
2475 | 32 | 1 | SanMateo | 2006-01-04 11:24 | 81000 | 0 | 06-0123 | 2006-01-04 | walt dabney | SanMateo | 2250 south delaware | san mateo | san mateo | 94403 |  |  | 2006-01-03 | 11:00:00 A | [5 empty] | RAINY WEATHER | High |  | STORM DRAIN | No |  | No | No | inspected creek |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanMateo | MANHOLE |  | FLOW CAPACITY DEFICIENCY | --Select None-- | --Select None-- |  | sanitary overflow | lead | WALT DABNEY | 2006-01-04 | 522-7367 | karmendy@ci.sanmateo.ca.us, | MAJOR | Bob Correa | SanMateo | 650-522-7354 |  | 1949 Pacific Blvd | San Mateo | San Mateo | 94403 | CITY OF SAN MATEO | PUBLIC WORKS | 650-522-7354 |  | 1949 PACIFIC BLVD | SAN MATEO | SAN MATEO | 94403
2405 | 24 | 1 | SanMateo | 2006-01-01 10:21 | 40500 | 0 | 06-008 | 2006-01-01 | city of san mateo | SanMateo | 2057 south norfolk | san mateo | san mateo | 94403 |  |  | 2005-12-31 | 3:00:00 AM | [5 empty] | RAINY WEATHER | High |  | STORM DRAIN | No |  | Yes | No | inspected creek |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanMateo | MANHOLE |  | FLOW CAPACITY DEFICIENCY | --Select None-- | --Select None-- |  | sanitary overflow | lead | walt dabney | 2006-01-01 | 522-7367 | karmendy@ci.sanmateo.ca.us, | MAJOR | Bob Correa | SanMateo | 650-522-7354 |  | 1949 Pacific Blvd | San Mateo | San Mateo | 94403 | CITY OF SAN MATEO | PUBLIC WORKS | 650-522-7354 |  | 1949 PACIFIC BLVD | SAN MATEO | SAN MATEO | 94403
2406 | 25 | 1 | SanMateo | 2006-01-01 10:28 | 35000 | 0 | 06-008 | 2006-01-01 | city of san mateo | SanMateo | 2051 south norflk | san mateo | san mateo | 94403 |  |  | 2005-12-31 | 3:00:00 AM | [5 empty] | RAINY WEATHER | High |  | STORM DRAIN | No |  | No | No | inspect creek |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanMateo | MANHOLE |  | CAUSE UNKNOWN | --Select None-- | --Select None-- |  | sanitary overflow | lead | walt dabney | 2006-01-01 | 522-7367 | karmendy@ci.sanmateo.ca.us, | MAJOR | Bob Correa | SanMateo | 650-522-7354 |  | 1949 Pacific Blvd | San Mateo | San Mateo | 94403 | CITY OF SAN MATEO | PUBLIC WORKS | 650-522-7354 |  | 1949 PACIFIC BLVD | SAN MATEO | SAN MATEO | 94403
2407 | 26 | 1 | SanMateo | 2006-01-01 10:36 | 9000 | 0 | 06-008 | 2006-01-01 | city of san mateo | SanMateo | 228 west 24th | san mateo | san mateo | 94403 |  |  | 2005-12-31 | 2:00:00 AM | [5 empty] | RAINY WEATHER | Medium |  | STORM DRAIN | No |  | No | No | inspected storm drains |  | Yes | Yes | No | No | No | Yes | Yes | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanMateo | MANHOLE |  | CAUSE UNKNOWN | --Select None-- | --Select None-- |  | sanitary overflow | lead | walt dabney | 2006-01-01 | 522-7367 | karmendy@ci.sanmateo.ca.us, | MAJOR | Bob Correa | SanMateo | 650-522-7354 |  | 1949 Pacific Blvd | San Mateo | San Mateo | 94403 | CITY OF SAN MATEO | PUBLIC WORKS | 650-522-7354 |  | 1949 PACIFIC BLVD | SAN MATEO | SAN MATEO | 94403
2408 | 27 | 1 | SanMateo | 2006-01-01 10:42 | 18000 | 0 | 06-008 | 2006-01-01 | city of san mateo | SanMateo | #5 barroilhet | san mateo | san mateo | 94403 |  |  | 2005-12-31 | 3:00:00 AM | [5 empty] | RAINY WEATHER | High |  | STORM DRAIN | No |  | No | No | storm drains inspected |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanMateo | MANHOLE |  | BYPASS | --Select None-- | --Select None-- |  | sanitary overflow | lead | WALT DABNEY | 2006-01-01 | 522-7367 | karmendy@ci.sanmateo.ca.us, | MAJOR | Bob Correa | SanMateo | 650-522-7354 |  | 1949 Pacific Blvd | San Mateo | San Mateo | 94403 | CITY OF SAN MATEO | PUBLIC WORKS | 650-522-7354 |  | 1949 PACIFIC BLVD | SAN MATEO | SAN MATEO | 94403
2409 | 28 | 1 | SanMateo | 2006-01-01 10:48 | 9000 | 0 | 06-008 | 2006-01-01 | CITY OF SAN MATEO | SanMateo | 38TH&ELCAMINO | SAN MATEO | SAN MATEO | 94403 |  |  | 2005-12-31 | 4:00:00 AM | [5 empty] | RAINY WEATHER | Medium |  | STORM DRAIN | No |  | No | No | STORM DRAINS INSPECTED |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanMateo | MANHOLE |  | CAUSE UNKNOWN | --Select None-- | --Select None-- |  | SANITARY OVERFLOW | LEAD | WALT DABNEY | 2006-01-01 | 522-7367 | karmendy@ci.sanmateo.ca.us, | MAJOR | Bob Correa | SanMateo | 650-522-7354 |  | 1949 Pacific Blvd | San Mateo | San Mateo | 94403 | CITY OF SAN MATEO | PUBLIC WORKS | 650-522-7354 |  | 1949 PACIFIC BLVD | SAN MATEO | SAN MATEO | 94403
2410 | 29 | 1 | SanMateo | 2006-01-01 10:54 | 135000 | 0 | 06-008 | 2006-01-01 | CITY OF SAN MATEO | SanMateo | SARATOGA&DELAWARE | SAN MATEO | SAN MATEO | 94403 |  |  | 2005-12-31 | 1:00:00 AM | [5 empty] | RAINY WEATHER | High |  | STORM DRAIN | No |  | No | No | INSPECTED CREEK |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanMateo | MANHOLE |  | FLOW CAPACITY DEFICIENCY | --Select None-- | --Select None-- |  | SANITARY OVERFLOW | LEAD | walt dabney | 2006-01-01 | 522-7367 | karmendy@ci.sanmateo.ca.us, | MAJOR | Bob Correa | SanMateo | 650-522-7354 |  | 1949 Pacific Blvd | San Mateo | San Mateo | 94403 | CITY OF SAN MATEO | PUBLIC WORKS | 650-522-7354 |  | 1949 PACIFIC BLVD | SAN MATEO | SAN MATEO | 94403
2411 | 30 | 1 | SanMateo | 2006-01-01 10:59 | 54000 | 0 | 06-008 | 2006-01-01 | city of san mateo | SanMateo | 2057 s delaware | san mateo | san mateo | 94033 |  |  | 2005-12-31 | 1:00:00 AM | [5 empty] | RAINY WEATHER | High |  | STORM DRAIN | No |  | No | No | creek inspected |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanMateo | MANHOLE |  | CAUSE UNKNOWN | --Select None-- | --Select None-- |  |  | lead | walt dabney | 2006-01-01 | 522-7367 | karmendy@ci.sanmateo.ca.us, | MAJOR | Bob Correa | SanMateo | 650-522-7354 |  | 1949 Pacific Blvd | San Mateo | San Mateo | 94403 | CITY OF SAN MATEO | PUBLIC WORKS | 650-522-7354 |  | 1949 PACIFIC BLVD | SAN MATEO | SAN MATEO | 94403
2326 | 22 | 1 | SanMateo | 2005-12-23 14:51 | 21000 | 0 | 05-7404 | 2005-12-23 | steve camilleri | SanMateo | 2057 s delaware | san mateo | san mateo | 94403 |  |  | 2005-12-22 | 3:00:00 PM | [5 empty] | RAINY WEATHER | High |  | STORM DRAIN | No |  | No | Yes | inspected creek |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanMateo | MANHOLE |  | FLOW CAPACITY DEFICIENCY | --Select None-- | --Select None-- |  | sanitary overflow | lead | steve camilleri | 2005-12-23 | 650 522 7354 | karmendy@ci.sanmateo.ca.us, | MAJOR | Bob Correa | SanMateo | 650-522-7354 |  | 1949 Pacific Blvd | San Mateo | San Mateo | 94403 | CITY OF SAN MATEO | PUBLIC WORKS | 650-522-7354 |  | 1949 PACIFIC BLVD | SAN MATEO | SAN MATEO | 94403
2327 | 23 | 1 | SanMateo | 2005-12-23 14:54 | 21000 | 0 | 05-7404 | 2005-12-23 | steve camilleri | SanMateo | saratoga &s delaware | san mateo | san mateo | 94403 |  |  | 2005-12-22 | 3:00:00 PM | [5 empty] | RAINY WEATHER | High |  | STORM DRAIN | No |  | No | Yes | inspected creek |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanMateo | MANHOLE |  | FLOW CAPACITY DEFICIENCY | --Select None-- | --Select None-- |  | sanitary overflow | lead | steve camilleri | 2005-12-23 | 650 522 7354 | karmendy@ci.sanmateo.ca.us, | MAJOR | Bob Correa | SanMateo | 650-522-7354 |  | 1949 Pacific Blvd | San Mateo | San Mateo | 94403 | CITY OF SAN MATEO | PUBLIC WORKS | 650-522-7354 |  | 1949 PACIFIC BLVD | SAN MATEO | SAN MATEO | 94403
2828 | 34 | 1 | SanMateo | 2006-02-16 14:46 | 305 | 0 |  | 2006-02-16 14:46 |  | -- | Cutriss & 38th Ave | San Mateo | San Mateo | 94403 |  |  | 2005-12-09 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanMateo | MANHOLE |  | CAUSE UNKNOWN | --Select None-- |  |  |  | PW Supervisor | Bob Correa | 2006-02-16 | 650-522-7354 | bcorrea@cityofsanmateo.org | MINOR
2474 | 31 | 1 | SanMateo | 2006-01-04 11:14 | 67500 | 0 | 06-0122 | 2006-01-04 | walt dabney | SanMateo | saratoga& delaware | san mateo | san mateo | 94403 |  |  | 2005-01-03 | 11:00:00 A | [5 empty] | RAINY WEATHER | High |  | STORM DRAIN | No |  | Yes | No | inspected creek |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanMateo | MANHOLE |  | FLOW CAPACITY DEFICIENCY | --Select None-- | --Select None-- |  | sanitary overflow | lead | walt dabney | 2006-01-04 | 522-7367 | karmendy@ci.sanmateo.ca.us, | MAJOR | Bob Correa | SanMateo | 650-522-7354 |  | 1949 Pacific Blvd | San Mateo | San Mateo | 94403 | CITY OF SAN MATEO | PUBLIC WORKS | 650-522-7354 |  | 1949 PACIFIC BLVD | SAN MATEO | SAN MATEO | 94403
4974 | 17 | 1 | SanMateoCounty | 2007-03-21 10:14 | 175 | 0 |  | 2007-03-21 10:14 |  | -- | Vicinity of 155 Eleanor Dr. | Woodside | San Mateo | 94062 |  |  | 2007-03-10 |  |  |  | Blockage in main line caused by roots and sticks introduced to the system by others. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Public Works Technic | Norm Merrill | 2007-03-21 | 650-363-4100
4155 | 16 | 1 | SanMateoCounty | 2006-11-27 15:58 | 600 | 0 |  | 2006-11-27 15:58 |  | -- | Vicinity of 1624 Ascencion Dr. | San Mateo | San Mateo | 94402 |  |  | 2006-11-18 |  |  |  | Blockage in mainline caused by grease. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Public Works Technic | Norm Merrill | 2006-11-27 | 650-363-4100
4151 | 15 | 1 | SanMateoCounty | 2006-11-27 15:45 | 600 | 0 |  | 2006-11-27 15:45 |  | -- | Vicinity of 500 Polhemus Rd. | San Mateo | San Mateo | 94402 |  |  | 2006-11-18 |  |  |  | Blockage in mainline caused by debris and rooting. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Public Works Technic | Norm Merrill | 2006-11-27 | 650-363-4100
3816 | 14 | 1 | SanMateoCounty | 2006-08-30 17:33 | 500 | 0 |  | 2006-08-30 17:33 |  | -- | Vicinity of Polhemus Road and Ascension Drive. | San Mateo | San Mateo | 94402 |  |  | 2006-08-21 |  |  |  | Contractor working for SFPUC broke sewer main while excavating rock in dewatered creek bed. 8 inch VCP main was broken and wastewater began filling trench. Spill was contained and directed back into pipe until maintenance crew was able to pump wastewater back into downstream manhole while perfoming repair. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanMateoCounty | PIPE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Public Works Technic | Norm Merrill | 2006-08-30 | 650-363-4100 | astillman@co.sanmateo.ca.us,mchow@co.sanmateo.ca.us,nmerrill@co.sanmateo.ca.us, ncullen@co.sanmateo.ca.us | MINOR
3039 | 10 | 1 | SanMateoCounty | 2006-03-20 09:19 | 3000 | 0 | 06-1666 | 2006-03-20 | Norm Merrill |  | Vicinity of 639 Park Rd. | Redwood City | San Mateo | 94062 |  |  | 2006-03-19 | 8:45:00 AM | 2006-03-19 | 6:00:00 PM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | District Engineer | Ann Stillman | 2006-03-20 | 650-599-1417 | astillman@co.sanmateo.ca.us,mchow@co.sanmateo.ca.us,nmerrill@co.sanmateo.ca.us, ncullen@co.sanmateo.ca.us | 24HR |  |  | 650-363-4100 | [6 empty] | SanMateoCounty
3076 | 13 | 1 | SanMateoCounty | 2006-03-27 16:31 | 3000 | 0 | 06-1666 | 2006-03-20 | County | Norm Merrill | Vicinity of 639 Park Rd. | Redwood City | San Mateo | 94062 |  |  | 2006-03-19 | 8:45:00 AM | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | No | No debris entered waters of the State. |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SanMateoCounty | PIPE |  | NATURAL DISASTER | --Select None-- | --Select None-- | Landslide on private property. |  | District Engineer | Ann Stillman | 2006-03-27 | 650-599-1417 | astillman@co.sanmateo.ca.us,mchow@co.sanmateo.ca.us,nmerrill@co.sanmateo.ca.us, ncullen@co.sanmateo.ca.us | MAJOR | Ann Stillman | SanMateoCounty | 650-599-1417 |  | 555 County Center, 5th Floor | Redwood City | San Mateo | 94063 |  | Private Property
2373 | 9 | 3 | SanMateoCounty | 2005-12-29 12:35 | 900 | 0 |  | 2005-12-29 12:35 |  | -- | Vicinity of 140 Tiptoe Ln. | Burlingame | San Mateo | 94010 |  |  | 2005-12-26 |  |  |  | Blockage in mainline due to roots. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanMateoCounty | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Public Works Technic | Norm Merrill | 2005-12-28 | 650-599-1434 | nmerrill@co.sanmateo.ca.us, astillman@co.sanmateo.ca.us, mchow@co.sanmateo.ca.us | MINOR
2036 | 8 | 2 | SanMateoCounty | 2005-10-25 09:34 | 500 | 0 |  | 2005-10-25 09:34 |  | -- | Vicinity of 525 Polhemus Rd. | San Mateo | San Mateo | 94402 |  |  | 2005-10-23 |  |  |  | Blockage in main line due to debris and small amount of rooting. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanMateoCounty | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Public Works Technic | Norm Merrill | 2005-10-25 | 650-599-1434 | astillman@co.sanmateo.ca.us, mchow@co.sanmateo.ca.us, nmerrill@co.sanmateo.ca.us | MINOR
897 | 7 | 1 | SanMateoCounty | 2005-01-21 15:21 | 150 | 0 |  | 2005-01-21 15:22 |  | -- | Vicinity of 1735 Randall Rd. | San Mateo | San Mateo | 94402 |  |  | 2005-01-18 |  |  |  | Blockage due to grit and debris in line. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanMateoCounty | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Public Works Tech | Norm Merrill | 2005-01-21 | 650-599-1434 | astillman@co.sanmateo.ca.us,nmerrill@co.sanmateo.ca.us | MINOR
890 | 6 | 1 | SanMateoCounty | 2005-01-21 12:56 | 500 | 0 |  | 2005-01-21 12:56 |  | -- | Vicinity of 147 Chesham Ave. | San Carlos | San Mateo | 94070 |  |  | 2005-01-16 |  |  |  | Blockage due to grease in line. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanMateoCounty | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Public Works Tech | Norm Merrill | 2005-01-21 | 650-599-1434 | astillman@co.sanmateo.ca.us,nmerrill@co.sanmateo.ca.us | MINOR
785 | 5 | 1 | SanMateoCounty | 2005-01-07 10:53 | 750 | 0 |  | 2005-01-07 10:53 |  | -- | Vicinity of 518 Hillcrest Rd. | Redwood City | San Mateo | 94062 |  |  | 2004-12-30 |  |  |  | Second overflow at this location. Blockage caused by contractor leaving brick and mortar debris after raising manhole to grade. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanMateoCounty | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Public Works Tech | Norm Merrill | 2005-01-07 | 650-599-1434 | astillman@co.sanmateo.ca.us,nmerrill@co,sanmateo.ca.us | MINOR
783 | 4 | 1 | SanMateoCounty | 2005-01-07 10:46 | 400 | 0 |  | 2005-01-07 10:46 |  | -- | Vicinity of 2446 Lake Blvd. | Redwood City | San Mateo | 94062 |  |  | 2004-12-29 |  |  |  | Blockage caused by roots and grease | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanMateoCounty | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Public Works Tech | Norm Merrill | 2005-01-07 | 650-599-1434 | astillman@co.sanmateo.ca.us,nmerrill@co,sanmateo.ca.us | MINOR
694 | 1 | 1 | SanMateoCounty | 2004-12-30 14:03 | 500 | 0 |  | 2004-12-30 14:03 |  | -- | Vicinity of 518 Hillside Rd. | Redwood City | San Mateo | 94062 |  |  | 2004-12-23 |  |  |  | Found bricks and mortar left over from contractor raising manholes after street re-surfacing. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanMateoCounty | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Public Works Tech | Norm Merrill | 2004-12-30 | 650-599-1434 | astillman@co.sanmateo.ca.us,nmerrill@co.sanmateo.ca.us | MINOR
696 | 2 | 1 | SanMateoCounty | 2004-12-30 14:11 | 475 | 0 |  | 2004-12-30 14:11 |  | -- | Vicinity of 665 Stanford Ave. | Redwood City | San Mateo | 94063 |  |  | 2004-12-23 |  |  |  | Found grease and debris in line. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanMateoCounty | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Public Works Tech | Norm Merrill | 2004-12-30 | 650-599-1434 | astillman@co.sanmateo.ca.us,nmerrill@co.sanmateo.ca.us | MINOR
713 | 3 | 1 | SanMateoCounty | 2005-01-03 13:58 | 800 | 0 |  | 2005-01-03 13:58 |  | -- | Intersection of Lakeview Way & W. Summit Drive | RedwoodCity | San Mateo | 94062 |  |  | 2004-12-20 |  |  |  | Sewage from a failed sewer pipe entered the storm drain through holes of storm drain pipe, daylighted into an open drainage swale and entered a lake which is currently closed to the public. The open drainage swale was cleaned and deodorized. San Mateo County Environmental Health Services Department was notified of the incident. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanMateoCounty | PIPE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Ms. | Ann M. Stillman | 2004-12-23 | 650-599-1417 | astillman@co.sanmateo.ca.us,mchow@co.sanmateo.ca.us | MINOR
5061 | 84 | 1 | SanRafaelSD | 2007-04-16 08:04 | 250 | 0 |  | 2007-04-16 08:04 |  | -- | 199 Riviera Dr. | San Rafael | Marin | 94901 |  |  | 2007-04-12 |  |  |  | Contractor working for Peacock Gap Golf Course hit sewer pipe. Called in pumper truck to clean up the contained overflow. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | PIPE |  | INFRASTRUCTURE FAILURE | -- Select One -- |  |  |  | Supervisor | Matt Smith | 2007-04-16 | 415 485 3374
5059 | 83 | 1 | SanRafaelSD | 2007-04-16 07:18 | 50 | 0 |  | 2007-04-16 07:18 |  | -- | 42 Alexander Ave | San Rafael | Marin | 94901 |  |  | 2007-04-12 |  |  |  | Vactored up and returned to system | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2007-04-16 | 415 485 3374
5045 | 82 | 1 | SanRafaelSD | 2007-04-06 07:43 | 70 | 0 |  | 2007-04-06 07:43 |  | -- | 124 Park Street | San Rafael | Marin | 94901 |  |  | 2007-04-05 |  |  |  | Vactored out storm drain. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | BLOCKAGE | ROOTS |  | Rodhole |  | Supervisor | Matt Smith | 2007-04-06 | 415 485 3374
4958 | 81 | 1 | SanRafaelSD | 2007-03-19 10:42 | 90 | 0 |  | 2007-03-19 10:42 |  | -- | 192 Peacock Dr. | San Rafael | Marin | 94901 |  |  | 2007-03-17 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Matt Smith | 2007-03-19 | 415 485 3374
4722 | 80 | 1 | SanRafaelSD | 2007-02-09 13:08 | 450 | 0 |  | 2007-02-09 13:08 |  | -- | 6 Ross Valley Drive | San Rafael | Marin | 94901 |  |  | 2007-02-08 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Supervisor | Matt Smith | 2007-02-09 | 415 485 3374
4678 | 79 | 1 | SanRafaelSD | 2007-02-06 08:12 | 450 | 0 |  | 2007-02-06 08:12 |  | -- | 265 Union Street | San Rafael | Marin | 94901 |  |  | 2007-02-04 |  |  |  | Easement behind home was blocked with grease and paper towels. Cleared by Roto-Rooter. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Supervisor | Matt Smith | 2007-02-06 | 415 485 3374
4663 | 78 | 1 | SanRafaelSD | 2007-02-02 10:40 | 200 | 0 |  | 2007-02-02 10:40 |  | -- | 123 Forbes Ave | San Rafael | Marin | 94901 |  |  | 2007-02-02 |  |  |  | Rags and roots caused blockage. Cleaned storm drain with Vac-Con truck, retuned to system. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Supervisor | Matt Smith | 2007-02-02 | 415 485 3374
4661 | 77 | 1 | SanRafaelSD | 2007-02-02 10:35 | 20 | 0 |  | 2007-02-02 10:35 |  | -- | 79 Summit Ave | San Rafael | Marin | 94901 |  |  | 2007-02-01 |  |  |  | Cleaned up with Vac-Con, Plugged with paper products. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | Supervisor | Matt Smith | 2007-02-02 | 415 485 3374
4659 | 76 | 1 | SanRafaelSD | 2007-02-02 10:31 | 50 | 0 |  | 2007-02-02 10:31 |  | -- | 75 Montecito Rd. | San Rafael | Marin | 94901 |  |  | 2007-02-01 |  |  |  | Cleaned up with Vac-Con | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2007-02-02 | 415 485 3374
4580 | 75 | 1 | SanRafaelSD | 2007-01-22 11:27 | 60 | 0 |  | 2007-01-22 11:27 |  | -- | 35 Glen Dr. | San Rafael | Marin | 94901 |  |  | 2007-01-21 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2007-01-22 | 415 485 3374
4578 | 74 | 1 | SanRafaelSD | 2007-01-22 11:20 | 50 | 0 |  | 2007-01-22 11:20 |  | -- | 108 Courtright Rd. | San Rafael | Marin | 94901 |  |  | 2007-01-20 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2007-01-22 | 415 485 3374
4575 | 73 | 1 | SanRafaelSD | 2007-01-22 10:34 | 20 | 0 |  | 2007-01-22 10:34 |  | -- | 41 Marinita Ave. | San Rafael | Marin | 94901 |  |  | 2007-01-18 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2007-01-22 | 415 485 3375
4573 | 72 | 1 | SanRafaelSD | 2007-01-22 10:31 | 85 | 0 |  | 2007-01-22 10:31 |  | -- | 47 Dowitcher Way | San Rafael | Marin | 94901 |  |  | 2007-01-18 |  |  |  | Failure on wet well level controller. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | ELECTRICAL POWER FAILURE | -- Select One -- |  |  |  | Supervisor | Matt Smith | 2007-01-22 | 415 485 3374
4356 | 71 | 1 | SanRafaelSD | 2006-12-18 07:41 | 450 | 0 |  | 2006-12-18 07:41 |  | -- | 1955 5th Ave | San Rafael | Marin | 94901 |  |  | 2006-12-14 |  |  |  | captured and reclaimed at storm drain. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Supervisor | Matt Smith | 2006-12-18 | 415 485 3374
4269 | 70 | 1 | SanRafaelSD | 2006-12-08 06:56 | 50 | 0 |  | 2006-12-08 06:56 |  | -- | Magnolia Ave. @ Palm Ave | San Rafael | Marin | 94901 |  |  | 2006-12-07 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Supervisor | Matt Smith | 2006-12-08 | 415 485 3374
4252 | 69 | 1 | SanRafaelSD | 2006-12-06 10:15 | 120 | 0 |  | 2006-12-06 10:15 |  | -- | 321 Laurel Place | San Rafael | Marin | 94901 |  |  | 2006-12-04 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2006-12-06 | 415 485 3374
4157 | 68 | 1 | SanRafaelSD | 2006-11-28 07:44 | 20 | 0 |  | 2006-11-28 07:44 |  | -- | 321 Laurel Place | San Rafael | Marin | 94901 |  |  | 2006-11-24 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Supervisor | Matt Smith | 2006-11-28 | 415 485 3374
4052 | 67 | 1 | SanRafaelSD | 2006-11-02 09:12 | 20 | 0 |  | 2006-11-02 09:12 |  | -- | 100 Yacht Club Dr. | San Rafael | Marin | 94901 |  |  | 2006-11-01 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Matt Smith | 2006-11-02 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
4027 | 66 | 1 | SanRafaelSD | 2006-10-26 12:39 | 80 | 0 |  | 2006-10-26 12:39 |  | -- | 1800 2nd St. | San Rafael | Marin | 94901 |  |  | 2006-10-25 |  |  |  | Cleaned up with vac-con truck | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Matt Smith | 2006-10-26 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
3908 | 65 | 1 | SanRafaelSD | 2006-09-21 10:55 | 5 | 0 |  | 2006-09-21 10:55 |  | -- | 16 Vineyard Drive | San Rafael | Marin | 94901 |  |  | 2006-09-20 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | OTHER | Rod Hole | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2006-09-21 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
3873 | 63 | 1 | SanRafaelSD | 2006-09-13 08:28 | 5 | 0 |  | 2006-09-13 08:28 |  | -- | 225 San Marino Dr. | San Rafael | Marin | 94901 |  |  | 2006-09-08 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2006-09-13 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
3875 | 64 | 1 | SanRafaelSD | 2006-09-13 08:32 | 60 | 0 |  | 2006-09-13 08:32 |  | -- | 4 Beryl Lane | San Rafael | Marin | 94901 |  |  | 2006-09-06 | [9 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2006-09-13 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
3786 | 62 | 1 | SanRafaelSD | 2006-08-25 09:10 | 40 | 0 |  | 2006-08-25 09:10 |  | -- | 180 Palm Ave. | San Rafael | Marin | 94901 |  |  | 2006-08-22 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2006-08-25 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
3717 | 61 | 1 | SanRafaelSD | 2006-08-11 11:28 | 800 | 0 |  | 2006-08-11 11:28 |  | -- | 110 Ross Street | San Rafael | Marin | 94901 |  |  | 2006-08-10 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2006-08-11 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
3641 | 60 | 1 | SanRafaelSD | 2006-07-20 12:53 | 100 | 0 |  | 2006-07-20 12:53 |  | -- | 50 Acacia Ave | San Rafael | Marin | 94901 |  |  | 2006-07-20 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Supervisor | Matt Smith | 2006-07-20 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
3631 | 59 | 1 | SanRafaelSD | 2006-07-19 09:27 | 20 | 0 |  | 2006-07-19 09:27 |  | -- | 230 Coleman Dr. | San Rafael | Marin | 94901 |  |  | 2006-07-18 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2006-07-19 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
3595 | 58 | 1 | SanRafaelSD | 2006-07-05 07:27 | 325 | 0 |  | 2006-07-05 07:27 |  | -- | 565 Canal St | San Rafael | Marin | 94901 |  |  | 2006-06-29 |  |  |  | Captured and returned to system. Crews clean up spill on the street and cleaned nearby c/b | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Matt Smith | 2006-07-05 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
3472 | 57 | 1 | SanRafaelSD | 2006-06-08 12:52 | 40 | 0 |  | 2006-06-08 12:52 |  | -- | 71 Twin Oaks | San Rafael | Marin | 94901 |  |  | 2006-06-07 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2006-06-08 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
3422 | 56 | 1 | SanRafaelSD | 2006-05-30 07:35 | 20 | 0 |  | 2006-05-30 07:35 |  | -- | 34 Twin Oaks Ave. | San Rafael | Marin | 94901 |  |  | 2006-05-30 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2006-05-30 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
3354 | 55 | 1 | SanRafaelSD | 2006-05-17 07:40 | 100 | 0 |  | 2006-05-17 07:40 |  | -- | 301 Riviera Drive | San Rafael | Marin | 94901 |  |  | 2006-05-16 |  |  |  | Riviera pump station is undergoing major rehabilitation construction. The temporary bypass pump installed by the contractor, Anderson Pacific, failed and caused the overflow at Manhole #S1856 | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | CAUSE UNKNOWN | --Select None-- |  |  |  | Supervisor | Matt Smith | 2006-05-17 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
3312 | 54 | 1 | SanRafaelSD | 2006-05-08 08:10 | 50 | 0 |  | 2006-05-08 08:10 |  | -- | Quarry Rd. easement M/H #S617 (Behind 38 Twin Oaks Ave.) | San Rafael | Marin | 94901 |  |  | 2006-05-08 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2006-05-08 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
3241 | 53 | 1 | SanRafaelSD | 2006-04-27 07:44 | 2 | 0 |  | 2006-04-27 07:44 |  | -- | 184 Coleman Dr. | San Rafael | Marin | 94901 |  |  | 2006-04-25 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2006-04-27 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
3185 | 52 | 1 | SanRafaelSD | 2006-04-17 10:06 | 200 | 0 |  | 2006-04-17 10:06 |  | -- | 338 Coleman Dr. | San Rafael | Marin | 94901 |  |  | 2006-04-17 |  |  |  | Cleaned up and returned to system with vacuum truck. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2006-04-17 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
3110 | 51 | 1 | SanRafaelSD | 2006-04-03 07:29 | 50 | 0 |  | 2006-04-03 07:29 |  | -- | Sewer easement off Pt. San Pedro Rd @ Bellevue Ave.M/H S2106 | San Rafael | Marin | 94901 |  |  | 2006-03-30 |  |  |  | Cleaned up and sanitized around M/H. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2006-04-03 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
3088 | 50 | 1 | SanRafaelSD | 2006-03-28 12:33 | 5 | 0 |  | 2006-03-28 12:33 |  | -- | 29 Edgewood Way | San Rafael | Marin | 94901 |  |  | 2006-03-27 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2006-03-28 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
3049 | 49 | 1 | SanRafaelSD | 2006-03-23 07:18 | 450 | 0 |  | 2006-03-23 07:18 |  | -- | 46 Hillcrest Dr. | San Rafael | Marin | 94901 |  |  | 2006-03-17 |  |  |  | Contained under house. 400 gal. pumped out and returned to sewer system. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | Supervisor | Matt Smith | 2006-03-23 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
2850 | 48 | 1 | SanRafaelSD | 2006-02-21 14:05 | 550 | 0 |  | 2006-02-21 14:05 |  | -- | 58 West Crescent Dr | San Rafael | Marin | 94901 |  |  | 2006-02-20 |  |  |  | Overflow absorbed into dirt, no debris paper ect... | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | PIPE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2006-02-21 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
2812 | 47 | 1 | SanRafaelSD | 2006-02-15 13:57 | 50 | 0 |  | 2006-02-15 13:57 |  | -- | 34 Fair Dr. | San Rafael | Marin | 94901 |  |  | 2006-02-15 |  |  |  | Captured in gutter and vactored up | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2006-02-15 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
2775 | 46 | 2 | SanRafaelSD | 2006-02-08 07:30 | 75 | 0 |  | 2006-02-08 07:30 |  | -- | 24 Fremont Rd. | San Rafael | Marin | 94901 |  |  | 2006-02-07 |  |  |  | Sewer pipe cracked. Overflow captured at c/b, vactored up and returned to collection system. Retuned appx.65 gal. Sewer main repaired. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | PIPE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Supervisor | Matt Smith | 2006-02-08 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
2689 | 45 | 1 | SanRafaelSD | 2006-01-27 06:56 | 75 | 0 |  | 2006-01-27 06:56 |  | -- | 71 Twin Oaks Ave. | San Rafael | Marin | 94901 |  |  | 2006-01-26 |  |  |  | Possibly broken by a fence post,recently installed by the property owner . Crews recovered 20 gal. and returned it to the collection system. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | PIPE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Supervisor | Matt Smith | 2006-01-27 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
2625 | 42 | 1 | SanRafaelSD | 2006-01-17 08:32 | 100 | 0 |  | 2006-01-17 08:32 |  | -- | East St. @ Second St. | San Rafael | Marin | 94901 |  |  | 2006-01-17 |  |  |  | Captured and returned to system with Vac-Con truck | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Matt Smith | 2006-01-17 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
2631 | 44 | 1 | SanRafaelSD | 2006-01-17 11:27 | 50 | 0 |  | 2006-01-17 11:27 |  | -- | Miramar Ave. @ Miraflores Ave | San Rafael | Marin | 94901 |  |  | 2006-01-17 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2006-01-17 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
2629 | 43 | 1 | SanRafaelSD | 2006-01-17 11:22 | 10 | 0 |  | 2006-01-17 11:22 |  | -- | 5th Ave. @ Leafwood Cir. | San Rafael | Marin | 94901 |  |  | 2006-01-14 |  |  |  | Roto Rooter Call out | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Matt Smith | 2006-01-17 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
2616 | 41 | 1 | SanRafaelSD | 2006-01-12 08:54 | 50 | 0 |  | 2006-01-12 08:54 |  | -- | 38 Twin Oaks Ave | San Rafael | Marin | 94901 |  |  | 2006-01-12 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2006-01-12 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
2510 | 40 | 1 | SanRafaelSD | 2006-01-05 07:36 | 20 | 0 |  | 2006-01-05 07:36 |  | -- | 44 Lochness Lane | San Rafael | Marin | 94901 |  |  | 2006-01-04 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2006-01-05 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
2293 | 39 | 1 | SanRafaelSD | 2005-12-21 08:49 | 100 | 0 |  | 2005-12-21 08:49 |  | -- | 881 4th Street | San Rafael | Marin | 94901 |  |  | 2005-12-20 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Matt Smith | 2005-12-21 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
2187 | 38 | 1 | SanRafaelSD | 2005-11-29 11:04 | 150 | 0 |  | 2005-11-29 11:04 |  | -- | 1533 4th St. | San Rafael | Marin | 94901 |  |  | 2005-11-28 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Matt Smith | 2005-11-29 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
2179 | 37 | 1 | SanRafaelSD | 2005-11-28 09:08 | 100 | 0 |  | 2005-11-28 09:08 |  | -- | 77 Manderly Rd. | San Rafael | Marin | 94901 |  |  | 2005-11-27 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2005-11-28 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
2144 | 36 | 1 | SanRafaelSD | 2005-11-21 07:04 | 80 | 0 |  | 2005-11-21 07:04 |  | -- | 154 Maywood Way | San Rafael | Marin | 94901 |  |  | 2005-11-18 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2005-11-21 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
2135 | 35 | 1 | SanRafaelSD | 2005-11-17 14:02 | 70 | 0 |  | 2005-11-17 14:02 |  | -- | 17 Upper Fremont | San Rafael | Marin | 94901 |  |  | 2005-11-11 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | upervisor | Matt Smith | 2005-11-17 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
2083 | 34 | 1 | SanRafaelSD | 2005-11-07 07:18 | 15 | 0 |  | 2005-11-07 07:18 |  | -- | 531 C St. | San Rafael | Marin | 94901 |  |  | 2005-11-06 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | Supervisor | Matt Smith | 2005-11-07 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
2076 | 32 | 1 | SanRafaelSD | 2005-11-04 07:30 | 15 | 0 |  | 2005-11-04 07:30 |  | -- | 35 Maywood way | San Rafael | Marin | 94901 |  |  | 2005-11-03 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2005-11-04 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
2079 | 33 | 1 | SanRafaelSD | 2005-11-04 10:40 | 360 | 0 |  | 2005-11-04 10:40 |  | -- | 314 Du Bois St. | San Rafael | Marin | 94901 |  |  | 2005-11-03 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Supervisor | Matt Smith | 2005-11-04 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
2072 | 31 | 1 | SanRafaelSD | 2005-11-01 08:03 | 20 | 0 |  | 2005-11-01 08:03 |  | -- | 324 Laurel Place | San Rafael | Marin | 94901 |  |  | 2005-10-31 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Supervisor | Matt Smith | 2005-11-01 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
2043 | 30 | 1 | SanRafaelSD | 2005-10-27 06:56 | 50 | 0 |  | 2005-10-27 06:56 |  | -- | 16 Vineyard Drive | San Rafael | Marin | 94901 |  |  | 2005-10-26 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | PIPE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2005-10-27 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
2013 | 29 | 1 | SanRafaelSD | 2005-10-24 11:54 | 500 | 0 |  | 2005-10-24 11:54 |  | -- | 6 Bay Ct. | San Rafael | Marin | 94901 |  |  | 2005-10-23 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2005-10-24 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1944 | 28 | 1 | SanRafaelSD | 2005-10-11 06:55 | 20 | 0 |  | 2005-10-11 06:55 |  | -- | 65 Billou St. | San Rafael | Marin | 94915 |  |  | 2005-10-08 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Matt Smith | 2005-10-11 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1913 | 27 | 1 | SanRafaelSD | 2005-10-04 13:07 | 30 | 0 |  | 2005-10-04 13:07 |  | -- | 508 San Pedro Cove | San Rafael | Marin | 94901 |  |  | 2005-10-03 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2005-10-04 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1876 | 26 | 1 | SanRafaelSD | 2005-09-27 12:50 | 75 | 0 |  | 2005-09-27 12:50 |  | -- | 1012 Mission Ave. | San Rafael | Marin | 94901 |  |  | 2005-09-27 | [9 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2005-09-27 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1776 | 24 | 1 | SanRafaelSD | 2005-09-14 07:36 | 5 | 0 |  | 2005-09-14 07:36 |  | -- | 125 Altena St. | San Rafael | Marin | 94901 |  |  | 2005-09-10 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2005-09-14 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1778 | 25 | 1 | SanRafaelSD | 2005-09-14 07:40 | 3 | 0 |  | 2005-09-14 07:40 |  | -- | 383 Irwin St. | San Rafael | Marin | 94901 |  |  | 2005-09-10 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Matt Smith | 2005-09-14 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1674 | 23 | 1 | SanRafaelSD | 2005-08-04 07:11 | 15 | 0 |  | 2005-08-04 07:11 |  | -- | 11 Eye St. | San Rafael | Marin | 94901 |  |  | 2005-08-03 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2005-08-04 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1621 | 22 | 1 | SanRafaelSD | 2005-07-18 07:47 | 10 | 0 |  | 2005-07-18 07:47 |  | -- | 180 Bret Harte Rd. | San Rafael | Marin | 94901 |  |  | 2005-07-15 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Matt Smith | 2005-07-18 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1615 | 21 | 1 | SanRafaelSD | 2005-07-14 12:57 | 75 | 0 |  | 2005-07-14 12:57 |  | -- | 7 Windsor Ave. | San Rafael | Marin | 94901 |  |  | 2005-07-14 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2005-07-14 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1606 | 20 | 1 | SanRafaelSD | 2005-07-11 11:16 | 55 | 0 |  | 2005-07-11 11:16 |  | -- | 55 Chula Vista Dr. | San Rafael | Marin | 94901 |  |  | 2005-07-11 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2005-07-11 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1604 | 19 | 1 | SanRafaelSD | 2005-07-08 09:46 | 15 | 0 |  | 2005-07-08 09:46 |  | -- | Lynn Ct. @ Irwin St. | San Rafael | Marin | 94901 |  |  | 2005-07-03 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | Matt Smith | 2005-07-08 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1602 | 18 | 1 | SanRafaelSD | 2005-07-08 09:35 | 5 | 0 |  | 2005-07-08 09:35 |  | -- | 732 Belle Ave. | San Rafael | Marin | 94901 |  |  | 2005-07-02 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2005-07-08 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1481 | 17 | 1 | SanRafaelSD | 2005-06-03 07:44 | 20 | 0 |  | 2005-06-03 07:44 |  | -- | 1520 Grand Ave. (Domincan College rod hole #432 on Magnolia Ave). | San Rafael | Marin | 94901 |  |  | 2005-06-02 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2005-06-03 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1445 | 16 | 1 | SanRafaelSD | 2005-05-23 13:44 | 75 | 0 |  | 2005-05-23 13:44 |  | -- | 608 C Street | San Rafael | Marin | 94901 |  |  | 2005-05-23 |  |  |  | Vactored out storm drain system on C Street | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | PIPE |  | BLOCKAGE | DEBRIS |  |  |  | Supervisor | Matt Smith | 2005-05-23 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1443 | 15 | 1 | SanRafaelSD | 2005-05-23 13:36 | 50 | 0 |  | 2005-05-23 13:36 |  | -- | 16 Upper Fremont Dr. | San Rafael | Marin | 94901 |  |  | 2005-05-20 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Supervisor | Matt Smith | 2005-05-23 | 415 485 3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1353 | 14 | 1 | SanRafaelSD | 2005-05-03 14:15 | 80 | 0 |  | 2005-05-03 14:15 |  | -- | 4 Coleman Dr. | San Rafael | Marin | 94915 |  |  | 2005-05-03 |  |  |  | Blockage in mainline backed up into home at 4 Coleman Dr. Sewer crew did initial cleaning. Called cleaning contractor for carpet removal,drying and disenfecting of contaminated property. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | PIPE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2005-05-03 | 415-485-3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1344 | 13 | 1 | SanRafaelSD | 2005-05-02 07:57 | 20 | 0 |  | 2005-05-02 07:57 |  | -- | 1352 Grand Ave | San Rafael | Marin | 94915 |  |  | 2005-05-01 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2005-05-02 | 415-485-3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1323 | 12 | 1 | SanRafaelSD | 2005-04-25 11:26 | 75 | 0 |  | 2005-04-25 11:26 |  | -- | 498 Pt. San Pedro Rd. | San Rafael | Marin | 94915 |  |  | 2005-04-24 |  |  |  | Air release valve had a mechanical failure. Float was not seating properly | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | OTHER | Leaking ARV | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Supervisor | Matt Smith | 2005-04-25 | 415-485-3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1304 | 11 | 1 | SanRafaelSD | 2005-04-21 10:28 | 55 | 0 |  | 2005-04-21 10:28 |  | -- | 7 Dowitcher Way | San Rafael | Marin | 94915 |  |  | 2005-04-21 |  |  |  | Storm drain cleaned with Vactor, no water contact | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Supervisor | Matt Smith | 2005-04-21 | 415-485-3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1300 | 10 | 1 | SanRafaelSD | 2005-04-19 13:56 | 80 | 0 |  | 2005-04-19 13:56 |  | -- | 116 Dubois St. | San Rafael | Marin | 94915 |  |  | 2005-04-19 |  |  |  | Partial blockage in main line. Lateral backed up into garage sink. No clean out at 116 Dubois St. Concrete slab floor. No property damage. Vactor cleaned up overflow at curb & gutter. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | PIPE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2005-04-19 | 415-485-3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1258 | 9 | 1 | SanRafaelSD | 2005-04-06 10:09 | 88 | 0 |  | 2005-04-06 10:09 |  | -- | 71 Twin Oaks Ave | San Rafael | Marin | 94915 |  |  | 2005-03-28 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | PIPE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2005-04-06 | 415-485-3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1197 | 8 | 1 | SanRafaelSD | 2005-03-17 09:51 | 10 | 0 |  | 2005-03-17 09:51 |  | -- | 9 Alta Vista Way | San Rafael | Marin | 94915 |  |  | 2005-03-16 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2005-03-17 | 485-3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1178 | 7 | 1 | SanRafaelSD | 2005-03-14 08:47 | 500 | 0 |  | 2005-03-14 08:47 |  | -- | 226 Magnolia Ave. | San Rafael | Marin | 94915 |  |  | 2005-03-11 |  |  |  | Roots and grease caused the blockage. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Supervisor | Matt Smith | 2005-03-14 | 485-3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1174 | 6 | 1 | SanRafaelSD | 2005-03-14 08:28 | 55 | 0 |  | 2005-03-14 08:28 |  | -- | 33 Lisbon St. | San Rafael | Marin | 94915 |  |  | 2005-03-10 |  |  |  | Concrete from a contractor plugged main. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | PIPE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Supervisor | Matt Smith | 2005-03-14 | 485-3374 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1082 | 5 | 1 | SanRafaelSD | 2005-02-25 08:45 | 30 | 0 |  | 2005-02-25 08:45 |  | -- | 106 Treanor St. | San Rafael | Marin | 94915 |  |  | 2005-02-25 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | sanrafaelsd | OTHER | Rod Hole | BLOCKAGE | DEBRIS |  |  |  | Supervisor | Matt Smith | 2005-02-25 | 415-485-3374 |  | MINOR
1054 | 4 | 1 | SanRafaelSD | 2005-02-17 08:22 | 130 | 0 |  | 2005-02-17 08:22 |  | -- | 51 Arguelo Cir | San Rafael | Marin | 94915 |  |  | 2005-02-17 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | PIPE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Matt Smith | 2005-02-17 | 415-454-4001 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
1020 | 3 | 1 | SanRafaelSD | 2005-02-14 10:30 | 20 | 0 |  | 2005-02-14 10:30 |  | -- | 230 Catalina Blvd | San Rafael | Marin | 94915 |  |  | 2005-02-14 |  |  |  | Spill contained and vactored up. No water contact | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Sewer Maint, Supervi | Matt Smith | 2005-02-14 | 415-454-4001 | matt.smith@ci.san-rafael.ca.us, andy.preston@ci.san-rafael.ca.us | MINOR
598 | 2 | 1 | SanRafaelSD | 2004-12-20 13:09 | 10 | 0 |  | 2004-12-20 13:09 |  | -- | 27 Las Casas Dr. | San Rafael | Marin | 94915 |  |  | 2004-12-20 | [9 empty] | NO WATER INVOLVED | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Maint. Sup. | Matt Smith | 2004-12-20 | 415-485-3374 | matt.smith@ci.san-rafael.ca.us | MINOR
596 | 1 | 1 | SanRafaelSD | 2004-12-20 12:59 | 5 | 0 |  | 2004-12-20 12:59 |  | -- | 40 Miraflores Ave. | San Rafael | Marin | 94915 |  |  | 2004-12-17 | [9 empty] | NO WATER INVOLVED | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SanRafaelSD | OTHER | Rod Hole | BLOCKAGE | DEBRIS |  |  |  | Sewer Maint. Sup. | Matt Smith | 2004-12-20 | 415-485-3374 | matt.smith@ci.san-rafael.ca.us | MINOR
3604 | 3 | 2 | SantaClaraCity | 2006-07-06 10:45 | 15 | 0 |  | 2006-07-06 10:45 |  | -- | 3863 Sullivan Dr. | Santa Clara | Santa Clara | 95050 |  |  | 2006-07-05 |  |  |  | Overflow had not reached the catch basins. Contained at gutter line. Cleaned up gutter line no debris. Hydro-flushed main to relieve stoppage. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SantaClaraCity | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sewer Superintendent | John Peterson | 2006-07-06 | 408-615-2062 | rsaunders@ci.santa-clara.ca.us, akurotori@ci.santa-clara.ca.us | MINOR
698 | 3 | 2 | SASouthernMarin | 2004-12-31 09:45 | 600 | 0 |  | 2004-12-31 09:45 |  | -- | Almonte Blvd 200' north of intersection with Shoreline Highway. | Mill valley | Marin | 94941 |  |  | 2004-12-27 |  |  |  | Discussions with Roto Rooter on 12/29 (after the SSO) reveal that scheduled cleaning of a downstream inverted syphon had not been completed prior to the storm as planned (due to equipment failure). It is likely that the SSO occurred at least in part due to partial blockage of the inverted syphon. The cleaning project was completed on 12/29/04. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SASouthernMarin | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | General Manager | David Coe | 2004-12-28 | 415-388-2402 | dcoe@cityofmillvalley.org | MINOR
699 | 2 | 2 | SASouthernMarin | 2004-12-31 09:46 | 1200 | 0 | 04-6823 | 2004-12-28 | David Coe | SASouthernMarin | Intersection Almonte Blvd and Wisteria Lane. | Mill valley | Marin | 94941 |  |  | 2004-12-27 | 9:00:00 AM | [5 empty] | RAINY WEATHER | High | Richardson Bay | STORM DRAIN | No |  | No | Yes | No visual evidence of wastewtaer in the receiving water body due to massive dilution with storm runoff. |  | Yes | No | No | No | No | Yes | Yes | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SASouthernMarin | MANHOLE | Extreme wet weather resulting in excessive I/I to the sewer system. | INFLOW & INFILTRATION | --Select None-- | LEAKS OF COLLECTION SYSTEM | Extreme wet weather resulting in excessive I/I to the sewer system. | Heavy rain beginning 12/26/04 and ending 12/27/04 resulted in excessive I/I in the sewer system resulting in overflow of dilute raw sewage from a manhole. Discussions with Roto Rooter on 12/29 (after the SSO) reveal that scheduled cleaning of a downstream inverted syphon had not been completed prior to the storm as planned (due to equipment failure). It is likely that the SSO occurred at least in part due to partial blockage of the inverted syphon. The cleaning project was completed on 12/29/04. | General Manager | David Coe | 2004-12-28 | 415-388-2402 | dcoe@cityofmillvalley.org | MAJOR | David Coe | SASouthernMarin | 415-388-2402 | 17 | 450 Sycamore Ave | Mill valley | Marin | 94941 | David Coe | Sewerage Agency of Southern Marin | 415-388-2402 | 17 | P.O. Box 1029 | Mill Valley | Marin | 94941
700 | 1 | 2 | SASouthernMarin | 2004-12-31 09:47 | 6000 | 0 | 04-6822 | 2004-12-28 | David Coe | SASouthernMarin | Miller Avenue at Tam High baseball field. | Mill valley | Marin | 94941 |  |  | 2004-12-27 | 9:00:00 AM | [5 empty] | RAINY WEATHER | High | Richardson Bay | STORM DRAIN | No |  | No | Yes | No visual evidence of wastewater in the receiving water body due to massive dilution with storm runoff. |  | Yes | No | No | No | No | Yes | Yes | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SASouthernMarin | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | LEAKS OF COLLECTION SYSTEM | Extreme wet weather resulting in excessive I/I to the sewer system. | Heavy rain beginning 12/26/04 and ending 12/27/04 resulted in excessive I/I in the sewer system resulting in overflow of dilue sewage from a manhole. Discussions with Roto Rooter on 12/29 (after the SSO) reveal that scheduled cleaning of a downstream inverted syphon had not been completed prior to the storm as planned (due to equipment failure). It is likely that the SSO occurred at least in part due to partial blockage of the inverted syphon. The cleaning project was completed on 12/29/04. | General Manager | David Coe | 2004-12-28 | 415-388-2402 | dcoe@cityofmillvalley.org | MAJOR | David Coe | SASouthernMarin | 415-388-2402 | 17 | 450 Sycamore Ave | Mill valley | Marin | 94941 | David Coe | Sewerage Agency of Southern Marin | 415-388-2402 | 17 | P.O. Box 1029 | Mill Valley | Marin | 94941
4982 | 6 | 1 | Sausalito | 2007-03-22 12:43 | 5 | 0 |  | 2007-03-22 12:43 |  | -- | 164 Donahue Rd adjacent to Marin city Liabrary | Marin City | Marin | 94965 |  |  | 2007-03-21 |  |  |  | Spill caused by disposable diapers. Advised daycare center not to dispose of diapers in the toilet | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | General Manager | Bob Simmons | 2007-03-22 | 415.332.0244
4299 | 5 | 1 | Sausalito | 2006-12-13 09:49 | 450 | 0 |  | 2006-12-13 09:49 |  | -- | Marinship near Harbor Drive MH 380000/377000 | Sausalito | Marin | 94966 |  |  | 2006-12-12 |  |  |  | Rex Franklyn, O&M Spuervisor, responded to and confirmed the spill report. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | INFLOW & INFILTRATION | -- Select One -- |  |  |  | District Manager | Robert Simmons | 2006-12-13 | (415) 332-0244
4113 | 4 | 1 | Sausalito | 2006-11-15 12:00 | 300 | 0 |  | 2006-11-15 12:00 |  | -- | 19 Park Circle Drive | Marin City | Marin | 94966 |  |  | 2006-11-14 |  |  |  | The subject spill was reported at noon on November 14, 2006. Rex Franklyn, O&M Supervisor, reponded to the call and determined that the cause of the blockage was roots. The line was rodded and the blockage was cleared by 2:30 p.m. The estimated spill rate was 2 gpm. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Sausalito | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | District Manager | Robert Simmons | 2006-11-15 | (415) 332-0244 | rex@smcsd.net, bob@smcsd.net | MINOR
3368 | 3 | 1 | Sausalito | 2006-05-19 08:04 | 100 | 0 |  | 2006-05-19 08:04 |  | -- | 152 Shoreline Drive/in front of Frantoio Restaurant | Mill Valley | Marin | 94941 |  |  | 2006-05-13 |  |  |  | Spill report responded to by Operator Stenvers and blockage cleared by Roys Sewer Service the same day. Follow-up rodding and cleaning work performed on 5/19/06 by Roys Sewer Service | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Sausalito | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Manager | Robert A. Simmons | 2006-05-19 | 415.332.0244 | rex@smcsd.net, bob@smcsd.net | MINOR
2404 | 2 | 1 | Sausalito | 2005-12-31 18:38 | 700 | 0 |  | 2005-12-31 18:38 |  | -- | # 1 Fort Baker Road | Sausalito | Marin | 94966 |  |  | 2005-12-31 |  |  |  | Becauseof high inflow and infiltraion, the influent line energy dissipator box at the plant overflowed. Most of the flow was confined to the plant storm water system, which is captured and treated. A small amount of the influent flow overflow reached a drainage channel and discharge into the bay | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | sausalito | OTHER | Energy Dissipator Box | INFLOW & INFILTRATION | --Select None-- |  |  |  | General Manager | Bob Simmons | 2005-12-31 | 415.332.0244 | rex@smcsd.net, bob@smcsd.net | MINOR
768 | 1 | 1 | Sausalito | 2005-01-05 11:52 | 500 | 0 |  | 2005-01-05 11:52 |  | -- | 3250 Bridgeway at Coloma Street | Sausalito | Marin | 94966 |  |  | 2004-12-27 |  |  |  | On December 27th, a large rain storm hit the bay area. About 4-inches of rain fell in Marin, resulting in significant I/I into the District's conveyance system. A District Maintenance Mechanic observed the overflow which he described as intermittent leakage around the perimeter of the manhole cover, lasting about 10 minutes | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | sausalito | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | General Manager | Robert Simmons | 2005-01-05 | 415.332.0244 | bob@smcsd.net, rex@smcsd.net | MINOR
4040 | 2 | 1 | SausalitoCity | 2006-10-30 12:12 | 60 | 0 |  | 2006-10-30 12:12 |  | -- | BEHIND #71 WOODWARD AVENUE IN THE WOODED AREA. | SAUSALITO | MAIN | 94965 |  |  | 2006-10-24 |  |  |  | CREW CLEARED BLOCKAGAE, BAGGED ROOT MATERIAL FOUND, LIMED AREA, AND REMOVED ANY PAPER PRODUCTS THAT WERE FOUND IN AREA. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SausalitoCity | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SEWER COORDINATOR | LEONARD MICHAELS | 2006-10-30 | (415) 289-4192 | michaels@ci.sausalito.ca.us, dwhitson@ci.sausalito.ca.us | MINOR
2668 | 1 | 1 | SausalitoCity | 2006-01-23 09:52 | 900 | 0 |  | 2006-01-23 09:52 |  | -- | On beach area at intersection of Bridgeway and Valley Street | Sausalito | Marin | 94965 |  |  | 2006-01-23 |  |  |  | Manhole is located on beach area. Overflow went directly into SF Bay. Bagged and retained as much as possible. This line segment is in design at present for replacement. I have directed sewer crew to inspect manhole and main each Monday and Friday until line segment has been replaced and manhole rehabed. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SausalitoCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Sewers Systems Coord | Leonard Michaels | 2006-01-19 | 415-289-4192 | michaels@ci.sausalito.ca.us, dwhitson@ci.sausalito.ca.us | MINOR
3361 | 1 | 4 | SFInternationalAirport | 2006-05-17 10:42 | 2250 | 0 | 06-2177 | 2006-04-11 | Mark Costanzo | SFInternationalAirport | Airfield of Boarding Area A, Gate A2 | San Francisco | San Mateo | 94128 |  |  | 2006-04-11 | 10:30:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | The overflow liquid was dilluted with rain water and was void of solids. |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SFInternationalAirport | MANHOLE | Construction debris (Concrete) looks to have come from the old Cypress Freeway rehab project. | BLOCKAGE | MULTIPLE CAUSES | --Select None-- |  | An overflow was detected coming from a sewer manhole where sewer liquid came from the small holes in the manhole lid and flowed to the nearest catchbasin. It rained hard during the overflow and rain continued after the event. | Utilities Manager | Mark Costanzo | 2006-04-11 | 650-821-7809 | mark.costanzo@flysfo.com | MAJOR | Mark Costanzo | SFIA | 650-642-4798 |  | 676 McDonnell Road | SF | SF | 94128 |  | SFInternationalAirport
4894 | 38 | 1 | SonomaValleyCountySD | 2007-03-12 07:35 | 600 | 0 |  | 2007-03-12 07:35 |  | -- | 19275 Sonoma Highway | Sonoma | Sonoma | 95476 |  |  | 2007-03-10 |  |  |  | Roots in Manhole. Blocked channel. Overflow of 600 gal high est> | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | LM Maint Wk | M. Conachy | 2007-03-12 | 707-527-1892
4614 | 37 | 3 | SonomaValleyCountySD | 2007-01-24 | 1200 | 150 | 07-0546 | 2007-01-24 | Ops | SonomaValleyCountySD | Corner of Herbazal & South Temelec Circle | Sonoma | Sonoma | 95476 |  |  | 2007-01-24 | 0.35417 | [6 empty] | Low |  | STORM DRAIN | No |  | No | No | Overflow traveled across street into drop box. Drop boxes and drainage system contained dirt and leaves through out the system. Much of this was vac up from the drop boxes. |  | Yes | Yes | No |  |  | No | No |  |  |  | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | -- Select One -- | -- Select One -- |  | Crew open main and cleaned up street and vac out Drop Boxes ( debris held back by Mh lid). Crew followed drainage system and vac out any drop boxes that held water and or mud. An operator arrived on site and inspected all culverts or drainage ditches dumping into the creek (a couple 1000 ft away)looking for any signs of discharge from overflow. None was found. This section of line that stopped up was last cleaned on 1-6-05. Line that stopped up will be videoed as a precaution. | Lead Maint. Wk | Michael J Conachy Sr | 2007-01-24 | 707-547-1062
3890 | 36 | 3 | SonomaValleyCountySD | 2006-09-18 08:58 | 22 | 0 | 06-5484 | 2006-09-15 | M. Conachy | SonomaValleyCountySD | Corner of East Napa St & Third St East | Sonoma | Sonoma | 95476 |  |  | 2006-09-14 | 7:30:00 AM | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | Yes | Water was clear, No signs of any debri. Depth of creek was about 3 to 6 inches deep and 1 to 4 feet across in places, moving at about a foot every 3 secs. |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SonomaValleyCountySD | PIPE | Hair line crack in main which dripped into concrete 30 inch storm drain. | INFRASTRUCTURE FAILURE | --Select None-- | BREAKAGE OF COLLECTION SYSTEM | Hair line crack in main which dripped into concrete 30 inch storm drain. | Main line was laid on top of concrete 30inch storm drain. The concrete 30 inch storm drain was cut so mainline could fit. (Unknown when this was done. This was done years ago) Mainline developed a hair line crack which drip at a rate of 12 drops per minute. The culvert was dry except for sewage that dripped into the storm drain which caused an odor. (On a few occasions the storm drain was flowing with water from local lawn irrigation.) Once problem was found manhole upstream was plugged to stop sewage from flowing into main, this stopped the sewer from dripping into the storm drain. A plug was also set into the storm drain to contain any overflow that may occur in the storm drain. The main is being repaired on 9-18-06. The concrete 30 inch storm drain will then be flushed and vac out with the Vac truck to insure nothing gets into the creek. | Lead Maint. | Michael J Conachy Sr | 2006-09-15 | 707-547-1062 | roni@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, misom@sonoma-county.org, kbooker@scwa.ca.gov | MAJOR | Ken Goddard | Sonoma County Water Agency | 707-521-1892 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95407 |  | SonomaValleyCountySD
3310 | 35 | 1 | SonomaValleyCountySD | 2006-05-08 07:49 | 300 | 0 |  | 2006-05-08 07:49 |  | -- | 1254 Broadway | Sonoma | Sonoma | 95476 |  |  | 2006-05-08 |  |  |  | Line was last cleaned on 9-05. No signs of gravel at that time. Stoppage caused by gravel. Since the last time line was cleaned, new lines have been added. Believed gravel was flushed down into our lines from construction on new lines. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SonomaValleyCountySD | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | Lead Maint. | M Conachy | 2006-05-08 | 707-547-1062 | roni@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, misom@sonoma-county.org, kbooker@scwa.ca.gov, mconachy@scwa.ca.gov | MINOR
3277 | 34 | 1 | SonomaValleyCountySD | 2006-05-03 17:05 | 400 | 0 | 06-2669 | 2006-05-03 | M.Conachy |  | Corner of 4th Street East and East Spain Street | Sonoma | County | 95476 |  |  | 2006-05-03 | 3:45:00 PM | 2006-05-03 | 4:20:00 PM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Lead Maint. Wk | Michael J Conachy Sr | 2006-05-03 | 707-547-1062 | roni@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, misom@sonoma-county.org, kbooker@scwa.ca.gov, mconachy@scwa.ca.gov | 24HR |  |  | 707-547-1062 | [6 empty] | SonomaValleyCountySD
3163 | 33 | 3 | SonomaValleyCountySD | 2006-04-13 08:19 | 10500 | 0 | 06-2217 | 2006-04-13 | Mike Conachy | SonomaValleyCountySD | Penngrove lift station 49 Ely Road (Note: Penngrove CSD, not SVCSD) | Penngrove | Sonoma | 94951 |  |  | 2006-04-11 | 10:13:00 P | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | GROUND WATER IMPACTED | No |  | No | No | I&I due to Severe Weather and flooding. Lichua Creek jumped its banks. 5 to 10+ above normal. Running at 15-20ft per Lichua Creek jumped its banks. 5 to 10+ above normal. Running at 15-20ft per sec |  | No | No | No | No | No | Yes | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | When Tech arrived to take samples there was no signs of a spill. Pump readings at Op’s desk showed there should have been a spill. The assumption was made a spilled occurred because of the readings even though there were no signs of one.. UPDATED NUMBERS FROM REPORT #3162 | Lead Maint. Wk | Michael J Conachy Sr | 2006-04-13 | 707-547-1062 | roni@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, misom@sonoma-county.org, kbooker@scwa.ca.gov | MAJOR | Ken Goddard | Sonoma County Water Agency | 707-547-1062 |  | 2150 College Ave | Santa rosa | Sonoma | 95401 |  | SonomaValleyCountySD
2934 | 32 | 5 | SonomaValleyCountySD | 2006-03-06 11:02 | 3900 | 0 | 06-1380 | 2006-03-06 | Mike Conachy | SonomaValleyCountySD | 27 Ely Rd | Penngrove | Sonoma | 94951 |  |  | 2006-03-06 | 2:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | SURFACE WATER IMPACT | No |  | No | No | Lichau Creek up by 5 to 10+ feet moving at 20+ ft per sec. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SonomaValleyCountySD | PUMP STATION |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- | Heavy rains and flooding. | Due to sever storm and some flood, sewer system (including L/S) was over whelmed. | Lead Maint. Wk. | Michael J Conachy Sr | 2006-03-06 | 707-547-1062 | roni@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, misom@sonoma-county.org, kbooker@scwa.ca.gov | MAJOR | Ken Goddard | Sonoma county Water Agency | 707-547-1062 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95407 |  | SonomaValleyCountySD
2893 | 31 | 3 | SonomaValleyCountySD | 2006-02-28 10:03 | 3180 | 0 | 061199 | 2006-02-27 | Mike Conachy | SonomaValleyCountySD | Near 27 Ely Rd | Penngrove | Sonoma | 94951 |  |  | 2006-02-27 | 10:45:00 A | [5 empty] | RAINY WEATHER | Low |  | SURFACE WATER IMPACT | No |  | No | Yes | Lichau Creek up by 10+ feet moving at 20+ ft per sec. |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SonomaValleyCountySD | PUMP STATION |  | NATURAL DISASTER | --Select None-- | --Select None-- | Heavy rains and flooding. | Due to sever storm and flooding, sewer system (including L/S) was over whelmed. | Lead Maint | Michael J Conachy Sr | 2006-02-27 | 707-547-1062 | roni@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, misom@sonoma-county.org, kbooker@scwa.ca.gov | MAJOR | Ken Goddard | Sonoma county Water Agency | 707-547-1062 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95407 |  | SonomaValleyCountySD
2766 | 30 | 2 | SonomaValleyCountySD | 2006-02-07 08:25 | 350 | 0 | 06-0739 | 2006-02-07 | M. Conachy | SonomaValleyCountySD | 4th St East/ East Spain St | Sonoma | Sonoma | 95476 |  |  | 2006-02-03 | 1:05:00 PM | [5 empty] | CLOUDY WEATHER | Low |  | STORM DRAIN | No |  | No | No | Creek up by 1ft then normal traveling at 10ft per sec. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE | System overwhelmed, possibly from Sebastiani Winery discharge. | FLOW CAPACITY DEFICIENCY | --Select None-- | --Select None-- |  | Overflow stopped before crew arrived. Unclear whether overflow reached creek. Creek was up and moving to fast for samples. ALL OVERFLOW and GPM discharge numbers on report are strictly est. There was no standing water, only a stain in the street that may have been caused by recent overflow (street was already dry). Crew took measurement of stain and est. overflow. Crew also ran main to make sure there was no resrictions. None was found. | Lead Maint | Michael J Conachy Sr | 2006-02-07 | 707-547-1062 | roni@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, misom@sonoma-county.org, kbooker@scwa.ca.gov | MAJOR | Ken Goddard | Sonoma County Water Agency | 547-1062 |  | 2150 W. College Ave | Santa Rosa | Sonoma | 95407 |  | SonomaValleyCountySD
2437 | 26 | 3 | SonomaValleyCountySD | 2006-01-03 09:20 | 1800 | 0 | 06-0055 | 2006-01-02 | Hagwood | SonomaValleyCountySD | Near 628 Craig Ave | Boyes Hot Spring | Sonoma | 95416 |  |  | 2006-01-02 | 10:15:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Low | Sonoma Creek | STORM DRAIN | No |  | No | No | Creek was up by 15-20 ft running at approx 20ft per sec. |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- | Also I&I in system. | Heavy storms in area for past few days. Causing I&I in line. Grease was also found (listed as cause). Overfow dumped directly into DI which dumped into Sonoma Creek which was 15 to 20 ft higher then normal. Running at 20+ ft per sec. Samples were taken. This section of line was cleaned first weeks of Dec. 2005 | Lead Maint | Michael J Conachy Sr | 2006-01-03 | 707-547-1062 | roni@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, SCAREY@sonoma-county.org, kbooker@scwa.ca.gov, mconachy@scwa.ca.gov | MAJOR | Ken Goddard | Sonoma County Water Agency | 707-521-1892 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95407 |  | SonomaValleyCountySD
2505 | 24 | 2 | SonomaValleyCountySD | 2006-01-04 15:35 | 10200 | 0 | 06-7615 | 2006-01-02 | Ken Goddard | SonomaValleyCountySD | 4th ST E & East Spain St | Sonoma | Sonoma | 95476 |  |  | 2005-12-31 | 10:30:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | GROUND WATER IMPACTED | No |  | No | No | Creek was up 8ft and running at 15+ ft per sec. |  | Yes | Yes | No | No | No | Yes | No | No | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- | Severe storms and flooding | Due to severe storms and flooding. System was overwhelmed Area posted. Once overflow ceased area was rinsed and vac up. | WA Coordinator | Ken Goddard | 2006-01-02 | 707 521-1892 | roni@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, SCAREY@sonoma-county.org, kbooker@scwa.ca.gov | MAJOR | Ken Goddard | Sonoma county water Agency | 707 521-1892 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95407 |  | SonomaValleyCountySD
2521 | 22 | 2 | SonomaValleyCountySD | 2006-01-05 13:45 | 58500 | 0 | 06-7615 | 2006-01-02 | Ken Goddard | SonomaValleyCountySD | Bokman Place | Boyes Hot Springs | Sonoma | 95476 |  |  | 2005-12-31 | 6:13:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | Yes | Sonoma Creek was up 25+ ft and running at 35+ per sec. |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- | Severe storms and flooding | Due to severe storms and flooding. System was overwhelmed Overflow was controlled and posted. Once overflow ceased area was rinsed and vac up. | WA Coordinator | Ken Goddard | 2006-01-02 | 707-521-1892 | roni@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, SCAREY@sonoma-county.org, kbooker@scwa.ca.gov | MAJOR | Ken Goddard | Sonoma county water Agency | 707-521-1892 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95407 |  | SonomaValleyCountySD
2508 | 25 | 3 | SonomaValleyCountySD | 2006-01-04 16:28 | 10200 | 0 | 06-7616 | 2006-01-02 | Ken Goddard | SonomaValleyCountySD | 18880 Meadow Brook Park (private system) | Boyes Hot Springs | Sonoma | 95476 |  |  | 2005-12-31 | 10:30:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | GROUND WATER IMPACTED | No |  | No | No | Creek was up 8+ ft and running at 20+ per sec. |  | Yes | Yes | No | No | No | Yes | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE | Severe storms and flooding | INFLOW & INFILTRATION | --Select None-- | --Select None-- | Severe storms and flooding | Due to severe storms and flooding. System was overwhelmed Overflow was controlled and posted. Once overflow ceased area was rinsed and vac up. | WA Coordinator | Ken Goddard | 2006-01-02 | 707 521-1892 | mconachy@scwa.ca.gov, rdp@scwa.ca.gov | MAJOR | Ken Goddard | Sonoma county water Agency | 707 521-1892 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95407 |  | SonomaValleyCountySD
2448 | 23 | 5 | SonomaValleyCountySD | 2006-01-03 16:06 | 56250 | 0 | 06-7615 | 2006-01-02 | Ken Goddard | SonomaValleyCountySD | 18579 Happy Lane | Boyes Hot Springs | Sonoma | 95476 |  |  | 2005-12-31 | 6:30:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | Sonoma Creek raised by 15-20 ft running at 20+ft per sec. |  | No | No | No | No | No | Yes | Yes | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE | Severe weather, flooding | INFLOW & INFILTRATION | --Select None-- | --Select None-- | Severe weather, flooding | Due to heavy weather and flooding, system was overwhelmed. Overflow was controled into DI | WA Coordinator | Ken Goddard | 2006-01-02 | 707 521-1892 | roni@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, SCAREY@sonoma-county.org, kbooker@scwa.ca.gov | MAJOR | Ken Goddard | Sonoma County Water Agency | 707 521-1892 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95407 |  | SonomaValleyCountySD
2450 | 28 | 2 | SonomaValleyCountySD | 2006-01-03 16:34 | 288000 | 0 | 05-7550 | 2005-12-30 | Tyler | SonomaValleyCountySD | 200 Fuente Ln | Boyes | Sonoma | 95416 |  |  | 2005-12-30 | 8:00:00 PM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | Sonoma creek raised 20+ ft, water flow at 15+ ft per sec. |  | No | No | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- | Severe weather and flooding | Due to severe weather and flooding system was over whelmed. Overflow was controled into DI. | Lead Maint. | Michael J Conachy Sr | 2006-01-03 | 707-547-1062 | roni@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, SCAREY@sonoma-county.org, kbooker@scwa.ca.gov | MAJOR | Ken Goddard | Sonoma County water Agency | 707-523-1070 |  | 2150 West college Ave | Santa rosa | Sonoma | 95407 |  | SonomaValleyCountySD
2489 | 29 | 2 | SonomaValleyCountySD | 2006-01-04 14:20 | 79500 | 0 | 05-7547 | 2006-01-04 | M Conachy | SonomaValleyCountySD | 395 Bokman Pl | Boyes | Sonoma | 95416 |  |  | 2005-12-30 | 5:47:00 PM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | GROUND WATER IMPACTED | No |  | No | Yes | Sonoma Creek was up by 20+ft and running at15+ft per sec. |  | Yes | Yes | No | No | No | Yes | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- | Severe Storm and flooding. | Due to severe storms and flooding. System was overwhelmed Overflow was controlled and posted. Once overflow ceased, area was rinsed and vac up. (24 hr and this report late. efforts were into returning system to normal operation conditions) | Lead Maint. | Michael J Conachy Sr | 2006-01-04 | 707-547-1062 | roni@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, SCAREY@sonoma-county.org, kbooker@scwa.ca.gov | MAJOR | Ken Goddard | Sonoma county water Agency | 707-521-1892 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95407 |  | SonomaValleyCountySD
2443 | 27 | 3 | SonomaValleyCountySD | 2006-01-03 14:20 | 400950 | 0 | 05-7553 | 2006-01-03 | Ops | SonomaValleyCountySD | 27 Ely Rd | Penngrove | Sonoma | 94951 |  |  | 2005-12-30 | 10:00:00 P | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | SURFACE WATER IMPACT | No |  | No | No | Lichua Creek jumped its banks. 10+ above normal. Running at 15-20ft per sec |  | No | No | No | No | No | Yes | Yes | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SonomaValleyCountySD | PUMP STATION | I&I due to Severe Weather and flooding. | INFLOW & INFILTRATION | --Select None-- | --Select None-- | I&I due to Severe Weather and flooding. | Due to sever storm and flooding, sewer system was over whelmed. ( 24 hr report late due to number of reports caused by storm.) | Lead Maint. | Michael J Conachy Sr | 2006-01-03 | 707-547-1062 | roni@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, SCAREY@sonoma-county.org, kbooker@scwa.ca.gov | MAJOR | Ken Goddard | Sonoma County Water Agency | 707-523-1070 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95407 |  | SonomaValleyCountySD
2380 | 20 | 1 | SonomaValleyCountySD | 2005-12-29 13:45 | 30 | 0 |  | 2005-12-29 13:45 |  | -- | 200 Fuente Lane | Aqua Caliente | Sonoma | 95476 |  |  | 2005-12-29 |  |  |  | Overflow was not witnessed, only evidence of a burp. Site cleaned up. Surrounding area wet from days of rain. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SonomaValleyCountySD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | WA Coordinator | Ken Goddard | 2005-12-29 | 707 521-1892 | mconachy@scwa.ca.gov, rdp@scwa.ca.gov | MINOR
2495 | 21 | 2 | SonomaValleyCountySD | 2006-01-04 15:02 | 38000 | 28000 | 05-7520 | 2005-12-30 | Dale Dunlap | SonomaValleyCountySD | 977 West Napa St. | Sonoma | Sonoma | 95746 |  |  | 2005-12-29 | 10:30:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | SURFACE WATER IMPACT | No |  | No | No | Sonoma Creek was up 25+ ft and running at 35+ per sec |  | Yes | Yes | No | No | No | Yes | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SonomaValleyCountySD | PIPE | Construction company broke capped line. | INFRASTRUCTURE FAILURE | --Select None-- | BREAKAGE OF COLLECTION SYSTEM | Construction company broke capped line. | While digging to install footing for new bridge, construction company hit a capped of abandon line. | WA Coodinator | Ken Goddard | 2005-12-30 | 707-521-1892 | roni@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, SCAREY@sonoma-county.org, kbooker@scwa.ca.gov | MAJOR | Ken Goddard | Sonoma county water Agency | 707-521-1892 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95407 |  | SonomaValleyCountySD
2490 | 16 | 2 | SonomaValleyCountySD | 2006-01-04 14:28 | 58500 | 0 | 05-7499 | 2005-12-29 | Jim Zambenini | SonomaValleyCountySD | 18579 Happy Lane | Sonoma | Sonoma | 95476 |  |  | 2005-12-28 | 1:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | GROUND WATER IMPACTED | No |  | No | Yes | spill went to DI then to Sonoma Creek. High volume of water flowing in creek. |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE | Severe storms and flooding | INFLOW & INFILTRATION | --Select None-- | --Select None-- | Severe storms and flooding | Due to severe storms and flooding. System was overwhelmed Overflow was controlled and posted. Once overflow ceased area was rinsed and vac up. | WA Coordinator | Ken Goddard | 2005-12-29 | 707 521-1892 | roni@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, SCAREY@sonoma-county.org, kbooker@scwa.ca.gov | MAJOR | Ken Goddard | Sonoma County Water Agency | 707-521-1892 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95406 |  | SVCSD | 707 523-1070 |  | keng@scwa.ca.gov | Santa Rosa | Sonoma | 95401
2511 | 18 | 2 | SonomaValleyCountySD | 2006-01-05 10:39 | 10800 | 0 | 05-7504 | 2005-12-29 | Dale Dunlap | SonomaValleyCountySD | 18880 Meadow Brook Park (private system) | Boyes Hot Springs | Sonoma | 95476 |  |  | 2005-12-28 | 3:44:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | GROUND WATER IMPACTED | No |  | No | Yes | Creek was up 8ft and running at 20ft per sec |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- | Severe storms and flooding | Due to severe storms and flooding. System was overwhelmed Overflow was controlled and posted. Once overflow ceased, area was rinsed and vac up. ( This report late. efforts were into returning system to normal operation conditions) | WA Coordinator | Ken Goddard | 2005-12-29 | 707-521-1892 | roni@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, SCAREY@sonoma-county.org, kbooker@scwa.ca.gov | MAJOR | Ken Goddard | Sonoma county water Agency | 707-521-1892 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95407 |  | SonomaValleyCountySD
2520 | 19 | 2 | SonomaValleyCountySD | 2006-01-05 13:33 | 63000 | 0 | 05-7484 | 2005-12-29 | Dale Dunlap | SonomaValleyCountySD | 588 Bokman Place | Boyes Hot Springs | Sonoma | 95476 |  |  | 2005-12-28 | 10:13:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | Yes | Sonoma Creek was up 25+ ft and running at 35+ per sec |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- | Severe storms and flooding | Sonoma Creek was up 25+ ft and running at 35+ per sec. | WA Coordinator | Ken Goddard | 2005-12-29 | 707-521-1892 | roni@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, SCAREY@sonoma-county.org, kbooker@scwa.ca.gov | MAJOR | Ken Goddard | Sonoma county water Agency | 707-521-1892 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95407 |  | SonomaValleyCountySD
2599 | 17 | 2 | SonomaValleyCountySD | 2006-01-11 08:39 | 9900 | 0 | 05-7483 | 2005-12-29 | Dale Dunlap | SonomaValleyCountySD | Penngrove lift station 25 Ely Road | Penngrove | Sonoma | 94951 |  |  | 2005-12-28 | 10:00:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | SURFACE WATER IMPACT | No |  | No | No | Lichua Creek jumped its banks. 10+ above normal. Running at 15-20ft per sec. |  | No | No | No | No | No | Yes | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- | I&I due to Severe Weather and flooding. | Due to sever storm and flooding, sewer system was over whelmed | WA Coordinator | Ken Goddard | 2005-12-29 | 707-521-1892 | roni@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, misom@sonoma-county.org, kbooker@scwa.ca.gov | MAJOR | Ken Goddard | Sonoma county Water Agency | 707 521-1892 |  | 2150 West College Ave | Santa Rosa | Sonoma | 94951 |  | SonomaValleyCountySD
2335 | 15 | 1 | SonomaValleyCountySD | 2005-12-27 10:18 | 1800 | 0 | 05-7445 | 2005-12-26 | Dale Dunlap | SonomaValleyCountySD | 710 Arroyo | Sonoma | Sonoma | 95476 |  |  | 2005-12-26 | 10:30:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | SURFACE WATER IMPACT | No |  | No | No | spill went to DI then to Creek. High volume of water flowing in creek. |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES | --Select None-- | Roots and Grease |  | WA Coordinator | Ken Goddard | 2005-12-27 | 707 521-1892 | keng@scwa.ca.gov | MAJOR | Michael Conachy | Sonoma County Water Agency | 707-547-1062 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95406 |  | SVCSD | 707 523-1070 |  | keng@scwa.ca.gov | Santa Rosa | Sonoma | 95457
2218 | 14 | 3 | SonomaValleyCountySD | 2005-12-05 14:21 | 850 | 800 | 05-7003 | 2005-12-05 | Hody Wilson | SonomaValleyCountySD | Near Corner of Greger St & Boyes Blvd | Boyes | Sonoma | 95416 |  |  | 2005-12-04 | 10:45:00 A | [5 empty] | SUNNY WEATHER | Low | Sonoma Creek | STORM DRAIN | No |  | No | No | Overflow left Mh traveled 15ft to DI. DI dumps into Sonoma Ck 1500 feet away. Once line was open. Vac truck set up at end of DI and Vac up all of water leaving DI. Street was washed down and Vac up. No debris left sewer system. Mh cover held back debris. Sonoma Creek and water leaving DI were tested. Results not back. Unclear if overflow actully reached Sonoma Creek. SPILL UNDER 1000 GALS. |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE | New construction going on in area. Although grease was in the line, gravel and dirt may have also been factor in SSO. Line was last cleaned 1-12-05. SPILL UNDER 1000 GALS.---- ON 12-5-05 A FOLLOW UP WAS DONE ON LINE THAT STOPPAGE ACCURED IN ON 12-04-05. CREW RAN LINE AGAIN AND FORCED OUT A FLASHLIGHT FROM LINE. THIS WAS MAJOR CAUSE OF STOPPAGE. | BLOCKAGE | GREASE | --Select None-- |  | SPILL UNDER 1000 GALS. Filled out wrong form for RWQCBSFBR. Crew opened up line that was restricted. Vac up all overflow that could be reached in DI and set up at end of DI outlet before water dumps into creek and vac up water from there. Although crew were unclear on whether overflow reached Sonoma Creek 1500 ft away, crew treated it as if it did and had water tested and took all necessary steps. This section of line was last cleaned 1-12-05. Although some grease was found in the line, crew also notices dirt and gravel. Suspect this to be from recent construction in area and new lines added to the system these past 6 months. ON 12-5-05 A FOLLOW UP WAS DONE ON LINE THAT STOPPAGE ACCURED IN ON 12-04-05. CREW RAN LINE AGAIN AND FORCED OUT A FLASHLIGHT FROM LINE. THIS WAS MAJOR CAUSE OF STOPPAGE. | Lead Maint. Wk | Michael J Conachy Sr | 2005-12-05 | 707-547-1062 | mconachy@scwa.ca.gov, roni@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, SCAREY@sonoma-county.org, kbooker@scwa.ca.gov | MAJOR | Ken Goddard | Sonoma County Water Agency | 707-523-1892 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95407 |  | SonomaValleyCountySD | 707-5231070
2091 | 13 | 2 | SonomaValleyCountySD | 2005-11-07 14:40 | 90 | 0 |  | 2005-11-07 14:40 |  | -- | 19275 Sonoma Hwy | Sonoma | Sonoma | 95476 |  |  | 2005-10-25 |  |  |  | After reevaluating the stoppage the next day on a follow up. Taken into account they amount of flow, area of flow and absorption area (dirt) and distant flow had to travel, a more realist estimate (on the high side) is 80 to 90 gals total overflow | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SonomaValleyCountySD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Coordinator | Ken Goddard | 2005-10-25 | 707 521-1892 | keng@scwa.ca.gov, rdp@scwa.ca.gov | MINOR
659 | 9 | 1 | SonomaValleyCountySD | 2004-12-28 09:51 | 4200 | 0 | 04-6826 | 2004-12-28 | Ken Goddard |  | Vailletti & Casa Bella Dr | Sonoma | Sonoma | 95476 |  |  | 2004-12-27 | 12:30:00 P | 2004-12-28 | 2:00:00 AM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | WA Coordinator | Ken Goddard | 2004-12-28 | 707 521-1892 | edean@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, SCAREY@sonoma-county.org | 24HR |  |  | 707 521-1892 | [6 empty] | SonomaValleyCountySD
724 | 10 | 2 | SonomaValleyCountySD | 2005-01-03 15:38 | 139500 | 0 | 04-6825 | 2004-12-28 | Ken Goddard | SonomaValleyCountySD | 18579 Happy Lane | Sonoma | Sonoma | 95476 |  |  | 2004-12-27 | 10:35:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Low | Sonoma Creek | SURFACE WATER IMPACT | No |  | No | Yes | Due to heavy rains in the past 2 days, Sonoma Creek raised 4 to 5 feet and was rushing at about 10 to 15 per sec |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | Due to heavy rains in the past 2 days (4 inches of rain fall in 36 hrs) system became charged with I&I. Mh97-7 overflowed onto the street traveling 2 to 3 feet into a DI. Due to the amount of overflow caused by I&I, crew was unable to contain. Using woddles, sandbags, the crew was able to control the flow into the DI. A barricade was placed on the manhole and area posted.. Once system returned to normal, the area was picked up and effected area was washed down and rinse water and debris was vac up. Time is estimated that overflow ceased at mid-night. Estimated overflow ceased time was figured by taking the flow readings coming into the plant. Overflow could have stopped before mid-night or a little after. | Lead Maint. Worker | Mike Conachy | 2005-01-03 | 707 547-1062 | edean@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov | MAJOR | Ken Goddard | SCWA | 707 521-1892 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95407 |  | SonomaValleyCountySD
732 | 7 | 2 | SonomaValleyCountySD | 2005-01-03 16:06 | 153000 | 75 | 04-6827 | 2004-12-28 | Ken Goddard | SonomaValleyCountySD | 598 Bokman Place | Sonoma | Sonoma | 95476 |  |  | 2004-12-27 | 8:45:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low | Sonoma Creek | SURFACE WATER IMPACT | No |  | No | Yes | Due to heavy rains in the past 2 days, Sonoma Creek raised 4 to 5 feet and was rushing at about 10 to 15 per sec. |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | Due to heavy rains in the past 2 days (4 inches of rain fall in 36 hrs) system became charged with I&I. Mh78-24 overflowed on the street (at the end of Bokman Pl.) and into DI. Due to the amount of overflow caused by I&I, crew was unable to contain. Using woddles, sandbags and sheets of plywood the crew were able to control the flow into the DI. The street that was affected by the overflow was washed into control area. The control area was also covered for further protection. Area was posted at manhole and at DI. Although overflow stopped at 24:00 on the 27th, woddles, sandbags and sheets of plywood (along with the postings) were left in place for the next few days due to more rain forecasted. However, overflow did not reoccur. Once the risk of further overflow was gone, the area was picked up and effected area was washed down and rinse water and debris was vac up. Time is estimated that overflow ceased at mid-night. Estimated overflow ceased time was figured by taking the flow readings coming into the plant. Overflow could have stopped before mid-night or a little after. Visual inspection was done during the day for the next few days. No signs of reoccurs of the overflow. | Lead Maint. Worker | Mik Conachy | 2005-01-03 | 707 547-1062 | edean@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov | MAJOR | Ken Goddard | SCWA | 707 521-1892 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95407 |  | SonomaValleyCountySD
736 | 12 | 2 | SonomaValleyCountySD | 2005-01-04 08:51 | 46000 | 0 | 04-6784 | 2004-12-28 | Ken Goddard | SonomaValleyCountySD | Penngrove lift station 49 Ely Road (Note: Penngrove CSD, not SVCSD) | Penngrove | Sonoma | 94951 |  |  | 2004-12-27 | 10:23:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Low | Lichau Creek | SURFACE WATER IMPACT | No |  | No | Yes | Due to heavy rains in the past 2 days, Lichau Creek raised 4 to 5 feet and was rushing at about 10 to 15 per sec. |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | Due to heavy rains in the past 2 days (4 inches of rain fall in 36 hrs), system became charged with I&I. The lift station was unable to keep up with the inflow causing the system to back up. Once the system back up, 2 manholes before the lift station began to overflow and dumping onto the ground then combining with run off water from the storm, ran into Lichua Creek. Due to the amount of overflow caused by I&I, crew was unable to contain overflow. Because the area involved was a grassy field area with thick brush in some areas there was no direct contact or risk to the public. During overflow area was barricade and posted. Once system returned to normal, the area was picked up and effected area was washed down, racked and rinse water and debris was vac up. Time is estimated that overflow ceased at mid-night. Estimated overflow ceased time was figured by taking the flow meter readings coming into the lift station. Overflow may have stopped before mid-night or a little after. Visual inspection was done through out the next day. No reoccurs of the overflow occurred. | Lead Maint. Worker | Mike Conachy | 2005-01-04 | 707 547-1062 | edean@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov | MAJOR | Ken Goddard | SCWA | 707 521-1892 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95448 |  | SonomaValleyCountySD
725 | 11 | 3 | SonomaValleyCountySD | 2005-01-03 15:39 | 25500 | 0 | 04-6828 | 2004-12-28 | Ken Goddard | SonomaValleyCountySD | intersection of 4th St E & E Spain St | Sonoma | Sonoma | 95476 |  |  | 2004-12-27 | 9:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low | Natheson Creek | SURFACE WATER IMPACT | No |  | No | Yes | Due to heavy rains in the past 2 days, Natheson Creek raised 3 to 4 feet and was rushing at about 10 to 15 per sec. |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | Due to heavy rains in the past 2 days (4 inches of rain fall in 36 hrs), system became charged with I&I. Mh139-7 on the corner of East Spain & 4th St East overflowed, traveled across street down curb into DI which dumped into Natheson Ck.. Due to the amount of I&I we were unable to contain overflow. Because of location of overflow we could not control path of overflow. To do so would have caused a traffic hazard. A barricade was placed on the manhole, along with cones placed around manhole and barricade. Area was posted at manhole and curb. The next day, the area was picked up and effected area was washed down and rinse water and debris was vac up. Time is estimated when overflow ceased at mid-night. Estimated overflow ceased time was figured by taking the flow readings coming into the plant. Overflow could have stopped before mid-night or a little after. | Lead Maint. Worker | Mike Conachy | 2005-01-03 | 707 547-1062 | edean@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov | MAJOR | Ken Goddard | SCWA | 707 521-1892 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95407 |  | SonomaValleyCountySD
728 | 6 | 3 | SonomaValleyCountySD | 2005-01-03 15:42 | 9000 | 0 | 04-6824 | 2004-12-28 | Ken Goddard | SonomaValleyCountySD | 18715 Sonoma HWY | Sonoma | Sonoma | 95476 |  |  | 2004-12-27 | 11:15:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Low | Sonoma Creek | SURFACE WATER IMPACT | No |  | No | Yes | Due to heavy rains in the past 2 days, Sonoma Creek raised 4 to 5 feet and was rushing at about 10 to 15 per sec |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | Within 36 hrs 4 inches of rain dropped. Because of the heavy rains the system became charged with I&I. Due to the amount of I&I, we were unable to contain overflow. However the overflow was controlled with the use of woddles and sandbags for the public safety. Area was also posted. Once system returned to normal, effected area was picked up and washed down. All rinse water and remaining debris was vac up. | Lead Maint. Worker | Mike Conachy | 2005-01-03 | 707 547-1062 | edean@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov | MAJOR | Ken | Goddard | 707 523-1070 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95407 |  | SonomaValleyCountySD
727 | 8 | 5 | SonomaValleyCountySD | 2005-01-03 15:41 | 4200 | 0 | 04-6826 | 2004-12-28 | Ken Goddard | SonomaValleyCountySD | Vailetti / Casabella Drive | Sonoma | Sonoma | 95476 |  |  | 2004-12-27 | 12:30:00 P | [5 empty] | RAINING FOR SEVERAL DAYS | Low | Sonoma Creek | STORM DRAIN | No |  | No | Yes | Due to heavy rains in the past 2 days, Sonoma Creek raised 4 to 5 feet and was rushing at about 10 to 15 per sec |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SonomaValleyCountySD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | Within 36 hrs 4 inches of rain dropped. Because of the heavy rains the system became charged with I&I. Due to the amount of I&I, we were unable to contain overflow. However the overflow was controlled with the use of woddles and sandbags for the public safety. Area was also posted. Once system returned to normal, effected area was picked up and washed down. All rinse water and remaining debris was vac up. | Lead Maint. | Mike Conachy | 2005-01-03 | 707 547-1062 | edean@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov | MAJOR | Ken Goddard | SCWA | 707 521-1892 |  | 2150 West College | Santa Rosa | Sonoma | 95407 |  | SonomaValleyCountySD
591 | 5 | 1 | SonomaValleyCountySD | 2004-12-20 08:43 | 480 | 0 |  | 2004-12-20 08:43 |  | -- | 312 5th St. West | Sonoma | Sonoma | 95476 |  |  | 2004-12-19 |  |  |  | Crew ran main line in front of address with the affected property line clean out that was overflowing. Nothing was pulled back that appeared it would have caused a stoppage. Rags did appear once charged line began to drain and drop to normal. This may have been cause. Follow up on this line was done on 12-20-04. This section of main line was last cleaned on 11-22-04, one month before this incident. Overflow flowed into DI. The overflow then absorbed into the dirt that was in the DI and the storm drain pipe. DI was rinsed and vac out. All the areas where the overflow made contact on the street and gutter, was rinsed down and vac up. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SonomaValleyCountySD | CLEAN OUT | Property Line C/O | BLOCKAGE | DEBRIS |  |  |  | Lead Maint. Worker | Michael J Conachy Sr | 2004-12-20 | 707-547-1062 | edean@scwa.ca.gov, keng@scwa.ca.gov, hody@scwa.ca.gov, jdz@scwa.ca.gov, mconachy@scwa.ca.gov | MINOR
508 | 4 | 2 | SonomaValleyCountySD | 2004-12-13 09:17 | 13500 | 0 | 04-6408 | 2004-12-08 | M. Conachy | SonomaValleyCountySD | Corner of 4th Street East & East Spain street | Sonoma | Sonoma | 95476 |  |  | 2004-12-08 | 8:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | SURFACE WATER IMPACT | No |  | No | Yes | Natheson Ck raised by 2 to 3 feet. Rushing at 10 to 15 feet per sec. |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jyl@rb2.swrcb.ca.gov | SonomaValleyCountySD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | MULTIPLE CAUSES |  | Due to heavy rains in the past 3 days, system became charged with I&I. Mh139-7 on the corner of East Spain & 4th St East overflowed, traveled across street down curb into DI which dumped into Natheson Ck. Due to the amount of I&I we were unable to contain overflow. Because of location of overflow we could not control path of overflow. To do so would have caused a traffic hazard. A barricade was placed on the manhole, along with cones placed around manhole and barricade. Area was posted at manhole and curb. Area was monitored until overflow stopped. The next day, once the overflow stopped and system returned to normal, the area was picked up and effected area was washed down and rinse water vac up. NO SOLIDS ESCAPED SYSTEM. Solids were held back by manhole lid. | Lean Maint. Worker | Michael J Conachy Sr | 2004-12-08 | 707-547-1062 |  | MAJOR | Michael Conachy | Sonoma County Water Agency | 707-547-1062 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95406 |  | SonomaValleyCountySD
512 | 1 | 2 | SonomaValleyCountySD | 2004-12-13 10:24 | 750 | 0 | 04-6410 | 2004-12-08 | M. Conachy | SonomaValleyCountySD | 18519 Happy Ln | Boyes Hot Springs | Sonoma | 95416 |  |  | 2004-12-08 | 12:00:00 P | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | SURFACE WATER IMPACT | No |  | No | Yes | Due to rains in the past 3 days, Sonoma Creek raised 4 to 5 feet and was rushing at about 10 to 15 per sec. |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jyl@rb2.swrcb.ca.gov | SonomaValleyCountySD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | LEAKS OF COLLECTION SYSTEM |  | Due to heavy rains in the past 3 days, system became charged with I&I. Mh97-7 overflowed onto the street traveling 2 to 3 feet into a DI. Crew found the problem. Due to the amount of overflow caused by I&I, crew was unable to contain. Using woddles, sandbags, the crew were able to control the flow into the DI. A barricade was placed on the manhole and area posted. . Although overflow stopped at 14:30, woddles, sandbags and postings were left in place until the next day. Area was then picked up and rinsed down. All rinse water was vac up. NO SOLIDS ESCAPED SYSTEM. Solids were held back by manhole lid | Lead Maint. Worker | Michael J Conachy Sr | 2004-12-08 | 707-547-1062 |  | MAJOR | Michael Conachy | Sonoma County Water Agency | 707-547-1062 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95406 |  | SonomaValleyCountySD
507 | 2 | 3 | SonomaValleyCountySD | 2004-12-13 08:49 | 3000 | 0 | 04-6406 | 2004-12-08 | M. Conachy | SonomaValleyCountySD | 19355 Arkay Ct | Sonoma | Sonoma | 95476 |  |  | 2004-12-08 | 8:30:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | SURFACE WATER IMPACT | No |  | No | No | Due to rains in the past 3 days, Sonoma Creek raised 4 to 5 feet and was rushing at about 10 to 15 per sec. |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jyl@rb2.swrcb.ca.gov | SonomaValleyCountySD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | LEAKS OF COLLECTION SYSTEM |  | Due to heavy rains in the past 3 days, system became charged with I&I. Because the truck line was charge, it was backing into Arkay Ct. The Crew arrived on site. Shut valve to isolate Arkay Ct from system. This stopped the truck line from backing into Arkay’s system. At this time the crew Vac out Arkay’s system. This stopped all overflow. The crew then rinsed down effect areas and vac up all rinse water. Arkay’s system would act as a storage area, which the crew monitored and vac out as needed. Once truck line returned to normal, Arkay’s valve was opened and allowed to operate normally. NO SOLIDS ESCAPED THE SYSTEM. Solids were held back by manhole lid. | Lead maint. Worker | Michael J Conachy Sr | 2004-12-08 | 707-547-1062 |  | MAJOR | Michael Conachy | Sonoma County Water Agency | 707-547-1062 |  | 2150 West College | Santa Rosa | Sonoma | 95406 |  | SonomaValleyCountySD
534 | 3 | 3 | SonomaValleyCountySD | 2004-12-14 11:49 | 6750 | 0 | 04-6407 | 2004-12-08 | M. Conachy | SonomaValleyCountySD | 588 Bokman Pl | Boyes Hot Spring | Sonoma | 95416 |  |  | 2004-12-08 | 7:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | SURFACE WATER IMPACT | No |  | No | Yes | Due to rains in the past 3 days, Sonoma Creek raised 4 to 5 feet and was rushing at about 10 to 15 per sec. |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jyl@rb2.swrcb.ca.gov | SonomaValleyCountySD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | LEAKS OF COLLECTION SYSTEM |  | Due to heavy rains in the past 3 days, system became charged with I&I. Mh78-24 overflowed on the street (at the end of Bokman Pl.) and into DI. Crew responded once they received call. Due to the amount of overflow caused by I&I, crew was unable to contain. Using woddles, sandbags and sheets of plywood the crew were able to control the flow into the DI. The street that was affected by the overflow was washed into control area. The control area was also covered for further protection. Area was posted at manhole and at DI. Although overflow stopped at 14:30, woddles, sandbags and sheets of plywood (along with the postings) were left in place until the next day. Area was then picked up and rinsed down. All rinse water was vac up. NO SOLIDS ESCAPED SYSTEM. Solids were held back by manhole lid. | Lead Maint. Worker | Michael J Conachy Sr | 2004-12-08 | 707-547-1062 |  | MAJOR | Michael Conachy | Sonoma County Water Agency | 707-547-1062 |  | 2150 West College Ave | Santa Rosa | Sonoma | 95406 |  | SonomaValleyCountySD
4167 | 1 | 2 | SouthBaysideSystemAuthority | 2006-11-28 | 5200 | 5200 | 06-7015 | 2006-11-28 | Robert Donaldson | SBSA | 150 Monte Vista Dr, San Carlos and the San Carlos Airport | San Carlos | San Mateo | 64065 |  |  | 2006-11-27 | 9:30 | [6 empty] | Low |  |  | No |  | No | No |  |  | Yes | Yes | [8 empty] | CLOSED | Johnson Lam | 510 622 2373 | jyl@rb2.swrcb.ca.gov | [9 empty] | Robert Donaldson | 2006-11-28 | 650-594-8411x127 | rdonaldson@sbsa.org
5041 | 58 | 1 | SouthSanFrancisco | 2007-04-05 08:30 | 450 | 0 |  | 2007-04-05 08:30 |  | -- | BADEN AVE. & LINDEN AVE. | SOUTH SAN FRANCISCO | SAN MATEO | 94080 |  |  | 2007-03-25 |  |  |  | RECOVERED 150 GAL.WITH SANDBAGS AND SPILL SHARK ABSORBANT.WILL FOLLOW-UP WITH CCTV. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | P.W. SUPERVISOR | DOUGLAS AGRESS | 2007-04-05 | 650-877-8552
4385 | 55 | 1 | SouthSanFrancisco | 2006-12-22 11:53 | 500 | 0 |  | 2006-12-22 11:53 |  | -- | Intersection of Mission Road and Holly Avenue. | South San Francisco | San Mateo | 94080 |  |  | 2006-12-22 |  |  |  | Spill was 99% water, all paper was swept up and removed from site. Spill eminated from two sidewalk cleanouts through vent holes. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Public Works Supervi | James D. Bombaci | 2006-12-22 | 650-877-8552
4289 | 54 | 1 | SouthSanFrancisco | 2006-12-12 | 8250 | 0 | 06-7334 | 2006-12-12 | Don Stupi | southsanfrancisco | Intersection of Clay Avenue and Longford Drive | South San Francisco | San Mateo | 94080 |  |  | 2006-12-12 | 0.36806 | [6 empty] | Low | Colma Creek | STORM DRAIN | No |  | No | No | Extremely Heavy wet weather. Roughly a 98% storm water influence. |  | Yes | Yes | No |  |  | No | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | GREASE | -- Select One -- |  | Sanitary Sewer Manhole at the intersection of Clay Avenue and Langford Drive "popped" open due to a large volume of water and estimated spill of 8250 Gallons, mostly I&I water. | Public Works Supervi | James D. Bombaci | 2006-12-12 | 650-877-8552
4187 | 53 | 1 | SouthSanFrancisco | 2006-12-05 07:59 | 100 | 0 |  | 2006-12-05 07:59 |  | -- | Corner of Linden Avenue and Railroad Avenue | South San Francisco | San Mateo | 94080 |  |  | 2006-12-02 |  |  |  | Area was broomed and cleaned | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Public Works Supervi | James D. Bombaci | 2006-12-05 | 650-877-8552
4021 | 52 | 1 | SouthSanFrancisco | 2006-10-24 08:28 | 250 | 0 |  | 2006-10-24 08:28 |  | -- | 618 W. Orange | South San Francisco | San Mateo | 94080 |  |  | 2006-10-24 |  |  |  | Recovered 500 Gallons with sandbags and Vacuum. Flushed and dissinfected area. Note: Mainline had been treated with foam. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | southsanfrancisco | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Supervisor | James D. Bombaci | 2006-10-24 | 650-877-8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
3937 | 51 | 1 | SouthSanFrancisco | 2006-09-28 08:04 | 700 | 0 |  | 2006-09-28 08:04 |  | -- | Corner of Belle Aire Rd. and South Airport Blvd. | South San Francisco | San Mateo | 94080 |  |  | 2006-09-28 |  |  |  | Swept up and Vacuumed grease from line. Jetted main line. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | southsanfrancisco | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Public WorSupervisor | James D. Bombaci | 2006-09-28 | 605-877-8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
3857 | 50 | 1 | SouthSanFrancisco | 2006-09-07 13:43 | 675 | 0 |  | 2006-09-07 13:43 |  | -- | Buri-Buri Park | South San Francisco | San Mateo | 94080 |  |  | 2006-09-07 |  |  |  | Some effluent spilled onto the earth near the manhole, Swept and picked up solids and contaminated debris. Flushed with fresh water and disinfectant. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | southsanfrancisco | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Pubic Works Supervis | James D. Bombaci | 2006-09-07 | 650-877-8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
3781 | 49 | 1 | SouthSanFrancisco | 2006-08-24 09:32 | 70 | 0 |  | 2006-08-24 09:32 |  | -- | 195 Belle Air Road | South San Francisco | San Mateo | 94080 |  |  | 2006-08-18 |  |  |  | Pipe sagged due to settling of back fill. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | PIPE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Technical Services S | Cassandra Prudhel | 2006-08-24 | 650-829-3840 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net,; cassie.prudhel@ssf.net | MINOR
3742 | 48 | 1 | SouthSanFrancisco | 2006-08-15 14:01 | 2000 | 0 | 06-4822 | 2006-08-12 | Homeowner | SouthSanFrancisco | 328 Alta Mesa | South San Francisco | San Mateo | 94080 |  |  | 2006-08-12 | 11:00:00 A | [5 empty] | SUNNY WEATHER | Medium | Colma Creek | STORM DRAIN | No |  | No | No | City cleanout was overflowing due to a main line plug which backed up into homeowners basement |  | Yes | No | No | No | No | No | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SouthSanFrancisco | CLEAN OUT |  | BLOCKAGE | GREASE | --Select None-- |  | City cleanout was overflowing due to a main line plug which backed up into homeowners basement | James | Bombaci | 2006-08-15 | 650-877-8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MAJOR | Cassie Prudhel | South San Francisco | 650-829-3840 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080 | City of South San Francisco | City of SouthSan Francisco | 650-877-8555 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080
3690 | 46 | 1 | SouthSanFrancisco | 2006-08-05 08:23 | 1440 | 0 | 06-4656 | 2006-08-05 | Robert Hahn |  | Intersection of Commercial AVe & Linden Ave | South San Francisco | San Mateo | 94080 |  |  | 2006-08-04 | 10:00:00 A | 2006-08-04 | 6:00:00 PM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Supt. of P.W. | Robert T. Hahn | 2006-08-05 | 650-829-3830 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | 24HR |  |  | 650-829-3830 | [6 empty] | SouthSanFrancisco
3718 | 47 | 1 | SouthSanFrancisco | 2006-08-11 14:35 | 1440 | 0 | 06-4656 | 2006-08-04 | Don Stupi | southsanfrancisco | Corner of Commercial Ave and Linden Ave. | South San Francisco | San Mateo | 94080 |  |  | 2006-08-04 | 10:00:00 A | [5 empty] | SUNNY WEATHER | Low | Colma Creek | STORM DRAIN | No |  | No | No | No sewage noted in waterways |  | Yes | Yes | No | No | No | No | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | southsanfrancisco | OTHER | Cracks in street ashalt | BLOCKAGE | GREASE | --Select None-- |  | Cal Water Employee reported water and odor comming from cracks in asphalt at the corner of Commercial Ave and Linden Ave at 1000. Don Stupi reported to the scene at 1000 and checked all manholes. No surcharge. Don Stupi returned to site and jet flushed lines at 1800 after determining that it was a sewer problem and not a water problem. | Public Works Supervi | James D. Bombaci | 2006-08-11 | 650-877-8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MAJOR | Cassie Prudhel | South San Francisco | 650-829-3840 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080 | City of South San Francisco | City of SouthSan Francisco | 650-877-8555 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080
3677 | 45 | 1 | SouthSanFrancisco | 2006-08-01 08:15 | 150 | 0 |  | 2006-08-01 08:15 |  | -- | Corner of Newman Drive and King Drive | South San Francisco | San Mateo | 94080 |  |  | 2006-07-27 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Public Works Supervi | James D. Bombaci | 2006-08-01 | 650-877-8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
3554 | 44 | 1 | SouthSanFrancisco | 2006-06-26 10:52 | 180 | 0 |  | 2006-06-26 10:52 |  | -- | 728 Parkway | South San Francisco | San Mateo | 94080 |  |  | 2006-06-25 |  |  |  | Cleaned up spill and flushed area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Public Works Supervi | James D. Bombaci | 2006-06-26 | 6508778552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
4734 | 57 | 1 | SouthSanFrancisco | 2007-02-12 11:41 | 300 | 0 |  | 2007-02-12 11:41 |  | -- | Camaritas Avenue and Arroyo Drive | South San Francisco | San Mateo | 94080 |  |  | 2006-05-23 |  |  |  | Recovered 200 Gallons | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Public Works Supervi | James D. Bombaci | 2007-02-12 | 650-877-8552
4732 | 56 | 1 | SouthSanFrancisco | 2007-02-12 11:38 | 500 | 0 |  | 2007-02-12 11:38 |  | -- | 630 Baden Avenue | South San Francisco | San Mateo | 94080 |  |  | 2006-05-14 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Public Works Supervi | James D. Bombaci | 2007-02-12 | 650-877-8552
3111 | 42 | 2 | SouthSanFrancisco | 2006-04-03 09:58 | 3375 | 0 | 06-1860 | 2006-03-29 | Cassie Prudhel | SouthSanFrancisco | Manhole on Camaritas Ave at intersection with Clara Ave. | South San Francisco | San Mateo | 94080 |  |  | 2006-03-29 | 2:00:00 PM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | No Visual Inspection |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | VANDALISM | --Select None-- | Stick of wood blocking out flow |  | Superintendent | Robert T. Hahn | 2006-04-03 | 650-829-3830 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, cassie.prudhel@ssf.net | MAJOR | Cassie Prudhel | South San Francisco | 650-829-3840 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080 | Unknown | SouthSanFrancisco
2722 | 41 | 1 | SouthSanFrancisco | 2006-02-01 08:48 | 150 | 0 |  | 2006-02-01 08:48 |  | -- | 1004 HEMLOCK | SOUTHSANFRANCISCO | SAN MATEO | 94080 |  |  | 2006-01-31 |  |  |  | BROKEN PIPE, GREASE,ROOTS. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | SUPERVISOR | MICHAEL CHARAN | 2006-02-01 | 650-877-8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
2691 | 40 | 1 | SouthSanFrancisco | 2006-01-27 11:41 | 200 | 0 |  | 2006-01-27 11:41 |  | -- | BURI BURI PARK | SOUTHSANFRANCISCO | SAN MATEO | 94080 |  |  | 2006-01-23 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SUPERVISOR | MICHAEL CHARAN | 2006-01-27 | 650-877-8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
2627 | 38 | 1 | SouthSanFrancisco | 2006-01-17 09:59 | 100 | 0 |  | 2006-01-17 09:59 |  | -- | 632 FIRST LANE | SOUTHSANFRANCISCO | SAN MATEO | 94080 |  |  | 2006-01-13 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SUPERVISOR | MICHAEL CHARAN | 2006-01-17 | 650-877-8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
2634 | 39 | 1 | SouthSanFrancisco | 2006-01-17 14:04 | 5500 | 0 | 06-0274 | 2006-01-11 | COLMA PUBLIC WORKS | SouthSanFrancisco | EL CAMINO REAL +ARLINGTON DRIVE | SOUTH SANFRANCISCO | SAN MATEO | 94080 |  |  | 2006-01-11 | 7:56:00 AM | [5 empty] | RAINY WEATHER | Low | S.F. BAY | STORM DRAIN | No |  | No | No | NO VISUAL INSPECTION |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- |  | KEVIN MCCARTHY LEAD WORKER OF DALY CITY RESPONDED+UNPLUGED MAIN LINE BEFORE SSF ARRIVED ALL ESTIMATE ARE PER KEVIN OUR AGENCY RECEIVED REPORT AT 07:56 WE ARRIVED AT 08:15 KEVIN ESTIMATED SPILL AT 100 GPM FOR 55 MINUTES. NOTE cOLMA INITIALLY REPORTED sso TO DALY CITY AT APPROXIMATELY 7:15AM. | SUPERVISOR | MICHAEL CHARAN | 2006-01-17 | 650-877-8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MAJOR | Cassie Prudhel | South San Francisco | 650-829-3840 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080 | City of South San Francisco | City of SouthSan Francisco | 650-877-8555 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080
2601 | 37 | 1 | SouthSanFrancisco | 2006-01-11 11:08 | 100 | 0 |  | 2006-01-11 11:08 |  | -- | SISTERCITIES BLVD+SOUTH SAN FRANCISCO DR | SOUTH SAN FRANCISCO | SAN MATEO | 94080 |  |  | 2006-01-07 |  |  |  | ROPE IN MAIN LINE CAUSED BLOCKAGE | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | VANDALISM |  |  |  | SUPERVISOR | MICHAEL CHARAN | 2006-01-11 | 650-877-8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
2463 | 36 | 1 | SouthSanFrancisco | 2006-01-03 20:37 | 900 | 0 |  | 2006-01-03 20:37 |  | -- | E002 Outfall, 801 Forbes @DNA Way, South San Francisco | South San Francisco | San Mateo | 94080 |  |  | 2005-12-31 |  |  |  | The breather line broke off and dechlorinated treated effluent spilled at a rate of 5 gpm for 3 hours onto the surrounding grass, then flowed onto the Genentech Driveway and down the storm drain. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | OTHER | Outfall station | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | EC Coordinator | Cassie Prudhel | 2006-01-03 | 650-829-3840 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, cassie.prudhel@ssf.net | MINOR
2383 | 34 | 1 | SouthSanFrancisco | 2005-12-30 07:39 | 300 | 0 |  | 2005-12-30 07:39 |  | -- | 745 GRAND AVE | SOUTHSANFRANCISCO | SAN MATEO | 94080 |  |  | 2005-12-29 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SUPERVISOR | MICHEAL CHARAN | 2005-12-30 | 650-877-8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
2384 | 35 | 1 | SouthSanFrancisco | 2005-12-30 08:34 | 1800 | 0 | 05-7440 | 2005-12-26 | TOM DONALDSON | SouthSanFrancisco | 303 HAZELWOOD DR | SOUTHSANFRANCISCO | SAN MATEO | 94080 |  |  | 2005-12-26 | 12:30:00 A | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | No | NO VISUAL INSPECTION |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SouthSanFrancisco | CLEAN OUT |  | BLOCKAGE | GREASE | --Select None-- |  |  | SUPERVISOR | MICHEAL CHARAN | 2005-12-30 | 650-877-8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MAJOR | Cassie Prudhel | South San Francisco | 650-829-3840 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080 | City of South San Francisco | City of SouthSan Francisco | 650-877-8555 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080
2347 | 32 | 1 | SouthSanFrancisco | 2005-12-28 12:36 | 600 | 0 |  | 2005-12-28 12:36 |  | -- | 131 TERMINAL CT | SOUTHSANFRANCISCO | SAN MATEO | 94080 |  |  | 2005-12-22 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | SUPERVISOR | MICHEAL CHARAN | 2005-12-28 | 650=877=8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
2239 | 31 | 1 | SouthSanFrancisco | 2005-12-12 13:46 | 150 | 0 |  | 2005-12-12 13:46 |  | -- | MAPLE + RAILROAD AVE | S.S.F | SAN MATEO | 94080 |  |  | 2005-12-09 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SUPERVISOR | MICHEAL CHARAN | 2005-12-12 | 650-877-8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
2194 | 28 | 2 | SouthSanFrancisco | 2005-11-30 16:47 | 3000 | 0 | 05-6845 | 2005-11-28 | Cassie Prudhel | SouthSanFrancisco | 618 W Orange Ave | South San Francisco | San Mateo | 94080 |  |  | 2005-11-24 | 10:00:00 A | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | No | No Visual Inspection |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- |  | Initially, the standby leader thought spill was for 30 minutes and approximately 30 gpm which equals 900 gallons. Later over weekend and into Monday morning he realized spill was at least an hour in duration and approximately 50 gpm which translates into 3000 gallons. | Acting Superintenden | Robert T. Hahn | 2005-11-30 | 650-829-3830 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, ;cassie.prudhel@ssf.net | MAJOR | Cassie Prudhel | South San Francisco | 650-829-3840 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080 | City of South San Francisco | City of SouthSan Francisco | 650-877-8555 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080
1764 | 27 | 1 | SouthSanFrancisco | 2005-09-07 09:17 | 200 | 0 |  | 2005-09-07 09:17 |  | -- | 20 ESCANYO DR | SSF | SAN MATEO | 94080 |  |  | 2005-09-05 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SUPERVISOR | MIKE CHARAN | 2005-09-07 | 650-8778550 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
1762 | 26 | 1 | SouthSanFrancisco | 2005-09-07 09:12 | 800 | 0 |  | 2005-09-07 09:12 |  | -- | WILLOW +GRAND AVE | SSF | SAN MATEO | 94080 |  |  | 2005-09-03 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SUPERVISOR | MIKE CHARAN | 2005-09-07 | 650-8778552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
1664 | 25 | 1 | SouthSanFrancisco | 2005-08-01 08:52 | 200 | 0 |  | 2005-08-01 08:52 |  | -- | 62 SO.LINDEN | SOUTHSANFRANCISCO | SANMATEO | 94080 |  |  | 2005-07-29 |  |  |  | PAPER | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | SUPERVISOR | MIKE CHARAN | 2005-08-01 | 650-877 8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
1627 | 22 | 1 | SouthSanFrancisco | 2005-07-20 08:54 | 500 | 0 |  | 2005-07-20 08:54 |  | -- | PONDEROSA+FAIRWAY | SOUTHSANFRANCISCO | SANMATEO | 94080 |  |  | 2005-07-10 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SOUTHSanFrancisco | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SUPERVISOR | MICHAEL CHARAN | 2005-07-20 | 650-877 8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
1629 | 23 | 1 | SouthSanFrancisco | 2005-07-20 09:05 | 500 | 0 |  | 2005-07-20 09:05 |  | -- | 1080 MISSON ROAD | SOUTH SAN FRANCISCO | SAN MATEO | 94080 |  |  | 2005-07-10 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SOUTHSanFrancisco | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SUPERVISOR | MICHAEL CHARAN | 2005-07-20 | 650-877 8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
1549 | 21 | 1 | SouthSanFrancisco | 2005-06-21 14:09 | 800 | 0 |  | 2005-06-21 14:09 |  | -- | JUNIPERO SERRA +CLAY | SOUTHSANFRANCISCO | SAN MATEO | 94080 |  |  | 2005-06-13 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE | The display screen from the PLC reportedly had been left in manual mode on a page that showed fault conditions. The station has a telephone line to report high wet levels. For some unknown reason the phone line was inoperative. When checked there was continuity from the station to the SBC Pacific Bell connection. It appears that trouble was encountered between their connection and their substation. We are installing equipment which will notify rounds personnel of phone line problems. | BLOCKAGE | GREASE |  |  |  | SUPERVISOR | MIKE CHARAN | 2005-06-21 | 650-877 8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
1393 | 20 | 1 | SouthSanFrancisco | 2005-05-12 14:19 | 700 | 0 |  | 2005-05-12 14:19 |  | -- | MILLER + MAGNOLIA AVE | SSF | SAN MATEO | 94080 |  |  | 2005-05-07 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SUPERVISOR | MICHEAL CHARAN | 2005-05-12 | 650 877 8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
1349 | 19 | 2 | SouthSanFrancisco | 2005-05-02 18:00 | 4350 | 0 | 05-2390 | 2005-04-21 | Cassandra Prudhel | SouthSanFrancisco | Pump Station #14 Veterans Blvd/Oyster Point | South San Francisco | San Mateo | 94080 |  |  | 2005-04-20 | 8:53:00 AM | [5 empty] | SUNNY WEATHER | Low | San Francisco Bay | STORM DRAIN | No |  | No | No | No impact in receiving water |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SouthSanFrancisco | PUMP STATION | There was a fault on the programmable logic controller. | INFRASTRUCTURE FAILURE | --Select None-- | PUMP STATION FAILURE | There was a fault on the programmable logic controller. The display screen from the PLC reportedly had been left in manual mode on a page that showed fault conditions. The station has a telephone line to report high wet levels. For some unknown reason the phone line was inoperative. When checked there was continuity from the station to the SBC Pacific Bell connection. It appears that trouble was encountered between their connection and their substation. We are installing equipment which will notify ro | Rounds crews responded and observed a fault on the programmable logic controller. the last fault recorded before the spill indicated that a low voltage incident had been encountered. Unknown source... The display screen from the PLC reportedly had been left in manual mode on a page that showed fault conditions. The station has a telephone line to report high wet levels. For some unknown reason the phone line was inoperative. When checked there was continuity from the station to the SBC Pacific Bell connection. It appears that trouble was encountered between their connection and their substation. We are installing equipment which will notify rounds personnel of phone line problems. | Lab Supervisor | Cassandra Prudhel | 2005-05-02 | 650-829-3840 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, cassie.prudhel@ssf.net | MAJOR | Cassandra Prudhel | City of South San Francisco | 650-829-3840 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080 | Dave Bockhaus | SouthSanFrancisco | 650-829-3850 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080
1280 | 18 | 1 | SouthSanFrancisco | 2005-04-14 09:22 | 300 | 0 |  | 2005-04-14 09:22 |  | -- | CALIFORNIA + CYPRESS | SOUTH SAN FRANCISCO | SAN MATEO | 94080 |  |  | 2005-04-08 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | SUPERVISOR | MIKE CHARAN | 2005-04-14 | 650 877 8552 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
1254 | 15 | 1 | SouthSanFrancisco | 2005-04-04 18:22 | 600 | 0 |  | 2005-04-04 18:22 |  | -- | Westborough at Fleetwood | South San Francisco | San Mateo | 94080 |  |  | 2005-04-02 |  |  |  | SSO was caused by a collapsed line. Emergency funds to repair the line have been requested. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Lab Supervisor | Cassandra Prudhel | 2005-04-04 | 650-829-3840 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, cassie.prudhel@ssf.net | MINOR
1269 | 16 | 1 | SouthSanFrancisco | 2005-04-08 14:36 | 500 | 0 |  | 2005-04-08 14:36 |  | -- | 508 Serra | South San Francisco | San Mateo | 94080 |  |  | 2005-04-02 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Lab Supervisor | Cassandra Prudhel | 2005-04-08 | 650-829-3840 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, cassie.prudhel@ssf.net | MINOR
1252 | 14 | 1 | SouthSanFrancisco | 2005-04-04 18:18 | 600 | 0 |  | 2005-04-04 18:18 |  | -- | Westborough at Fleetwood | South San Francisco | San Mateo | 94080 |  |  | 2005-04-01 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Lab Supervisor | Cassandra Prudhel | 2005-04-04 | 650-829-3840 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, cassie.prudhel@ssf.net | MINOR
1139 | 12 | 1 | SouthSanFrancisco | 2005-03-08 15:29 | 316 | 0 |  | 2005-03-08 15:29 |  | -- | South Airport and San Mateo Avenue | South San Francisco | San Mateo | 94080 |  |  | 2005-03-07 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Lab Supervisor | Cassandra Prudhel | 2005-03-08 | 650-829-3840 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, cassie.prudhel@ssf.net | MINOR
1137 | 11 | 1 | SouthSanFrancisco | 2005-03-08 15:25 | 150 | 0 |  | 2005-03-08 15:25 |  | -- | 814 Baden | South San Francsico | San Mateo | 94080 |  |  | 2005-03-05 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Lab Supervisor | Cassandra Prudhel | 2005-03-08 | 650-829-3840 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, | MINOR
1250 | 13 | 1 | SouthSanFrancisco | 2005-04-04 18:14 | 500 | 0 |  | 2005-04-04 18:14 |  | -- | 131 Terminal | South San Francisco | San Mateo | 94080 |  |  | 2005-02-15 |  |  |  | Jet main line clear. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Lab Supervisor | Cassandra Prudhel | 2005-04-04 | 650-829-3840 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net, cassie.prudhel@ssf.net | MINOR
1076 | 10 | 1 | SouthSanFrancisco | 2005-02-23 09:16 | 30000 | 0 | 05-1079 | 2005-02-17 | Ron Dahlen | SouthSanFrancisco | Vacant Lot at Southwest Corner of Intersection of Camaritas Avenue and hickey Boulevard | South San Francisco | San Mateo | 94080 |  |  | 2005-02-13 | 12:00:00 P | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | No | No Visual Inspection |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS | --Select None-- |  |  | Superintendent | Robert T. Hahn | 2005-02-23 | 650-829-3830 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net | MAJOR | Cassie Prudhel | SouthSanFrancisco | 650-829-3840 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080 | Crown Management | South San Francisco | 888-871-0087 |  | 2033 Ralston Ave #100 | Belmont | San Mateo | 94002
822 | 8 | 1 | SouthSanFrancisco | 2005-01-11 15:31 | 150 | 0 |  | 2005-01-11 15:31 |  | -- | Lux and Maple | South San Francisco | San Mateo | 94080 |  |  | 2005-01-03 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Environmental Compli | Cassandra Prudhel | 2005-01-11 | 650-829-3840 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net | MINOR
666 | 1 | 1 | SouthSanFrancisco | 2004-12-28 12:45 | 1800000 | 0 | 04-6780 | 2004-12-28 | Ken Navarre | SouthSanFRancisco | 1479 San Mateo Avenue | South San Francisco | San Mateo | 94080 | 37.64948N | 122.40950W | 2004-12-27 | 8:05:00 AM | [5 empty] | RAINY WEATHER | Low | San Francisco Bay | SURFACE WATER IMPACT | No |  | No | Yes | No impact due to high dilution rate caused by excessive flows in Colma Creek. |  | Yes | Yes | Yes | No | No | No | No | Yes | No | 2005-01-15 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SouthSanFRancisco | PUMP STATION |  | INFRASTRUCTURE FAILURE | --Select None-- | PUMP STATION FAILURE |  | It appears that a power spike damaged newly installed variable frequency drives controlling the pumps. The spill continued until the drives could be rewired. | Environmental Compli | Cassie Prudhel | 2004-12-28 | 650-829-3840 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net | MAJOR | Cassie Prudhel | SouthSanFrancisco | 650-829-3840 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080 | City of South San Francisco | City of South San Francisco | 650-877-8555 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080
733 | 2 | 1 | SouthSanFrancisco | 2005-01-04 07:52 | 3300 | 0 | 04-6813 | 2004-12-27 | Don Stupi | SouthSanFrancisco | 11 Airport Boulevard | South San Francisco | San Mateo | 94080 |  |  | 2004-12-27 | 8:45:00 AM | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | Yes | No visual inspection |  | Yes | Yes | Yes | No | No | No | No | Yes | No | 2005-01-15 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SouthSanFrancisco | MANHOLE |  | INFRASTRUCTURE FAILURE | --Select None-- | PUMP STATION FAILURE |  |  | Supintendent | Robert T. Hahn | 2005-01-04 | 650-829-3830 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net | MAJOR | Cassie Prudhel | SouthSanFrancisco | 650-829-3840 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080 | City of South San Francisco | City of South San Francisco | 650-877-8555 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080
734 | 3 | 1 | SouthSanFrancisco | 2005-01-04 08:06 | 4950 | 0 | 04-6814 | 2004-12-27 | Don Stupi | SouthSanFrancisco | 1373 Lowrie Avenue | South San Francisco | San mateo | 94080 |  |  | 2004-12-27 | 9:00:00 AM | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | Yes | No visual inspection |  | Yes | Yes | Yes | No | No | No | No | Yes | No | 2005-01-15 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SouthSanFrancisco | MANHOLE |  | INFRASTRUCTURE FAILURE | --Select None-- | PUMP STATION FAILURE |  |  | Superintendent | Robert T.Hahn | 2005-01-04 | 650-829-3830 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net | MAJOR | Cassie Prudhel | SouthSanFrancisco | 650-829-3840 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080 | City of South San Francisco | City of South San Francisco | 650-877-8555 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080
735 | 4 | 1 | SouthSanFrancisco | 2005-01-04 08:20 | 120000 | 0 | 04-6815 | 2004-12-27 | Doug Agress | SouthSanFrancisco | 320 Victory Avenue | South San Francisco | San Mateo | 94080 |  |  | 2004-12-27 | 8:00:00 AM | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | Yes | No visual inspection |  | Yes | Yes | Yes | No | No | No | No | Yes | No | 2005-01-15 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SouthSanFrancisco | MANHOLE |  | INFRASTRUCTURE FAILURE | --Select None-- | PUMP STATION FAILURE |  |  | Superintendent | Robert T. Hahn | 2005-01-04 | 650-829-3830 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net | MAJOR | Cassie Prudhel | SouthSanFrancisco | 650-829-3840 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080 | City of South San Francisco | City of South San Francisco | 650-877-8555 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080
737 | 5 | 1 | SouthSanFrancisco | 2005-01-04 09:41 | 18000 | 0 | 04-6816 | 2004-12-27 | Doug Agress | SouthSanFrancisco | 605 Cypress Avenue (corner Cypress and California) | South San Francisco | San Mateo | 94080 |  |  | 2004-12-27 | 11:00:00 A | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | No | No visual inspection |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SouthSanFrancisco | CLEAN OUT |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  |  | Superintendent | Robert T. Hahn | 2005-01-04 | 650-829-3830 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net | MAJOR | Cassie Prudhel | SouthSanFrancisco | 650-829-3840 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080 | City of South San Francisco | City of South San Francisco | 650-877-8555 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080
738 | 6 | 1 | SouthSanFrancisco | 2005-01-04 09:52 | 2100 | 0 | 04-6817 | 2004-12-27 | Don Stupi | SouthSanFrancisco | 114 South Maple Avenue | South San Francisco | San Mateo | 94080 |  |  | 2004-12-27 | 8:00:00 AM | [5 empty] | RAINY WEATHER | Low |  | STORM DRAIN | No |  | No | Yes | No visual inspection |  | Yes | Yes | Yes | No | No | No | No | Yes | No | 2005-01-15 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | SouthSanFrancisco | MANHOLE | The primary cause of spill was pump station failure but inflow and infiltration also contributed to spill. | INFRASTRUCTURE FAILURE | --Select None-- | PUMP STATION FAILURE |  |  | Superintendent | Robert T. Hahn | 2005-01-04 | 650-829-3830 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net | MAJOR | Cassie Prudhel | SouthSanFrancisco | 650-829-3840 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080 | City of South San Francisco | City of South San Francisco | 650-877-8555 |  | 195 Belle Air Road | South San Francisco | San Mateo | 94080
824 | 9 | 1 | SouthSanFrancisco | 2005-01-11 15:37 | 600 | 0 |  | 2005-01-11 15:37 |  | -- | El Camino Real and Second Street | South San Francisco | San Mateo | 94080 |  |  | 2004-12-14 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Environmental Compli | Cassandra Prudhel | 2005-01-11 | 650-829-3840 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net | MINOR
820 | 7 | 3 | SouthSanFrancisco | 2005-01-11 14:50 | 180 | 0 |  | 2005-01-11 14:50 |  | -- | 434 Alida | South San Francisco | San Mateo | 94080 |  |  | 2004-12-10 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SouthSanFrancisco | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Environmental Compli | Cassandra Prudhel | 2005-01-11 | 650-829-3840 | dcastagnola@ssf.net; terry.white@ssf.net; knavarre@ssf.net;cassie.prudhel@ssf.net | MINOR
4761 | 14 | 1 | StegeSanitary | 2007-02-15 09:28 | 120 | 0 |  | 2007-02-15 09:28 |  | -- | 8457 Terrace Drive | El Cerrito | Contra Costa | 94530 |  |  | 2007-02-07 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | District Manager | Doug Humphrey | 2007-02-15 | 510 524-4668
4509 | 13 | 1 | StegeSanitary | 2007-01-14 09:58 | 900 | 0 |  | 2007-01-14 09:58 |  | -- | 7321 Gladys Avenue | El Cerrito | Contra Costa | 94530 |  |  | 2007-01-06 |  |  |  | Area was washed down with dechlorinated water, and affected area of creek was flushed with 3000 gallons of dechlorinated water. No impacts noted. This SSO was initially reported by using the Water Board SSO eReporting program version 2.0. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | General Manager | Douglas Humphrey | 2007-01-12 | 510-524-4668
2519 | 12 | 1 | StegeSanitary | 2006-01-05 12:21 | 600 | 0 |  | 2006-01-05 12:21 |  | -- | 1080 Contra Costa Drive | El Cerrito | Contra Costa | 94530 |  |  | 2006-01-02 |  |  |  | Heavy storm - high storm flow drainage in street at time of overflow, impossible to capturre overflow volume. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | StegeSanitary | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Manager | Douglas Humphrey | 2006-01-05 | 510 524-4668 | doug@stegesd.dst.ca.us, | MINOR
2515 | 10 | 1 | StegeSanitary | 2006-01-05 12:14 | 800 | 0 |  | 2006-01-05 12:14 |  | -- | 398 Coventry | Kensington | Contra Costa | 94707 |  |  | 2005-12-31 |  |  |  | Heavy rains caused oveflow at manhole located at the bottom of a steep hill. Main line turns about 90 degrees at manhole. No possibility ot recover overflowed sewage, excessive runoff and storm drainage in streets, sidewalks and walkways in the area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | StegeSanitary | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | Manager | Douglas Humphrey | 2006-01-05 | 510 524-4668 | doug@stegesd.dst.ca.us, | MINOR
2517 | 11 | 1 | StegeSanitary | 2006-01-05 12:18 | 400 | 0 |  | 2006-01-05 12:18 |  | -- | 648 Wellesley | Kensington | Contra Costa | 94707 |  |  | 2005-12-31 |  |  |  | Heavy rains caused overflow at manhole located on a steep street - flow changes direction at two manholes, couldn't contain the flow from a surcharged main line. No possibility to capture overflow, excessive storm drainage on street. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | StegeSanitary | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | Manager | Douglas Humphrey | 2006-01-05 | 510 524-4668 | doug@stegesd.dst.ca.us, | MINOR
2513 | 9 | 1 | StegeSanitary | 2006-01-05 12:10 | 100 | 0 |  | 2006-01-05 12:10 |  | -- | 8457 Terrace Drive | El Cerrito | Contra Costa | 94530 |  |  | 2005-12-28 |  |  |  | Sewage flowed out of property owner's clean out for a few minutes during heavy rains. Clean out set at a very low elevation, allowing this overflow when main line surcharged. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | StegeSanitary | CLEAN OUT |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | Manager | Douglas humphrey | 2006-01-05 | 510 524-4668 | doug@stegesd.dst.ca.us, | MINOR
2365 | 7 | 1 | StegeSanitary | 2005-12-29 11:20 | 200 | 0 |  | 2005-12-29 11:20 |  | -- | 4 Pomona Ave. | El Cerrito | Contra Costa | 94530 |  |  | 2005-12-22 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | StegeSanitary | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | District Manager | Douglas Humphrey | 2005-12-29 | 510 524-4668 | doug@stegesd.dst.ca.us, | MINOR
2375 | 8 | 1 | StegeSanitary | 2005-12-29 13:03 | 500 | 0 |  | 2005-12-29 13:03 |  | -- | 398 Ocean View | Kensington | Contra Costa | 94707 |  |  | 2005-12-22 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | StegeSanitary | MANHOLE |  | FLOW CAPACITY DEFICIENCY | --Select None-- |  |  |  | District Manager | Douglas Humphrey | 2005-12-29 | 510 524-4668 | doug@stegesd.dst.ca.us, | MINOR
2317 | 6 | 1 | StegeSanitary | 2005-12-23 12:42 | 300 | 0 |  | 2005-12-23 12:42 |  | -- | 10601 San Pablo Avenue | El Cerrito | Contra Costa | 94530 |  |  | 2005-12-18 |  |  |  | Significant rain during this event, the overflow mixed with runoff/storm drainage that was running in the curb to storm drain - impossible to capture and return to sewer system. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | StegeSanitary | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Manager | Doug Humphrey | 2005-12-23 | 510 524-4668 | doug@stegesd.dst.ca.us, | MINOR
1519 | 5 | 1 | StegeSanitary | 2005-06-13 14:55 | 250 | 0 |  | 2005-06-13 14:55 |  | -- | 55 Stratford Ave. | Kensington | Contra Costa | 94530 |  |  | 2005-06-11 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | StegeSanitary | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Manager | Doug Humphrey | 2005-06-13 | 510 524-4668 | doug@stegesd.dst.ca.us, | MINOR
1315 | 4 | 1 | StegeSanitary | 2005-04-22 10:57 | 240 | 0 |  | 2005-04-22 10:57 |  | -- | 537 Coventry Road | El Cerrito | Contra Costa | 94530 |  |  | 2005-04-14 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | StegeSanitary | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Manager | Douglas Humphrey | 2005-04-22 | 524-4668 | doug@stegesd.dst.ca.us, | MINOR
762 | 3 | 1 | StegeSanitary | 2005-01-05 08:53 | 440 | 0 |  | 2005-01-05 08:53 |  | -- | 940 Leneve Place | El Cerrito | contra costa | 94530 |  |  | 2004-12-30 |  |  |  | Overflow was into property owner's bathroom. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | StegeSanitary | OTHER | bathroom in house | BLOCKAGE | ROOTS |  |  |  | Manager | Douglas Humphrey | 2005-01-05 | 524-4668 | doug@stegesd.dst.ca.us | MINOR
2709 | 1 | 3 | StegeSanitary | 2006-01-31 11:19 | 900 | 0 |  | 2006-01-31 11:19 |  | -- | 1121 Arlington Blvd. | El Cerrito | Contra Costa | 94530 |  |  | 2004-12-25 |  |  |  | It is estimated that the overflow volume was about 900 gallons total, but all but 250 gallons was diverted to the downstream manhole, and returned to the sewer system. Overflow was caused by a broken pipe, which was repaired later in the day. Originally reported address was incorrect, and originally reported volume was the net, not the gross volume spilled. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | StegeSanitary | PIPE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Manager | Douglas Humphrey | 2006-01-31 | 524-4668 | doug@stegesd.dst.ca.us | MINOR
2711 | 2 | 2 | StegeSanitary | 2006-01-31 11:22 | 450 | 0 |  | 2006-01-31 11:22 |  | -- | 1129 Arlington Blvd. | El Cerrito | contra costa | 94530 |  |  | 2004-12-23 |  |  |  | Total overflow volume was about 450 gallons, but only about 90 gallons was not returned to the downstream manhole and entered the storm drain. Blockage due to failing pipe was cleared and regular flow was restored. Originally reported address was incorrect and originally reported volume was the net rather than the gross volume spilled. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | StegeSanitary | MANHOLE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Manager | Douglas Humphrey | 2006-01-31 | 524-4668 | doug@stegesd.dst.ca.us | MINOR
4116 | 1 | 1 | StHelena | 2005-11-23 | 1000 | 1000 | 05-6783 | 2005-11-23 | Jonathon Goldman | StHelena | SR29 at Sulphur Creek | SAINT HELENA | NAPA | 94574 |  |  | 2005-11-23 | 0.62361 |  |  | Sewage left main line underground and infiltrated into storm drain and discharged to SW |  |  |  | Medium | Sulphur Creek/Napa River | SURFACE WATER IMPACT | No |  | No | No | City employee noticed problem, storm drain temporary plug installed and sewage pumped to tank, OES and Water Board notified. Blockage cleared, additional pumping and situation monitoring continued through holiday weekend. |  | Yes | Yes | No |  |  | No | No |  |  |  | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | PIPE | Sewage left main line underground and infiltrated into storm drain and discharged to SW | BLOCKAGE | GREASE | -- Select One -- |  |  | Dir Pub Wks | Jonathon Goldman | 2006-11-17 | 7079682658
5007 | 2 | 1 | SuisunCity | 2007-03-27 07:48 | 225 | 0 |  | 2007-03-27 07:48 |  | -- | Spill on Emperor Dr. - cross street Graylag Dr. | Suisun City | Solano | 94585 |  |  | 2007-02-19 |  |  |  | This small SSO entered only one storm drain and was at least 95% recovered. Roto Rooter was called in and they vacuumed out one down-stream SWI and washed the street down. Public Works returned the next day and cleaned out 350ft. of SWI and retrieved excess grease. There was no property damage. Affected area was the gutter line. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Admin Assist | Amanda Dum | 2007-03-27 | 707-421-7349
2942 | 1 | 1 | SuisunCity | 2006-03-07 13:27 | 290 | 0 |  | 2006-03-07 13:27 |  | -- | marina cir. @ whispering bay | suisun | solano | 94585 |  |  | 2006-03-06 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SuisunCity | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | foreman | david martinez | 2006-03-07 | 707421 7349 | gcullen@suisun.com, | MINOR
2874 | 2 | 1 | SunnyvaleCity | 2006-02-24 10:23 | 1335 | 1335 | 06-1154 | 2006-02-24 | City of Sunnyvale | SunnyvaleCity | 510 E. El Camino Real | Sunnyvale | Santa Clara | 94086 |  |  | 2006-02-23 | 11:09:00 A | [5 empty] | SUNNY WEATHER | Low |  | CAPTURED IN STORM DRAIN | No |  | No | No | Spillage was contained in storm drain system before reaching flood control channel. Storm flow at downstream manholes checked all the way to channel did not show any signs of sewage. |  | Yes | Yes | Yes | No | No | No | No | No | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | SunnyvaleCity | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- |  |  | Sr. PW Leader | Eric Tokutomi | 2006-02-24 | 408-730-7566 | jcraig@ci.sunnyvale.ca.us, mrose@ci.sunnyvale.ca.us | MAJOR | Tony Pineda | SunnyvaleCity | 408-730-7559 |  | 221 Commercial | Sunnyvale | Santa Clara | 94085 | Tony Pineda | SunnyvaleCity | 408-730-7559 |  | 221 Commercial | Sunnyvale | Santa Clara | 94085
1437 | 1 | 1 | SunnyvaleCity | 2005-05-20 13:53 | 375 | 0 |  | 2005-05-20 13:53 |  | -- | 664 Johanna | Sunnyvale | Santa Clara | 94088 |  |  | 2005-05-11 |  |  |  | Approximatly 375 gallons exited the system. The overflow did not enter the storm drain system. The sewage was contained, vacumed up and disposed of. The effected area was cleaned and sanitized. The sewage and wash water was contained, vacumed up and disposed of into the sanitary sewer system. The segment has been re-flushed using a high pressure and high output grease nozzle and is now clear of any debris at this time. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | SunnyvaleCity | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | P W Supervisor | Tony Pineda | 2005-05-20 | 730-7559 | tpineda@ci.sunnyvale.ca.us, mrose@ci.sunnyvale.ca.us | MINOR
5138 | 24 | 2 | Tamalpais | 2007-04-24 13:36 | 50 | 0 |  | 2007-04-24 13:36 |  | -- | 532 Pine Crest | Mill Valley | Marin Co | 94941 |  |  | 2007-04-26 | [9 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | Bob Bunce | 2007-04-24 | 415-388-6393
5134 | 23 | 1 | Tamalpais | 2007-04-24 13:31 | 50 | 0 |  | 2007-04-24 13:31 |  | -- | 1031 Erica Rd | Mill Valley | Marin Co | 94941 |  |  | 2007-04-24 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | Bob Bunce | 2007-04-24 | 415-388-6393
5132 | 22 | 1 | Tamalpais | 2007-04-24 13:25 | 120 | 0 |  | 2007-04-24 13:25 |  | -- | Shore Line Hwy | Mill Valley | Marin co. | 94941 |  |  | 2007-04-20 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | Bob Bunce | 2007-04-24 | 415-388-6939
4990 | 21 | 1 | Tamalpais | 2007-03-23 13:06 | 100 | 0 |  | 2007-03-23 13:06 |  | -- | 806 smith rd | mill valley | marin | 94941 |  |  | 2007-03-23 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | Bob Bunce | 2007-03-23 | 415-388-6393
4789 | 20 | 1 | Tamalpais | 2007-02-22 08:11 | 100 | 0 |  | 2007-02-22 08:11 |  | -- | 558 fairview | mill valley | marin | 94941 |  |  | 2007-02-18 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | Bob Bunce | 2007-02-22 | 415-388-6393
4787 | 19 | 1 | Tamalpais | 2007-02-22 08:04 | 30 | 0 |  | 2007-02-22 08:04 |  | -- | 410 maple st | mill valley | marin | 94941 |  |  | 2007-02-15 |  |  |  | Grease&Roots | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | pws | Bob Bunce | 2007-02-22 | 415-388-6393
4738 | 18 | 1 | Tamalpais | 2007-02-06 | 3300 | 0 | 07-0827 | 2007-02-06 | Tamalpais | Tamalpais | Intersection of Ross St and Linda St. | Mill Valley | Marin | 94941 |  |  | 2007-02-06 | 0.33681 |  |  | Caltrans guard rail replacement project adjacent to salt marsh wetlands repeatedly punctured Force Main to Sausalito-Marin City Sanitation District. Caltrans did not properly notify the District regarding the project, and the punctures occurred in the middle of the night. After the main pump station was shut off at about 3:30 am and some sewage spilled to a marsh (see separate report), deployed tanker trucks carried the District’s sewage to another pump station tributary to SASM in Mill Valley. These trucks handled the sewage flows between 3:30 and about 8:00 am. As other tanker trucks were en route to address the higher morning flows, some overflow in the collection system occurred between 8:05 and 8:30 am, spilling to a small 300-foot, unvegetated drainage ditch tributary to a stormwater pump station and Coyote Creek. |  |  |  | Medium | Coyote Creek (Marin) | SURFACE WATER IMPACT | No |  | No | No | District staff noted some overflow escaped deployed booms down to a drainage ditch by a pedestrian bridge at 8:05 am, before additional tanker trucks were able to arrive at 8:30 am. After this point, sewage solids were raked up and properly disposed and the area hydroflushed with about 1,500 gallons of clean water. Adjacent storm drains were blocked and pumped out. |  | Yes | Yes | No |  |  | No | No |  |  | 2007-02-20 | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE | Caltrans guard rail replacement project adjacent to salt marsh wetlands repeatedly punctured Force Main to Sausalito-Marin City Sanitation District. Caltrans did not properly notify the District regarding the project, and the punctures occurred in the middle of the night. After the main pump station was shut off at about 3:30 am and some sewage spilled to a marsh (see separate report), deployed tanker trucks carried the District’s sewage to another pump station tributary to SASM in Mill Valley. These trucks handled the sewage flows between 3:30 and about 8:00 am. As other tanker trucks were en route to address the higher morning flows, some overflow in the collection system occurred between 8:05 and 8:30 am, spilling to a small 300-foot, unvegetated drainage ditch tributary to a stormwater pump station and Coyote Creek. | INFRASTRUCTURE FAILURE | -- Select One -- | DAMAGE TO COLLECTION SYSTEM |  | The District's main Force Main was damaged in four locations along Shoreline Hwy. by Caltrans contractors in the middle of the night, and they had not properly pre-notified the District of this work. As such, it took a few hours to shut down the pump station and force main and deploy tanker trucks to move the sewage to an alternate pump station for treatment, during which time about 1,600 gallons were spilled to the marsh, reported separately. As the force main was being repaired in an emergency response, the morning sewage flows exceeded the capacity of the deployed tanker trucks for about 25 minutes, causing an associated 3,300-gallon spill in a tributary to Coyote Creek. Based on an analysis of pumping records and trucked amounts, a total of 4,900 gallons was estimated to have not been captured during the force main outage. | Public Works Super. | Bob Bunce | 2007-02-12 | 415 388 6393
4735 | 17 | 1 | Tamalpais | 2007-02-06 | 1600 | 0 | 07-0827 | 2007-02-06 | Marin Co. Sheriff | Tamalpais | Shoreline Highway (State Route 1) between Tennessee Valley Road and Redwood Highway (U.S. Route 101) | Mill Valley | Marin | 94941 |  |  | 2007-02-06 | 0.53125 |  |  | Caltrans guard rail replacement project adjacent to salt marsh wetlands repeatedly punctured Force Main to Sausalito-Marin City Sanitation District. Caltrans did not properly notify the District regarding the project, and the punctures occurred in the middle of the night. Four pumping events of 8 minute duration occurred between the punctures and when the pump station was shut off. During these events, raw sewage was observed by Caltrans contractors rising up in a 3-foot deep pit and periodically spilling over the top into the adjacent wetlands. |  |  |  | Low | Coyote Creek (Marin) and Richardson Bay | SURFACE WATER IMPACT | Yes | NONE | No | No | A high marsh area adjacent to Coyote Creek and Richardson Bay is characterized by small ponded areas unconnected to receiving waters. One pond next to the highway contained turbidity from the spill and associated erosion of the road bank. There was no visual evidence of raw sewage solids. The pond is tidally inundated only during high spring tides, which did not occur the week of the spill, and therefore, no raw sewage reached the creek or Bay. As a cleanup action, approx. 10,000 gallons were pumped out of this ponded area from the discharge point and sent to SASM for treatment. |  | Yes | Yes | No |  |  | Yes | Yes |  |  | 2007-02-20 | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | PIPE | Caltrans guard rail replacement project adjacent to salt marsh wetlands repeatedly punctured Force Main to Sausalito-Marin City Sanitation District. Caltrans did not properly notify the District regarding the project, and the punctures occurred in the middle of the night. Four pumping events of 8 minute duration occurred between the punctures and when the pump station was shut off. During these events, raw sewage was observed by Caltrans contractors rising up in a 3-foot deep pit and periodically spilling over the top into the adjacent wetlands. | INFRASTRUCTURE FAILURE | -- Select One -- | DAMAGE TO COLLECTION SYSTEM | Punctured Force Main | The District's main Force Main was damaged in four locations along Shoreline Hwy. by Caltrans contractors in the middle of the night, and they had not properly pre-notified the District of this work. As such, it took a few hours to shut down the pump station and force main, and deploy tanker trucks to move the sewage to an alternate pump station for treatment. As the force main was being repaired in an emergency response, the morning sewage flows exceeded the capacity of the deployed tanker trucks for about 25 minutes, causing an associated 3,300-gallon spill in a tributary to Coyote Creek, reported separately. Based on an analysis of pumping records and trucked amounts, a total of 4,900 gallons was estimated to have not been captured during the force main outage. | Public Works Super. | Bob Bunce | 2007-02-12 | 415 388 6393
4179 | 16 | 1 | Tamalpais | 2006-12-04 10:12 | 40 | 0 |  | 2006-12-04 10:12 |  | -- | 335 s morning sun | mill valley | marin co | 94941 |  |  | 2006-12-02 | [9 empty] | GROUND WATER IMPACTED | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | pws | Bob Bunce | 2006-12-04 | 415-388-6393
4143 | 15 | 1 | Tamalpais | 2006-11-22 08:10 | 0 | 0 |  | 2006-11-22 08:10 |  | -- | 247 shoreline hwy | mill valley | marin | 94941 |  |  | 2006-11-20 | [9 empty] | NO WATER INVOLVED | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | pws | Bob Bunce | 2006-11-22 | 415 388 6939
3777 | 14 | 1 | Tamalpais | 2006-08-23 07:39 | 450 | 0 |  | 2006-08-23 07:39 |  | -- | 335 jean st | mill valley | marin | 94941 |  |  | 2006-08-19 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tamalpais | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | pws | Bob Bunce | 2006-08-23 | 415-388-6393 | bbunce@tcsd.us, | MINOR
3727 | 11 | 1 | Tamalpais | 2006-08-14 14:52 | 100 | 0 |  | 2006-08-14 14:52 |  | -- | 360 jean st | mill valley | marin | 94941 |  |  | 2006-08-14 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tamalpais | MANHOLE |  | ELECTRICAL POWER FAILURE | GREASE |  |  |  | pws | bob bunce | 2006-08-14 | 415-388-6393 | bbunce@tcsd.us | MINOR
3731 | 12 | 1 | Tamalpais | 2006-08-14 14:57 | 30 | 0 |  | 2006-08-14 14:57 |  | -- | 301 enterprise concour. | mill vallet | marin | 94941 |  |  | 2006-08-13 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tamalpais | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | pws | bob bunce | 2006-08-14 | 415-388-6393 | bbunce@tcsd.us, jnelson@tcsd.us | MINOR
2917 | 10 | 1 | Tamalpais | 2006-03-03 09:00 | 600 | 0 |  | 2006-03-03 09:00 |  | -- | chamberlain ct | mill valley | marin | 94941 |  |  | 2006-02-22 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tamalpais | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWS | Bob Bunce | 2006-03-03 | 415-388-6393 | bbunce@tcsd.us | MINOR
2682 | 9 | 1 | Tamalpais | 2006-01-25 13:55 | 200 | 0 |  | 2006-01-25 13:55 |  | -- | 315 carrera dr | mill valley | marin co | 94941 |  |  | 2006-01-23 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tamalpais | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | Robert Bunce | 2006-01-25 | 415-388-6939- | bbunce@tcsd.us, | MINOR
2640 | 8 | 1 | Tamalpais | 2006-01-18 08:04 | 100 | 0 |  | 2006-01-18 08:04 |  | -- | 295 morning sun | mill valley | marin | 94941 |  |  | 2006-01-17 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tamalpais | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | pws | Robert Bunce | 2006-01-18 | 415-388-6939 | bbunce@tcsd.us, | MINOR
2196 | 2 | 1 | Tamalpais | 2005-12-02 09:31 | 25 | 0 |  | 2005-12-02 09:31 |  | -- | 309 carrera | Mill Valley | Marin co | 94941 |  |  | 2005-12-02 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tamalpais | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWS | Bob Bunce | 2005-12-02 | 415 388 6393 | bbunce@tcsd.us, | MINOR
2198 | 3 | 1 | Tamalpais | 2005-12-02 09:36 | 0 | 0 |  | 2005-12-02 09:36 |  | -- | W Calif & Shoreline Hwy | Mill Valley | Marin Co | 94941 |  |  | 2005-12-02 | [9 empty] | NO WATER INVOLVED | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tamalpais | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWS | Bob Bunce | 2005-12-02 | 415 388 6393 | bbunce@tcsd.us, | MINOR
2200 | 4 | 1 | Tamalpais | 2005-12-02 10:01 | 200 | 0 |  | 2005-12-02 10:01 |  | -- | 388 Carrera | Mill Valley | Marin Co | 94941 |  |  | 2005-12-02 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tamalpais | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWS | Bob Bunce | 2005-12-02 | 415 388 6393 | bbunce@tcsd.us, | MINOR
2208 | 5 | 1 | Tamalpais | 2005-12-02 10:22 | 100 | 0 |  | 2005-12-02 10:22 |  | -- | Shoreline Hwy & Tenn Ave | Mill VAlley | Marin Co | 94941 |  |  | 2005-12-02 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tamalpais | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWS | Bob Bunce | 2005-12-02 | 415 388 6393 | bbunce@tcsd.us, jnelson@tcsd.us | MINOR
2191 | 1 | 1 | Tamalpais | 2005-11-30 11:35 | 3600 | 1500 | 05-6781 | 2005-11-22 | Bob Bunce | Bob Bunce | 203 Marin ave | Mill Valley | Marin co. | 94941 |  |  | 2005-11-22 | 3:00:00 AM | [5 empty] | SUNNY WEATHER | Low | 2 | SURFACE WATER IMPACT | No |  | No | No | DISCOLORATION IN THE WATER |  | Yes | Yes | No | No | No | Yes | Yes | No | No | 2005-12-09 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Tamalpais | OTHER | Force main | INFRASTRUCTURE FAILURE | --Select None-- | --Select None-- | Broken force main | Upon further investigation staff discovered a small (2" diam.)stream of water emerging from the shallow buried 15 Bell Lane sewage force main crossing the creek | P W Superintendent | Bob Bunce | 2005-11-30 | 415-388-6393 | bbunce@tcsd.us, | MAJOR | Bob Bunce | Tamalpais | 415-388-6393 | 12 | 305 Bell Lane | Mill Valley | Marin co. | 94941 | Bob Bunce | Tamalpais c s d | 415-388-6393 | 12 | 305 Bell Lane | Mill Valley | Marin co. | 94941
2210 | 6 | 1 | Tamalpais | 2005-12-02 10:30 | 30 | 0 |  | 2005-12-02 10:30 |  | -- | 296 Morning Sun Ave | Mill Valley | Marin Co | 94941 |  |  | 2005-10-12 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tamalpais | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | PWS | Bob Bunce | 2005-12-02 | 415 388 6393 | bbunce@tcsd.us, jnelson@tcsd.us | MINOR
2213 | 7 | 1 | Tamalpais | 2005-12-02 10:34 | 100 | 0 |  | 2005-12-02 10:34 |  | -- | 1045 Erica Rd. | Mill valley | Marin Co | 94941 |  |  | 2005-09-04 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tamalpais | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | PWS | Bob Bunce | 2005-12-02 | 388 6393 | bbunce@tcsd.us, | MINOR
5119 | 47 | 1 | Tiburon | 2007-04-23 10:39 | 50 | 0 |  | 2007-04-23 10:39 |  | -- | 29 Oak Place | Belvedere | Marin | 94920 |  |  | 2007-04-21 |  |  |  | Employee SD responded to call out.Did not witness any overflow but did see evidence of a prior spill, estimated at 50 gallons max. Asked Roto-Rooter to clean from RH NE11 to MH NE10. Roots removed. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | SO/LD | Tim O'Day | 2007-04-23 | 415-435-1501
5066 | 46 | 1 | Tiburon | 2007-04-17 09:22 | 100 | 0 |  | 2007-04-17 09:22 |  | -- | 8 Eucalyptus | Belvedere | Marin | 94920 |  |  | 2007-04-16 |  |  |  | Employee DL responded to call out. Found rod hole # FA16 overflowing slowly and intermittently. Called Roto Rooter to clean, removed roots. DL estimates total spill at less than 100 gallons. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Senior Operator | Tim O'Day | 2007-04-17 | 415-435-1501
5026 | 45 | 1 | Tiburon | 2007-03-31 | 1200 | 0 | 07-2034 | 2007-03-31 | Steve Balzan (SD5) | Tim O'Day (SD5) | 2270 Mar East | Tiburon | Marin | 94920 |  |  | 2007-03-30 | 0.64653 | [6 empty] | Low | Richardson Bay | STORM DRAIN | No |  | No | No | Yes, By employee TO 03/31/2007. No adverse effects noted. |  | Yes | Yes | No |  |  | Yes | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | INFRASTRUCTURE FAILURE | -- Select One -- | DAMAGE TO COLLECTION SYSTEM |  | Staff responded to SSO report. Found broken 6" sewer line. Damage possibly caused by contractor working at the site. Emergency repair performed by contractor, who replaced a 6' section of the line. | Senior Operator | Tim O'Day | 2007-03-31 | 415-435-1501
5014 | 44 | 1 | Tiburon | 2007-03-27 12:30 | 900 | 0 |  | 2007-03-27 12:30 |  | -- | 1801 Vistazo West | Tiburon | Marin | 94920 |  |  | 2007-03-20 |  |  |  | Employee SD responded to call out. He called RotoRooter to assist.Cleaned from MH# 90 downstream, then upstream from MH#89 to cleanout. Spill estimated at 900 gallons. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Senior Operator | Tim O'Day | 2007-03-27 | 415-435-1501
4821 | 43 | 1 | Tiburon | 2007-02-26 11:40 | 100 | 0 |  | 2007-02-26 11:40 |  | -- | Spring Lane and Rolling Hill Rd., | Tiburon | Marin | 94920 |  |  | 2007-02-22 |  |  |  | Employee TO responded.Found blockage between MH# 250 and MH# 249. MH# 250 filled, did not overflow, but back flowed to a private manhole/christy box which services 3 residences).Spill volume 100 gallons, Roto-Rooter cleared blockage, roots. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | BLOCKAGE | ROOTS |  | Private manhole/ christy box |  | WFM | Tim O'Day | 2007-02-26 | 415-435-1501
4819 | 42 | 1 | Tiburon | 2007-02-26 11:31 | 10 | 0 |  | 2007-02-26 11:31 |  | -- | 34 Cove Rd., | Belvedere | Marin | 94920 |  |  | 2007-02-22 |  |  |  | Employee RA responded. Found minor spill, max 10 gallons at cleanout/rod hole N5.Unsure about reason for spill. Asked Roy's Sewer Co to hydroflush all lines in the area. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | CAUSE UNKNOWN | -- Select One -- |  |  |  | WFM | Tim O'Day | 2007-02-26 | 415-435-1501
4815 | 41 | 1 | Tiburon | 2007-02-26 11:11 | 400 | 0 |  | 2007-02-26 11:11 |  | -- | 245 Round Hill Rd. | Tiburon | Marin | 94920 |  |  | 2007-02-20 |  |  |  | Employee DL responded.Overflowing clean out due to blockage in main sewer line. Called Roto-Rooter to clear from MH# 257 to MH# 256. Removed roots, spill approx 400 gallons. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | WFM | TIm O"Day | 2007-02-26 | 415-435-1501
3972 | 39 | 1 | Tiburon | 2006-10-11 09:07 | 600 | 0 |  | 2006-10-11 09:07 |  | -- | Intersection of Solano St. and Paradise Drive, | Tiburon | Marin | 94920 |  |  | 2006-10-10 |  |  |  | Employees RA/DL responded to report of overflowing manhole (#50). Called Roto Rooter to remove blockage (rags and roots). Estimated spill volume 600 gallons (5gpm for 120 minutes). The spill entered a storm drain and employee TO visually inspected the site where this drain reaches Racoon Straits.There was no adverse effects to aquatic life noted, no fish kill and no abnormal coloration.The area is secluded with difficult access and it was concluded that the spill did not imminently and substantially endanger human health. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | WFM | Timothy O'Day | 2006-10-11 | 415-435-1501 | today@sani5.org | MINOR
3882 | 38 | 1 | Tiburon | 2006-09-15 08:40 | 500 | 0 |  | 2006-09-15 08:40 |  | -- | 215 Roundhill Rd., | Tiburon | Marin | 94920 |  |  | 2006-09-13 |  |  |  | Roto Rooter responded to call from homeoner regarding overflowing cleanout.They determined that the blockage causing the spill was in a District line. Removed blockage (grease, paper towels). Estimated spill volume 500 gallons.Roto Rooter scheduled to return for clean up. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | tiburon | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | WFM | Tim O'Day | 2006-09-15 | 415-435-1501 | today@sani5.org | MINOR
3770 | 37 | 1 | Tiburon | 2006-08-22 07:36 | 200 | 0 |  | 2006-08-22 07:36 |  | -- | 15 Toyon | Belveder | Marin | 94920 |  |  | 2006-08-21 |  |  |  | Employees SD/TO responded to report of sewage spill.Found a broken line (ND12-ND11) leaking very close to manhole ND11. Contained the spill with sandbags, diverting it to the manhole.Arranged for a video inspection of the line followed by a repair/replacement.Work is ongoing 08/22. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | PIPE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | WFM | Tim O'Day | 2006-08-22 | 415-435-1501 | today@sani5.org | MINOR
3708 | 36 | 1 | Tiburon | 2006-08-10 09:22 | 25 | 0 |  | 2006-08-10 09:22 |  | -- | 87 East View | Tiburon | Marin | 94920 |  |  | 2006-08-08 |  |  |  | Employee SB responded to call from homeowner.Found a "trickle" of sewage coming from a small break in the sewer line which was blocked. Called Roto Rooter to clean.Parts of this line were repaired recently.Due to the number of small cracks in the line the whole line (MH 360-643)is to be replaced promptly. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | PIPE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | WFM | Tim O'Day | 2006-08-10 | 415-435-1501 | today@sani5.org | MINOR
3692 | 35 | 1 | Tiburon | 2006-08-07 12:05 | 600 | 0 |  | 2006-08-07 12:05 |  | -- | 987 Tiburon Blvd | Tiburon | Marin | 94920 |  |  | 2006-08-03 |  |  |  | Previously incorrectly reported as private, 08/04, SSO# 3685.Information re-entered per request of Michael Chee (510-622-2333). Manhole #323, 600 gallons spilled, roots removed 100 ft towards # 322.Cleaned by Roto Rooter. SD5 employees RA/JB. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | WFM | Timothy O'Day | 2006-08-07 | 415-435-1501 | today@sani5.org | MINOR
3675 | 34 | 1 | Tiburon | 2006-08-01 07:57 | 200 | 0 |  | 2006-08-01 07:57 |  | -- | 87 East View | Belvedere | Marin | 94920 |  |  | 2006-07-28 |  |  |  | Employee RA found a blockage caused by a small break in the 6" main line on the property of 87 East View.Called Roy's Sewer Service to clean.Estimated spill 200 gallons.RA contacted contractor to repair break in line.Repair process is ongoing as of 08/01/06. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | PIPE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | WFM | Tim O'Day | 2006-08-01 | 415-435-1501 | today@sani5.org | MINOR
3659 | 33 | 1 | Tiburon | 2006-07-25 10:30 | 150 | 0 |  | 2006-07-25 10:30 |  | -- | 228 Beach Rd. | Belvedere | Marin | 94920 |  |  | 2006-07-24 |  |  |  | Overflowing manhole # R24. Roto Rooter estimate 50 gallons spill total. Cleaned from R24 to main line downstream.Found an unmarked manhole further down the line, while cleaning this a second spill of approx 100 gallons occured.Repair work to the line is on going. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | WFM | Tim O'Day | 2006-07-25 | 415-435-1501 | today@sani5.org, | MINOR
3657 | 32 | 1 | Tiburon | 2006-07-25 10:20 | 50 | 0 |  | 2006-07-25 10:20 |  | -- | 40 Harbor Oak Drive, | Tiburon | Marin | 94920 |  |  | 2006-07-22 |  |  |  | Employee TO investigated call out regarding "bubbling manhole". Found manhole #103 overflowing intermittently. Estimated spill 25-50 gallons, which went into storm drain further down the road. Called Roto-Rooter to clean from #103 to #102, roots removed approx 30 ft in. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | WFM | Tim O'Day | 2006-07-25 | 415-435-1501 | today@sani5.org | MINOR
4763 | 40 | 1 | Tiburon | 2007-02-15 09:31 | 50 | 0 |  | 2007-02-15 09:31 |  | -- | 8 Buckeye Drive | Belvedere | Marin | 94920 |  |  | 2006-05-17 |  |  |  | Continuation of #3377 (submitted 5/22/06) and #4759 (submitted 02/15/06). | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | WFM | Tim O'Day | 2007-02-15 | 415-435-1501
3328 | 31 | 1 | Tiburon | 2006-05-10 08:29 | 10 | 0 |  | 2006-05-10 08:29 |  | -- | 16 Eucalyptus | Belvedere | Marin | 94920 |  |  | 2006-05-08 |  |  |  | Employee RA responded and found manhole #FA13 full but not overflowing. There was evidence of a previous overflow (toilet tissue etc). Called Roto Rooter to clean from FA13 to FA14 with 4" then 6" blades.RA saw no spill but estimates earlier spill at 10 gallons max. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | MANHOLE |  | CAUSE UNKNOWN | --Select None-- |  |  |  | WFM | Tim O'Day | 2006-05-10 | 415-435-1501 | today@sani5.org | MINOR
3247 | 30 | 1 | Tiburon | 2006-04-28 09:59 | 50 | 0 |  | 2006-04-28 09:59 |  | -- | 1940 Straights View | Tiburon | Marin | 94920 |  |  | 2006-04-26 |  |  |  | Employees RA/DL investigated and found overflowing rod hole. Roto Rooter cleaned from manhole 81 to manhole 81A and then to "81B" (which is not located on our mapping system).Spill volume est at 50 galls max, all of which soaked into the hillside. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | WFM | Tim O'Day | 2006-04-28 | 415-435-1501 | today@sani5.org | MINOR
3222 | 29 | 1 | Tiburon | 2006-04-21 14:05 | 25 | 0 |  | 2006-04-21 14:05 |  | -- | 8 Crest Rd. | Belverdere | Marin | 94920 |  |  | 2006-04-19 |  |  |  | Employees DL/RA responded and found rod hole #NE13 overflowing slowly ("dribbling")and intermittently. Called Roto Rooter to clear.R/Rooter noted no spill,SD5 estimate 25 gallons max.Dye tested 4/20 from rod hole NE13 to manhole NE5 (Oak) to ensure blockage removed,all OK. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | WFM | Tim O'Day | 2006-04-21 | 415-716-6371 | today@sani5.org | MINOR
2814 | 28 | 1 | Tiburon | 2006-02-15 14:24 | 10 | 0 |  | 2006-02-15 14:24 |  | -- | 1725 Vistazo West | Tiburon | Marin | 94920 |  |  | 2006-02-15 |  |  |  | Resident reported sewer spill close to 1725 Vistazo West. Employee RA responded,found manhole #75 full but not overflowing.There was evidence of previous spillage, RA estimated very minor, maximum 10 gallons. Called R/Rooter mainliner to clean from manhole #75 to manhole # 85. Blockage of roots and grease removed, approx 450 ft upstream from #75. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | WFM | Tim O'Day | 2006-02-15 | 415-435-1501 | today@sani5.org | MINOR
2796 | 27 | 1 | Tiburon | 2006-02-13 14:12 | 100 | 0 |  | 2006-02-13 14:12 |  | -- | 1875 Mountain View Drive | Tiburon | Marin | 94920 |  |  | 2006-02-13 |  |  |  | Employee RA responded to callout. Found Cleanout #91A overflowing slowly and intermittently.Called R/Rooter. "Small machine" unable to dislodge blockage, eventually requested the "mainliner" which removed a large ball of roots. RA estimated spill at "less than 100 gallons". | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | WFM | Tim O'Day | 2006-02-13 | 415-435-1501 | today@sani5.org | MINOR
2782 | 25 | 1 | Tiburon | 2006-02-09 07:51 | 100 | 0 |  | 2006-02-09 07:51 |  | -- | 1810 Vistazo West | Tiburon | Marin | 94920 |  |  | 2006-02-08 |  |  |  | Rec'd call regarding "bubbling manhole" close to 1810 Vistazo West approx 5pm.Employee TO responded and found manhole #89 slowly and intermittently overflowing.Checked downstream manhole #75-slow but constant flow, indicating a partial blockage.Roto Rooter cleaned from #75 to #89 and removed the blockage-lots of roots. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | WFM | Tim O'Day | 2006-02-09 | 415-435-1501 | today@sani5.org | MINOR
2465 | 22 | 1 | Tiburon | 2006-01-04 08:24 | 50 | 0 |  | 2006-01-04 08:24 |  | -- | San Rafael Ave and Windward | Belvedere | Marin | 94920 |  |  | 2005-12-31 |  |  |  | Employee SB responded to report of overflowing manhole #C5, located close to the intersection of San Rafael Ave. and Windward. Found manhole #C5 spilling intermittently. Located blockage between manhole #C2 and Pump Station 3. Roto Rooter cleaned. Estimated spill 50 gallons max. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | WFM | Timothy O'Day | 2006-01-04 | 415-435-1501 | today@sani5.org | MINOR
2467 | 23 | 1 | Tiburon | 2006-01-04 08:35 | 500 | 0 |  | 2006-01-04 08:35 |  | -- | 1165 Tiburon Blvd | Tiburon | Marin | 94920 |  |  | 2005-12-31 |  |  |  | Employees RL and SB responded to call from Tiburon PD regarding overflowing manhole. Found manhole #301 to be overflowing slowly but constantly.Combination of high tides,heavy rain and temporary malfunction at Pump Station 7 caused the spill. No blockage.Estimated spill volume 250-500 gallons. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | WFM | Timothy O'Day | 2006-01-04 | 415-435-1501 | today@sani5.org | MINOR
2469 | 24 | 1 | Tiburon | 2006-01-04 08:42 | 200 | 0 |  | 2006-01-04 08:42 |  | -- | Mar East | Tiburon | Marin | 94920 |  |  | 2005-12-31 |  |  |  | Employees RL and SB responded to report of overflowing manhole. Found manhole #37 to be overflowing. Cleaned from manhole #35 to #37 with Roto Rooter.Estimated spill volume 100-200 gallons.Found evidence of broken pipe-stones etc. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | WFM | Timothy O'Day | 2006-01-04 | 415-435-1501 | today@sani5.org | MINOR
2340 | 21 | 1 | Tiburon | 2005-12-28 09:41 | 25 | 0 |  | 2005-12-28 09:41 |  | -- | Alcatraz Avenue,close to Main St., | Tiburon | Marin | 94920 |  |  | 2005-12-27 |  |  |  | Employee DL responded to report of overflowing manhole (#29/643) and noted small but constant overflow. Called Roto Rooter to clear with "small machine".Spill volume estimated at 25 gallons maximum. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | WFM | Timothy O'Day | 2005-12-28 | 415-435-1501 | today@sani5.org | MINOR
2332 | 20 | 1 | Tiburon | 2005-12-24 08:59 | 100 | 0 |  | 2005-12-24 08:59 |  | -- | 29 Eucalyptus | Belvedere | Marin | 94920 |  |  | 2005-12-23 |  |  |  | Employee TO received call regarding overflowing manhole. Found manhole #FC2 full and intermittently overflowing. Checked downstream manhole #FC1-constant but slow flow from #FC2. Called Roto Rooter to clear, using a "small machine" as distance between manholes was short. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | WFM | Timothy O'Day | 2005-12-24 | 415-435-1501 | today@sani5.org | MINOR
2304 | 19 | 1 | Tiburon | 2005-12-22 10:08 | 50 | 0 |  | 2005-12-22 10:08 |  | -- | 46 Bay View | Belvedere | Marin | 94920 |  |  | 2005-12-19 |  |  |  | Resident reported sewer spill close to 46 Bay View, approx 1700 hrs. Employees TO and JB responded, found signs of prior spill (tissue paper)but no spill or flow at time of inspection.Called Roto Rooter to clear. Employee RA followed up and checked 12/20 am and found all OK. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | WFM | Timothy O'Day | 2005-12-22 | 415-435-1501 | today@sani5.org | MINOR
2256 | 18 | 1 | Tiburon | 2005-12-15 09:25 | 25 | 0 |  | 2005-12-15 09:25 |  | -- | 152 Bella Vista | Belvedere | Marin | 94920 |  |  | 2005-12-13 |  |  |  | Overflowing manhole (#RA3) reported 12/13 approx 2100 hours.Employee SB responded, found manhole not overflowing, appro 1/2 full but there were signs of a previous overflow (wet ground around manhole).SB worked with Roto Rooter until 12/14 0030 hours, cleaning from manhole RA3 towards manhole RA2 (120 ft cleaned), then from RA2 (which was about 1/2 full) towards manhole RA1 (120 ft cleaned). Work continued 12/14:Employees SB and RA continued working with Roto Rooter cleaning 120 ft RA3 to RA2 with larger blades (4") Work continued 12/15: Employees RA and SB continued working with Roto Rooter (small mainliner), cleaning RA3 to RA2 completely with 6" blades. No spill was actually seen by SD5 employees. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | WFM | Timothy O'Day | 2005-12-15 | 415-435-1501 | today@sani5.org | MINOR
2174 | 17 | 1 | Tiburon | 2005-11-27 06:26 | 100 | 0 |  | 2005-11-27 06:26 |  | -- | 242 Bay View | Belvedere | Marin | 94920 |  |  | 2005-11-24 |  |  |  | Resident called regarding overflowing manhole (#RA2) close to 242 Bay View.Employee TO responded. Called for Roto Rooter small mainliner. Unable to remove blockage from intermittently overflowing manhole, continous but slow flow at downstream manhole (#RA1).Roto Rooter rod and blade (4") broke and became stuck in line. Stopped work at 2030 hrs. Continued 11/25 a.m. (employee TO with Roto Rooter), removed blockage, tried without success to remove rod and blade. Estimated spill: max 100 gallons | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | tiburon | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | WFM | Tim O'Day | 2005-11-27 | 415-435-1501 | today @sani5.org | MINOR
2131 | 16 | 1 | Tiburon | 2005-11-17 06:20 | 10 | 0 |  | 2005-11-17 06:20 |  | -- | 107 Golden Gate Ave. | Belvedere | Marin | 94920 |  |  | 2005-11-16 |  |  |  | Employee RA responded to callout, resident had reported wetness around a manhole (#FA15). No overflow noted, but wetness present and manhole close to full. Called Roto Rooter to clean from MH FA15 to MH FA10 with "mainliner" using 6" blades (after punching a hole with 2" blades). | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | WFM | Timothy O'Day | 2005-11-17 | 415-435-1501 | today@sani5.org | MINOR
2067 | 14 | 1 | Tiburon | 2005-10-31 07:00 | 100 | 0 |  | 2005-10-31 07:00 |  | -- | Rod hole close to 312 Beach Rd., Belvedere. | Tiburon | Marin | 94920 |  |  | 2005-10-28 |  |  |  | Intermittent spill, small volume, estimate 100 gallons max.See SSO # 2030.Roto Rooter cleaned with 4" then 6" blades.Stoppage cleared approx 1345 hrs, roots found 80' downstream of rod hole. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | WFM | Tim O'Day | 2005-10-31 | 415-435-1501 | today@sani5.org | MINOR
2030 | 13 | 1 | Tiburon | 2005-10-25 06:04 | 100 | 0 |  | 2005-10-25 06:04 |  | -- | Rod hole #RD1 close to 312 Beach Rd. | Belvedere | Marin | 94920 |  |  | 2005-10-24 |  |  |  | Resident called in overflow approx 4:30pm. Called Roto Rooter to assist, RR technician (David) cleaned with 2" then 4" blades, removing roots, will return 10/25 to clean with 6" blades. Blockage cleared approx 5:45pm.Spill was intermittent,stop and go, estimate 100 gallons max. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | WFM | Tim O'Day | 2005-10-25 | 415-435-1501 | today@sani5.org | MINOR
2005 | 11 | 1 | Tiburon | 2005-10-24 10:55 | 100 | 0 |  | 2005-10-24 10:55 |  | -- | 1735 Vistazo West | Tiburon | Marin | 94920 |  |  | 2005-10-21 |  |  |  | 10/21/05 approx 8:30 pm resident called Roto Rooter, reported sewage entering his bathtub. RR cleared blockage in District sewer line via previously closed clean-out located in garage.Before blockage removed sewage overflowed from bath tub onto floor and also from opened clean-out into garage.RR tech (Phil) estimated spill at 100 gallons.RR returned 10/22/05 8:00 am to continue cleaning District line from manhole 85 with 6" blades.Talked with home owner 10/22 and 10/24, will call again 10/27. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | PIPE |  | BLOCKAGE | ROOTS |  |  |  | WFM | Tim O'Day | 2005-10-24 | 415-435-1501 | today@sani5.org | MINOR
2007 | 12 | 1 | Tiburon | 2005-10-24 10:59 | 100 | 0 |  | 2005-10-24 10:59 |  | -- | 1735 Vistazo West | Tiburon | Marin | 94920 |  |  | 2005-10-21 |  |  |  | 10/21/05 approx 8:30 pm resident called Roto Rooter, reported sewage entering his bathtub. RR cleared blockage in District sewer line via previously closed clean-out located in garage.Before blockage removed sewage overflowed from bath tub onto floor and also from opened clean-out into garage.RR tech (Phil) estimated spill at 100 gallons.RR returned 10/22/05 8:00 am to continue cleaning District line from manhole 85 with 6" blades.Talked with home owner 10/22 and 10/24, will call again 10/27. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | PIPE |  | BLOCKAGE | ROOTS |  |  |  | WFM | Tim O'Day | 2005-10-24 | 415-435-1501 | today@sani5.org | MINOR
1979 | 9 | 1 | Tiburon | 2005-10-17 14:29 | 100 | 0 |  | 2005-10-17 14:29 |  | -- | Manhole #67, close to 1920 Centro West. | Tiburon | Marin | 94920 |  |  | 2005-10-17 |  |  |  | Overflowing manhole (#67)reported to office.Tim O'Day investigated, found signs of spill (wet road surface and wet land next to road)but blockage cleared. Called Roto-Rooter to clean the line anyway-to prevent further problems.Cleaned from MH67 to MH68 | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | WFM | Timothy O'Day | 2005-10-17 | 415-435-1501 | today@sani5.org | MINOR
1907 | 8 | 1 | Tiburon | 2005-10-03 12:48 | 75 | 0 |  | 2005-10-03 12:48 |  | -- | 64 Lagood Road, Belvedere/ Pump Station # 9 | Belvedere | Marin | 94920 |  |  | 2005-10-03 |  |  |  | Recieved call of sewage spilling for home owners cleanout at Number 64 Lagoon Rd.@ 1021hr. Staff found manholes on Lagoon Rd. full Check Pump Station # 9 and found inlet pipe to station plugged. Used Hand Rod to clear stoppage. Everything back to normal at 1045hr. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | CLEAN OUT |  | CAUSE UNKNOWN | --Select None-- |  |  |  | Asst Dist Manager | Robert L .Lynch | 2005-10-03 | 415-435-1501 | rlynch@sani5.org | MINOR
1816 | 7 | 1 | Tiburon | 2005-09-21 14:00 | 100 | 0 |  | 2005-09-21 14:00 |  | -- | No. 7 Bellview Ave | Belvedere | Marin | 94920 |  |  | 2005-09-21 |  |  |  | Recieved call of wetness on ground around Manhole in front of No. 7 Bellview Ave At 1129 hr. Called Roto Rooter,they cleared stoppage at 1215hr | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Assistant Dist Mang | Robert Lynch | 2005-09-21 | 415-435-11501 | rlynch@sani5.org | MINOR
1551 | 6 | 1 | Tiburon | 2005-06-21 15:30 | 300 | 0 |  | 2005-06-21 15:30 |  | -- | 90 Round Hill Rd | Tiburon | Marin | 94920 |  |  | 2005-06-21 |  |  |  | Roots from upstream came down and blocked MH outlet | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | tiburon | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Sr Operator | Michael Jones | 2005-06-21 | 415 435-1501 | mjones@sani5.org | MINOR
967 | 5 | 1 | Tiburon | 2005-02-04 11:20 | 50 | 0 |  | 2005-02-04 11:20 |  | -- | While performing GPS Locating for Sewer System Evalution staff found Rodhole No.8-B overflowing. Called Roto Rooter closes street address 1915 Mar West. Recieved call at 1030hr and Roto Rooter Arrived at 1100hr stoppage cleared at 1130hr.Had Roto Rooter clean both directions from M/H No.8 from 8 to 8A and 8 to 8B | Tiburon | Marin | 94920 |  |  | 2005-02-04 |  |  |  | There is only one home on this short section of pipe. sewage was not spilling when district staff arrived but it looked like it was recently Responding party Randy Armbruster | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Robert Lyncg | 2005-02-04 | 415-435-1501 | rlynch3718@aol.com | MINOR
885 | 4 | 1 | Tiburon | 2005-01-21 09:18 | 50 | 0 |  | 2005-01-21 09:18 |  | -- | 280 Round Hill Road. Clean-out at 280 Round Hill Rd overfowing District line plugged with roots. Called Roto Rooter and cleared stoppage. | Tiburon | Marin | 94920 |  |  | 2005-01-20 |  |  |  | Recieved call home owner at 280 Round Hill Road at 1550 hr responded and found Rescue Rooter working on homeowners privare line. Rescue Rooter cleaned approx 110ft and was unable to clear stoppage. District Staff had Roto Rooter clear stoppage from M/H No. 259 to next man-Hole stoppage at 130 feet.Med roots | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Robert Lynch | 2005-01-21 | 415-435-1501 | rlynch3718@aol.com | MINOR
879 | 3 | 1 | Tiburon | 2005-01-19 16:48 | 425 | 0 |  | 2005-01-19 16:48 |  | -- | 101Mount Tiburon Manhole No. 278 | Tiburon | Marin | 94920 |  |  | 2005-01-19 |  |  |  | Recieved Call of Overflowing Manhole at1505 hr Called Roto Roote. Roto Rooter arrived at 1610 hr and stopage was cleared at 1630 hr.Roto Rooter ran from M/H No.277 to M/H No. 278 Stopage was 6" roots 4 foot long 65 feet out. Roto Rooter cleaned entire line from M/H 277to 278 | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Robert Lynch | 2005-01-19 | 415-435-1501 | rlynch3718@aol.com | MINOR
498 | 2 | 1 | Tiburon | 2004-12-10 14:44 | 200 | 0 |  | 2004-12-10 14:44 |  | -- | Neds Way behind Telephone Builbing | Tiburon | Marin | 94920 |  |  | 2004-12-10 |  |  |  | R'cd call at 1310hr arrived on site of spill at 1316hr Called Roto Rooter. Roto Rooter arrived at 1415hr . Stopage was cleared at 1425hr.The manhole was not spilling when we arrived. Looking at the surounding area it appears to be Approx: 200 gallons | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Tiburon | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Acting Superintenden | Robert Lynch | 2004-12-10 | 415-435-1051 |  | MINOR
398 | 1 | 1 | Tiburon | 2004-12-02 14:47 | 105 | 0 |  | 2004-12-02 | Robert Lynch |  | 1476 Vistazo West Man-Hole No.135 | Tiburon | Marin | 94920 |  |  | 2004-12-02 | 9:30:00 AM | 2004-12-02 | 11:15:00 A | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Acting/ Superentende | Robert Lynch | 2004-12-02 | 1-415-435-1501 |  | 24HR |  |  | 1-415-435-1501 | [6 empty] | Tiburon
4704 | 11 | 2 | Union | 2007-02-08 11:29 | 480 | 0 |  | 2007-02-08 11:29 |  | -- | USD MH# T23068, 631 Enos St. X Coit Dr. | Fremont | Alameda | 94536 |  |  | 2006-12-27 |  |  |  | Spill was contained in the storm drain. Spill area, storm drain, and manholes washed down and all waste water reclaimed. It was determined that this was caused by debris from construction of a new development. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Manager | Andy Morrison | 2007-02-08 | 510-477-7542
3980 | 10 | 1 | Union | 2006-10-13 15:15 | 300 | 0 |  | 2006-10-13 15:15 |  | -- | Mission Blvd. and the Masonic Home. | Union City | Alameda | 94587 |  |  | 2006-10-05 |  |  |  | Rags from Masonic home. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | union | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Coach | Shawn Nesgis | 2006-10-13 | 510-477-7552 | andy_morrison1@unionsanitary.com, rich_currie@unionsanitary.com | MINOR
4702 | 10 | 3 | Union | 2007-02-08 11:27 | 300 | 0 |  | 2007-02-08 11:27 |  | -- | near 34400 Mission Blvd. the Masonic Home. | Union City | Alameda | 94587 |  |  | 2006-10-05 |  |  |  | Rags from Masonic home were the cause of the blockage. The area was washed down all the water was returned to the collection system. The case was referred to our Environmental Compliance Team for source control. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Manager | Andy Morrison | 2007-02-08 | 510-477-7542
3879 | 9 | 1 | Union | 2006-09-14 09:07 | 150 | 0 |  | 2006-09-14 09:07 |  | -- | Union Sanitary District Manhole #AB09027, Ardenwood Road, 1300'north of Paseo Padre Parkway. | Fremont | Alameda | 94555 |  |  | 2006-09-03 |  |  |  | This is the location of a emergency temporary by-pass for Alameda Creek. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Union | OTHER | by-pass pump | BYPASS | --Select None-- |  |  |  | coach | Shawn Nesgis | 2006-09-14 | 510-477-7552 | andy_morrison1@unionsanitary.com, rich_currie@unionsanitary.com | MINOR
4700 | 9 | 2 | Union | 2007-02-08 11:22 | 150 | 0 |  | 2007-02-08 11:22 |  | -- | Union Sanitary District Manhole #AB09027, Ardenwood Road, 1300'north of Paseo Padre Parkway. | Fremont | Alameda | 94555 |  |  | 2006-09-03 |  |  |  | This is the location of an emergency temporary by-pass for a 33" trunk which crosses Alameda Creek. The contractor misconfigured the discharge line, which cracked open. The area was washed down and all the water was returned to the collection system. USD staff directed the contractor to replace the solid discharge lines with flexible lines. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | OTHER |  | BYPASS | -- Select One -- |  | by-pass pump |  | Manager | Andy Morrison | 2007-02-08 | 510-477-7542
3338 | 8 | 1 | Union | 2006-05-15 14:06 | 300 | 0 |  | 2006-05-15 14:06 |  | -- | 32220 Dyer | Union City | Alameda | 94587 |  |  | 2006-05-09 |  |  |  | Contained spill in storm drain, cleaned contaminated strom drain and reclaimed wash down water | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Union | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Coach | James Schofield | 2006-05-15 | 510-477-7553 | andy_morrison1@unionsanitary.com, rich_currie@unionsanitary.com | MINOR
4698 | 8 | 2 | Union | 2007-02-08 11:18 | 300 | 0 |  | 2007-02-08 11:18 |  | -- | 32220 Dyer | Union City | Alameda | 94587 |  |  | 2006-05-09 |  |  |  | Contained spill in storm drain, cleaned contaminated strom drain and reclaimed wash down water. Our main was placed on Selective Maintenance and the case was referred to our Environmental Compliance Team for soruce control. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Manager | Andy Morrison | 2007-02-08 | 510-477-7542
2586 | 7 | 1 | Union | 2006-01-09 12:19 | 500 | 0 |  | 2006-01-09 12:19 |  | -- | 43694 Pine st. | Fremont | Alameda | 94536 |  |  | 2005-12-31 |  |  |  | Washed down street and cleaned storm drain, Reclaimed spill and wash down water and returned to sanitary sewer. Reviewed history of the structure and preformed CCTV; placed line on 24 month hydro/chain flail to control grease build up. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Union | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Coach | James Schofield | 2006-01-09 | 510-477-7553 | andy_morrison1@unionsanitary.com, rich_currie@unionsanitary.com | MINOR
1869 | 6 | 7 | Union | 2005-09-26 13:51 | 13200 | 12540 | 05-4120 | 2005-07-12 | Roger Ham | union | 8700 Thornton Ave. (Union Sanitary District's Newark Pump Station) | Newark | Alameda | 94560 |  |  | 2005-07-12 | 7:04:00 AM | [5 empty] | SUNNY WEATHER | Low |  | YARD/LAND | No | Not applicable | No | No | Did not enter waters of the State or reciving water |  | Yes | Yes | No | No | No | No | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | union | OTHER | When changing valve configuration to allow boosting of the force main,operator did not verify valve(s) status causing pumping against a closed valve and over flow of system surge tower | FLOW CAPACITY DEFICIENCY | --Select None-- | --Select None-- |  | While attempting to boost force main flow, operator directed flow to a closed valve, causing wastewater to be discharged from the system surge tower. The majority of the discharge drained back to the gravity sewer via catch basins in the asphatted area around the pump station. Approximatel 13,2000 gallons accummulated on bare land adjacent to the station. Clean up was under taken immediately, using vactors and portable pumping, with an estimated recovery of 95% or 12,540 gallons. The spill area and paved area around the station was flushed with fresh water which was recovered and returned to the sanitary sewer. All evidence of sewer debris was removed. Masking agent was applied to mitigate any possible odors. | Workgroup Manager | Roger Ham | 2005-07-12 | 510-477-7450 | andy_morrison1@unionsanitary.com, rich_currie@unionsanitary.com | MAJOR | Roger Ham | Union | 510-477-7540 |  | 5072 Benson Road | Union City | Alameda | 94587 | Roger Ham | Union Sanitary District | 510-477-7540 |  | 5072 Benson Road | Union City | Alameda | 94587
1189 | 5 | 1 | Union | 2005-03-15 14:40 | 350 | 0 |  | 2005-03-15 14:40 |  | -- | 4685 Pine | Fremont | Alamed | 94536 |  |  | 2005-02-28 |  |  |  | Will inspect line for cause and place on appropriate preventative maintenance | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Union | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Coach | James Schofield | 2005-03-15 | 510-477-7553 | andy_morrison1@unionsanitary.com, rich_currie@unionsanitary.com | MINOR
1057 | 4 | 4 | Union | 2005-02-17 16:54 | 51540 | 48963 | 05-0871 | 2005-02-08 | Roger Ham | union | 4800 ft. South of Automall Prkwy & 3000 feet west of Cushing Rd. | Fremont | Alameda | 94536 |  |  | 2005-02-07 | 1:55:00 PM | [5 empty] | SUNNY WEATHER | Medium |  | YARD/LAND | No |  | No | No | Spill contained in wet land area and did not reach recieving water. Sampling of near by flood control channel verified that spill was contained. |  | Yes | Yes | No | No | No | Yes | Yes | No | No | 2005-03-15 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | union | MANHOLE | 2" nipple on force main acess cover broke off at the threaded flange. | INFRASTRUCTURE FAILURE | --Select None-- | --Select None-- | 2" nipple on force main acess cover broke off at the threaded flange. | At 13:55 we recieved a service request informing us that a manhole was overflowing. Our first responder arrive at 14:30 to assess the situation, and called for a hydro-vac. A collection system supervisor arrived on site who determined the SSO was coming from a force main manhole, and notified the maintenance supervisor. At 15:37 the head gate at the pump station was closed to releave the pressure on the force main remotely via SCADA. A pump station mechanic was dispatched, and isolated the force main and began back draining to the pump station wet well. At 16:30 the SSO ceased completely. Collection system staff began recovery using two hydro-vacs that were on site. Due to the volumn of the spill, it was decided to start the recovery immediately. A 6" pump was set up and the recovered wastewater was pumped back into the force main through the access by 22:30 and continued until the pump lost suction at 23:50 at which time the operation was secured until the following day. (see attached chronology)Please note that field did not forward from version #2 to version #3 | Manager | Roger Ham | 2005-02-08 | 510-477-7540 | roger_ham@unionsanitary.com | MAJOR | Roger Ham | Union Sanitary District | 510-477-7540 |  | 5072 Benson Road | Union City | Alameda | 94587 | Roger Ham | union | 510-477-7540 |  | 5072 Benson Road | Union City | Alameda | 94587
959 | 3 | 1 | Union | 2005-02-04 07:30 | 850 | 0 |  | 2005-02-04 07:30 |  | -- | 2493 Plumleigh dr. | Fremont | Alameda | 94538 |  |  | 2005-01-29 |  |  |  | Cleaned storm drain and reclaimed water, changed maintenance schedule on line. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | union | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Coach | James Schofield | 2005-02-04 | 510-477-7553 | andy_morrison1@unionsanitary.com | MINOR
792 | 2 | 1 | Union | 2005-01-10 08:33 | 748 | 0 |  | 2005-01-10 08:33 |  | -- | In front of the adress of 511 Pickering rd. | Fremont | Alameda | 94538 |  |  | 2005-01-04 |  |  |  | Spill was contained in storm drain sump. All 748 gallons of spill recovered. Spill amount did not trigger affluent pump. Will inspect line and evaluate for next steps. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Union | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Coach | James Schofield | 2005-01-10 | 510-477-7553 | andy_morrison1@unionsanitary.com | MINOR
576 | 1 | 1 | Union | 2004-12-17 12:34 | 300 | 0 |  | 2004-12-17 12:34 |  | -- | In front of address 2265 Medallion Dr. | Union City | Alameda | 94587 |  |  | 2004-12-17 |  |  |  | Increased preventative maintentance schedule. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | Union | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Coach | James Schofield | 2004-12-17 | 510-477-7553 | james_schofield@unionsanitary.com | MINOR
4641 | 83 | 1 | VallejoSFCD | 2007-01-30 13:07 | 125 | 0 |  | 2007-01-30 13:07 |  | -- | 179 Viewmont Avenue | Vallejo | Solano | 94590 |  |  | 2007-01-27 |  |  |  | Cleared blockage and recovered 75 gallons of sewage and returned it to the sanitary sewer system. The rest soaked into the ground. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | FOPS Superintendent | Lonnie Holt | 2007-01-30 | 707-644-8949
4624 | 82 | 1 | VallejoSFCD | 2007-01-26 09:31 | 940 | 0 |  | 2007-01-26 09:31 |  | -- | 976 Admiral Callaghan Lane | Vallejo | Solano | 94590 |  |  | 2007-01-24 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | FOPS Superintendent | Lonnie Holt | 2007-01-26 | 707-644-8949
4550 | 80 | 1 | VallejoSFCD | 2007-01-18 11:25 | 500 | 0 |  | 2007-01-18 11:25 |  | -- | 3 Howard Street | Vallejo | Solano | 94590 |  |  | 2007-01-17 |  |  |  | Cleared blockage with jet machine and did cleanup with a vacuum truck. Recovered 400 gallons of the original spill and returned to the sanitary sewer system. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | FOPS Supt | Lonnie Holt | 2007-01-18 | 707-644-8949
4533 | 79 | 1 | VallejoSFCD | 2007-01-17 13:19 | 100 | 0 |  | 2007-01-17 13:19 |  | -- | 360 Del Mar Ave | Vallejo | Solano | 94590 |  |  | 2007-01-14 |  |  |  | Area Vacuumed up of debris. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | FOPS Supt | Lonnie Holt | 2007-01-17 | 707-644-8949
4442 | 78 | 1 | VallejoSFCD | 2007-01-04 07:06 | 100 | 0 |  | 2007-01-04 07:06 |  | -- | Magazine Street and Interstate 80 Highway | Vallejo | Solano | 94590 |  |  | 2006-12-30 |  |  |  | Area around overflow cleaned up (paper and debria) | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | FOPS Supt | Lonnie Holt | 2007-01-04 | 707-644-8949
4424 | 77 | 1 | VallejoSFCD | 2006-12-29 13:48 | 250 | 0 |  | 2006-12-29 13:48 |  | -- | 1812 Redwood Street | Vallejo | Solano | 94590 |  |  | 2006-12-29 |  |  |  | Used vacuum truck to clear blockage and a poker and shovel to remove big chunk of asphalt wedged in line. Used vacuum truck to clean up area around spill. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-12-29 | 707-644-8949
4422 | 76 | 1 | VallejoSFCD | 2006-12-29 | 2040 | 500 | 06-7680 | 2006-12-29 | Lonnie Holt | VallejoSFCD | 1812 Redwood Street | Vallejo | Solano | 94590 |  |  | 2006-12-28 | 0.81944 | [6 empty] | Low | Austin Creek/Napa River | STORM DRAIN | No |  | No | No | No visual sign of spill at point of discharge |  | Yes | Yes | No |  |  | Yes | Yes |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS | -- Select One -- |  | Used vacuum truck to suck down the overflowing manhole and a flusher to clear the blockage. Found large chunk of concrete in pipe that caused blockage. Used vacuum truck to clean up the area of the spill down to and including the inside of the catch basin that the spill entered to get into the storm drain system. | FOPS Superintendent | Lonnie Holt | 2006-12-29 | 707-644-8949
4191 | 75 | 1 | VallejoSFCD | 2006-12-05 08:48 | 500 | 0 |  | 2006-12-05 08:48 |  | -- | 480 Porter Street | Vallejo | Solano | 94590 |  |  | 2006-12-03 |  |  |  | Spill occurred while jetting line to clear blockage. Able to capture all 500 gals. and return to sanitary system with a vacuum truck. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-12-05 | (707) 644-8949
4189 | 74 | 1 | VallejoSFCD | 2006-12-05 08:41 | 200 | 0 |  | 2006-12-05 08:41 |  | -- | Intersection of Buss Avenue and Annette Avenue | Vallejo | Solano | 94589 |  |  | 2006-12-01 |  |  |  | Used jet machine to clear blockage and vacuum truck to recover all 200 gals., of the spill. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-12-05 | (707) 644-8949
4120 | 73 | 1 | VallejoSFCD | 2006-11-20 10:00 | 300 | 0 |  | 2006-11-20 10:00 |  | -- | The intersection of Buss and Russell at a manhole. | Vallejo | Solano | 94589 |  |  | 2006-11-20 |  |  |  | Manhole Overflowed 300 gallons and we recovered 275 gallons | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | FOPS Superintendant | Lonnie Holt | 2006-11-20 | (707) 644-8949
4111 | 72 | 2 | VallejoSFCD | 2006-11-14 11:29 | 1200 | 0 | 06-6701 | 2006-11-11 | Ken Taylor | VallejoSFCD | 617 Porter Street | Vallejo | Solano | 94590 |  |  | 2006-11-11 | 1:00:00 PM | [5 empty] | RAINY WEATHER | Low | Napa River/Mare Island Strait | STORM DRAIN | No |  | No | No | No visual signs of spill at point of storm drain discharge |  | Yes | Yes | No | No | No | Yes | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | VallejoSFCD | MANHOLE |  | BLOCKAGE | GREASE | --Select None-- |  | Blockage cleared with jet machine and area cleaned up with vacuum truck. Storm Drain system also cleaned and vacuumed. | FOPS Superintendent | Lonnie Holt | 2006-11-14 | (707) 644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MAJOR | Lonnie Holt | VallejoSFCD | 707-644-8949 | 271 | 450 Ryder Street | Vallejo | Solano | 94590 | Lonnie Holt | VallejoSFCD | 707-644-8949 | 271 | 450 Ryder Street | Vallejo | Solano | 94590
4105 | 71 | 1 | VallejoSFCD | 2006-11-14 08:53 | 600 | 0 |  | 2006-11-14 08:53 |  | -- | 14 Selfridge Street | Vallejo | Solano | 94590 |  |  | 2006-11-09 |  |  |  | Spill contained in crawl space under building and vacuumed up and all 600 gals. returned to the sanitary sewer system. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | PIPE |  | BLOCKAGE | ROOTS |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-11-14 | (707) 644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
4101 | 69 | 1 | VallejoSFCD | 2006-11-14 08:32 | 250 | 0 |  | 2006-11-14 08:32 |  | -- | 448 Washington Street | Vallejo | Solano | 94590 |  |  | 2006-11-08 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Field Operations Sup | Lonnie Holt | 2006-11-14 | (707) 644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
4103 | 70 | 1 | VallejoSFCD | 2006-11-14 08:40 | 125 | 0 |  | 2006-11-14 08:40 |  | -- | Intersection of Patrick Court and Parkwood Drive | Vallejo | Solano | 94590 |  |  | 2006-11-08 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-11-14 | (707) 644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
3998 | 68 | 1 | VallejoSFCD | 2006-10-17 09:30 | 400 | 0 |  | 2006-10-17 09:30 |  | -- | 27 St. Francis St. | Vallejo | Solano | 94590 |  |  | 2006-10-15 |  |  |  | Recovered all 400 gallons of the spill and returned it to the sanitary sewer system. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Field Operations Sup | Lonnie Holt | 2006-10-17 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
3914 | 66 | 1 | VallejoSFCD | 2006-09-22 08:30 | 200 | 0 |  | 2006-09-22 08:30 |  | -- | 1881 Mini Drive | Vallejo | Solano | 94590 |  |  | 2006-09-22 |  |  |  | Cleared blockage with Jet Machine and cleaned up with vacuum truck. Recovered 160- gallons of spill and returned to sanitary sewer system. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-09-22 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
3953 | 67 | 2 | VallejoSFCD | 2006-10-02 14:10 | 3800 | 0 | 06-5638 | 2006-09-21 | VallejoSFCD | VallejoSFCD | 1202 Sereno Drive - Back Propertyline easement main | Vallejo | Solano | 94590 | 38 07' N | 122 14' W | 2006-09-20 | 8:15:00 PM | [5 empty] | SUNNY WEATHER | Low | White Slough/Napa River | STORM DRAIN | No |  | No | No | No visable debris,discoloration of the water, or odors. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | VallejoSFCD | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- |  | TV'd mainline, found buried manhole, raised to grade and made entry to remove roots in channel and put on root foaming schedule. | FOPS Superintendent | Lonnie Holt | 2006-09-22 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MAJOR | Lonnie Holt | VallejoSFCD | 707-644-8949 | 271 | 450 Ryder Street | Vallejo | Solano | 94590 | Lonnie Holt | VallejoSFCD | 707-644-8949 | 271 | 450 Ryder Street | Vallejo | Solano | 94590
3833 | 64 | 1 | VallejoSFCD | 2006-09-05 11:44 | 100 | 0 |  | 2006-09-05 11:44 |  | -- | Intersection of 5th Street and McLane Street | Vallejo | Solano | 94590 |  |  | 2006-09-01 |  |  |  | Used flusher to clear blockage and vacuum truck to clean up and recover spill. Recovered all of spill and returned it to the sanitary sewer. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-09-05 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
3835 | 65 | 1 | VallejoSFCD | 2006-09-05 11:52 | 300 | 0 |  | 2006-09-05 11:52 |  | -- | 2799 Georgia Street | Vallejo | Solano | 94590 |  |  | 2006-08-31 |  |  |  | Used flusher to clear blockage and vacuum truck to clean up spill. Recovered 250 gallons of the spill and returned it to the sanitary sewer. The other 50 gallons was absorbed by the ground. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-09-05 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
3679 | 63 | 1 | VallejoSFCD | 2006-08-02 16:11 | 500 | 0 |  | 2006-08-02 16:11 |  | -- | Intersection of Sereno Drive and Tuolumne Street | Vallejo | Solano | 94590 |  |  | 2006-08-02 |  |  |  | Cleared with a flusher and recovered 450 gallons of spill with vacuum truck from storm drain system. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-08-02 | (707) 644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
3587 | 62 | 1 | VallejoSFCD | 2006-06-30 07:59 | 200 | 0 |  | 2006-06-30 07:59 |  | -- | 120 Whitesides Drive | Vallejo | Solano | 94590 |  |  | 2006-06-29 |  |  |  | Cleared blockage with flusher and cleaned up area that was affected by the spill. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-06-30 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
3370 | 61 | 1 | VallejoSFCD | 2006-05-19 09:19 | 400 | 0 |  | 2006-05-19 09:19 |  | -- | Intersection of 5th Street and Chestnut Street | Vallejo | Solano | 94590 |  |  | 2006-05-18 |  |  |  | Captured overflow and wash down water in storm drain and sucked out with vacuum truck and returned to the sanitary system. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-05-19 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
3357 | 60 | 1 | VallejoSFCD | 2006-05-17 08:43 | 150 | 0 |  | 2006-05-17 08:43 |  | -- | 4400 Georgia Street | Vallejo | Solano | 94590 |  |  | 2006-05-15 |  |  |  | Used jet machine to clear blockage and wash down. Used vacuum truck to suck up wastewater and wash down water and returned all to the sanitary sewer system. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-05-17 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
3324 | 59 | 1 | VallejoSFCD | 2006-05-09 14:10 | 100 | 0 |  | 2006-05-09 14:10 |  | -- | 186 Fleming ave | Vallejo | Solano | 94590 |  |  | 2006-05-03 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Lonnie Holt | 2006-05-09 | 707/644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
3153 | 58 | 1 | VallejoSFCD | 2006-04-12 11:08 | 220 | 0 |  | 2006-04-12 11:08 |  | -- | Intersection of San Gorgonio Avenue and Los Cerritos Drive | Vallejo | Solano | 94590 |  |  | 2006-04-09 |  |  |  | Plugged storm drain and vacuumed spill and returned to sanitary system. Recovered 190 gallons of wastewater. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-04-12 | (707) 644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
3103 | 57 | 1 | VallejoSFCD | 2006-03-30 07:28 | 500 | 0 |  | 2006-03-30 07:28 |  | -- | 127 Perkins Avenue | Vallejo | Solano | 94590 |  |  | 2006-03-20 |  |  |  | Cause of blockage is unknown. We used a vacuum truck and recovered 475 gallons of the 500 gallons spilled and returned it to the sewer system. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-03-30 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2936 | 53 | 1 | VallejoSFCD | 2006-03-06 13:16 | 200 | 0 |  | 2006-03-06 13:16 |  | -- | Meadows Dr. @ Azaleact. | Vallejo | Solano | 94590 |  |  | 2006-03-06 |  |  |  | The Sanitary Sewer System down stream of meadows Pump Station was surcharged due to a heavy rain Event and could not handle the additional flow from the Pump Station. The Pump Station was shut down until the downstream system capacity had improved then it was turned back on. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | Maintenance Super | Lonnie Holt | 2006-03-06 | (707)644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2938 | 54 | 1 | VallejoSFCD | 2006-03-06 13:23 | 400 | 0 |  | 2006-03-06 13:23 |  | -- | 236 University Ave | Vallejo | Solano | 94589 |  |  | 2006-03-06 |  |  |  | Cleared with Vacuum truck and area cleaned up, 100 gallons recovered | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Superintendant | Lonie Holt | 2006-03-06 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2901 | 52 | 1 | VallejoSFCD | 2006-02-28 13:11 | 500 | 0 |  | 2006-02-28 13:11 |  | -- | Intersection of Carnation Circle and Meadows Drive | Vallejo | Solano | 94590 |  |  | 2006-02-27 |  |  |  | Downstream system surcharged, couldn't take the additional flow of a second pump coming on at the pump station. Shut off second pump to stop overflow. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | FLOW CAPACITY DEFICIENCY | --Select None-- |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-02-28 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2845 | 50 | 1 | VallejoSFCD | 2006-02-21 11:15 | 80 | 0 |  | 2006-02-21 11:15 |  | -- | Quincy Alley and Santa Clara Street | Vallejo | Solano | 94590 |  |  | 2006-02-20 |  |  |  | Vacuumed up 80 gallons and returned to sanitary sewer system | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-02-21 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2843 | 49 | 1 | VallejoSFCD | 2006-02-21 11:05 | 91 | 0 |  | 2006-02-21 11:05 |  | -- | 74 Beverly Druve | Vallejo | Solano | 94590 |  |  | 2006-02-18 |  |  |  | Vacuumed up 89 gallons and returned to sanitary sewer line. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-02-21 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2841 | 48 | 1 | VallejoSFCD | 2006-02-21 10:57 | 950 | 0 |  | 2006-02-21 10:57 |  | -- | 450 Ryder Street | Vallejo | Solano | 94590 |  |  | 2006-02-16 |  |  |  | During bypass pumping at night noticed hose fittings leaking and stopped bypass pumping operation. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | OTHER | Hose fittings on bypass line | BYPASS | --Select None-- |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-02-21 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2621 | 47 | 1 | VallejoSFCD | 2006-01-12 15:48 | 250 | 0 |  | 2006-01-12 15:48 |  | -- | Benecia Road and Maple Avenue | Vallejo | Solano | 94590 |  |  | 2006-01-11 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-01-12 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2594 | 46 | 1 | VallejoSFCD | 2006-01-10 08:28 | 100 | 0 |  | 2006-01-10 08:28 |  | -- | 244 Lofas Place | Vallejo | Solano | 94590 |  |  | 2006-01-08 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-01-10 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2592 | 45 | 1 | VallejoSFCD | 2006-01-10 08:25 | 150 | 0 |  | 2006-01-10 08:25 |  | -- | 316 Pecan Street | Vallejo | Solano | 94590 |  |  | 2006-01-07 |  |  |  | Debris in main line caused by infrastructure failure | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-01-10 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2546 | 37 | 1 | VallejoSFCD | 2006-01-05 18:04 | 600 | 0 |  | 2006-01-05 18:04 |  | -- | Mississippi Street and Napa Street | Vallejo | Solano | 94590 |  |  | 2006-01-02 |  |  |  | Waited for rains to stop/flows to subside | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-01-05 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2548 | 38 | 1 | VallejoSFCD | 2006-01-05 18:07 | 750 | 0 |  | 2006-01-05 18:07 |  | -- | Missouri Street and Sonoma Boulevard | Vallejo | Solano | 94590 |  |  | 2006-01-02 |  |  |  | Waited for rains to stop/flows to subside | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-01-05 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2550 | 39 | 1 | VallejoSFCD | 2006-01-05 18:10 | 850 | 0 |  | 2006-01-05 18:10 |  | -- | Hampshire Street and Couch Street | Vallejo | Solano | 94590 |  |  | 2006-01-02 |  |  |  | Waited for rains to stop/flows to subside | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-01-05 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2590 | 44 | 1 | VallejoSFCD | 2006-01-09 16:18 | 20000 | 19800 | 060028 | 2006-01-01 | Andy Jannings | VallejoSFCD | 440 Illinois St | Vallejo | Solano | 94590 |  |  | 2006-01-01 | 11:00:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Medium | Napa River/ Mare Island Strait | BUILDING/STRUCTURE | No |  | No | No | Contained in buildings basement |  | Yes | Yes | Yes | No | No | No | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | VallejoSFCD | OTHER | Illegal patio drain tied to sanitary sewer | INFLOW & INFILTRATION | --Select None-- | --Select None-- | Below Grade patio Drain overflowed during system surcharge | SSO caused by low point patio drain while system was surcharged during heavy rains | Fops Superintendent | Lonnie Holt | 2006-01-09 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MAJOR | Lonnie Holt | VallejoSFCD | 707-644-8949 | 271 | 450 Ryder Street | Vallejo | Solano | 94590 | Lonnie Holt | VallejoSFCD | 707-644-8949 | 271 | 450 Ryder Street | Vallejo | Solano | 94590
2530 | 29 | 1 | VallejoSFCD | 2006-01-05 17:33 | 500 | 0 |  | 2006-01-05 17:33 |  | -- | 329 Pecan Street | Vallejo | Solano | 94590 |  |  | 2005-12-31 |  |  |  | Debris from infrastructure failure | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-01-05 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2532 | 30 | 1 | VallejoSFCD | 2006-01-05 17:39 | 900 | 0 |  | 2006-01-05 17:39 |  | -- | Meadows Drive and Jack London Drive | Vallejo | Solano | 94590 |  |  | 2005-12-31 |  |  |  | Shut down station and waited for surcharging downstream to subside enough to start station back up. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-01-05 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2534 | 31 | 1 | VallejoSFCD | 2006-01-05 17:43 | 900 | 0 |  | 2006-01-05 17:43 |  | -- | 300 Pepper Drive | Vallejo | Solano | 94590 |  |  | 2005-12-31 |  |  |  | Waited for rains to stop/flows to subside. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-01-05 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2536 | 32 | 1 | VallejoSFCD | 2006-01-05 17:47 | 200 | 0 |  | 2006-01-05 17:47 |  | -- | 1826 Tennessee Street | Vallejo | Solano | 94590 |  |  | 2005-12-31 |  |  |  | Waited for rains to stop/flows to subside | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-01-05 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2538 | 33 | 1 | VallejoSFCD | 2006-01-05 17:50 | 850 | 0 |  | 2006-01-05 17:50 |  | -- | 403 Sutter Street | Vallejo | Solano | 94590 |  |  | 2005-12-31 |  |  |  | Waited for rains to stop/flows to subside | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-01-05 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2540 | 34 | 1 | VallejoSFCD | 2006-01-05 17:53 | 900 | 0 |  | 2006-01-05 17:53 |  | -- | Hampshire Street and Couch Street | Vallejo | Solano | 94590 |  |  | 2005-12-31 |  |  |  | Waited for rains to stop/flows to subside | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-01-05 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2542 | 35 | 1 | VallejoSFCD | 2006-01-05 17:57 | 900 | 0 |  | 2006-01-05 17:57 |  | -- | Misssouri Street and Sonoma Boulevard | Vallejo | Solano | 94590 |  |  | 2005-12-31 |  |  |  | Waited for rains to stop/flows to subside | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-01-05 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2544 | 36 | 1 | VallejoSFCD | 2006-01-05 18:00 | 800 | 0 |  | 2006-01-05 18:00 |  | -- | Mississippi Street and Napa Street | Vallejo | Solano | 94590 |  |  | 2005-12-31 |  |  |  | Waited for rains to stop/flows to subside | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | FOPS Superintendent | Lonnie Holt | 2006-01-05 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2575 | 40 | 1 | VallejoSFCD | 2006-01-09 08:25 | 153000 | 0 | 057606 | 2005-12-31 | Frank Silvera | VallejoSFCD | St. Francis and Wilson Avenue | Vallejo | Solano | 94590 |  |  | 2005-12-31 | 3:15:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | STORM DRAIN | No |  | No | No | Unable to see any effect due to high flows in the Mare Island Straight of the Napa River |  | Yes | Yes | Yes | No | No | Yes | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | VallejoSFCD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | SSO caused by system surcharge due to inflow/infiltration from the ground being saturated from heavy rains | FOPS Superintendent | Lonnie Holt | 2006-01-09 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MAJOR | Lonnie Holt | VallejoSFCD | 707-644-8949 | 271 | 450 Ryder Street | Vallejo | Solano | 94590 | Lonnie Holt | VallejoSFCD | 707-644-8949 | 271 | 450 Ryder Street | Vallejo | Solano | 94590
2587 | 41 | 1 | VallejoSFCD | 2006-01-09 14:40 | 26625 | 0 | 057605 | 2005-12-31 | Frank Silvera | VallejoSFCD | Lighthouse Drive and Wilson Avenue | Vallejo | Solano | 94590 |  |  | 2005-12-31 | 3:15:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | High | Napa River/Mare Island Strait | STORM DRAIN | No |  | No | No | Due to high flows in the Napa River at the Mare Island Strait, we were unable to visually see anychange in the water. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | VallejoSFCD | MANHOLE |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | SSO caused by system surcharge due to inflow/infiltration from the ground being saturated from heavy rains | FOPS Superintendent | Lonnie Holt | 2006-01-09 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MAJOR | Lonnie Holt | VallejoSFCD | 707-644-8949 | 271 | 450 Ryder Street | Vallejo | Solano | 94590 | Lonnie Holt | VallejoSFCD | 707-644-8949 | 271 | 450 Ryder Street | Vallejo | Solano | 94590
2588 | 42 | 1 | VallejoSFCD | 2006-01-09 14:56 | 4200 | 0 | 060010 | 2005-12-31 | Andy Jannings | VallejoSFCD | 106 Ifland | Vallejo | Solano | 94590 |  |  | 2005-12-31 | 10:30:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Medium | Napa River/Mare Island Strait | STORM DRAIN | No |  | No | No | Due to high flows we were unable to detect any changes in water. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | VallejoSFCD | CLEAN OUT |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | SSO caused by system surcharge dut to inflow/infiltration from the ground being saturated from heavy rains | FOPS Superintendent | Lonnie Holt | 2006-01-09 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MAJOR | Lonnie Holt | VallejoSFCD | 707-644-8949 | 271 | 450 Ryder Street | Vallejo | Solano | 94590 | Lonnie Holt | VallejoSFCD | 707-644-8949 | 271 | 450 Ryder Street | Vallejo | Solano | 94590
2589 | 43 | 1 | VallejoSFCD | 2006-01-09 15:28 | 1500 | 0 | 060011 | 2006-01-01 | Andy Jannings | VallejoSFCD | 932 Keats Dr | Vallejo | Solano | 94590 |  |  | 2005-12-31 | 10:20:00 A | [5 empty] | RAINING FOR SEVERAL DAYS | Low | Napa River/ Mare Island Strait | STORM DRAIN | No |  | No | No | Due to high flows we were unable to detect any changes in water |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | VallejoSFCD | CLEAN OUT |  | INFLOW & INFILTRATION | --Select None-- | --Select None-- |  | SSO caused by system surcharge due to inflow/infiltration from the ground being saturated from heavy rains | Fops Superintendent | Lonnie Holt | 2006-01-09 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MAJOR | Lonnie Holt | VallejoSFCD | 707-644-8949 | 271 | 450 Ryder Street | Vallejo | Solano | 94590 | Lonnie Holt | VallejoSFCD | 707-644-8949 | 271 | 450 Ryder Street | Vallejo | Solano | 94590
2352 | 28 | 1 | VallejoSFCD | 2005-12-28 14:42 | 450 | 0 |  | 2005-12-28 14:42 |  | -- | 445 Maple st | Vallejo | Solano | 94590 |  |  | 2005-12-26 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Superintendent | Lonnie Holt | 2005-12-28 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2302 | 27 | 1 | VallejoSFCD | 2005-12-22 08:49 | 250 | 0 |  | 2005-12-22 08:49 |  | -- | In backyard of 124 Jordan Street | Vallejo | Solano | 94590 |  |  | 2005-12-21 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | FOPS Superintendent | Lonnie Holt | 2005-12-22 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2297 | 26 | 1 | VallejoSFCD | 2005-12-21 09:29 | 450 | 0 |  | 2005-12-21 09:29 |  | -- | Intersection of Vervais Avenue and Mayfair Avenue | Vallejo | Solano | 94590 |  |  | 2005-12-18 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | FOPS Superintendent | Lonnie Holt | 2005-12-21 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2295 | 25 | 1 | VallejoSFCD | 2005-12-21 09:12 | 250 | 0 |  | 2005-12-21 09:12 |  | -- | 2126 Georgia Street | Vallejo | Solano | 94590 |  |  | 2005-12-16 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | FOPS Superintendent | Lonnie Holt | 2005-12-21 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2228 | 24 | 1 | VallejoSFCD | 2005-12-07 10:23 | 900 | 0 |  | 2005-12-07 10:23 |  | -- | 1012 Pine St. | Vallejo | Solano | 94589 |  |  | 2005-12-03 |  |  |  | Private Contractor Bored into Sanitary Sewer Main. 400 Gallons of the Spill were Recovered. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | PIPE |  | INFRASTRUCTURE FAILURE | CONSTRUCTION DEBRIS |  |  |  | FOPS Superintendant | Lonnie Holt | 2005-12-07 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2226 | 23 | 1 | VallejoSFCD | 2005-12-07 10:18 | 100 | 0 |  | 2005-12-07 10:18 |  | -- | Griffin at Denninger | Vallejo | Solano | 94590 |  |  | 2005-11-28 |  |  |  | Used Jet Machine to clear Blockage | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | FOPS superintendant | Lonnie Holt | 2005-12-07 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2168 | 22 | 1 | VallejoSFCD | 2005-11-23 15:21 | 200 | 0 |  | 2005-11-23 15:21 |  | -- | 100 Foster Street | Vallejo | Solano | 94590 |  |  | 2005-11-20 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | FOPS Superintendent | Lonnie Holt | 2005-11-23 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2139 | 21 | 1 | VallejoSFCD | 2005-11-18 07:50 | 150 | 0 |  | 2005-11-18 07:50 |  | -- | Richardson Drive and Hobbs Avenue | Vallejo | Solano | 94590 |  |  | 2005-11-14 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | FOPS Superintendent | Lonnie Holt | 2005-11-18 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2109 | 20 | 1 | VallejoSFCD | 2005-11-14 14:03 | 100 | 0 |  | 2005-11-14 14:03 |  | -- | 6th Street and Atherton Street | Vallejo | Solano | 94590 |  |  | 2005-11-10 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Field Operations Sup | Lonnie Holt | 2005-11-14 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2107 | 19 | 1 | VallejoSFCD | 2005-11-14 13:55 | 100 | 0 |  | 2005-11-14 13:55 |  | -- | 509 Grant Street | Vallejo | Solano | 94590 |  |  | 2005-11-05 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | Field Operations Sup | Lonnie Holt | 2005-11-14 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
2047 | 18 | 1 | VallejoSFCD | 2005-10-27 09:15 | 300 | 0 |  | 2005-10-27 09:15 |  | -- | 318 Central Avenue | Vallejo | Solano | 94590 |  |  | 2005-10-25 |  |  |  | Recovered 275 gallons of spill and returned it to the sanitary sewer system. The other 25 gallons of the spill the homeowner had put on the grass in the yard before we arrived. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | OTHER | Basement Floor Drain | BLOCKAGE | DEBRIS |  |  |  | FOPS Superintendent | Lonnie Holt | 2005-10-27 | (707) 644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
1982 | 17 | 1 | VallejoSFCD | 2005-10-18 08:42 | 200 | 0 |  | 2005-10-18 08:42 |  | -- | 122 Fleming Avenue | Vallejo | Solano | 94590 |  |  | 2005-10-17 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | FOPS Superintendent | Lonnie Holt | 2005-10-18 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
1747 | 16 | 1 | VallejoSFCD | 2005-08-31 11:42 | 500 | 0 |  | 2005-08-31 11:42 |  | -- | 18th Street and Railroad Ave. Mare Island | Vallejo | Solano | 94592 |  |  | 2005-08-29 |  |  |  | Vibration of heavy equipment running over shallow sewer main during demolition of buildings caused pipe to fail. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | INFRASTRUCTURE FAILURE | --Select None-- |  |  |  | Field Operations Sup | Lonnie Holt | 2005-08-31 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
1645 | 15 | 1 | VallejoSFCD | 2005-07-26 11:49 | 100 | 0 |  | 2005-07-26 11:49 |  | -- | 480 Glen Cove Parkway | Vallejo | Solano | 94591 |  |  | 2005-07-24 |  |  |  | Pumps in pump station became air-bound causing spill. Bled air off of pumps. Pumps back operational. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | FOPS Supernitendent | Lonnie Holt | 2005-07-26 | (707)644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
1600 | 14 | 1 | VallejoSFCD | 2005-07-07 10:27 | 800 | 0 |  | 2005-07-07 10:27 |  | -- | 3899 Sonoma Blvd. | Vallejo | Solano | 94590 |  |  | 2005-07-01 |  |  |  | Of the 800 gallons spilled, 400 gallons were recovered and put back into the sewer system, the rest was absorbed into the ground. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | FOPS Superintendent | Lonnie Holt | 2005-07-07 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
1406 | 13 | 1 | VallejoSFCD | 2005-05-16 13:27 | 600 | 0 |  | 2005-05-16 13:27 |  | -- | 731 Steffan Street | Vallejo | Solano | 94590 |  |  | 2005-05-13 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | FOPS Superintendent | Lonnie Holt | 2005-05-16 | 644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
1376 | 12 | 1 | VallejoSFCD | 2005-05-06 17:53 | 700 | 0 |  | 2005-05-06 17:53 |  | -- | 1005 Lewis Avenue | Vallejo | Solano | 94590 |  |  | 2005-04-28 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Field Ops. Supt. | Lonnie Holt | 2005-05-06 | 644-8949x271 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
1334 | 11 | 1 | VallejoSFCD | 2005-04-27 13:26 | 700 | 0 |  | 2005-04-27 13:26 |  | -- | 15 Frisbie Street | Vallejo | Solano | 94590 |  |  | 2005-04-26 |  |  |  | Cleared using hydro-flusher. Area around spill cleaned of debris. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Field Ops. Supt. | Lonnie Holt | 2005-04-27 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
1261 | 10 | 1 | VallejoSFCD | 2005-04-07 09:42 | 750 | 0 |  | 2005-04-07 09:42 |  | -- | 210 Newells Drive cross Street is Coach Lane | Vallejo | Solano | 94590 |  |  | 2005-04-07 |  |  |  | Although this was a small spill it did flow directly into Blue Rock Springs Creek and therefore I notified OES and received control #05-2115. There was not any debris spilled out of the manhole, only wastewater. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Field Operations Sup | Lonnie Holt | 2005-04-07 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
1256 | 9 | 1 | VallejoSFCD | 2005-04-05 14:09 | 600 | 0 |  | 2005-04-05 14:09 |  | -- | 343 Gilcrest Avenue | Vallejo | Solano | 94590 |  |  | 2005-03-31 |  |  |  | Recovered approximately 200 gallons of the overflow with a vacuum truck and disposed of it at the treatment plant | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | FOPS Superintendent | Lonnie Holt | 2005-04-05 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
1242 | 8 | 1 | VallejoSFCD | 2005-04-01 10:05 | 100 | 0 |  | 2005-04-01 10:05 |  | -- | 840 Nebraska Street | Vallejo | Solano | 94590 |  |  | 2005-03-28 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Field Operations Sup | Lonnie Holt | 2005-04-01 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
1193 | 7 | 2 | VallejoSFCD | 2005-03-16 08:48 | 4750 | 0 | 05-1472 | 2005-03-04 | Ken Taylor | VallejoSFCD | 512 Cedar Street | Vallejo | Solano | 94590 |  |  | 2005-03-15 | 9:45:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | High |  | STORM DRAIN | No |  | No | No | None |  | Yes | Yes | Yes | No | No | No | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | VallejoSFCD | OTHER | overflow in home | BLOCKAGE | ROOTS | --Select None-- |  | VallejoSFCD service call person responded, main plugged backing up house lateral into home. We removed screw cap on outside cleanout and ran flusher hose thru lateral to clear main line. TV'd main to see what caused blockage, roots coming in around downstream lateral blocking main line. Used "HOG" nozzle to clear roots and dug and repaired lateral connection to main line to prevent further blockages. | Field Operations Sup | Lonnie Holt | 2005-03-15 | 707-644-8949 | lholt@vsfcd.com, rmatheson@vsfcd.com | MAJOR | Lonnie Holt | VallejoSFCD | 707-644-8949 | 271 | 450 Ryder Street | Vallejo | Solano | 94590 | Lonnie Holt | VallejoSFCD | 707-644-8949 | 271 | 450 Ryder Street | Vallejo | Solano | 94590
1060 | 6 | 1 | VallejoSFCD | 2005-02-18 13:51 | 900 | 0 |  | 2005-02-18 13:51 |  | -- | 1084 ORCHARD AVE | VALLEJO | SOLANO | 94590 |  |  | 2005-02-16 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Superintendent | Lonnie Holt | 2005-02-18 | 707-6448949 | Lholt@vsfcd.com | MINOR
1012 | 5 | 1 | VallejoSFCD | 2005-02-10 09:07 | 100 | 0 |  | 2005-02-10 09:07 |  | -- | Capitol St at Railroad tracks | Vallejo | Solano | 94590 |  |  | 2005-02-08 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Environmental Servic | Lonnie Holt | 2005-02-10 | 707-644-8949 x2 | lholt@vsfcd.com, rmatheson@vsfcd.com | MINOR
938 | 4 | 1 | VallejoSFCD | 2005-02-01 10:04 | 550 | 0 |  | 2005-02-01 10:04 |  | -- | seaport/seacrest | Vallejo | solano | 94590 |  |  | 2005-01-27 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Fops Supt | Lonnie Holt | 2005-02-01 | 707-6448949 | lholt@vsfcd.com | MINOR
866 | 3 | 1 | VallejoSFCD | 2005-01-18 13:37 | 700 | 0 |  | 2005-01-18 13:37 |  | -- | 2833 Tennessee Street | Vallejo | Solano | 94590 |  |  | 2005-01-16 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Field Operations Sup | Lonnie Holt | 2005-01-18 | (707)644-8949 | lholt@vsfcd.com | MINOR
776 | 2 | 1 | VallejoSFCD | 2005-01-06 15:22 | 195 | 0 |  | 2005-01-06 15:22 |  | -- | 104 Clay Street | Vallejo | Solano | 94590 |  |  | 2005-01-03 |  |  |  | Spill contained and vacuumed out from under house and taken to sanitary sewer treatment plant. All of spill was recovered. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | OTHER | Open plumbing under house | BLOCKAGE | GREASE |  |  |  | Field Operations Sup | Lonnie Holt | 2005-01-06 | (707) 644-8949 | lholt@vsfcd.com | MINOR
505 | 1 | 1 | VallejoSFCD | 2004-12-12 11:19 | 500 | 0 |  | 2004-12-12 11:19 |  | -- | 224 Los Gatos | Vallejo | Solano | 94590 |  |  | 2004-12-02 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | VallejoSFCD | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | FOPS Supt | Lonnie Holt | 2004-12-12 | 644-8949X271 |  | MINOR
5009 | 32 | 1 | WestBay | 2007-03-27 08:32 | 150 | 0 |  | 2007-03-27 08:32 |  | -- | 1236 Madera Avenue | Menlo Park | San Mateo | 94025 |  |  | 2007-03-26 |  |  |  | SSO was in a Residential Easement, 100 gallons was returned to sanitary sewer. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | GREASE |  |  |  | R.C.C. | John Simonetti | 2007-03-27 | 650-321-0384
4935 | 31 | 1 | WestBay | 2007-03-15 13:21 | 240 | 0 |  | 2007-03-15 13:21 |  | -- | 3300 Alpine Road | Portola Valley | San Mateo | 94028 |  |  | 2007-03-08 |  |  |  | 53 gallons entered a private storm drainage system, at that time the final destination was not known (we know the outfall location now)the out fall pipe has rotted. Recovered approximately 60 gallons, approximately 127 gallons saturated into the soil. Cleaned up area. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | RCC | John Simonetti | 2007-03-15 | 650-321-0384
4930 | 30 | 1 | WestBay | 2007-03-15 11:31 | 40 | 0 |  | 2007-03-15 11:31 |  | -- | 90 Ridgeview Drive | Atherton | San Mateo | 94027 |  |  | 2007-03-08 |  |  |  | PArtial Recovery of SSO. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | RCC | John Simonetti | 2007-03-15 | 650-321-0384
4928 | 29 | 1 | WestBay | 2007-03-15 11:13 | 50 | 0 |  | 2007-03-15 11:13 |  | -- | LAurel Street x Ravenswood | Menlo Park | San Mateo | 94025 |  |  | 2007-02-22 |  |  |  | Paper blockage, SSO contained to buble up storm basin, returned to sanitary sewer. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | RCC | John Simonetti | 2007-03-15 | 650-321-0384
4926 | 28 | 1 | WestBay | 2007-03-15 11:10 | 50 | 0 |  | 2007-03-15 11:10 |  | -- | 1031 Noel Street | Menlo Park | San Mateo | 94025 |  |  | 2007-02-22 |  |  |  | SSO contained and returned to Sanitary sewer | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | RCC | John Simonetti | 2007-03-15 | 650-321-0384
4924 | 27 | 1 | WestBay | 2007-03-15 11:08 | 45 | 0 |  | 2007-03-15 11:08 |  | -- | 201 Partridge Avenue | Menlo Park | San Mateo | 94025 |  |  | 2007-02-15 |  |  |  | SSO reurned to sanitary Sewer. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | RCC | John Simonetti | 2007-03-15 | 650-321-0384
4922 | 26 | 1 | WestBay | 2007-03-15 11:05 | 630 | 0 |  | 2007-03-15 11:05 |  | -- | 1000 El Camino Real | Menlo Park | San Mateo | 94025 |  |  | 2007-02-10 |  |  |  | SSO was contained (in easement)to a low spot in parking lot. Clean up performed by WBSD. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | RCC | John Simonetti | 2007-03-15 | 650-321-0384
4920 | 25 | 1 | WestBay | 2007-03-15 10:59 | 425 | 0 |  | 2007-03-15 10:59 |  | -- | 824 Harvard Ave | Menlo Park | San Mateo | 94025 |  |  | 2007-02-01 |  |  |  | SSO was contained, burmed and returned to sanitary sewer with rinse water. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | RCC | John Simonetti | 2007-03-15 | 650-321-0384
4918 | 24 | 1 | WestBay | 2007-03-15 07:10 | 2 | 0 |  | 2007-03-15 07:10 |  | -- | 737 Live Oak Avenue | Menlo Park | San Mateo | 94025 |  |  | 2007-02-01 | [9 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | RCC | John Simonetti | 2007-03-15 | 650-321-0384
4916 | 23 | 1 | WestBay | 2007-03-15 07:08 | 14 | 0 |  | 2007-03-15 07:08 |  | -- | 3300 Alpine Road | Portola Valley | San Mateo | 94028 |  |  | 2007-01-29 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | RCC | John Simonetti | 2007-03-15 | 650-321-0384
4914 | 22 | 1 | WestBay | 2007-03-15 07:05 | 25 | 0 |  | 2007-03-15 07:05 |  | -- | Pope Street x Gilbert | Menlo Park | San MAteo | 94025 |  |  | 2007-01-29 | [9 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | RCC | John Simonetti | 2007-03-15 | 650-321-0384
4627 | 21 | 1 | WestBay | 2007-01-27 15:51 | 800 | 0 |  | 2007-01-27 15:51 |  | -- | 1101 Del Norte Avenue | Menlo Park | San Mateo | 94025 |  |  | 2007-01-27 |  |  |  | Recovered approximately 600 gallons and returned to sanitary sewer. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Reg. Comp. Coord. | John Simonetti | 2007-01-27 | 650-321-0384
4615 | 20 | 1 | WestBay | 2007-01-24 | 4547 | 4547 | 07-0553 | 2007-01-24 | WBSD | WestBay | 3455 AlamedaaDe Las Pulgas | Menlo Park | San Mateo | 94025 |  |  | 2007-01-24 | 0.36111 | [6 empty] | Low |  | STORM DRAIN | No |  | No | Yes | SSO entered storm drain inlet 200 feet downstream of overflow. Staff plugged off storm drain line and performed by-pass operations and hydro flush cleaning of affected storm lines. |  | Yes | Yes | Yes |  |  | No | No |  |  | 2007-01-26 | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | ROOTS | -- Select One -- |  | Staff performed by-passing operations 1/8 of a mile down stream in the storm drainage system while clean up opeations were taking place until flow ceased from the clean up operations. | Reg. Comp. Coord. | John Simonetti | 2007-01-24 | 650-384-5068
4625 | 19 | 2 | WestBay | 2007-01-23 | 7530 | 1765 | 07-0525 | 2007-01-23 | Property Manager | WestBay | 3455 Alameda De Las Pulgas | Menlo Park | San Mateo | 94025 |  |  | 2007-01-22 | 0 | [6 empty] | Low | Atherton Channel | STORM DRAIN | No |  | No | Yes | Contained to section of the Atherton Channel, affected section of the sotrm drainage basin have been hydro flushed and returned to the sanitary sewer. |  | Yes | Yes | Yes |  |  | No | Yes |  |  | 2007-01-31 | OPEN ACTIVE | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | ROOTS | -- Select One -- |  | Samples were taken on 01-25-07. I discussed the over flow with Greg Smith (New COntact for Sewage Spills) of the San Mateo County Environmental Health Department. Samples were taken to the San Mateo COunty Environmental Health Departments Laboratory on 01-25-07. Results are due next week. | Reg. Comp.Coord. | John Simonetti | 2007-01-23 | 650-384-5068
4293 | 18 | 1 | WestBay | 2006-12-13 07:09 | 550 | 0 |  | 2006-12-13 07:09 |  | -- | 140 Escanyo Way | Ladera | San Mateo | 94028 |  |  | 2006-12-13 |  |  |  | SSO was contained to small section of the storm drainage basin. Staff performed pumping operations to recover the SSO and rinse water and return to the sanitary sewer system | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Reg. Comp. Coordinat | John Simonetti | 2006-12-13 | 650-321-0384
3952 | 17 | 1 | WestBay | 2006-10-02 13:49 | 375 | 0 |  | 2006-10-02 13:49 |  | -- | Georgia Lane x Protola Road | Portola Valley | San Mateo | 94028 |  |  | 2006-10-02 |  |  |  | Transfomer for control circuitry blown fuse. SSO to storm drain which flows to the Corte Madera Creek. The town of Portola Valley has been notified, 1-resident informed and near by school. 1-access point was tagged. Informed San Mateo County Health Department. Samples taken to the County Health Laboratory. | [5 empty] | SURFACE WATER IMPACT | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestBay | MANHOLE |  | ELECTRICAL POWER FAILURE | --Select None-- |  |  |  | R.C.C. | John Simonetti | 2006-10-02 | 650-321-0384 | jsimonetti@westbaysanitary.org, | MINOR
3940 | 15 | 1 | WestBay | 2006-09-28 13:55 | 1 | 0 |  | 2006-09-28 13:55 |  | -- | 1303 Sevier Avenue | Menlo Park | San Mateo | 94025 |  |  | 2006-09-25 |  |  |  | SSO to small to measure, listed as 1 gallon | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestBay | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | R.C.C. | John Simonetti | 2006-09-28 | 650-321-0384 | jsimonetti@westbaysanitary.org, | MINOR
3942 | 16 | 1 | WestBay | 2006-09-28 13:57 | 5 | 0 |  | 2006-09-28 13:57 |  | -- | Ohlone x Sunhill | Portola Valley | San Mateo | 94028 |  |  | 2006-09-21 |  |  |  | SSO contained to catch basin. Recovered and returned to sanitary sewer. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestBay | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | R.C.C. | John Simonetti | 2006-09-28 | 650-321-0384 | jsimonetti@westbaysanitary.org, | MINOR
3653 | 14 | 1 | WestBay | 2006-07-24 14:11 | 450 | 0 |  | 2006-07-24 14:11 |  | -- | 2071 Sterling Avenue | Menlo Park | San Mateo | 94025 |  |  | 2006-07-22 |  |  |  | SSO was recovered at storm. The storm drainage channel was visually inspected and samples were taken to the San Mateo COunty Environmental Health Departments Laboratory. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestBay | MANHOLE | Mainline stoppage SSO @ Clean out | BLOCKAGE | ROOTS |  |  |  | R.C.C. | John Simonetti | 2006-07-24 | 650-321-0384 | jsimonetti@westbaysanitary.org, | MINOR
3598 | 13 | 1 | WestBay | 2006-07-05 10:14 | 261 | 0 |  | 2006-07-05 10:14 |  | -- | 140 Lucero Way | Portola Valley | San Mateo | 94028 |  |  | 2006-06-29 |  |  |  | SSO saturated into soil in an easement whihc backs up to a large inaccessable pice of property. SSO volume was estimated on the property owners initial observation. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestBay | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | R.C.C. | John Simonetti | 2006-07-05 | 650-321-0384 | jsimonetti@westbaysanitary.org, | MINOR
3558 | 12 | 1 | WestBay | 2006-06-26 15:38 | 200 | 0 |  | 2006-06-26 15:38 |  | -- | 2086 Mills Avenue | Menlo Park | San Mateo | 94025 |  |  | 2006-06-08 |  |  |  | We tried to report this last week, and we ould not link to your system for some reason. Recovered approximately 30 gallons, the rest saturated into the soil. Residential SSO. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestBay | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Reg. Comp. | John Simonetti | 2006-06-26 | 650-321-0384 | jsimonetti@westbaysanitary.org, | MINOR
2114 | 11 | 1 | WestBay | 2005-11-15 11:48 | 127 | 0 |  | 2005-11-15 11:48 |  | -- | 1852 Valparaiso Avenue x American Atherton-Menlo Park | Menlo Park | San Mateo | 94025 |  |  | 2005-11-15 |  |  |  | SSO entered a direct inlet which flows to the Atherton Channel, water condition at that point is clear without odor or debris. The SSO was from a residential area. The San Mateo County Environmental Health DEpartment and the Town of Atherton shall be notified. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestBay | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | SC Insp. | John Simonetti | 2005-11-15 | 650-321-0384 | jsimonetti@westbaysanitary.org, | MINOR
1916 | 10 | 1 | WestBay | 2005-10-05 14:12 | 10 | 0 |  | 2005-10-05 14:12 |  | -- | 111 N. Costanya | Portola Valley | San Mateo | 94028 |  |  | 2005-10-03 |  |  |  | THE affected section of mainline is in an paved easement or pathway. While being repaved the DIstricts facilities were illegally accessed. The contractor removed the cover during the paving operation, allowing asphalt to flow into the channel thus creating the blockage. Emergency dig, completion on 10-05-05. Investigation underway. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestBay | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | Source Control Insp. | John Simonetti | 2005-10-05 | 650-321-0384 | jsimonetti@westbaysanitary.org, | MINOR
1810 | 9 | 1 | WestBay | 2005-09-20 10:43 | 1 | 0 |  | 2005-09-20 10:43 |  | -- | 229 Newbridge Avenue | Menlo Park | San Mateo | 94025 |  |  | 2005-09-17 |  |  |  | SSO was contained and cleaned up. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestBay | CLEAN OUT | Mainline Stoppage sso at Clean out | BLOCKAGE | ROOTS |  |  |  | Source Control Insp | John Simonetti | 2005-09-20 | 650-321-0384 | jsimonetti@westbaysanitary.org, | MINOR
1782 | 8 | 1 | WestBay | 2005-09-14 15:27 | 696 | 0 |  | 2005-09-14 15:27 |  | -- | 396 Atherton Avenue | Atherton | San Mateo | 94027 |  |  | 2005-09-14 |  |  |  | Root & paper blockage. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestBay | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Source Control Insp | John Simonetti | 2005-09-14 | 650-321-0384 | jsimonetti@westbaysanitary.org, | MINOR
1655 | 6 | 1 | WestBay | 2005-07-28 11:23 | 60 | 0 |  | 2005-07-28 11:23 |  | -- | 701 Menlo Oaks Drive | Menlo Park | San Mateo | 94025 |  |  | 2005-07-23 |  |  |  | Rags/towel caused the blockage. The overflow was pumped to a tree area at the referenced address. The overflow did not enter storm drainage system. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestBay | OTHER | Floor Drain | BLOCKAGE | DEBRIS |  |  |  | Source Control Inspe | John Simonetti | 2005-07-28 | 650-321-0384 | jsimonetti@westbaysanitary.org, | MINOR
1657 | 7 | 1 | WestBay | 2005-07-28 11:27 | 20 | 0 |  | 2005-07-28 11:27 |  | -- | 170 Mimosa | Portola Valley | San Mateo | 94028 |  |  | 2005-07-22 |  |  |  | Trickle overflow onto yard, area cleaned up. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestBay | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Soource Control Insp | John Simonetti | 2005-07-28 | 650-321-0384 | jsimonetti@westbaysanitary.org, | MINOR
1301 | 5 | 2 | WestBay | 2005-04-20 13:53 | 2473 | 1850 | 05-2238 | 2005-04-14 | Resident | WestBay | Newbridge x Laurel | East Palo Alto | San Mateo | 94025 |  |  | 2005-04-14 | 12:00:00 A | [5 empty] | SUNNY WEATHER | Low | n/a | CAPTURED IN STORM DRAIN | No |  | No | No | SSO contained in open channel, in process of being recovered. |  | Yes | Yes | Yes | No | No | No | No | No | No | 2005-04-22 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | WestBay | MANHOLE |  | BLOCKAGE | DEBRIS | --Select None-- | Hand Towels discharged to SS system. | SSo contained to storm drainage system. Recovery operations in process, should be completed by 13:00 hours. WBSD will update report upon completion of clean up operations. 04-20-05, Rev SSO vol 1850 gals. recovered and an estimated 623 gals saturated into soil. | Source Control Insp. | J. Simonetti | 2005-04-14 | 650-321-0384 | jsimonetti@westbaysanitary.org, | MAJOR | John Simonetti | WestBay | 650-321-0384 |  | 500 Laurel | Menlo Park | San Mateo | 94025 | J. simonetti | West Bay Sanitary District | 650-321-0384 |  | 500 Laurel Street | Menlo Park | San Mateo | 94025
1236 | 4 | 2 | WestBay | 2005-03-31 09:31 | 3050 | 250 | 05-1864 | 2005-03-25 | Howard Young | WestBay | La Cuesta x Alpine Road | Ladera | San Mateo | 94025 |  |  | 2005-03-25 | 8:20:00 AM | [5 empty] | SUNNY WEATHER | Low | Los Trancos Creek | SURFACE WATER IMPACT | No | n/a | No | Yes | Upstream creek flow is heavy and murky from recent storms. Flow rate of creek at outfall is approximately 120 gallons per second. |  | Yes | Yes | No | No | No | No | No | Yes | No | 2005-03-30 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | WestBay | MANHOLE | Rat Bait block, suspended by wire, slipped off rung and plugged the pipe. | BLOCKAGE | MULTIPLE CAUSES | --Select None-- |  |  | Source Control Insp. | J. Simonetti | 2005-03-25 | 650-321-0384 | jsimonetti@westbaysanitary.org, | MAJOR | John Simonetti | WestBay | 650-321-0384 |  | 500 Laurel | Menlo Park | San Mateo | 94025 | J. simonetti | West Bay Sanitary District | 650-321-0384 |  | 500 Laurel Street | Menlo Park | San Mateo | 94025
1104 | 3 | 2 | WestBay | 2005-03-01 11:56 | 1882 | 1500 | 05-0909 | 2005-02-11 | On site Contractor | WestBay | 730 Monte Rosa Drive | Menlo Park | San Mateo | 94025 |  |  | 2005-02-10 | 9:00:00 AM | [5 empty] | SUNNY WEATHER | Low | Atherton Channel | SURFACE WATER IMPACT | No |  | No | Yes | High flow run off to this section of the channel, 300-500 gpm. |  | Yes | Yes | Yes | No | No | No | No | Yes | No | 2005-02-18 | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | WestBay | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- |  |  | Source Control Inspe | John Simonetti | 2005-02-11 | 650-321-0384 | jsimonetti@westbaysanitary.org, | MAJOR | John Simonetti | WestBay | 650-321-0384 |  | 500 LAurel | Menlo Park | San Mateo | 94025 | J. Simonetti | West Bay Sanitary District | 650-321-0384 |  | 500 Laurel Street | Menlo Park | San Mateo | 94025
928 | 2 | 2 | WestBay | 2005-01-31 11:38 | 4000 | 0 | 05-0467 | 2005-01-19 | Teri Hessel | westbay | 4 Portola Green Circle | Portola Valley | San Mateo | 94025 |  |  | 2005-01-18 | 8:48:00 AM | [5 empty] | SUNNY WEATHER | Low |  | SURFACE WATER IMPACT | No |  | No | Yes | SSO entered an underground drainage system which entered the Corte Madera Creek which flows to the Searsville Lake. |  | Yes | Yes | No | No | No | Yes | No | Yes | No | 2005-01-21 | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | westbay | MANHOLE |  | BLOCKAGE | ROOTS | --Select None-- |  | Final reoprt is attached for your review, it is in a pdf format. Sample results were clean, San Mateo County Health Department confirmed and said to remove the posted signs. Please contact me upon your review of the report. I want to know you were able to open the pdf document. | Source Control Inspe | John SImonetti | 2005-01-19 | 650-321-0384 | jsimonetti@westbaysanitary.org | MAJOR | John Simonetti | WestBay | 650-321-0384 |  | 500 LAurel | Menlo Park | San Mateo | 94025 | J. Simonetti | West Bay Sanitary District | 650-321-0384 |  | 500 Laurel Street | Menlo Park | San Mateo | 94025
494 | 1 | 1 | WestBay | 2004-12-10 14:05 | 238 | 0 |  | 2004-12-10 14:05 |  | -- | Sunset Lane x Monte Rosa Drive | Menlo Park | USA | 94025 |  |  | 2004-12-09 |  |  |  | Location of overflow (street): Sunset Lane Cross street: Monte Rosa Drive U/S Manhole: (o/f manhole)I14060 D/S Manhole: I14056 Dates of overflow: December 09, 2004 Time reported: 0750 hours Line Cleared @ 0828 hours Time Completed: 0900 hours Total overflow time: 38 minutes Estimated volume of overflow: 238 gallons Receiving waters (if applicable): Atherton Channel at Meadow Lane Description of incident: Passer-by reported overflowing manhole at 0750 hours. Staff responded and cleared the blockage. 41 homes are connected upstream of the blockage, estimated flow rate approximately 6.2 gallons per minute. The SSO flowed into a direct inlet which is located 25 feet from the overflowing manhole, which flows into the Atherton Channel. Storm water Tributaries in this area are flowing at 250 to 500 gallons per minute. Regulatory agencies notified: San Mateo County Environmental Health Department and the Town of Atherton. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestBay | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Source Control Insp. | J. Simonetti | 2004-12-10 | 650-321-0384 |  | MINOR
5174 | 31 | 1(24 hr Report) | WestCounty | 2007-04-30 | 2100 | 0 | 07-2613 | 2007-04-30 | Craig Gridley |  | John at Collins | San Pablo | Contra Costa | 94806 |  |  | 2007-04-28 | 0.25 | [9 empty] | No |  | No | No |  |  | No | No | No |  |  | No | No | [15 empty] | Agency Manager | Craig Gridley | 2007-04-30 | 510-237-6603
5169 | 30 | 1 | WestCounty | 2007-04-27 12:49 | 45 | 0 |  | 2007-04-27 12:49 |  | -- | 3926 La Colina | El Sobrante | Contra Costa | 94803 |  |  | 2007-04-26 |  |  |  | WCWD Mainline 150711 plugged by fibered cleaning rags. Area cleaned. Estimated <45 gallons total spilled. Recovered approx. 8 gallons. Remainder soaked into ground. Line televised, history reviewed, and maint. shed. updated. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | DEBRIS |  |  |  | CSO LW II | Cecil Viloria | 2007-04-27 | 510.222.6700
4972 | 29 | 1 | WestCounty | 2007-03-21 07:47 | 525 | 0 |  | 2007-03-21 07:47 |  | -- | 1300 Amador Way | San Pablo | Contra Costa | 94806 |  |  | 2007-03-21 |  |  |  | Doesn't appear that any sewage reached any waterways. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | INFRASTRUCTURE FAILURE | -- Select One -- |  |  |  | Lead Worker | Gordon Times | 2007-03-21 | 510-222-6700
4956 | 27 | 2 | WestCounty | 2007-03-19 09:22 | 225 | 0 |  | 2007-03-19 09:22 |  | -- | 2002 Thompson Ln. | El Sobrante | Contra Costa | 94803 |  |  | 2007-03-18 |  |  |  | No discharge into storm drains of state waterways. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Lead Worker | Gordon Times | 2007-03-19 | 510-222-6700
5001 | 28 | 2 | WestCounty | 2007-03-19 | 262000 | 251000 | 07-1753 | 2007-03-19 | Craig Gridley | WestCounty | 810 Market Avenue / BNSF Railroad easement | San Pablo | Contra Costa | 94806 |  |  | 2007-03-17 | 0.35417 |  |  | Damaged reclaimed water line. Transmission line owned by Chevron; purveyor of treated/reclaimed effluent is East Bay MUD. |  |  |  | Low |  | STORM DRAIN | No |  | No | No | No visible impact. |  | Yes | Yes | No |  |  | No | No |  |  | 2007-03-22 | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | PIPE | Damaged reclaimed water line. Transmission line owned by Chevron; purveyor of treated/reclaimed effluent is East Bay MUD. | INFRASTRUCTURE FAILURE | -- Select One -- | -- Select One -- | Reclaimed water line |  | Agency Maintenance Manager | Craig W. Gridley | 2007-03-26 | 510-237-6603
4845 | 26 | 1 | WestCounty | 2007-03-01 08:25 | 5 | 0 |  | 2007-03-01 08:25 |  | -- | 1825 Church Ln. | San Pablo | Contra costa | 94806 |  |  | 2007-02-26 |  |  |  | Allwater was retrieveed. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | INFRASTRUCTURE FAILURE | GREASE |  |  |  | Supervisor | Marc Raynor | 2007-03-01 | 510-222-6700
4586 | 25 | 1 | WestCounty | 2007-01-23 09:23 | 150 | 0 |  | 2007-01-23 09:23 |  | -- | 543 Appian Wy. | ElSobrante | Contra Costa County | 94806 |  |  | 2007-01-22 |  |  |  | 6" line collapsed causing a blockage in the main line. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | INFRASTRUCTURE FAILURE | -- Select One -- |  |  |  | Supervisor | Marc Raynor | 2007-01-22 | 510-222-6700
4560 | 24 | 1 | WestCounty | 2007-01-19 10:22 | 85 | 0 |  | 2007-01-19 10:22 |  | -- | 437 Rincon Ln. | ElSobrante | Contra Costa County | 94806 |  |  | 2007-01-17 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Supervisor | Marc Raynor | 2007-01-19 | 510-222-6700
4529 | 23 | 1 | WestCounty | 2007-01-17 08:00 | 65 | 0 |  | 2007-01-17 08:00 |  | -- | San pablo Dam Rd. x Lila Ln. | El Sobrante | Contra Costa | 94803 |  |  | 2007-01-17 |  |  |  | All contained and recovered. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | CSO LW II | Cecil Viloria | 2007-01-17 | 510.222.6700
3958 | 21 | 1 | WestCounty | 2006-10-03 07:50 | 450 | 0 |  | 2006-10-03 | Cecil Viloria |  | 13484 San Pablo Avenue | San Pablo | Ca | 94806 |  |  | 2006-10-01 | 1:50:00 PM | 2006-10-01 | 2:35:00 PM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | CSO Crew Leader II | Cecil Viloria | 2006-10-03 | 510-222-6700 | pwinnicki@wcwd.org; eshalaby@wcwd.org, eshalaby@wcwd.org, mraynor@wcwd.org, cviloria@wcwd.org | 24HR |  |  | 510.222.6700 | [6 empty] | WestCounty
3963 | 22 | 1 | WestCounty | 2006-10-03 14:19 | 5616 | 5016 | 065849 | 2006-10-03 | west County | Marc Raynor | 13830 San Pablo Ave | San Pablo | Contra Costa | 94806 |  |  | 2006-10-01 | 6:20:00 PM | [5 empty] | CLOUDY WEATHER | Medium |  | STORM DRAIN | No | NO | No | Yes | None |  | Yes | Yes | Yes | No | No | Yes | No | Yes | No | 2006-10-06 | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | westcounty | OTHER | Fixtures | BLOCKAGE | GREASE | --Select None-- | Grease and rages in the line. | We had a main line blockage in a 6"line that caused a backup into 13830 San Pablo Ave.Clean up was started shortly after. | Supervisor | Marc Raynor | 2006-10-03 | 510-222-6700 | mraynor@wcwd.orgpwinnicki@wcwd.org; eshalaby@wcwd.org, eshalaby@wcwd.org | MAJOR | Marc Raynor | WestCounty | 510-222-6700 | 2240 | 2910 Hilltop Dr. | Richmond | Contra Costa | 94806 | Marc Raynor | West County Wastewater | 510-222-6700 | 2240 | 2910 Hilltop Dr. | Richmond | Contra Costa | 94806
3927 | 20 | 1 | WestCounty | 2006-09-25 15:24 | 20 | 0 |  | 2006-09-25 15:24 |  | -- | 1131 Mitchel Way | El Sobrante | Contra Costa | 94806 |  |  | 2006-09-25 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | westcounty | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Supervisor | Marc Raynor | 2006-09-25 | 510-222-6700 | mraynor@wcwd.orgpwinnicki@wcwd.org; eshalaby@wcwd.org, eshalaby@wcwd.org | MINOR
3869 | 19 | 1 | WestCounty | 2006-09-11 14:50 | 75 | 0 |  | 2006-09-11 14:50 |  | -- | 4010 Granada ln. | El Sobrante | Contra Costa | 94806 |  |  | 2006-08-29 | [9 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | westcounty | CLEAN OUT |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | Supervisor | Marc Raynor | 2006-09-11 | 510-2226700 | mraynor@wcwd.org pwinnicki@wcwd.org; eshalaby@wcwd.org, eshalaby@wcwd.org | MINOR
3744 | 18 | 1 | WestCounty | 2006-08-16 09:00 | 990 | 0 |  | 2006-08-16 09:00 |  | -- | 4301 Appian Way | El Sobrabte | Contra Costa County | 94806 |  |  | 2006-08-16 |  |  |  | It appears there was a Partial blockage of the main line.The line was clear when found it. We washed down down the creek with 8000 plus gallons of decorinized water. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | westcounty | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Supervisor | marc Raynor | 2006-08-16 | 510-222-6700 | mraynor@wcwd.org pwinnicki@wcwd.org; eshalaby@wcwd.org, eshalaby@wcwd.org | MINOR
3682 | 17 | 1 | WestCounty | 2006-08-03 11:56 | 610 | 0 |  | 2006-08-03 11:56 |  | -- | 1533 4th.st.north richmond | Richmond | Contra Costa | 94801 |  |  | 2006-08-01 |  |  |  | A CONTRACTOR MADE A LATERAL CONNECTION TO THE MAIN LINE AND LET ROCK GET INTO OUR LINE CAUSING THE backup. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestCounty | MANHOLE |  | BLOCKAGE | DEBRIS FROM LATERALS |  |  |  | supervisor | Marc Raynor | 2006-08-03 | 510-222-6700 | pwinnicki@wcwd.org; eshalaby@wcwd.org, eshalaby@wcwd.org; mraynor@wcwd.org | MINOR
3330 | 15 | 1 | WestCounty | 2006-05-12 15:58 | 750 | 250 | 06-2866 | 2006-05-12 | 21:30 |  | 1816 Emeric Avenue | San Pablo | Contra Costa | 94806 |  |  | 2006-05-11 | 4:45:00 PM | 2006-05-11 | 10:45:00 P | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Agency Manager | Cecil Viloria | 2006-05-12 | 510-222-6700 | pwinnicki@wcwd.org; eshalaby@wcwd.org, eshalaby@wcwd.org, cviloria@wcwd.org | 24HR |  |  | 510.222.3700 | [6 empty] | WestCounty
3332 | 16 | 1 | WestCounty | 2006-05-12 16:00 | 750 | 0 |  | 2006-05-12 16:00 |  | -- | 1816 Emeric Ave. | San Pablo | Contra Costa | 94806 |  |  | 2006-05-11 |  |  |  | Partial blockage caused by broken pipe. Sewage flowed from private cleanout to crawlspace of 1816 emeric. All contained and cleanup in progress by Restoration Management Service via EV Link. No discharge into state waters. OES control #06-2866. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestCounty | CLEAN OUT |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | CSO LW II | Cecil Viloria | 2006-05-12 | 510.222.6700 | pwinnicki@wcwd.org; eshalaby@wcwd.org, eshalaby@wcwd.org, cviloria@wcwd.org | MINOR
2720 | 14 | 1 | WestCounty | 2006-02-01 07:17 | 336 | 0 |  | 2006-02-01 07:18 |  | -- | 2391 Rancho Road | El Sobrante | Contra Costa | 94803 |  |  | 2006-01-31 |  |  |  | While excavating contractor hit and poked a hole in a E.B.M.U.D. water line. This filled the ditch and caused a overflow to the street and adjacent land. Mixed with the fresh water,> 1,000, was approximately 336gal. of sewage. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestCounty | OTHER | Excavation site | BLOCKAGE | CONSTRUCTION DEBRIS |  |  |  | C.S.O. Super. | Tom Eckert | 2006-02-01 | 510-222-6700 | pwinnicki@wcwd.org; eshalaby@wcwd.org, eshalaby@wcwd.org, teckert@wcwd.org,sdamm@wcwd.org | MINOR
2220 | 13 | 1 | WestCounty | 2005-12-06 07:59 | 2250 | 0 | 05-0726 | 2005-12-06 | Cecil Viloria |  | 2682 Kavanagh. Cross Street Shamrock. | San Pablo | Contra Costa | 94806 |  |  | 2005-12-05 | 6:40:00 PM | 2005-12-05 | 7:20:00 PM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | CSO Crew Leader | Cecil Viloria | 2005-12-06 | 510-222-6700 | pwinnicki@wcwd.org; eshalaby@wcwd.org, eshalaby@wcwd.org; teckert@wcwd.org; cviloria@wcwd.org; bhill@wcwd.org | 24HR |  |  | 510.222.6700 | [6 empty] | WestCounty
2184 | 12 | 3 | WestCounty | 2005-11-28 15:32 | 24000 | 2000 | 05-6808 | 2005-11-25 | Tom Eckert | WestCounty | Tara Hills Dr./Montara Bay Park | San Pablo | Contra Costa | 94806 |  |  | 2005-11-25 | 2:00:00 PM | [5 empty] | SUNNY WEATHER | Low |  | SURFACE WATER IMPACT | No |  | No | No | most of the spill went out to san pablo bay with an out going tide. On 11/28/2005 the W.C.W>D. crew replaced the MH frame and cover that vandals removed. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | WestCounty | MANHOLE |  | BLOCKAGE | VANDALISM | --Select None-- | vandalism | SSO occcurred when a MH frame and cover were removed by vandals and trash/debris were deposited in the structure. Contra Costa County Health Dept. personel were present on site and were satisfied with W.C.W.D. response and cleanup efforts. | C.S.O. Supervisor | Tom Eckert | 2005-11-25 | 510-222-6700 | pwinnicki@wcwd.org; eshalaby@wcwd.org; bhill@wcwd.org; teckert@wcwd.org | MAJOR | Tom Eckert | West County | 510-222-6700 |  | 2910 Hilltop Dr. | Richmond | Contra Costa | 94806 |  | WestCounty | 510-222-6700 |  | 2910 Hilltop Dr. | Richmond | Contra Costa | 94806
2171 | 11 | 1 | WestCounty | 2005-11-24 14:16 | 300 | 0 |  | 2005-11-24 | Tom Eckert |  | 4256 Santa Rita Road | El Sobrante | Contra Costa | 94805 |  |  | 2005-11-24 | 10:15:00 A | 2005-11-24 | 12:15:00 P | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | C.S.O. Supervisor | Tom Eckert | 2005-11-24 | 510-222-6700 | pwinnicki@wcwd.org; eshalaby@wcwd.org; bhill@wcwd.org; teckert@wcwd.org | 24HR |  |  | 510-222-6700 | [6 empty] | WestCounty
1801 | 9 | 1 | WestCounty | 2005-09-18 15:34 | 1800 | 50 | 05-5422 | 2005-09-18 | Craig Gridley |  | N. Parkside Drive at W. View | Richmond | Contra Costa | 94803 |  |  | 2005-09-18 | 2:30:00 AM | 2005-09-18 | 2:50:00 AM | [7 empty] | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [13 empty] | Agency Manager | Paul Winnicki | 2005-09-18 | 510-222-6700 | pwinnicki@wcwd.org; eshalaby@wcwd.org, eshalaby@wcwd.org | 24HR |  |  | 510-812-8280 | [6 empty] | WestCounty
1874 | 10 | 1 | WestCounty | 2005-09-27 10:27 | 1800 | 50 | 05-5422 | 2005-09-18 | Craig Gridley | WestCounty | N. Parkside Drive at W. View | Richmond | Contra Costa | 94803 |  |  | 2005-09-18 | 2:50:00 AM | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | No | No visual effects at receiving water. |  | Yes | Yes | No | No | No | Yes | Yes | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | WestCounty | PUMP STATION |  | ELECTRICAL POWER FAILURE | --Select None-- | --Select None-- |  | Cause - Power overvoltage tripped variable frequency drive. Sample Results 9/20/5 (Tues) East section: DO = 5.54 and Ammonia = 1.7 mg/L West section: DO = 11.10 and Ammonia = 1.4mg/L 9/22/5 (Thurs) East section: DO = 7.07 and Ammonia = 0.3 mg/L West section: DO = 8.41 and Ammonia = 0.3 mg/L Results, thus far, show no downstream effects. Coliform results not yet available. | Plant Superintendent | Brian E. Hill | 2005-09-27 | 510.237.6603 | pwinnicki@wcwd.org; eshalaby@wcwd.org, eshalaby@wcwd.org, bhill@wcwd.org | MAJOR | Craig Gridley | WestCounty | 510.237.6603 |  | 2910 Hilltop Drive | Richmond | Contra Costa | 94806 |  | West County Wastewater | 510.222.6700 |  | 2910 Hilltop Drive | Richmond | Contra Costa | 94591
1597 | 8 | 1 | WestCounty | 2005-07-06 13:06 | 700 | 0 |  | 2005-07-06 13:06 |  | -- | 3080 San Pablo Dam Rd. x street Morrow Dr. | San Pablo | Contra Costa | 94806 |  |  | 2005-07-06 |  |  |  | Partial stoppage of debris in district mainline 050102.7. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestCounty | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | CSO Leadworker II | Cecil Viloria | 2005-07-06 | (510)222-6700 | pwinnicki@wcwd.org; eshalaby@wcwd.org, eshalaby@wcwd.org, cviloria@wcwd.org, teckert@wcwd.org, karinehs@ci.san-pablo.ca.us | MINOR
1573 | 7 | 1 | WestCounty | 2005-06-28 11:05 | 540 | 0 |  | 2005-06-28 11:05 |  | -- | 6100 North Arlington | El Sobrante | Contra Costa | 94806 |  |  | 2005-06-27 |  |  |  | Stoppage due to possible structural problem. Spill destination crawlspace of residence. Overflow estimate calculator indicates 540gal. which is being removed by cleanup contractor (Restoration Management via EV Link). | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestCounty | MANHOLE |  | BLOCKAGE | --Select None-- |  |  |  | CSO Leadworker II | Cecil Viloria | 2005-06-28 | (510)222-6700 | pwinnicki@wcwd.org; eshalaby@wcwd.org, eshalaby@wcwd.org, cviloria@wcwd.org, | MINOR
1508 | 6 | 1 | WestCounty | 2005-06-10 09:18 | 475 | 0 |  | 2005-06-10 09:18 |  | -- | Sewage Pump Station at end of access road near 5470 Sobrante Avenue. | El Sobrante | Contra Costa | 94803 |  |  | 2005-06-07 |  |  |  | A homeowner hired a contractor to perform swimming pool maintenance. The contractor pumped the pool contents into the residential lateral clean out at a rate higher than WCWD system pump station design capacity. The excess pool water overflowed the pump station wet well. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestCounty | PUMP STATION |  | INFLOW & INFILTRATION | --Select None-- |  |  |  | Maintenance Supervis | Craig W. Gridley | 2005-06-10 | 510-237-6603 | pwinnicki@wcwd.org; eshalaby@wcwd.org, eshalaby@wcwd.org | MINOR
1462 | 5 | 1 | WestCounty | 2005-05-31 08:21 | 100 | 0 |  | 2005-05-31 08:21 |  | -- | 3320 S.P Dam Dr. | El Sobrante | Contra Costa | 94806 |  |  | 2005-05-30 |  |  |  | Line blockage caused by hat. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestCounty | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Leadworker 2 | Marc Raynor | 2005-05-31 | 510-222-6700 | pwinnicki@wcwd.org; eshalaby@wcwd.org, eshalaby@wcwd.org | MINOR
1348 | 4 | 1 | WestCounty | 2005-05-02 15:38 | 825 | 0 |  | 2005-05-02 15:38 |  | -- | 4929 San Pablo Dam Rd. | El Sobrante | Contra Costa | 94564 |  |  | 2005-05-02 | [9 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestCounty | PIPE |  | BLOCKAGE | GREASE |  |  |  | CSO LEADWOKER 2 | MARC RAYNOR | 2005-05-02 | (510)2226700 | mraynor@wcwd.org; pwinnicki@wcwd.org; eshalaby@wcwd.org, eshalaby@wcwd.org | MINOR
1283 | 3 | 2 | WestCounty | 2005-04-18 09:17 | 2400 | 2400 | 05-2312 | 2005-04-18 | WestCounty | WestCounty | 3401 San Pablo Dam Rd. | El Sobrante | Contra Costa | 94803 |  |  | 2005-04-17 | 7:00:00 PM | [5 empty] | SUNNY WEATHER | Low |  | BUILDING/STRUCTURE | No |  | No | No | No Discharge into state waters or storm drains. |  | No | No | No | No | No | No | No | No | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | WestCounty | CLEAN OUT |  | BLOCKAGE | GREASE | --Select None-- |  |  | CSO Leadworker II | Cecil Viloria | 2005-04-18 | 510-222-6700 | cviloria@wcwd.org; pwinnicki@wcwd.org; eshalaby@wcwd.org, eshalaby@wcwd.org | MAJOR | Cecil Viloria | WestCounty | (510)222-6700 |  | 2910 Hilltop Dr. | Richmond | Contra Costa | 94806 |  | WestCounty | (510)222-3700 |  | 2910 Hilltop Dr. | Richmond | Contra Costa | 94803
1240 | 2 | 2 | WestCounty | 2005-04-01 09:16 | 7200 | 0 | 05-1998 | 2005-04-01 | Cecil Viloria | WestCounty | 4441/4443 Appian Wy. | El Sobrante | Contra Costa | 94803 |  |  | 2005-03-31 | 7:00:00 AM | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | No | Clear water. No solids reached recieving water. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | OPEN ACTIVE | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | WestCounty | MANHOLE |  | BLOCKAGE | --Select None-- | --Select None-- |  |  | CSO Leadworker II | Cecil Viloria | 2005-04-01 | 510-222-6700 | cviloria@wcwd.org | MAJOR | Cecil Viloria | WestCounty | (510)222-6700 |  | 2910 Hilltop Dr. | Richmond Ca. | Contra Costa | 94806 |  | WestCounty | (510)222-6700 |  | 2910 Hilltop Dr. | Richmond | Ca | 94806
955 | 1 | 1 | WestCounty | 2005-02-03 14:34 | 300 | 0 |  | 2005-02-03 14:34 |  | -- | 1070 North Rancho Road | El Sobrante | Contra Costa | 94803 |  |  | 2005-02-02 |  |  |  | Spill caused by electrical problem in station control circuitry. Problem has been rectified. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestCounty | PUMP STATION |  | ELECTRICAL POWER FAILURE | --Select None-- |  |  |  | Maint. Supervisor | Craig W. Gridley | 2005-02-03 | 510-237-6603 | pwinnicki@wcwd.org; eshalaby@wcwd.org | MINOR
5159 | 28 | 1 | WestValley | 2007-04-26 13:25 | 120 | 0 |  | 2007-04-26 13:25 |  | -- | 13421 Oak Drive, WVSD Manhole 8-010-08 | Monte Sereno | Santa Clara | 95030 |  |  | 2007-04-17 |  |  |  | Entire spill amount contained in grassy area and soaked into ground. CCTV confirmed that blockage was causeed by roots. No surface water impact. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Dir Eng & Ops | Peter V. Sevcik | 2007-04-26 | 408-378-2407
5073 | 27 | 1 | WestValley | 2007-04-18 14:42 | 200 | 0 |  | 2007-04-18 14:42 |  | -- | 210 Milbrae LN | Los Gatos | Santa Clara | 95032 |  |  | 2007-04-13 |  |  |  | Entire spill amount contained and recovered. CCTV inspection confirmed that blockage was caused by roots. Cleaning operation changed from high velocity water jetting to rodding. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | CLEAN OUT |  | BLOCKAGE | ROOTS |  |  |  | Dir Eng & Ops | Peter V. Sevcik | 2007-04-18 | 408-378-2407
4823 | 26 | 1 | WestValley | 2007-02-26 12:26 | 100 | 0 |  | 2007-02-26 12:26 |  | -- | 15900 Kennedy Road | Los Gatos | Santa Clara | 95032 |  |  | 2007-02-20 |  |  |  | Root blockage in unmapped sanitary sewer in former Town of Los Gatos system caused backup into structure. District assumed maintenance responsibility for Town system on 11/1/2005 and line was not on mapping of Town system. Line cleaned, scheduled for CCTV inspection and added to District's line cleaning program. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | PIPE |  | BLOCKAGE | ROOTS |  |  |  | Dir Eng & Ops | Peter V. Sevcik | 2007-02-26 | 408-378-2407
4718 | 25 | 1 | WestValley | 2007-02-09 09:49 | 400 | 0 |  | 2007-02-09 09:49 |  | -- | 17194 Zena Avenue 17216 Zena Avenue District Line Segment Number 6-068-05 to 6-069-05 | Monte Sereno | Santa Clara | 95030 |  |  | 2007-02-04 |  |  |  | Blockage in District sewer mainline 6-068-05 to 6-069-05 caused backflow into basements. Backflow prevention devices required by District Ordinance code for these properties. Unknown at this point if backflow devices never installed or if backflow devices failed. CCTV inspection indicates that blockage was caused by roots. Cleaning operation changed to rodding and cleaning frequency increased. | [5 empty] | BUILDING/STRUCTURE | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | PIPE |  | BLOCKAGE | ROOTS |  |  |  | Dir Eng & Ops | Peter V. Sevcik | 2007-02-09 | 408-378-2407
4715 | 24 | 1 | WestValley | 2007-02-09 08:21 | 150 | 0 |  | 2007-02-09 08:21 |  | -- | 16179 Camellia Terrace, District Manhole 9-011-06 | Los Gatos | Santa Clara | 95032 |  |  | 2007-02-02 |  |  |  | District Manhole 9-011-06 overflowed into adjacent stormwater conveyance system. Sewage was contained and recovered. CCTV inspection indicates that blockage was caused by a combination of roots and grease. Cleaning frequency for line increased. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Dir of Eng & Ops | Peter V Sevcik | 2007-02-09 | 408-378-2407
4676 | 23 | 2 | WestValley | 2007-01-24 | 1750 | 1750 | 07-0552 | 2007-01-24 | Peter Sevcik | WestValley | 14670 Hancock Court | Los Gatos | Santa Clara | 95030 |  |  | 2007-01-24 | 0.375 | [6 empty] | Low |  | CAPTURED IN STORM DRAIN | No |  | No | No | No receiving water affected |  | Yes | Yes | No |  |  | No | No |  |  |  | CLOSED | Michael Chee |  | mchee@waterboards.ca.gov |  | MANHOLE |  | BLOCKAGE | ROOTS | -- Select One -- |  | District manhole number 6-071-93 overflowed into adjacent stormwater conveyance system. Sewage was contained and recovered. CCTV inspection indicates that blockage was caused by roots infiltrating mainline sewer from sewer lateral. Cleaning frequency for line increased. | Director of Engineering and Operations | Peter V. Sevcik | 2007-01-24 | 408-378-2407
4598 | 22 | 1 | WestValley | 2007-01-23 14:02 | 250 | 0 |  | 2007-01-23 14:02 |  | -- | District Manhole #6-821-02 on Vista Del Lago at Casitas Bulevar | Los Gatos | Santa Clara | 95032 |  |  | 2007-01-15 |  |  |  | Relieved stoppage in line two sections downstream of line that overflowed and recovered entire overflow amount. CCTV inspection revealed partially collapsed line two sections downstream of line that overflowed. Line scheduled for repair. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No |  |  | No | No | [8 empty] | MANHOLE |  | INFRASTRUCTURE FAILURE | -- Select One -- |  |  |  | Dir of Eng & Ops | Peter V. Sevcik | 2007-01-23 | 408-347-2407
3912 | 21 | 1 | WestValley | 2006-09-21 14:04 | 20 | 0 |  | 2006-09-21 14:04 |  | -- | 108 Newell Avenue, District Manhole 6-085-84 | Los Gatos | Santa Clara | 95032 |  |  | 2006-09-14 |  |  |  | Overflow caused by grease buildup. Water evaporated before reaching any storm drains. Line cleaning frequency increased to six months. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestValley | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Director E & O | Peter V. Sevcik | 2006-09-21 | 408-378-2407 | psevcik@westvalleysan.org, rreid@westvalleysan.org | MINOR
3910 | 20 | 1 | WestValley | 2006-09-21 13:42 | 500 | 0 |  | 2006-09-21 13:42 |  | -- | 15768 Kavin Lane, District Manhole 8-034-81 | Los Gatos | Santa Clara | 95032 |  |  | 2006-09-13 |  |  |  | Overflow caused by grease buildup in siphon. Entire overflow quantity captured in storm drain and recovered. Washdown water also captured and recovered. Line put on two month cleaning cycle. | [5 empty] | CAPTURED IN STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestValley | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Director of E & O | Peter V. Sevcik | 2006-09-21 | 408-378-2407 | psevcik@westvalleysan.org, rreid@westvalleysan.org | MINOR
3754 | 19 | 2 | WestValley | 2006-08-18 08:39 | 27000 | 0 | 06-4809 | 2006-08-11 | Peter V Sevcik | WestValley | 13631 Saratoga Avenue, Manhole # 3-103-04 in rear yard | Saratoga | Santa Clara | 95070 |  |  | 2006-08-11 | 8:00:00 AM | [5 empty] | SUNNY WEATHER | Low |  | YARD/LAND | No |  | No | No | No discharge to surface water. |  | Yes | Yes | Yes | No | No | No | No | No | No | 2006-09-13 | OPEN ENFORCEMENT | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | WestValley | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS | --Select None-- |  | Overflow resulted from blockage caused by hot-mix asphalt being dumped into District's easement manhole by contractor working for private property owner. Overflow was contained in depression on neighbors private property and allowed to soak into ground since property owner did not want recovery equipment on his property. All solids were raked up and removed. District is pursuing civil penalties against contractor. | Director of Engineer | Peter V. Sevcik | 2006-08-11 | 408-378-2407 | psevcik@westvalleysan.org, rreid@westvalleysan.org | MAJOR | Peter Sevcik | West Valley Sanitation District | 408-378-2407 |  | 100 E. Sunnyoaks Avenue | Campbell | Santa Clara | 95008 | James Burroughs | XL Construction | 408-271-2427 | 130 | 1500 Berger Drive | San Jose | Santa Clara | 95112
3420 | 18 | 1 | WestValley | 2006-05-26 17:22 | 100 | 0 |  | 2006-05-26 17:22 |  | -- | Manhole 3-091-01 near 18831 Martha Avenue | Saratoga | Santa Clara | 95070 |  |  | 2006-05-26 |  |  |  | Spill contained in street. Recovered entire overflow volume with vacuum truck. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestValley | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Dir of E & O | Peter Sevcik | 2006-05-26 | 408-378-2407 | psevcik@westvalleysan.org, rreid@westvalleysan.org | MINOR
3075 | 17 | 1 | WestValley | 2006-03-27 14:58 | 100 | 0 |  | 2006-03-27 14:58 |  | -- | Manhole 9-011-05 near 16243 Camellia Terrace | Los Gatos | Santa Clara | 95032 |  |  | 2006-03-21 |  |  |  | Cleaning frequency increased to every 12 months. Line was on 24 month cleaning cycle. No previous history of stoppages or overflows. Scheduled for CCTV inspection to check for defects. Previous CCTV inspection in 2002 did not reveal any structural defects. Recovered 5 gallons. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestValley | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Dir of Eng & Ops | Peter V. Sevcik | 2006-03-27 | 408-378-2407 | psevcik@westvalleysan.org, rreid@westvalleysan.org | MINOR
2779 | 16 | 1 | WestValley | 2006-02-08 14:44 | 200 | 0 |  | 2006-02-08 14:44 |  | -- | Unmapped manhole upstream of Town of Los Gatos Manhole #8-056-84 behind 109 Vasona Oaks Drive | Los Gatos | Santa Clara | 95032 |  |  | 2006-01-30 |  |  |  | District assumed responsibility for Town of Los Gatos system on 11/1/2005. Manhole that overflowed was not mapped on Town's maps. Line added to District's maintenance program. Line also CCTV'd to assess condition. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestValley | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Director of Eng & Op | Peter V. Sevcik | 2006-02-08 | 408-378-2407 | psevcik@westvalleysan.org, rreid@westvalleysan.org | MINOR
2367 | 15 | 1 | WestValley | 2005-12-29 11:22 | 100 | 0 |  | 2005-12-29 11:22 |  | -- | Intersection of Palm Avenue and Hernandez Drive, Manhole 8-823-01 | Los Gatos | Santa Clara | 95032 |  |  | 2005-12-20 |  |  |  | Spill caused by gravel blockage. CCTV inpsection did not reveal source of gravel. Lines in area scheduled to be replaced in next four months as part of District's sewer replacement program. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestValley | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Dir of Eng & Ops | Peter V. Sevcik | 2005-12-29 | 408-378-2407 | psevcik@westvalleysan.org, rreid@westvalleysan.org | MINOR
2363 | 14 | 2 | WestValley | 2005-12-29 11:13 | 36000 | 36000 | 05-7330 | 2005-12-21 | Peter Sevcik | WestValley | Manhole 8-841-05 near 20 High School Court | Los Gatos | Santa Clara | 95032 |  |  | 2005-12-20 | 1:00:00 PM | [5 empty] | RAINY WEATHER | Medium |  | YARD/LAND | No |  | No | Yes | No surface water impact. |  | Yes | Yes | No | No | No | No | No | No | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | WestValley | MANHOLE | Blockage caused by two 12 inch diameter chunks of asphaltic concrete lodged in 12 inch diameter line. | BLOCKAGE | MULTIPLE CAUSES | --Select None-- |  | Blockage caused by two 12 inch diameter chunks of asphaltic concrete lodged in 12 inch diameter line. Duration estimated based on estimated volume of spill. Source of asphalt unknown - possible vandalism. | Director of Engineer | Peter V. Sevcik | 2005-12-29 | 408-378-2407 | psevcik@westvalleysan.org, rreid@westvalleysan.org | MAJOR | Peter Sevcik | West Valley Sanitation District | 408-378-2407 |  | 100 E. Sunnyoaks Avenue | Campbell | Santa Clara | 95008 |  | WestValley
2258 | 12 | 1 | WestValley | 2005-12-15 15:22 | 700 | 0 |  | 2005-12-15 15:22 |  | -- | Manhole 8-830-09 at 50 Park Avenue | Los Gatos | Santa Clara | 95032 |  |  | 2005-12-09 |  |  |  | CCTV inspection confirmed that blockage was caused by mortar that had been dumped into sanitary sewer by unknown persons. Mortar was removed to restore full capacity of pipe. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestValley | MANHOLE |  | BLOCKAGE | VANDALISM |  |  |  | Dir E & O | Peter V. Sevcik | 2005-12-15 | 408-378-2407 | psevcik@westvalleysan.org, rreid@westvalleysan.org | MINOR
2260 | 13 | 1 | WestValley | 2005-12-15 15:31 | 50 | 0 |  | 2005-12-15 15:31 |  | -- | Manhole 8-830-02 at 140 S. Santa Cruz Avenue | Los Gatos | Santa Clara | 95032 |  |  | 2005-12-09 |  |  |  | CCTV inspection indicated that line has minimal slope. Line cleaning frequency increased to prevent future occurrence. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestValley | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Dir e & O | Peter V. Sevcik | 2005-12-15 | 408-378-2407 | psevcik@westvalleysan.org, rreid@westvalleysan.org | MINOR
2246 | 10 | 1 | WestValley | 2005-12-13 07:27 | 100 | 0 |  | 2005-12-13 07:27 |  | -- | Manhole 9-835-02, near 120 Happy Acres Road | Los Gatos | Santa Clara | 95032 |  |  | 2005-12-08 |  |  |  | Entire amount spilled was recovered. Mud and long stick in manhole caused stoppage. Line had been last cleaned on 10/12/05. CCTV inspection did not identify any problems. Suspect that stick may have been inserted into manhole by vandals. | [5 empty] | STREET/CURB & GUTTER | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestValley | MANHOLE |  | BLOCKAGE | MULTIPLE CAUSES |  |  |  | Dir of Eng & Ops | Peter V. Sevcik | 2005-12-13 | 408-378-2407 | psevcik@westvalleysan.org, rreid@westvalleysan.org | MINOR
2253 | 11 | 1 | WestValley | 2005-12-14 08:30 | 700 | 0 |  | 2005-12-14 08:30 |  | -- | Manhole 8-846-22, near end of Maple Lane adjacent to Los Gatos Creek Trail | Los Gatos | Santa Clara | 95032 |  |  | 2005-12-08 |  |  |  | Entire volume of SSO was contained. Line scheduled to be replaced within next 12 months to a more accessible location. Cleaning frequency reduced from 12 months to 3 months. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestValley | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Dir Eng & Ops | Peter V. Sevcik | 2005-12-14 | 408-378-2407 | psevcik@westvalleysan.org, rreid@westvalleysan.org | MINOR
1814 | 9 | 1 | WestValley | 2005-09-20 13:02 | 500 | 0 |  | 2005-09-20 13:02 |  | -- | Manhole 3-043-22 at 778 Inwood Drive | Campbell | Santa Clara | 95008 |  |  | 2005-09-13 |  |  |  | Rag debris in siphon resulted in blockage that surcharged and overflowed upstream manhole. Siphon cleaned one week earlier as part of District's two month cycle siphon cleaning program. CCTV inspection of upstream segments did not reveal source of debris. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestValley | MANHOLE |  | BLOCKAGE | DEBRIS |  |  |  | Dir of Eng & Ops | Peter V. Sevcik | 2005-09-20 | 408-378-2407 | psevcik@westvalleysan.org, rreid@wvsd.dst.ca.us, | MINOR
1584 | 8 | 2 | WestValley | 2005-06-30 13:42 | 1500 | 0 | 05-3749 | 2005-06-23 | Peter V. Sevcik | WestValley | Manhole # 8-830-08 in intersection of Broadway and South Santa Cruz Avenue | Los Gatos | Santa Clara | 95031 |  |  | 2005-06-23 | 8:10:00 AM | [5 empty] | SUNNY WEATHER | Low |  | STORM DRAIN | No |  | No | No | No visible solids in storm drain. Storm drain flushed with water. |  | Yes | Yes | No | No | No | No | No | No | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | WestValley | MANHOLE |  | BLOCKAGE | CONSTRUCTION DEBRIS | --Select None-- |  | Stoppage caused by construction debris that originated upstream of blocked section. CCTV confirmed integrity of blocked lines and sections immediately upstream of blocked line. Contractor advised to take additional precautions to ensure that construction debris does not get into system. | Director of Eng & Op | Peter V. Sevcik | 2005-06-23 | 408-378-2407 | psevcik@westvalleysan.org, rreid@wvsd.dst.ca.us, | MAJOR | Peter Sevcik | West Valley Sanitation District | 408-378-2407 |  | 100 E. Sunnyoaks Avenue | Campbell | Santa Clara | 95008 |  | WestValley
1034 | 5 | 1 | WestValley | 2005-02-16 09:57 | 600 | 0 |  | 2005-02-16 09:57 |  | -- | WVSD Manhole #7-014-07 on Longfellow Avenue | Campbell | Santa Clara | 95008 |  |  | 2005-02-07 |  |  |  | CCTV Inspection determined that probable cause of stoppage was root intrusion at several joints. No previous stoppage history. Changed maintenance frequency to 6 months from 24 months. | [5 empty] | STORM DRAIN | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestValley | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Dir of Engr and Ops | Peter V. Sevcik | 2005-02-16 | 408-378-2407 | psevcik@westvalleysan.org, rreid@wvsd.dst.ca.us, | MINOR
1036 | 6 | 1 | WestValley | 2005-02-16 10:08 | 300 | 0 |  | 2005-02-16 10:08 |  | -- | WVSD Manhole 5-082-21 in rear of property at 20470 Montalvo Heights Drive | Saratoga | Santa Clara | 95070 |  |  | 2005-02-07 |  |  |  | CCTV Inspection determined that probable cause of stoppage was grease accumulation. Changed maintenance frequency to 6 months from 12 months. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestValley | MANHOLE |  | BLOCKAGE | GREASE |  |  |  | Dir Engr and Ops | Peter V. Sevcik | 2005-02-16 | 408-378-2407 | psevcik@westvalleysan.org, rreid@wvsd.dst.ca.us, | MINOR
1015 | 4 | 2 | WestValley | 2005-02-11 08:28 | 6000 | 4500 | 05-0792 | 2005-02-04 | Peter V. Sevcik | WestValley | 14995 Fruitvale Avenue (WVSD manhole #5-041-02 in back of property) | Saratoga | Santa Clara | 95070 |  |  | 2005-02-03 | 2:30:00 PM | [5 empty] | CLOUDY WEATHER | Low |  | STORM DRAIN | No |  | No | No | Over half of overflow quantity recovered from storm drain. Solids in creek area upstream of storm drain recovered and removed. Impacted storm drain flushed with clean water. |  | Yes | Yes | No | No | No | No | No | No | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | WestValley | MANHOLE | CCTV identified broken VCP mainline 7 feet downstream of WVSD Manhole #5-041-02. Blockage likely caused by debris getting caught and bulding up in area of broken pipe. | BLOCKAGE | MULTIPLE CAUSES | BREAKAGE OF COLLECTION SYSTEM |  | Blockage likely caused by debris getting caught and building up in area of broken pipe resulting in overflow. CCTV identified broken VCP mainline 7 feet downstream of WVSD Manhole #5-041-02. Pipe scheduled for repair. | Dir. of Eng & Ops | Peter V. Sevcik | 2005-02-04 | 408-378-2407 | rreid@wvsd.dst.ca.us;psevcik@westvalleysan.org | MAJOR | Peter V. Sevcik | West Valley Sanitation District | 408-378-2407 |  | 100 E. Sunnyoaks Avenue | Campbell | Santa Clara | 95008 |  | WestValley | 408-378-2407 |  | 100 E. Sunnyoaks Avenue | Campbell | Santa Clara | 95008
949 | 3 | 2 | WestValley | 2005-02-02 10:45 | 2250 | 1500 | 05-0660 | 2005-01-27 | Peter Sevcik | Peter Sevcik | Intersection of Audrey & Vale - Manhole 6-080-02 | Campbell | Santa Clara | 95008 | 139.1 | 47.5 | 2005-01-27 | 7:45:00 AM | [5 empty] | CLOUDY WEATHER | Low |  | SURFACE WATER IMPACT | No |  | No | No | Over half of overflow quantity recovered from stormdrain. Impacted storm drain flushed with clean water. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Johnson Lam | 510 622 2373 | jlam@waterboards.ca.gov | WestValley | MANHOLE | CCTV inspection determined that stoppage/overflow was caused by a combination of soap/grease build-up and two sags in line. | BLOCKAGE | MULTIPLE CAUSES | --Select None-- |  | CCTV inspection determined that stoppage/overflow was caused by a combination of soap/grease build-up and two sags in line. Changed frequency of cleaning from 24 months to 12 months to minimize potential for future overflows. | Dir of Eng & Ops | Peter V. Sevcik | 2005-01-27 | 408-378-2407 | psevcik@wvsd.dst.ca.us; rreid@westvalleysan.org | MAJOR | Peter Sevcik | West Valley Sanitation District | 408-378-2407 |  | 100 E. Sunnyoaks Avenue | Campbell | Santa Clara | 95008 |  | West Valley Sanitation District | 408-378-2407 |  | 100 E. Sunnyoaks Avenue | Campbell | Santa Clara | 95008
842 | 2 | 1 | WestValley | 2005-01-13 10:38 | 100 | 0 |  | 2005-01-13 10:38 |  | -- | Ronnie Way at Portos Court - Section 3-101-07 to 3-101-08 | Saratoga | Santa Clara | 95070 |  |  | 2005-01-10 |  |  |  | CCTV inspection determined that blockage was caused by roots. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestValley | MANHOLE |  | BLOCKAGE | ROOTS |  |  |  | Dir Eng and Ops | Peter V. Sevcik | 2005-01-13 | 408-378-2407 | psevcik@wvsd.dst.ca.us | MINOR
840 | 1 | 1 | WestValley | 2005-01-13 10:32 | 300 | 0 |  | 2005-01-13 10:32 |  | -- | 14099 Elvira Street | Saratoga | Santa Clara | 95070 |  |  | 2005-01-08 |  |  |  | CCTV inspection revealed blockage was caused by broom stick lodged in section that resulted in debris accumulation. | [5 empty] | YARD/LAND | No |  | No | No |  |  | No | No | No | No | No | No | No | No | No | [5 empty] | WestValley | CLEAN OUT |  | BLOCKAGE | VANDALISM |  |  |  | Dir of Eng and Ops | Peter V. Sevcik | 2005-01-13 | 408-378-2407 | psevcik@wvsd.dst.ca.us | MINOR
2559 | 1 | 2 | Woodside | 2006-01-06 12:34 | 21600 | 0 | 06-0106 | 2006-01-03 | Richard Chiu | Woodside | Woodside Road and Mountain Home Road | Woodside | San Mateo | 94062 |  |  | 2005-12-31 | 6:00:00 AM | [5 empty] | RAINING FOR SEVERAL DAYS | Low |  | SURFACE WATER IMPACT | No |  | No | No | No visual signs of sewage overflow. |  | Yes | Yes | No | No | No | No | No | Yes | No |  | CLOSED | Michael Chee | 510 622 2333 | mchee@waterboards.ca.gov | Woodside | OTHER | Creek overflowed into pump station filling up wet well and mixing with sewage in wet well. | NATURAL DISASTER | --Select None-- | --Select None-- |  |  | Town Engineer | Kent Dewell | 2006-01-03 | 650-851-6790 | dkdewell@woodsidetown.org, sgeorge@woodsidetown.org | MAJOR | Richard Chiu/Kent Dewell | Town of Woodside | 650-851-6790 |  | 2955 Woodside Road | Woodside | San Mateo | 94062 |  | Woodside