## Slide 1: City of Fresno CA1010007 Fresno County Jar Test Actiflo
by Guy Schott, P.E.
January 7, 2020

## Slide 2: Kings River

## Slide 3: City of Fresno Kings River Water Characteristics January 7, 2020
Source
Turbidity: 0.45 NTU
pH: 7.32
UVT: 91.7% (unfiltered)
UVA/cm: 0.038

## Slide 4: Actiflo Microsand Ballasted Clarification Treatment
Alum

## Slide 5: UVT/UVA
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 6: Coagulant Used for Jar Testing
Pro Pac 9800 (NTU Technologies)
50% Aluminum Chlorohydrate (ACH)
50% Water
SG = 1.34
Aluminum Sulfate
48.24% Aluminum Sulfate
8.2% Al2O3
SG = 1.34
Nalco – Optimer 8110 PULV
Polyacrylamide
Dry
Max use 1 mg/L

## Slide 7: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.32
LCA #1:
Optimer 8110: 0.06 mg/L as product
Alum: 6.29 mg/L as product
pH adjusted to 6.8 with acetic acid.

## Slide 8: City of Fresno – Northeast Plant, Jar Test 1-8 Results Flash Mix 200 RPM (30 sec), MR (Maturation)
Jar # | Alum mg/L | 110 RPM Mix min | Ballast Sand | 8110 PULV mg/L | 60 RPM MR min | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 5 min
J1 | 6 | 2 | ½ Tsp | 0.06 | 3 | 0.15 | 95.1 | 0.021 | 1.0
J2 | 8 | 2 | ½ Tsp | 0.06 | 3 | 0.09 | 95.8 | 0.019 | 0.81
J3 | 10 | 2 | ½ Tsp | 0.06 | 3 | 0.08 | 96.1 | 0.017 | 0.82
J4 | 12 | 2 | ½ Tsp | 0.06 | 3 | 0.08 | 96.3 | 0.016 | 0.96
J5 | 12 | 2 | ½ Tsp | 0.06 | 3 | 0.08 | 96.3 | 0.016 | 0.74
J6 | 14 | 2 | ½ Tsp | 0.06 | 3 | 0.07 | 96.3 | 0.016 | 0.74
J7 | 16 | 2 | ½ Tsp | 0.06 | 3 | 0.06 | 96.9 | 0.014 | 0.76
J8 | 18 | 2 | ½ Tsp | 0.06 | 3 | 0.10 | 96.7 | 0.015 | 0.76

## Slide 9: City of Fresno – Northeast Plant, Jar Test 9-16 Results Flash Mix 200 RPM (30 sec), MR (Maturation)
Jar # | Alum mg/L | 110 RPM Mix min | Ballast Sand | 8110 PULV mg/L | 60 RPM MR min | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 5 min
J9 | 12 | 2 | ½ Tsp | 1.0 | 3 | 0.08 | 96.3 | 0.016 | 0.77
J10 | 14 | 2 | ½ Tsp | 1.0 | 3 | 0.07 | 96.7 | 0.015 | 0.89
J11 | 16 | 2 | ½ Tsp | 1.0 | 3 | 0.06 | 96.7 | 0.015 | 0.75
J12 | 18 | 2 | ½ Tsp | 1.0 | 3 | 0.10 | 96.6 | 0.015 | 0.65
J13 | 12 | 2 | ½ Tsp | 0 | 3 | 0.12 | 96.1 | 0.017 | 0.71
J14 | 14 | 2 | ½ Tsp | 0 | 3 | 0.09 | 96.2 | 0.017 | 1.07
J15 | 16 | 2 | ½ Tsp | 0 | 3 | 0.13 | 96.0 | 0.018 | 0.78
J16 | 18 | 2 | ½ Tsp | 0 | 3 | 0.10 | 96.3 | 0.016 | 0.66

## Slide 10: City of Fresno – Northeast Plant, Jar Test 17-24 Results Flash Mix 200 RPM (30 sec), MR (Maturation)
Jar # | Alum mg/L | 110 RPM Mix min | Ballast Sand | 8110 PULV mg/L | 60 RPM MR min | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 5 min
J17 | 12 | 2 | 0 | 0.06 | 3 | 0.12 | 96.2 | 0.017 | 0.63
J18 | 14 | 2 | 0 | 0.06 | 3 | 0.11 | 96.4 | 0.016 | 0.65
J19 | 16 | 2 | 0 | 0.06 | 3 | 0.11 | 96.8 | 0.014 | 0.63
J20 | 18 | 2 | 0 | 0.06 | 3 | 0.09 | 96.7 | 0.015 | 0.57
J21 | 12 | 2 | 1/4 Tsp | 0.06 | 3 | 0.12 | 96.4 | 0.016 | 0.74
J22 | 14 | 2 | Tsp | 0.06 | 3 | 0.11 | 96.4 | 0.016 | 0.72
J23 | 16 | 2 | 1/4 Tsp | 0.06 | 3 | 0.08 | 96.5 | 0.015 | 0.87
J24 | 18 | 2 | 1/4 Tsp | 0.06 | 3 | 0.08 | 96.7 | 0.015 | 0.79
Jar # | Alum mg/L | 110 RPM Mix min | Ballast Sand | 8110 PULV mg/L | 60 RPM MR min | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 5 min
J17 | 12 | 2 | 0 | 0.06 | 3 | 0.12 | 96.2 | 0.017 | 0.63
J18 | 14 | 2 | 0 | 0.06 | 3 | 0.11 | 96.4 | 0.016 | 0.65
J19 | 16 | 2 | 0 | 0.06 | 3 | 0.11 | 96.8 | 0.014 | 0.63
J20 | 18 | 2 | 0 | 0.06 | 3 | 0.09 | 96.7 | 0.015 | 0.57
J21 | 12 | 2 | 1/4 Tsp | 0.06 | 3 | 0.12 | 96.4 | 0.016 | 0.74
J22 | 14 | 2 |  | 0.06 | 3 | 0.11 | 96.4 | 0.016 | 0.72
J23 | 16 | 2 | 1/4 Tsp | 0.06 | 3 | 0.08 | 96.5 | 0.015 | 0.87
J24 | 18 | 2 | 1/4 Tsp | 0.06 | 3 | 0.08 | 96.7 | 0.015 | 0.79

## Slide 11: City of Fresno – Northeast Plant, Jar Test 25-28 Results Flash Mix 200 RPM (30 sec), MR (Maturation)
Jar # | 9800 mg/L | 110 RPM Mix min | Ballast Sand | 8110 PULV mg/L | 60 RPM MR min | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 5 min
J25 | 7.0 | 2 | ½ Tsp | 0.06 | 3 | 0.08 | 96.4 | 0.016 | 0.73
J26 | 8.5 | 2 | ½ Tsp | 0.06 | 3 | 0.11 | 96.4 | 0.016 | 0.72
J27 | 10 | 2 | ½ Tsp | 0.06 | 3 | 0.10 | 96.6 | 0.015 | 0.80
J28 | 11.5 | 2 | ½ Tsp | 0.06 | 3 | 0.10 | 96.7 | 0.015 | 0.62

## Slide 12: Jar Testing – Procedures for Actiflo 1-Liter Jars
Fill jars with source water prior to coagulant injection; set paddle speed at 30 rpm
Add primary coagulant to each jar
Flash mix for 15-60 seconds (200 rpm for 1-liter jars)
Reduce paddled speed to (110 rpm for 1-liter jars)
Add ballast sand (1/2 tsp/liter)
Hold paddle speed for 2-minutes
Reduce paddle speed to (60 rpm for 1-liter jars)
Add polymer

## Slide 13: Jar Testing – Procedures for Actiflo 1-Liter Jars - continue
Hold paddle speed for 3-minutes (maturation basin)
Turn paddles off; raise paddles out of water; settled for 1 minute
Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um Isopore membrane into cuvette (drip rate, 15 mL/90 sec)
Measure filtrate turbidity, chlorine residual and %UVT or UVA
Measure settled water turbidity after 5 minutes of total setting
Record all data

## Slide 14: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 15: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 16: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 17: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 18: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732