STATE WATER RESOURCES CONTROL BOARD

BOARD MEETING SESSION – DIVISION OF WATER QUALITY

FEBRUARY 19, 2004

# ITEM  3

## SUBJECT

CONSIDERATION OF A RESOLUTION ADOPTING REGULATIONS THAT REQUIRE CERTIFICATION FOR UNDERGROUND STORAGE TANK (UST) OPERATORS, INSTALLERS, SERVICE TECHNICIANS, AND INSPECTORS

## DISCUSSION

Management of USTs in California is regulated under both federal and state law.  Applicable federal law is found in the Resource Conservation and Recovery Act (RCRA), Subtitle I, Section 9003, and regulations implementing federal laws are found in Title 40 of the Code of Federal Regulations, Part 280. Applicable state law is incorporated into Health and Safety Code (HSC) Chapter 6.7, commencing with section 25280, and related regulations in Title 23, Division 3, Chapter 16, California Code of Regulations.

The Legislature enacted HSC Chapter 6.7 in 1984.  Since then it has amended Chapter 6.7 in response to either federal mandates relating to USTs, or new information regarding changing industry practices or the performance of USTs meeting then-current UST regulatory standards in California. In October 1999 and April 2001, the Legislature again amended Chapter 6.7, enacting Senate Bill (SB) 989 (Stats. 1999, Ch. 812) and Assembly Bill (AB) 1465 (Stats. 2001, Ch. 154) respectively.

SB 989 essentially codified Executive Order D-5-99.  This Executive Order was the Governor’s response to a University of California report on the environmental impacts of methyl tertiary butyl ether (MTBE) -- an additive put into motor vehicle fuel beginning in the late 1980’s, and early 1990’s.  The Executive Order required the phase-out of MTBE in fuel by December 31, 2002, although this date was subsequently postponed by Executive Order D-52-02 to January 1, 2004.  SB 989 amended Chapter 6.7 to accompany the phase-out of MTBE with more stringent construction and monitoring standards for UST systems.  The State Water Resources Control Board’s (SWRCB’s) amended regulations to implement these new requirements went into effect in May 14, 2001.  However, SB 989 also included a new requirement for owners and operators of UST systems, local agency UST facility inspectors, UST system installers, and UST monitoring equipment service technicians to meet minimum industry-established training standards. Furthermore, AB 1465 expanded the tasks that a licensed tank tester can perform in California, to include performing annual monitoring certifications for leak detection equipment.  This includes installation, repair, maintenance, calibration, and annual certification of UST leak detection equipment.

A Notice of Proposed Rulemaking announcing the proposed amendments to the regulations was published in the March 7, 2003 issue of the California Regulatory Notice Register.  A public hearing regarding the proposed regulations was held on April 28, 2003 at the Cal/EPA Headquarters in Sacramento.  The SWRCB received several written and oral comments and, based on those comments, the proposed regulations were revised.  Pursuant to Government Code section 11346.8, subdivision (c), and section 44 of Title 1 of the California Code of Regulations, the revised regulations were mailed to all commenters and local implementing agencies to comment on the revisions within 15 days of the mailing.  Additional comments were received during the 15-day comment period and, based on those comments, the proposed regulations were revised again.  The revised proposal was then distributed for a second 15-day comment period.  Although additional comments were received during the second 15-day comment period, the SWRCB rejected all of these comments and no further revisions were made to the proposed regulations.

## POLICY ISSUE

Should the SWRCB adopt the amendments to the UST regulations as proposed?

## FISCAL ISSUE

State agencies that own or operate USTs may incur additional costs as a result of the proposed regulations.  Most of the cost will be incurred from certifying a designated UST operator and training of facility employees for each facility.  The total first year estimated cost to the state as a result of the proposed regulations is $40,700 and with an ongoing state cost of $32,800 annually.  The SWRCB expects that state agencies will be able to absorb these additional costs within their existing budgets and resources.

SWRCB staff work associated with or resulting from the proposed regulations can be accomplished within budgeted resources.

## REGIONAL BOARD IMPACT

None.

## STAFF RECOMMENDATION

Staff recommends adoption of a resolution adopting amendments to the UST regulations to interpret, clarify, and implement legislative changes made to Chapter 6.7 of Division 20 of the HSC pursuant to Senate Bill 989 (Stats. 1999, ch 812) and Assembly Bill 1465 (Stats. 2001, ch. 154), and for additional reasons presented in the rulemaking file.

The UST regulations are available electronically on the program website at

http://www.waterboards.ca.gov/water_issues/programs/ust/index.shtml.

STATE WATER RESOURCES CONTROL BOARD

RESOLUTION NO. 2004-

# RESOLUTION ADOPTING REGULATIONS THAT REQUIRE

CERTIFICATION FOR UNDERGROUND STORAGE TANK

OPERATORS, INSTALLERS, SERVICE TECHNICIANS, AND INSPECTORS.

WHEREAS:

- Underground tanks used for the storage of hazardous substances and wastes are potential sources of contamination of the ground and underlying aquifers, and may pose other dangers to public health and the environment.

- The State Water Resources Control Board (SWRCB) administers the Underground Storage Tank (UST) Program, and local agencies implement the program through UST permitting and enforcement.

- In October 1999, the Legislature amended Chapter 6.7 by enacting Senate Bill 989

(Stats. 1999, ch. 812), which directed the SWRCB to adopt regulations requiring UST owners, operators, service technicians, installers, and inspectors to meet minimum industry-established training standards

- Health and Safety Code Section 25299.33 of Chapter 6.7 authorizes the SWRCB to adopt regulations to implement Chapter 6.7.

- On March 7, 2003 the SWRCB published a notice of proposed rulemaking to implement, interpret, and clarify the recent amendments to Chapter 6.7.  On April 28, 2003, the SWRCB held a public hearing regarding the proposed regulations.

- The SWRCB received several written and/or oral comments.  Based on the accepted comments and on SWRCB-initiated changes, the SWRCB revised the proposed regulations and sent them to commenters for further comments. Additional comments were received during the 15-day comment period.  Based on the accepted comments and SWRCB-initiated changes, the SWRCB revised the proposed regulations and once again sent them to commenters. Although additional comments were received during the last 15-day comment period, the SWRCB rejected all of these comments and no further revisions were made to the proposed regulations.

THEREFORE BE IT RESOLVED THAT:

The State Water Resources Control Board adopts the proposed Underground Storage Tank regulations to implement, interpret, and make specific Chapter 6.7 of Division 20 of the Health and Safety Code, which will become effective as provided by the California Administrative Procedures Act upon approval by the Office of Administrative Law and filing with the Secretary of State, and directs the Executive Director to submit the regulations to the Office of Administrative Law for approval.

# CERTIFICATION

The undersigned, Clerk to the Board, does hereby certify that the foregoing is a full, true, and correct copy of a resolution duly and regularly adopted at a meeting of the State Water Resources Control Board held on February 19, 2004.

_________________________

Debbie Irvin

Clerk to the Board

STATE WATER RESOURCES CONTROL BOARD

UNDERGROUND STORAGE TANK REGULATIONS

TITLE 23, DIVISION 3, CHAPTER 16, CALIFORNIA CODE OF REGULATIONS

AMENDMENTS TO UNDERGROUND STORAGE TANK PERMITTING, INSPECTION, AND TRAINING REGULATIONS

TEXT OF REGULATIONS

###### Amend Title 23, Division 3, Chapter 16, of the California Code of Regulations to read as follows:

### Article 1. Definition of Terms.

§ 2611.  Additional Definitions

Unless the context requires otherwise, the following definitions shall apply to terms used in this chapter.

“Best management practice” means any underground storage tank system management and operation practice that is the most effective and practicable method of preventing or reducing the probability of a release.

•••

"Cathodic protection tester" means any individuala person who can demonstrate an understanding of the principles and measurements of all common types of cathodic protection systems as applied to buried or submerged metallic piping and underground storage tank systems. The term includes only persons who Such an individual shall possess a current certificate from the National Association of Corrosion Engineers or the International Code Council, demonstrating have education and experience in soil resistivity, stray current, structure-to-soil potential, and component electrical isolation measurements of buried or submerged metallic piping and underground storage tank systems.

"Corrosion specialist" means any individuala person who, by reason of thorough knowledge of the physical sciences and the principles of engineering and mathematics acquired by a professional education and related practical experience, is qualified to engage in the practice of corrosion control on metal underground storage tanks and associated piping buried or submerged metallic piping and underground storage tank systems.  The term includes only persons who have been Such an individual shall possess a current certificate from certified by the National Association of Corrosion Engineers as a corrosion specialist, or be a registered professional engineers with a current certificate or license requiringwho have certification or licensing that requires education and experience in corrosion control of underground storage tanks and associated piping buried or submerged metallic piping and underground storage tank systems.

•••

“Designated underground storage tank operator” or “designated UST operator”

means one or more individuals designated by the owner to have responsibility for

training facility employees and conducting monthly visual inspections at an

underground storage tank facility. A “designated UST operator” is not considered

the “operator” as defined in Chapter 6.7 of Division 20 of the Health and Safety

Code, although the same individual may hold both positions.

•••

“Facility employee” means an individual who is employed on-site at an underground storage tank facility, and who may be called upon to respond to spills, overfills, or other problems associated with the operation of the underground storage tank system.  A “facility employee” is not considered the “operator” as defined in Chapter 6.7 of Division 20 of the Health and Safety Code, although the same individual may hold both positions.

“Fail safe” means that a monitoring system will shut down the turbine pump in the event of a power outage, or when the monitoring system fails or is disconnected.

•••

## “Service technician” means any individual who installs or tests monitoring equipment, or provides maintenance, service, system programming or diagnostics, calibration, or trouble-shooting for underground storage tank system components.

•••

Authority cited: Sections 25299.3 and 25299.7, Health and Safety Code.

Reference:  Sections 25281, 25282, 25283, 25284, 25284.1, 25292.3 and 25299.5(a),

Health and Safety Code; 40 CFR 280.10 and 280.12.

Article 3. New Underground Storage Tank Design, Construction, and Monitoring Requirements.

§ 2630. General Applicability of Article.

•••

(d) All monitoring equipment used to satisfy the requirements of this article shall meet the requirements of section 2643(f) and shall be installed and maintained such that the equipment is capable of detecting a leak at the earliest possible opportunity.  Additionally, all monitoring equipment used to satisfy the requirements of this article shall be installed, calibrated, operated, and maintained in accordance with section 2637(b).  2638.

Authority: Sections 25299.3 and 25299.7, Health and Safety Code.

Reference: Sections 25281, 25284.1, 25291 and 25292.3, Health and Safety Code; 40 CFR 280.20.

§ 2631.1. Compatibility and Permeability Testing Requirements for All New Underground Storage Tanks.

- Owners and operators must use an underground storage tank system made of or

lined with materials that are compatible with the substance stored in the

underground storage tank system.

- For underground storage tank system components installed on or after July 1, 2004, the applicable approvals required in subsections 2631(b) and (d) shall include a list of the compatible products tested and the measured product permeation rates, if such testing is required by the industry code or engineering standard used to evaluate the component.  These results shall be provided to the local agency upon request.

Authority: Sections 25299.3 and 25299.7, Health and Safety Code.

Reference: Sections 25281, 25284.1, 25286, 25291 and 25299, Health and Safety Code: 40 CFR 280.20, 280.32, 280.40-280.45.

§ 2635. Installation and Testing Requirements for All New Underground Storage Tanks.

•••

(d) 	Owners or their agents shall certify that the installation of the tanks and piping, meets the conditions in subdivision (1) through (5) (4) below. The certification shall be made on a "Certificate of Compliance for Underground Storage Tank Installation Form C" (see Appendix V).

(1) The installer has been adequately trained as evidenced by a certificate of training issued by the tank and piping manufacturers.  On and after July 1, 2001, this certification shall be renewed by completion of the manufacturer’s refresher training at the time interval recommended by the manufacturer, or every 36 months, whichever is shorterhas met the requirements set forth in section 2715, subdivisions (g) and (h);

(2) The installer has been certified or licensed by the Contractors State License Board.

(3) (2) The underground storage tank, any primary piping, and any secondary containment, was installed according to applicable voluntary consensus standards and any manufacturer's written installation instructions;

(4) (3) All work listed in the manufacturer's installation checklist has been completed; and

(5) (4) The installation has been inspected and approved by the local agency, or, if required by the local agency, inspected and certified by a registered professional engineer who has education and experience with underground storage tank system installations.

Authority: Sections 25299.3 and 25299.7, Health and Safety Code.

Reference: Sections 25281, 25284.1, 25291 and 25299, Health and Safety Code: 40 CFR

280.20, 280.32, 280.40-280.45.

§ 2636. Design, Construction, Installation, Testing, and Monitoring Requirements for Piping.

•••

(f) Underground piping with secondary containment, including under-dispenser piping with secondary containment, shall be equipped and monitored with monitoring systems as follows:

(1) All secondary containment, including under-dispenser containment, and under-dispenser spill control or containment systems, shall be equipped with a continuous monitoring system that either activates an audible and visual alarm or stops the flow of product at the dispenser when it detects a leak.

(2) Within 6 months of the effective date of this paragraph, automatic line leak detectors shall be installed on underground pressurized piping, and shall be capable of detecting a 3-gallon per hour leak rate at 10 psi within 1 hour with a probability of detection of at least 95 percent and a probability of false alarm no greater than 5 percent, and shall restrict or shut off the flow of product through the piping when a leak is detected.

(3) For emergency generator tank systems, Oother monitoring methods may be used in lieu of the requirement in subdivision (2) if it is demonstrated to the satisfaction of the local agency that the alternate method is as effective as the methods otherwise required by this section.  For emergency generator tank systems, continuous monitoring systems as described in subdivision (1), which shut down the pump in addition to either activating activate an audible and visual alarm in the event of a leak or a malfunction of the monitoring system satisfy the automatic line leak detector requirement of subdivision (2), provided that the monitoring system is checked at least daily by either remote electronic access or on-site visual inspections.  A log of daily checks shall be available for local agency review upon request. the audible and visual alarm or stopping the flow of product at the dispenser satisfy the automatic line leak detector requirement of subdivision (2).

(4) Monitoring shall be conducted on all underground pressurized piping with

secondary containment at least annually at a pressure designated by the equipment manufacturer, provided that the method is capable of detecting a minimum release equivalent to 0.1 gallon per hour defined at 150 percent of the normal operating pressure of the product piping system at the test pressure with at least a 95 percent probability of detection and not more than a 5 percent probability of false alarm. This requirement is waived if the criteria in subsection (g) of this section are met.

(5) Continuous monitoring systems as described in subdivision (f)(1) satisfy the annual tightness testing requirement of subdivision (f)(4) if both of the following conditions are met:

(A) The monitoring system shuts down the pump or stops the flow of product at the dispenser when a leak is detected in the under- dispenser containment.

- The monitoring system for all product piping other than that contained in the under-dispenser containment is fail safe, and shuts down the pump when a leak is detected.

(g) Underground pressurized piping which meets all of the following requirements satisfies the annual tightness test requirements specified in subsection (f)(4):

(1) All secondary containment systems are equipped with continuous monitoring systems. The leak detection device may be located at the pump sump for sections of the piping that slope back to this point.

(2) All continuous monitoring systems for the piping are connected to the pumping system.

(3) All continuous monitoring systems for the piping shut down the pump and either

activate an audible and visual alarm or stop the flow of product at the dispenser when

they detect a leak.

(4) The pumping system shuts down automatically if any of the continuous monitoring systems for the piping fail or are disconnected.

(5) The requirements of subdivisions (3) and (4) do not apply to an emergency generator, provided the monitoring system is checked at least daily.

(h)(g) Under-dispenser containment shall be designed, constructed, and installed in accordance with the following:

(1) Owners or Operators of a UST system shall have the system fitted with under-dispenser containment, or an approved under-dispenser spill containment or control system according to the following schedule:

(A) At the time of installation for systems installed after January 1, 2000.

(B) By July 1, 2001, for systems installed after July 1, 1987 that are located within 1,000 feet of a public drinking water well, as identified pursuant to the state Geographic Information System mapping database.

(C) By December 31, 2003, for systems not subject to subsection 2636(h)(g) (1)(A) or (B).

(2) Under-dispenser containment shall be designed, constructed, installed, and monitored in accordance with section 2631, 2636(c)(2), 2636(e), and 2636(f).

(3) A manufacturer of an under-dispenser spill containment or control system may apply to the Division of Clean Water ProgramsWater Quality Underground Storage Tank Program Manager for approval of the system. Owners or operators shall not install an under-dispenser spill containment or control system that has not been approved.

- Applications for approval shall be submitted in writing and include the  following:

(i) A description of the proposed system.

(ii) Clear and convincing evidence that the system will protect the soil and beneficial uses of the waters of the state from unauthorized releases.

(B) The Program Manager shall review the application to determine if the proposed system adequately protects the soil and beneficial uses of groundwater before determining whether to approve the proposed system.

(C) The Program Manager may modify or revoke a previously issued approval if it finds that, based on new evidence, the approved system does not adequately protect the soil and beneficial uses of groundwater from unauthorized releases.

Authority: Sections 25299.3 and 25299.7, Health and Safety Code.

Reference: Sections 25281, 25284.1 25291 and 25299, Health and Safety Code; and 40 CFR 280.20 and  280.40-280.45.

§ 2636.1.  Final Division Decisions Regarding Under-Dispenser Containment or Control Systems.

(a) A manufacturer of an under-dispenser spill containment or control system who disagrees with a determination by the Program Manager not to approve the manufacturer's system under section 2636(h)(g)(3)(B) or to modify or revoke a previously issued approval of the manufacturer's system under section 2636(h)(g)(3)(C) may ask for review by the Division Chief.

•••

Authority: Sections 25299.3 and 25299.7, Health and Safety Code.

Reference: Section 25284.1, Health and Safety Code.

§ 2637.  Secondary Containment Testing. and Annual Maintenance Certification.

- Secondary containment systems installed on or after January 1, 2001 shall be tested upon installation, 6 months after installation, and every 36 months thereafter. Secondary containment systems installed prior to January 1, 2001 shall be tested by January 1, 2003 and every 36 months thereafter. Secondary containment testing shall be conducted as follows:

- (b) By December 31, 2002, the owner or operator of any secondary containment system that the owner or operator determines cannot be tested in accordance with this section shall replace the secondary containment system with a system that can be tested in accordance with this section. As an alternative, the owner or operator may submit a proposal and workplan for enhanced leak detection to the local agency in accordance with subdivisions 2644.1 (a)(1), (2), (4), and (5) by July 1, 2002; complete the program of enhanced leak detection by December 31, 2002; and replace the secondary containment system with a system that can be tested in accordance with this section by July 1, 2005. The local agency shall review the proposed program of enhanced leak detection within 45 days of submittal or re-submittal.

- (c) Periodic testing of secondary containment systems shall be conducted using a test procedure that demonstrates that the system performs at least as well as it did upon installation. For example, if the secondary containment system was tested upon installation by using a test method that applied a pressure of 5 psi, then the periodic test must be conducted using a method that tests the system at an equivalent pressure. These tests shall be performed in accordance with manufacturer’s guidelines or standards. If there are no manufacturer’s guidelines or standards, secondary containment systems must be tested using an applicable method specified in an industry code or engineering standard. If there are no applicable manufacturer’s guidelines, industry codes, or engineering standards a test method approved by a state registered professional engineer shall be used.

- (d) Secondary containment testing shall be performed by either a service technician or a licensed tank tester, both of which must meet the requirements of section 2715, subdivision (i). licensed tank tester, licensed tank installer, or any person meeting the requirements of subsection 2637(b)(1).

- (e) Underground storage tank owners and operators shall submit a copy of the test report to the local agency within 30 days of the completion of the test.

- (f) Owners and operators of underground storage tanks must notify the local agency at least 48 hours prior to conducting the test, unless this notification requirement is waived by the local agency.

- (g) Secondary containment systems where the continuous monitoring automatically monitors both primary and secondary containment, such as systems that are hydrostatically monitored or under constant vacuum, are exempt from periodic secondary containment testing.

Authority: Sections 25299.3 and 25299.7, Health and Safety Code.

Reference: Sections 25281, 25284.1, 25291 and 25292, Health and Safety Code; 40 CFR 280.41.

(b)

§ 2638. Annual Certification of Monitoring Equipment.

- All monitoring equipment used to satisfy the requirements of this article shall be installed, calibrated, operated and maintained in accordance with manufacturer’s instructions, and certified every 12 months for operability, proper operating condition, and proper calibration. Written records shall be maintained as required in section 2712. On or after January 1, 2002 the following shall also apply:

(1) (b) Persons performing installation, repair, maintenance, calibration, or annual certification of monitoring equipment shall meet the following requirements: set forth in section 2715, subdivision (i).

(A) Possess a current Class “A” General Engineering Contractor License,  C-10 Electrical Contractor License, C-34 Pipeline Contractor License,  C-36 Plumbing Contractor License, or C-61 (D40) Limited Specialty Service Station Equipment and Maintenance Contractor License issued by the Contractors State License Board.

(B) Be trained and certified by the manufacturer of the monitoring equipment; and,

(C) Be re-certified by the manufacturer by completion of a manufacturer’s refresher course. Additionally, this certification shall be renewed at the time interval recommended by the manufacturer, or every 36 months, whichever is shorter.

(2) Individuals employed by persons performing installation, repair, maintenance, calibration, or annual certification of monitoring equipment for the purpose of conducting this work shall meet the requirements of 2637(b)(1)(B) and (C).

(3) (c) Annual monitoring equipment certification shall be made on a “Monitoring System Certification” form (see Appendix VI).

(4) (d) UST owners and operators shall submit a completed “Monitoring System Certification” form to the local agency within 30 days after completion of the inspection.

(5) (e) The UST owner or operator shall notify the local agency at least 48 hours prior to conducting the installation, repair, replacement, calibration, or certification of monitoring equipment unless the notification requirement is waived by the local agency.

(6) (f) A person conducting UST monitoring equipment certification shall affix a tag/sticker on each monitoring equipment component that is being certified, repaired, or replaced. The tag/sticker shall be placed in a readily visible location and shall include the date the UST component was certified, repaired, or replaced, and the contractor’s license number.

Authority: Sections 25299.3 and 25299.7, Health and Safety Code.

Reference: Sections 25281, 25284.1, 25291 and 25292, Health and Safety Code; 40 CFR 280.41.

§ 2641. Monitoring Program Requirements.

•••

(j) Equipment and devices used to monitor underground storage tanks shall be installed, calibrated, operated, and maintained in accordance with section 2637(b)2638.

•••

Authority: Sections 25299.3 and 25299.7, Health and Safety Code.

Reference: Sections 25283, 25284.1, 25291 and 25292, Health and Safety Code; 40 CFR 280.40 and 280.41.

§ 2712. Permit Conditions.

•••

(e)   The local agency shall not renew an underground storage tank permit unless the underground storage tank has been inspected by the local agency or a special inspector within the previous 12 months and the inspection verified that the underground storage tank complied with the provisions of Article 3 or 4, as applicable, and with all existing permit conditions.  The inspection shall be conducted as specified in section 25288 the appropriate subsection of Chapter 6.7 of Division 20 of the Health and Safety Code.  If the inspection indicates noncompliance, the local agency shall verify by a follow-up inspection that all required corrections have been implemented before renewing the permit.

•••

Authority:	Health and Safety Code 25299.3, 25299.7

Reference:	Sections 25284, 25285, 25286, 25288, 25289, 25293, and 25294, Health and Safety Code; 40 CFR 280.31(d), 280.33(f), 280.45, and 281.32(e)

§ 2715. Certification, Licensing, and Training Requirements for Underground Storage Tank Owners, Operators, Installers, Service Technicians, and Inspectors.

- By January 1, 2005, owners of underground storage tank systems shall submit a signed statement to the local agency indicating that the owner understands and is in compliance with all applicable underground storage tank requirements, and identifying the designated UST operator(s) for each facility owned. The owner shall inform the local agency of any change of designated UST operator(s) no later than 30 days after the change.

- Effective January 1, 2005, designated UST operators shal possess a current certificate issued by the International Code Council (ICC) indicating he or she has passed the California UST System Operator exam.  The individual shall renew the ICC certification, by passing the California UST System Operator exam, every 24 months.

(c) The designated UST operator(s) shall perform monthly visual inspections of all underground storage tank systems for which they are designated.  The results of each inspection shall be recorded in a monthly inspection report.  The monthly visual inspection shall include, but is not limited to, the following:

(1) Reviewing the alarm history report or log for the previous month, and checking that each alarm condition was documented and responded to appropriately.  A copy of the alarm history report or log, along with documentation describing action taken in response to any alarm(s), shall be attached to the monthly visual inspection record.

- Inspecting for the presence of hazardous substance, water, or debris in spill containers.

- Inspecting for the presence of hazardous substance, water, or debris in under-dispenser containment areas, and checking that the monitoring equipment in these areas is located in the proper position to detect a leak at the earliest possible opportunity.

- Inspecting for the presence of hazardous substance, water, or debris in containment sumps that, in the past month, have had an alarm for which there is no record of a service visit, and checking that the monitoring equipment in these containment sumps is located in the proper position to detect a leak at the earliest possible opportunity.

- Checking that all required testing and maintenance for the underground storage tank system have been completed, and documenting the dates these activities occurred.

(6) Verifying that all facility employees have been trained in accordance with subdivision 2715(f).

(d) The designated UST operator(s) shall provide the owner or operator with a copy of each monthly inspection report, and alert the owner or operator of any condition discovered during the monthly visual inspection that may require follow-up actions.

(e) The owner or operator shall maintain a copy of the monthly inspection record and all attachments for the previous twelve months.  The records shall be maintained on-site or, if approved by the local agency, off-site at a readily available location.

(f) By July 1, 2005, and annually thereafter, the designated UST operator(s) shall train facility employees for which he or she is responsible in the proper operation and maintenance of the underground storage tank system.  For facility employees hired on or after July 1, 2005, the initial training shall be conducted within 30 days of the date of hire.

- The training for facility employees must include, but is not limited to:

- The operation of the underground storage tank system in a manner consistent with the facility’s best management practices.

- The facility employee’s role with regard to the monitoring equipment as specified in the facility’s monitoring plan.

- The facility employee’s role with regard to spills and overfills as specified in the facility’s response plan.

- The name of the contact person(s) for emergencies and monitoring equipment alarms.

- At least one of the facility employees present during operating hours shall have current training in accordance with subdivision (f)(1).  For facilities that are not routinely staffed, the designated UST operator shall implement a facility employee training program approved by the  local agency.

- A list of facility employees who have been trained by the designated UST operator(s), shall be maintained on-site or off-site at a readily available location, if approved by the local agency.  The list shall be provided to the local agency upon request.  The list shall include the dates of training for all facility employees, and the hiring dates for all facility employees hired on or after July 1, 2005.

(g) Any person(s) installing underground storage tank systems or components shall be certified or licensed by the Contractors State License Board.

(h) Any individual(s) installing underground storage tank system components shall meet the following requirements, or work under the direct and personal supervision of an individual physically present at the work site who meets the following requirements:

- The individual has been adequately trained as evidenced by a certificate of training issued by the manufacturer(s) of the underground storage tank system components.  On and after July 1, 2001, this certification shall be renewed by completion of manufacturer’s refresher training at the time interval recommended by the manufacturer, or every 36 months, whichever is shorter.

- Effective January 1, 2005, the individual shall possess a current underground storage tank system installer certificate from the International Code Council (ICC), indicating that the individual has passed the ICC UST Installation/Retrofitting exam. The individual shall renew the ICC certification, by passing the ICC UST Installation/Retrofitting exam, every 24 months.

(i) Any individual performing the work of a service technician must meet all of the following requirements:

(1) Possess or be employed by a person who possesses a current Class “A” General Engineering Contractor License, C-10 Electrical Contractor License, C-34 Pipeline Contractor License, C-36 Plumbing Contractor License, or a C-61 (D40) Limited Specialty Service Station Equipment and Maintenance Contractor License issued by the Contractors State License Board, as applicable.  Individuals who possess a tank testing license issued by the State Water Resources Control Board satisfy the licensing requirement of this paragraph.

(2) Be trained and certified by the manufacturer of the equipment as follows:

- For service technicians conducting secondary containment testing pursuant to section 2637(a), this training and certification may be obtained through the developer of the testing equipment or test method being used, or through the manufacturer of the secondary containment system being tested, as applicable.

- For service technicians performing work on monitoring equipment, training and certification shall be obtained from the manufacturer of the monitoring equipment.

- In the event that no training or certification exists that would satisfy the criteria of subparagraph (i)(2)(A) or (B), the local agency may approve comparable alternate training or certification.

(3) Renew all training and certifications issued by the manufacturer, through completion of a manufacturer’s refresher course, at the time interval recommended by the manufacturer, or every 36 months, whichever is shorter.

(4) Effective July 1, 2005, service technicians shall possess or work under the direct and personal supervision of an individual physically present at the work site who possesses a current certificate from the International Code Council (ICC), indicating he or she has passed the California UST Service Technician exam. If the California UST Service Technician exam is not available by July 1, 2004, this requirement shall be effective twelve months after the date the exam is available.  The individual shall renew the ICC certification, by passing the California UST Service Technician exam, every 24 months.

(j) 	Local agency inspectors or special inspectors conducting underground storage tank inspections must meet the following requirements:

(1) Effective September 1, 2005, these individuals shall possess a current inspector certificate issued by the International Code Council (ICC), indicating he or she has passed the ICC California UST Inspector exam.  Local agency inspectors hired on or after September 1, 2005, are subject to this requirement 180 days from the date of hire.  If the ICC California UST Inspector exam is not available by September 1, 2004, this requirement shall be effective twelve months after the date the exam is available.

(2)These individuals shall renew the California inspector certificate every 24 months, by either passing the ICC California UST Inspector exam or satisfying equivalent criteria as approved by the Division of Water Quality Underground Storage Tank Program Manager.

Authority: Section 25299.3, Health and Safety Code.

Reference: Section 25281, 25284.1, Health and Safety Code: 40 CFR 280.20.