## Source A (sample)
State of California -- Health and Human Services Agency | [10 empty] | California Department of Public Health
Drinking Water Program
MONTHLY FLUORIDATION OPERATIONS REPORT
TREATMENT SYSTEM OPERATIONS
(Single treated source)
| System Name: |  | ABC WD | [5 empty] | System Number: | 1910345
| Plant Name/ID: |  | Source A | [5 empty] | Month/Year: | 2011-01-01
| Contact Person: |  | John Doe | [5 empty] | Telephone No: | 916-555-1212
Day | Date | Water Production (MG) (a) | Chemical Usage (lbs) | Fluoride Used (lbs Fl) | Calculated Fluoride Dose (mg/L) | Chemical Data:
Fluoride Chemical Used (check one):
Sodium Fluoride
Sat | 1 | 2 | 42.7 | 18.3354 | 1.0992 |  | Sodium Silicofluoride
Sun | 2 | 2.1 | 42.7 | 18.3354 | 1.0469 |  | Hydrofluosilicic Acid
Mon | 3 | 2 | 42.7 | 18.3354 | 1.0992 |  | Other
Tue | 4 | 0.88 | 15.5 | 6.6557 | 0.90687
Wed | 5 | 1.5 | 15.5 | 6.6557 | 0.53203 |  | Purity (%) |  | 95
Thu | 6 | 1.03 | 15.5 | 6.6557 | 0.7748 |  | Available Fl Ion (AFI) |  | 0.452
Fri | 7 | 0.808 | 15.5 | 6.6557 | 0.98768
Sat | 8 | 0.586 | 10.1 | 4.3369 | 0.8874 | Testing and Monitoring:
Sun | 9 | 2.1 | 22.1 | 9.4897 | 0.54184 | Instrument (Make/model) |  |  | Hach Pocket Colorimeter
Mon | 10 | 2 | 21.1 | 9.0603 | 0.54319 | Analytical test method |  |  | SPADNS
Tue | 11 | 0.88 | 15.5 | 6.6557 | 0.90687 | Instrument Calibration:
Wed | 12 | 1.5 | 15.5 | 6.6557 | 0.53203 |  | Date | Instrument ID
Thu | 13 | 1.03 | 15.5 | 6.6557 | 0.7748 |  | 2011-01-03 | Hach Pocket Colorimeter-Larry H's
Fri | 14 | 0.808 | 15.5 | 6.6557 | 0.98768 |  | 2011-01-16 | Hach Pocket Colorimeter-Bill W's
Sat | 15 | 0.586 | 12.6 | 5.4104 | 1.1071
Sun | 16
Mon | 17 | 2.1 | 30 | 12.882 | 0.73553 | Optimal Fluoride Level (mg/L) (b) |  |  |  | 0.8
Tue | 18 | 2 | 30 | 12.882 | 0.7723 | Fluoride Control Range (mg/L) (b) |  |  | Low | 0.7
Wed | 19 | 0.88 | 15.2 | 6.5269 | 0.88932 | Fluoride Control Range (mg/L) (b) |  |  | High | 1.3
Thu | 20 | 1.5 | 30 | 12.882 | 1.0297 | Last raw water Fluoride level (mg/L)(c) |  |  |  | 0.2
Fri | 21 | 1.03 | 15.3 | 6.5698 | 0.7648 | Last raw water Fluoride sample date |  |  |  | 2006-03-15
Sat | 22 | 0.808 | 14.8 | 6.3551 | 0.94308 | Fluoride Dose Range (mg/L) (d) |  |  | Low | 0.5
Sun | 23 | 0.586 | 10.2 | 4.3799 | 0.89619 | Fluoride Dose Range (mg/L) (d) |  |  | High | 1.1
Mon | 24 | 2.1 | 30 | 12.882 | 0.73553 | (b)…..Level and range to be determined from annual average maximum air temperatures of past five years and temperature value, submitted to the CDPH annually. (Section 64433.2,T22,CCR)
Tue | 25 | 2 | 30 | 12.882 | 0.7723
Wed | 26 | 0.88 | 11.3 | 4.8522 | 0.66114 | (c)…..If value is "ND", use 1/2 of the detection level.
Thu | 27 | 1.5 | 30 | 12.882 | 1.0297 | (d)…..Dose Range is the Control Range value minus the raw water fluoride level.
Fri | 28 | 1.03 | 18.2 | 7.8151 | 0.90977 | Interuptions (date/time). [Add additional interuptions to back of page if needed]
Sat | 29 | 0.808 | 11.2 | 4.8093 | 0.71368 | Start | None |  | End
Sun | 30 | 0.586 | 9.8 | 4.2081 | 0.86104
Mon | 31
Totals |  | 37.616 | 604 | 259.3576 |  | Explain cause and corrective actions taken on back of page.
Min |  |  |  |  | 0.53203
Max |  |  |  |  | 1.1071 | Was CDPH notified of all overfeedings >10.0 mg/L?
Ave |  |  |  |  | 0.84282 |  | (Section 64433.7(d),T22,CCR) |  |  | (Y/N/NA) | NA
Count-Total |  |  |  |  | 29 | Were all interuption notification requirements taken?
Count within range |  |  |  |  | 28 |  | (Section 64433.7(c),T22,CCR) |  |  | (Y/N/NA) | NA
Within range % |  |  |  |  | 96.55% | Were fluoride levels in control range 95% of the time?
(a)…..Leave blank when not fluoridating | [6 empty] | (Section 64433.5(c),T22,CCR) |  |  | (Y/N/NA) | Y
NA…..Not Applicable
Certified Treatment Operator signature |  |  |  |  | John Doe |  |  | Date | 2011-02-02
To be received by CDPH District Office by 10th day of following month
Revised 7/11
State of California -- Health and Human Services Agency | [10 empty] | California Department of Public Health
Drinking Water Program
MONTHLY FLUORIDATION OPERATIONS REPORT
TREATMENT SYSTEM OPERATIONS
Explain cause and corrective actions taken for each interuption. (Section 64433.7(a)(2),T22,CCR)
[Only add this page to the report if interuptions occurred during the month. Add additional pages if needed]
Certified Treatment Operator signature | [7 empty] | Date
Note on A13: Column is frozen. Column auto fill when "Month/Year" is filled in
Note on B13: Column is frozen
Note on C47: Cell is frozen.
Note on D47: Cell is frozen.
Note on E13: Column is frozen. Equation uses input from "Purity%", "AFI", and "Chemical Usage".
Note on E47: Cell is frozen.
Note on F13: Colum is frozen. Equation uses input from "Fluoride used" and "Water Production".
Note on F48: Cell is frozen.
Note on F49: Cell is frozen.
Note on F50: Cell is frozen.
Note on F51: Cell is frozen.
Note on F52: Cell is frozen.
Note on F53: Cell is frozen.
Note on I27: Type in using the following format: MM/DD/YY
Note on I44: Type in using the following format: mm/dd/yy hh:mm
Note on L9: Type in the following format: MM/01/YY
Note on L36: Type in using the following format: MM/DD/YY
Note on L44: Type in using the following format: mm/dd/yy hh:mm

## Source A (blank)
State of California -- Health and Human Services Agency | [10 empty] | California Department of Public Health
Drinking Water Program
MONTHLY FLUORIDATION OPERATIONS REPORT
TREATMENT SYSTEM OPERATIONS
(Single treated source)
| System Name: | [7 empty] | System Number:
| Plant Name/ID: | [7 empty] | Month/Year:
| Contact Person: | [7 empty] | Telephone No:
Day | Date | Water Production (MG) (a) | Chemical Usage (lbs) | Fluoride Used (lbs Fl) | Calculated Fluoride Dose (mg/L) | Chemical Data:
Fluoride Chemical Used (check one):
Sodium Fluoride
| 1 | [5 empty] | Sodium Silicofluoride
| 2 | [5 empty] | Hydrofluosilicic Acid
| 3 | [5 empty] | Other
4
| 5 | [5 empty] | Purity (%)
| 6 | [5 empty] | Available Fl Ion (AFI)
7
| 8 |  |  |  |  | Testing and Monitoring:
| 9 |  |  |  |  | Instrument (Make/model)
| 10 |  |  |  |  | Analytical test method
| 11 |  |  |  |  | Instrument Calibration:
| 12 | [5 empty] | Date | Instrument ID
13
14
15
16
| 17 |  |  |  |  | Optimal Fluoride Level (mg/L) (b)
| 18 |  |  |  |  | Fluoride Control Range (mg/L) (b) |  |  | Low
| 19 |  |  |  |  | Fluoride Control Range (mg/L) (b) |  |  | High
| 20 |  |  |  |  | Last raw water Fluoride level (mg/L)(c)
| 21 |  |  |  |  | Last raw water Fluoride sample date
| 22 |  |  |  |  | Fluoride Dose Range (mg/L) (d) |  |  | Low
| 23 |  |  |  |  | Fluoride Dose Range (mg/L) (d) |  |  | High
| 24 |  |  |  |  | (b)…..Level and range to be determined from annual average maximum air temperatures of past five years and temperature value, submitted to the CDPH annually. (Section 64433.2,T22,CCR)
25
| 26 |  |  |  |  | (c)…..If value is "ND", use 1/2 of the detection level.
| 27 |  |  |  |  | (d)…..Dose Range is the Control Range value minus the raw water fluoride level.
| 28 |  |  |  |  | Interuptions (date/time). [Add additional interuptions to back of page if needed]
| 29 |  |  |  |  | Start |  |  | End
30
31
Totals | [5 empty] | Explain cause and corrective actions taken on back of page.
Min
Max | [5 empty] | Was CDPH notified of all overfeedings >10.0 mg/L?
Ave | [6 empty] | (Section 64433.7(d),T22,CCR) |  |  | (Y/N/NA)
Count-Total | [5 empty] | Were all interuption notification requirements taken?
Count within range | [6 empty] | (Section 64433.7(c),T22,CCR) |  |  | (Y/N/NA)
Within range % | [5 empty] | Were fluoride levels in control range 95% of the time?
(a)…..Leave blank when not fluoridating | [6 empty] | (Section 64433.5(c),T22,CCR) |  |  | (Y/N/NA)
na…..Not Applicable
Certified Treatment Operator signature | [7 empty] | Date
To be received by CDPH District Office by 10th day of following month
Revised 7/11
State of California -- Health and Human Services Agency | [10 empty] | California Department of Public Health
Drinking Water Program
MONTHLY FLUORIDATION OPERATIONS REPORT
TREATMENT SYSTEM OPERATIONS
Explain cause and corrective actions taken for each interuption. (Section 64433.7(a)(2),T22,CCR)
[Only add this page to the report if interuptions occurred during the month. Add additional pages if needed]
Certified Treatment Operator signature | [7 empty] | Date
Note on A13: Column is frozen. Column auto fill when "Month/Year" is filled in
Note on B13: Column is frozen
Note on C47: Cell is frozen.
Note on D47: Cell is frozen.
Note on E13: Column is frozen. Equation uses input from "Purity%", "AFI", and "Chemical Usage".
Note on E47: Cell is frozen.
Note on F13: Colum is frozen. Equation uses input from "Fluoride used" and "Water Production".
Note on F48: Cell is frozen.
Note on F49: Cell is frozen.
Note on F50: Cell is frozen.
Note on F51: Cell is frozen.
Note on F52: Cell is frozen.
Note on F53: Cell is frozen.
Note on I27: Type in using the following format: MM/DD/YY
Note on I44: Type in using the following format: mm/dd/yy hh:mm
Note on L9: Type in the following format: MM/01/YY
Note on L36: Type in using the following format: MM/DD/YY
Note on L44: Type in using the following format: mm/dd/yy hh:mm