## Instructions
FLUORIDATION TREATMENT MONTHLY REPORT FORM
FOR SATURATORS
1) The "Treatment System Operations Monthly Fluoridation Report" form is to be used for each fluoridation treatment facility.
2) This particular form is to be used for Sodium Fluoride Saturators only.
3) Cells highlighted in light blue are for data entry. All other cells are locked to prevent erroneous reporting.
4) Reporting of treatment operations for saturators are a special case when determining chemical usage for the calculation of fluoride dose because the saturated sodium fluoride solution is nearly always a 4% solution.
5) Begin by completing the heading. Note that the "Days" of the week are added to the table when the "Month/Year" is filled in.
6) Next, complete the right side of the form, except the last three questions at the bottom. Below are some comments to particular entries:
Purity (%): The purity of sodium fluoride is obtained from the chemical distributor and can vary from shipment to shipment. Purity is typically 96.0 to 98.0 %. Note that only chemicals (including sodium fluoride), tested and certified as meeting the NSF/ANSI 60 Standard, are allowed as drinking water additives.
Available Fluoride Ion (AFI): The AFI is the fraction of the molecular weight of the fluoride ion (19) to the molecular weight of NaF (42), or 19/42, or 0.452.
NaF Solution Saturation (%): A sodium fluoride saturator is unique in that the solution is nearly always 4%. This is due to the fact that sodium fluoride has a solubility which is nearly constant. For a saturator solution temperature of 0 to 20 degrees Celsius, the saturation varies from 4.0 to 4.05%.
7) Next add the values "Water Production (MG)" and "Water Added to Saturator (gals)" in the table for the corresponding days of the month.
8) Answer the three questions.
9) Sign, date, and submit the completed form to the CDPH District Office by the 10th day of the following month. The signature must be by a Certified Treatment Operation.
Explanations and examples of the equations used to determine the "Fluoride Used" and the "Calculated Fluoride Dose" are listed below:
Sodium Fluoride with saturators-
Chemical used (lbs/d) = vol of makeup water (gpd) x 8.34 (lbs/gal) x 0.04 (lbs NaF/lbs makeup water) x 1/purity of NaF chem.
Fluoride used (lbs/d) = Chemical used (lbs/d) x AFI.
Example:
Makeup water = 86.7 gal
Soln. Saturation % = 4.0%
Purity of NaF = 97%
Available Fluoride Ion (AFI) = 0.452
Chemical usage = 86.7 x 8.34 x 0.04 x 1/0.97
= 86.7 x 0.3336 x 1/0.97
= 86.7 x 0.3439
= 29.82 lbs/d
Fluoride usage = 29.82 x 0.452
= 13.48 lbs/d

## Source A (sample)
State of California -- Health and Human Services Agency | [10 empty] | California Department of Public Health
Drinking Water Program
MONTHLY FLUORIDATION OPERATIONS REPORT
TREATMENT SYSTEM OPERATIONS
(Saturators Only - Single treated source)
| System Name: |  | ABC Water District | [5 empty] | System Number: | 1910366
| Plant Name/ID: |  | Well #6 | [5 empty] | Month/Year: | 2011-01-01
| Contact Person: |  | John Doe | [5 empty] | Telephone No: | 916-555-1212
Day | Date | Water Production (MG) (a) | Water Added to Saturator (gals) | Fluoride Used (lbs Fl) | Calculated Fluoride Dose (mg/L) | Chemical Data:
Fluoride Chemical Used (check one):
Sodium Fluoride
Sat | 1 | 2 | 100 | 15.4214 | 0.92455 |  | Other
Sun | 2 | 2.1 | 110 | 16.9636 | 0.96857
Mon | 3 | 2 | 85 | 13.1082 | 0.78586 |  | Purity (%) |  | 99
Tue | 4 | 0.88 | 45.0689 | 6.9503 | 0.94701 |  | Available Fl Ion (AFI) |  | 0.452
Wed | 5 | 1.5 | 45.0689 | 6.9503 | 0.55558 |  | NaF Solution Saturation (%) |  |  | 4.05
Thu | 6 | 1.03 | 45.0689 | 6.9503 | 0.80909
Fri | 7 | 0.808 | 45.0689 | 6.9503 | 1.0314
Sat | 8 | 0.586 | 29.3675 | 4.5289 | 0.92668 | Testing and Monitoring:
Sun | 9 | 2.1 | 100 | 15.4214 | 0.88052 | Instrument (Make/model) |  |  | Hach/pocket colorimeter
Mon | 10 | 2 | 95 | 14.6503 | 0.87832 | Analytical test method |  |  | SPADNS
Tue | 11 | 0.88 | 45.0689 | 6.9503 | 0.94701 | Instrument Calibration:
Wed | 12 | 1.5 | 45.0689 | 6.9503 | 0.55558 |  | Date | Instrument ID
Thu | 13 | 1.03 | 45.0689 | 6.9503 | 0.80909 |  | 2011-01-03 | Hach pocket colorimeter-Bill W's
Fri | 14 | 0.808 | 45.0689 | 6.9503 | 1.0314 |  | 2011-01-16 | Hach pocket colorimeter-Harry O's
Sat | 15 | 0.586 | 36.6367 | 5.6499 | 1.1561
Sun | 16
Mon | 17 | 2.1 | 87.2302 | 13.4521 | 0.76808 | Optimal Fluoride Level (mg/L) (b) |  |  |  | 0.8
Tue | 18 | 2 | 87.2302 | 13.4521 | 0.80648 | Fluoride Control Range (mg/L) (b) |  |  | Low | 0.7
Wed | 19 | 0.88 | 44.1966 | 6.8157 | 0.92868 | Fluoride Control Range (mg/L) (b) |  |  | High | 1.3
Thu | 20 | 1.5 | 87.2302 | 13.4521 | 1.0753 | Last raw water Fluoride level (mg/L)(c) |  |  |  | 0.2
Fri | 21 | 1.03 | 44.4874 | 6.8606 | 0.79865 | Last raw water Fluoride sample date
Sat | 22 | 0.808 | 43.0336 | 6.6364 | 0.98481 | Fluoride Dose Range (mg/L) (d) |  |  | Low | 0.5
Sun | 23 | 0.586 | 29.6583 | 4.5737 | 0.93585 | Fluoride Dose Range (mg/L) (d) |  |  | High | 1.1
Mon | 24 | 2.1 | 87.2302 | 13.4521 | 0.76808 | (b)…..Level and range to be determined from annual average maximum air temperatures of past five years and temperature value, submitted to the CDPH annually. (Section 64433.2,T22,CCR)
Tue | 25 | 2 | 87.2302 | 13.4521 | 0.80648
Wed | 26 | 0.88 | 45 | 6.9396 | 0.94556 | (c)…..If value is "ND", use 1/2 of the detection level.
Thu | 27 | 1.5 | 87.2302 | 13.4521 | 1.0753 | (d)…..Dose Range is the Control Range value minus the raw water fluoride level.
Fri | 28 | 1.03 | 52.9197 | 8.161 | 0.95003 | Interuptions (date/time). [Add additional interuptions to back of page if needed]
Sat | 29 | 0.808 | 32.5659 | 5.0221 | 0.74526 | Start |  |  | End
Sun | 30 | 0.586 | 28.4952 | 4.3944 | 0.89915
Mon | 31
Totals |  | 37.616 | 1760.2938 | 271.4623 | -- | Explain cause and corrective actions taken on back of page.
Min |  | -- | -- | -- | 0.55558
Max |  | -- | -- | -- | 1.1561 | Was CDPH notified of all overfeedings >10.0 mg/L?
Ave |  | -- | -- | -- | 0.88601 |  | (Section 64433.7(d),T22,CCR) |  |  | (Y/N/NA) | NA
Count-Total |  | -- | -- | -- | 29 | Were all interuption notification requirements taken?
Count within range |  | -- | -- | -- | 28 |  | (Section 64433.7(c),T22,CCR) |  |  | (Y/N/NA) | NA
Within range % |  | -- | -- | -- | 96.55% | Were fluoride levels in control range 95% of the time?
(a)…..Leave blank when not fluoridating | [6 empty] | (Section 64433.5(c),T22,CCR) |  |  | (Y/N/NA) | Y
NA…..Not Applicable
Certified Treatment Operator signature |  |  |  | John Doe |  |  |  | Date | 2011-02-02
To be received by CDPH District Office by 10th day of following month
Rev 7/11
State of California -- Health and Human Services Agency | [10 empty] | California Department of Public Health
Drinking Water Program
MONTHLY FLUORIDATION OPERATIONS REPORT
TREATMENT SYSTEM OPERATIONS
Explain cause and corrective actions taken for each interuption. (Section 64433.7(a)(2),T22,CCR)
[Only add this page to the report if interuptions occurred during the month. Add additional pages if needed]
Certified Treatment Operator signature | [7 empty] | Date
Note on A11: Column is frozen. Column auto fill when "Month/Year" is filled in
Note on B11: Column is frozen
Note on C45: Cell is frozen.
Note on D45: Cell is frozen.
Note on E11: Column is frozen. Equation uses input from: "Purity%", "AFI", "NaF Solution Saturation%", and "Water added to Saturator".
Note on E45: Cell is frozen.
Note on F11: Colum is frozen. Equation uses input from "Fluoride used" and "Water Production".
Note on F46: Cell is frozen.
Note on F47: Cell is frozen.
Note on F48: Cell is frozen.
Note on F49: Cell is frozen.
Note on F50: Cell is frozen.
Note on F51: Cell is frozen.
Note on I25: Type in using the following format: MM/DD/YY
Note on I42: Type in using the following format: mm/dd/yy hh:mm
Note on L8: Type in the following format: MM/01/YY
Note on L34: Type in using the following format: MM/DD/YY
Note on L35: Cell is frozen. Equation uses input from "Fluoride Control Range Low" and "Last raw water Fluoride Level".
Note on L36: Cell is frozen. Equation uses input from "Fluoride Control Range High" and "Last raw water Fluoride Level".
Note on L42: Type in using the following format: mm/dd/yy hh:mm

## Source A (blank)
State of California -- Health and Human Services Agency | [10 empty] | California Department of Public Health
Drinking Water Program
MONTHLY FLUORIDATION OPERATIONS REPORT
TREATMENT SYSTEM OPERATIONS
(Saturators Only - Single treated source)
| System Name: | [7 empty] | System Number:
| Plant Name/ID: | [7 empty] | Month/Year:
| Contact Person: | [7 empty] | Telephone No:
Day | Date | Water Production (MG) (a) | Water Added to Saturator (gals) | Fluoride Used (lbs Fl) | Calculated Fluoride Dose (mg/L) | Chemical Data:
Fluoride Chemical Used (check one):
Sodium Fluoride
| 1 | [5 empty] | Other
2
| 3 | [5 empty] | Purity (%)
| 4 | [5 empty] | Available Fl Ion (AFI) |  | 0.452
| 5 | [5 empty] | NaF Solution Saturation (%)
6
7
| 8 |  |  |  |  | Testing and Monitoring:
| 9 |  |  |  |  | Instrument (Make/model)
| 10 |  |  |  |  | Analytical test method
| 11 |  |  |  |  | Instrument Calibration:
| 12 | [5 empty] | Date | Instrument ID
13
14
15
16
| 17 |  |  |  |  | Optimal Fluoride Level (mg/L) (b)
| 18 |  |  |  |  | Fluoride Control Range (mg/L) (b) |  |  | Low
| 19 |  |  |  |  | Fluoride Control Range (mg/L) (b) |  |  | High
| 20 |  |  |  |  | Last raw water Fluoride level (mg/L)(c)
| 21 |  |  |  |  | Last raw water Fluoride sample date
| 22 |  |  |  |  | Fluoride Dose Range (mg/L) (d) |  |  | Low
| 23 |  |  |  |  | Fluoride Dose Range (mg/L) (d) |  |  | High
| 24 |  |  |  |  | (b)…..Level and range to be determined from annual average maximum air temperatures of past five years and temperature value, submitted to the CDPH annually. (Section 64433.2,T22,CCR)
25
| 26 |  |  |  |  | (c)…..If value is "ND", use 1/2 of the detection level.
| 27 |  |  |  |  | (d)…..Dose Range is the Control Range value minus the raw water fluoride level.
| 28 |  |  |  |  | Interuptions (date/time). [Add additional interuptions to back of page if needed]
| 29 |  |  |  |  | Start |  |  | End
30
31
Totals |  |  |  |  | -- | Explain cause and corrective actions taken on back of page.
Min |  | -- | -- | --
Max |  | -- | -- | -- |  | Was CDPH notified of all overfeedings >10.0 mg/L?
Ave |  | -- | -- | -- |  |  | (Section 64433.7(d),T22,CCR) |  |  | (Y/N/NA)
Count-Total |  | -- | -- | -- |  | Were all interuption notification requirements taken?
Count within range |  | -- | -- | -- |  |  | (Section 64433.7(c),T22,CCR) |  |  | (Y/N/NA)
Within range % |  | -- | -- | -- |  | Were fluoride levels in control range 95% of the time?
(a)…..Leave blank when not fluoridating | [6 empty] | (Section 64433.5(c),T22,CCR) |  |  | (Y/N/NA)
NA…..Not Applicable
Certified Treatment Operator signature | [7 empty] | Date
To be received by CDPH District Office by 10th day of following month
Rev 7/11
State of California -- Health and Human Services Agency | [10 empty] | California Department of Public Health
Drinking Water Program
MONTHLY FLUORIDATION OPERATIONS REPORT
TREATMENT SYSTEM OPERATIONS
Explain cause and corrective actions taken for each interuption. (Section 64433.7(a)(2),T22,CCR)
[Only add this page to the report if interuptions occurred during the month. Add additional pages if needed]
Certified Treatment Operator signature | [7 empty] | Date
Note on A11: Column is frozen. Column auto fill when "Month/Year" is filled in
Note on B11: Column is frozen
Note on C45: Cell is frozen.
Note on D45: Cell is frozen.
Note on E11: Column is frozen. Equation uses input from: "Purity%", "AFI", "NaF Solution Saturation%", and "Water added to Saturator".
Note on E45: Cell is frozen.
Note on F11: Colum is frozen. Equation uses input from "Fluoride used" and "Water Production".
Note on F46: Cell is frozen.
Note on F47: Cell is frozen.
Note on F48: Cell is frozen.
Note on F49: Cell is frozen.
Note on F50: Cell is frozen.
Note on F51: Cell is frozen.
Note on I25: Type in using the following format: MM/DD/YY
Note on I42: Type in using the following format: mm/dd/yy hh:mm
Note on L8: Type in the following format: MM/01/YY
Note on L34: Type in using the following format: MM/DD/YY
Note on L35: Cell is frozen. Equation uses input from "Fluoride Control Range Low" and "Last raw water Fluoride Level".
Note on L36: Cell is frozen. Equation uses input from "Fluoride Control Range High" and "Last raw water Fluoride Level".
Note on L42: Type in using the following format: mm/dd/yy hh:mm