Slow-Sand Filter

Daily:

- Check river for clarity.

- Monitoring of water production and running time (zero flow meter).

- Change chart on NTU meter and chlorine analyzer (record results).

- Check chlorine reservoir, fill when ¼ full with water and two (2) gallons of 12% solution (record).

- Check pH and temperature.  Record results (pH never over 7, temp. never under 0.5degrees Celsius).

- Check all instruments for proper function. (Raw speed 53.00; treated 48.00; approximately 68 gpm).

- Check filter cell and well for water level.

Weekly:

- Calibrate pH and temperature meters.

- Check pressure tank.

- Check storage tanks.

- Take raw and filtered water samples to lab.

Monthly:

- Calibrate NTU meters, raw and filtered (1720c).

- Calibrate chlorine analyzer.

- Calibrate Hach 2100p NTU meter.

- Blow out lines to meters.

- Exercise all valves.