FILTRATION

Filtration Rate     (GPM/sq.ft)      = 	Filter Production   (gallons  per  day)     		sq. ft. =  square feet

(Filter area sq. ft.) x  (1,440 min/day)

Loading Rate  (GPM/ sq. ft.)   =     ( Flow Rate, GPM      )

( Filter Area, sq. ft.  )

Daily Filter Production (GPD)   =       (Filter Area, sq. ft. )  x  (GPM/ sq. ft.    x 1,440 min/day)

Backwash Pumping Rate  (GPM)    =   (Filter Area, sq. ft.) x (Backwash Rate, GPM/ sq. ft.)

Backwash Volume (Gallons)      =     (Filter Area, sq. ft. ) x (Backwash Rate, gpm/ sq. ft. )  x  (Time, min).

Backwash Rate, GPM/ sq. ft.      =   ( Backwash Volume,  gallons)

( Filter Area, sq. ft.) x (Time, min)

Rate of Rise (inches per min.)     =    (backwash  rate gpm/sq.ft.)  x  12 inches /ft

7.48 gal/cu.ft.

Unit Filter Run Volume, (UFRV)  =  (gallons produced in a filter run)

(filter area sq. ft.)

SEDIMENTATION

Surface Loading Rate, (GPD/ sq. ft.)    =            (   Total Flow, GPD   )

( Surface Area, sq.ft.)

Detention Time  =    Volume

flow

Detention Time hours = volume (cu ft) x 7.48 gal/cu ft x 24 hr/day

Gal/day

Flow Rate     =	 Volume

Time

Weir Overflow Rate, GPD/L.F.     =       (  Flow, GPD)

( Weir length, ft. )

C• t Calculations

C• t    =  (Chlorine Residual, mg/L)x(Time, minutes)

Time, minutes        =   (                 C• t             )

( Chlorine Residual, mg/L )

Chlorine Residual (mg/L)    =	 (           C• t       )

(  Time, minutes    )

Inactivation Ratio    =      (  Actual System C• t )

(  Table “E” C• t    )

C• t Calculated  =  T10 Value, minutes   x  Chlorine Residual, mg/L

Log Removal    = 1.0  -    % Removal  x  Log key  x  ( -1 )

100

Chemical Dosage Calculations

Note (% purity) and (% commercial purity) used in decimal form

Lbs/day gas feed dry =   MGD  x  (ppm or mg/L)  x 8.34 lbs/gal

Lbs/day =  MGD  x (ppm or mg/L) x  8.34 lbs/gal  
	                  % purity

GPD =  MGD  x  (ppm or mg/L) x  8.34 lbs/gal
		(% purity)  x  lbs/gal

GPD =  	      MGD  x  (ppm or mg/L)  x 8.34 lbs/gal    
 (commercial purity %) x (ion purity %)  x (lbs/gal)

ppm or mg/l =  lbs/day 	          	or 	gallons x % purity x lbs/gal

MGD  x 8.34 lbs/gal		     MG    x     8.34 lbs/gal