#### Units and Conversion Factors

1 cubic foot of water weighs 62.3832 lb

1 gallon of water weighs 8.34 lb

1 liter of water weighs 1,000 gm

1 mg/L = 1 part per million (ppm)

1% = 10,000 ppm

ft2 = square feet and ft3 = cubic feet

1 mile = 5,280 feet (ft)

1 yd3 = 27ft3    and   1 yard = 3 feet

1 acre (a) = 43,560 square feet (ft2)

1 acre foot = 325,829 gallons

1 cubic foot (ft3) = 7.48 gallons (gal)

1 gal = 3.785 liters (L)

1 L = 1,000 milliliters (ml)

1 pound (lb) = 454 grams (gm)

1 lb = 7,000 grains (gr)

1 grain per gallon (gpg) = 17.1 mg/L

1 gm = 1,000 milligrams (mg)

1 day = 24 hr = 1,440 min = 86,400 sec

1,000,000 gal/day ÷ 86,400 sec/day ÷  7.48 gal/cu ft = 1.55 cu ft/sec/MGD

# SOLUTIONS

Lbs/Gal    =  (Solution %)_ x 8. 34 lbs/gal x  Specific Gravity

100

Lbs Chemical   =

Specific Gravity x 8.34 lbs/gallons x Solution(gal)

Specific Gravity   =    Chemical Wt. (lbs/gal)

8. 34 (lbs/gal)

%  of Chemical  	 =    ( Dry Chemical, Lbs)         x     100

in   Solution	     (Dry Wt. Chemical, Lbs) + (Water, Lbs)

GPD    =     (MGD) x  (ppm or mg/L)  x  8.34 lbs/gal

( % purity )  x  Chemical Wt. (lbs/gal)

GPD     =	( Feed, ml/min. x 1,440 min/day )

( 1,000 ml/L x 3.785 L/Gal   )

Two – Normal Equations:

a)      C1V1  =     C2V2          		Q1   =   Q2

V1          V2

b)    C1V1 + C2V2 = C3V3

C = Concentration,    V = Volume,     Q = Flow

## PRESSURE

PSI     =   (  Head, ft.  )  	PSI    =	Head, ft.   x   0. 433 PSI/ft.

2.31ft./psi

lbs  Force    =     (0.785) ( D, ft. )2  x 144 in2/ft2 x PSI.

## SCADA =  4 mA to 20 mA analog signal

( live signal mA  -  4 mA off set )   x  process unit and range

(    16 mA span     )

4 mA = 0        20 mA full -range

PUMPING

1 horsepower (Hp) = 746 watts = 0.746 kw  = 3,960 gal/min/ft

Water Hp     =          ( GPM ) x ( Total Head, ft )

(3,960 gal/min/ft)

Brake Hp     =       ( GPM ) x ( Total Head, ft )

( 3,960 ) x (Pump  % Efficiency )

Motor Hp      =       ( GPM ) x ( Total Head, ft )

( 3,960 ) x Pump  % Eff.  x Motor  % Eff.

“Wire to Water”  Efficiency

=         ( Motor, % Efficiency  x  Pump % Efficiency )

Cost, $   =

( Hp ) x ( 0.746 Kw/Hp ) x ( Operating Hrs. ) x cents/Kw-Hr

## General

($) Cost / day       =       Lbs/day  x  ($) Cost/lb

## Removal, Percent   =	 (In  -  Out )  x  100

## In

Specific Capacity, GPM/ft.      =        Well Yield, GPM

Drawdown, ft.

Gals/Day   =   (Population) x (Gals/Capita/Day)

GPD   =	(Meter Read 2   -   Meter Read 1)

(Number of Days)

Volume, Gals   =    GPM   x   Time, minutes

## VOLUME

## Rectangular Basin        =

## Volume,  gal

## (Length, ft) x (Width, ft) x (Height, ft) x7.48 gal/cu.ft.

## Cylinder , Volume, gal    =                        		             (0.785) x (Dia, ft)2 x (Height, Depth, or Length in ft.) x 7.48 gal/ft3

Time, Hrs.    =          (               Volume,  gallons             )

(Pumping Rate, GPM, x 60 Min/Hr )

Supply, Hrs.=                       Storage Volume, Gals            d

( Flow In, GPM – Flow Out, GPM) x 60 min/hr.)	                				   			        2,000 lbs/Ton				                				    2,000 lbs/Ton

STATE OF CALIFORNIA

DEPARTMENT OF PUBLIC HEALTH

##### DRINKING WATER  OPERATOR CERTIFICATION PROGRAM

## CHLORINATION

## Dosage, mg/l   =   (Demand, mg/l) + (Residual, mg/l)

## (Gas) lbs   =   Vol, MG  x  ppm or mg/L  x  8.34 lbs/gal

## HTH Solid (lbs)        = 				  (Vol, MG) x (ppm or mg/L) x 8.34 lbs/gal

## ( % Strength / 100 )

## Liquid (gal)      =  (Vol, MG)  x  (ppm or mg/L) x  8.34 lbs/gal

## ( % Strength /100) x Chemical Wt. (lbs/gal)

### Flow, velocity, area

Q = A x V          Quantity = Area x Velocity

Flow (ft3/sec)  = Area(ft2)   x  Velocity (ft/sec)

MGD x 1.55 cu ft/sec/MGD                  =  cu ft/sec   =  ft/sec

.785 x pipe diameter ft x pipe diameter ft     =       sq ft