## Slide 1: Lazy S Mobile Ranch CA1700609, Lake County, Jar Test
by Guy Schott, P.E. May 5, 2023

## Slide 2: St. Helena Creek/Source

## Slide 3: Lazy S Mobile Ranch Source & Water Characteristics, May 5, 2023
Source – St. Helena Creek
Alkalinity: 96 mg/L as CaCO3
Turbidity: 0.35 NTU
UVT: 93.2%,
UVA: 0.030/cm
0.4 um Filtered
Turbidity: 0.16 NTU
UVT: 93.3%,
UVA: 0.030/cm
Plant Treatment
Settled Water
Turbidity: 1.55 NTU
Post Multi-Media Filter
Alkalinity: 95 mg/L as CaCO3
Turbidity: 0.09 NTU
UVT: 98.4%,
UVA: 0.006/cm
Post Membrane/GAC Filters
Turbidity: 0.04 NTU
UVT: 99.4%,
UVA: 0.002/cm

## Slide 4: Applied Coagulants for Jar Testing (1)
Pro Pac 9800 (NTU Technologies)
50% Aluminum Chlorohydrate
50% Water
23.62% Al2O3
12.5% Al
83% Basicity
SG = 1.25-1.34
NSF limit: 250 mg/L as Product
NTU Technologies
Pro Pac 9810
45-50% Aluminum Chlorohydrate
45-50% Water
~22.4% Al2O3
~11.9% Al
83% Basicity
5% polyamine (50% water, 50% active polyamines)
SG = 1.25-1.34
NSF limit: 200 mg/L as Product;
Product dose 10 mg/L = 0.25 mg/L polyamines active

## Slide 5: Applied Coagulants for Jar Testing (2)
961 (NTU Technologies)
32% Polyaluminum Hydroxychlorosulfate
2% pDADMAC (blend?)
66% Water
SG = 1.2-1.24
NSF limit: 255 mg/L as Product
Product dose 10 mg/L = 0.1-0.2 mg/L pDADMAC

## Slide 6: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (254 nm) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 7: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Aluminum Sulfate doses are reported as hydrated Al2(SO4)3*14.3H20.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 8: Lazy S Mobile Ranch; Jar Test 1 - 8 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 6 | 0.11 | 95.5 | 0.019 | 36.7 | 0.40
J2 | 8 | 0.04 | 98.0 | 0.008 | 73.3 | 0.65
J3 | 12 | 0.04 | 98.2 | 0.007 | 76.7 | 0.70
J4 | 16 | 0.04 | 98.5 | 0.006 | 80.0 | 0.66
J5 | 6 | 0.19 | 96.0 | 0.017 | 43.3 | 0.51
J6 | 8 | 0.19 | 96.4 | 0.015 | 50.0 | 0.62
J7 | 10 | 0.04 | 98.3 | 0.007 | 76.7 | 0.54
J8 | 12 | 0.03 | 98.4 | 0.007 | 76.7 | 0.76

## Slide 9: Lazy S Mobile Ranch; Jar Test 9 - 16 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | 9810 mg/L | 961 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 6 | - | 0.04 | 97.2 | 0.012 | 60.0 | 0.49
J10 | 8 | - | 0.03 | 97.6 | 0.010 | 66.7 | 0.78
J11 | 10 | - | 0.03 | 98.0 | 0.008 | 73.3 | 0.58
J12 | 12 | - | 0.03 | 98.0 | 0.008 | 73.3 | 0.83
J13 | - | 18 | 0.05 | 96.5 | 0.015 | 50.0 | 0.49
J14 | - | 24 | 0.03 | 97.0 | 0.013 | 56.7 | 0.56
J15 | - | 30 | 0.03 | 97.2 | 0.012 | 60.0 | 0.38
J16 | - | 36 | 0.04 | 97.4 | 0.011 | 63.3 | 0.40

## Slide 10: Lazy S Mobile Ranch; Jar Test 17 - 20 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (5 min)
Jar# | 9800 mg/L | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J17 | 10 | - | 0.05 | 98.3 | 0.007 |  | 0.55
J18 | 12 | - | 0.04 | 98.3 | 0.007 |  | 0.96
J19 | - | 10 | 0.10 | 97.5 | 0.010 |  | 0.63
J20 | - | 12 | 0.11 | 97.6 | 0.010 |  | 0.69

## Slide 11: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 20-30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 12: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 13: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 14: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 15: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 16: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Jar Testing Done Right training video: https://www.youtube.com/watch?v=aGByyxhelkI
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732