## Slide 1: Clearlake Oaks CWD CA1710001 Lake County Jar Test
by Guy Schott, P.E.
February 15, 2019

## Slide 2: Lucerne Water Co. Source Water: Clear Lake Conventional Treatment

## Slide 3: Conventional Treatment Plant

## Slide 4: Clearlake Oaks CWD.: Source Water Characteristics February 15, 2019
Source
Post Ozone Sample
Turbidity: 11.8 NTU
pH: 8.1
UVT: 78.9%
UVA: 0.1029/cm
0.4 um Filtered
UVT: 83.7%
UVA: 0.0773/cm

## Slide 5: UVT/UVA
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 6: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 8.1
LCA #1:
ACH (9800): 31.9 mg/L as product
pH adjusted to 7.5 w/acetic acid
LCA #2:
NaOCl added manually: 2.0 mg/L
ACH (9800): 31.9 mg/L as product
pH adjusted to 7.5 w/acetic acid

## Slide 7: Applied Coagulants for Jar Testing
Pro Pac 9800 (NTU Technologies)
50% Aluminum Chlorohydrate
50% Water
SG = 1.34
Pro Pac 9890 (NTU Technologies)
35-45% Aluminum Chlorohydrate
35-45% Water
SG = 1.25-1.34

## Slide 8: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength). Alum Sulfate is reported as Alum.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 9: Clearlake Oaks CWS: Jar Test 1-8 Results Post-Ozone Source Water
Jar | 200 RPM Flash seconds | 30 RPM Floc Mix minutes | NaOCl mg/L | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 25 min
J1 | 60 | 5 | 0 | 20 | 0.09 | 88.3 | 0.0540 | 0.8
J2 | 60 | 5 | 0 | 25 | 0.10 | 88.8 | 0.0516 | 0.8
J3 | 60 | 5 | 0 | 30 | 0.08 | 89.4 | 0.0487 | 1.2
J4 | 60 | 5 | 0 | 35 | 0.08 | 89.7 | 0.0472 | 1.1
J5 | 60 | 5 | 2 | 20 | 0.09 | 88.4 | 0.0535 | 0.8
J6 | 60 | 5 | 2 | 25 | 0.09 | 89.6 | 0.0477 | 0.8
J7 | 60 | 5 | 2 | 30 | n/a | n/a | n/a | 0.8
J8 | 60 | 5 | 2 | 35 | 0.06 | 90.6 | 0.0429 | 0.9

## Slide 10: Clearlake Oaks CWS: Jar Test 9-16 Results Post-Ozone Source Water, Flash Mix 60 sec (200 RPM)
Jar | 30 RPM Floc Mix minutes | NaOCl mg/L | 9800 mg/L | 9890 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 25 min
J9 | 5 | 2 | 20 | 1.0 | 0.05 | 90.3 | 0.044 | 0.5
J10 | 5 | 2 | 25 | 1.25 | 0.06 | 90.6 | 0.043 | 0.5
J11 | 5 | 2 | 30 | 1.5 | 0.06 | 90.8 | 0.042 | 0.7
J12 | 5 | 2 | 35 | 1.75 | 0.06 | 90.8 | 0.042 | 0.7
J13 | 5 | 2 | 20 | 2 | 0.06 | 89.8 | 0.047 | 0.6
J14 | 5 | 2 | 25 | 2.5 | 0.07 | 90.2 | 0.045 | 0.7
J15 | 5 | 2 | 30 | 3.0 | 0.05 | 90.4 | 0.044 | 0.8
J16 | 5 | 2 | 35 | 3.5 | 0.08 | 90.6 | 0.043 | 0.8

## Slide 11: Jars 1-4 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9800

## Slide 12: Jars 1-4: End of 5-minute flocculation (30 RPM) duration.
20 mg/L 9800
Filtrate 0.09 NTU
UVT: 88.3%
UVA: 0.054/cm
Settled: 0.8 NTU
25 mg/L 9800
Filtrate 0.10 NTU
UVT: 88.8%
UVA: 0.052/cm
Settled: 0.8 NTU
30 mg/L 9800
Filtrate 0.08 NTU
UVT: 89.4%
UVA: 0.049/cm
Settled: 1.2 NTU
35 mg/L 9800
Filtrate 0.08 NTU
UVT: 89.7%
UVA: 0.047/cm
Settled: 1.1 NTU

## Slide 13: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 14: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
20 mg/L 9800
Filtrate 0.09 NTU
UVT: 88.3%
UVA: 0.054/cm
Settled: 0.8 NTU
25 mg/L 9800
Filtrate 0.10 NTU
UVT: 88.8%
UVA: 0.052/cm
Settled: 0.8 NTU
30 mg/L 9800
Filtrate 0.08 NTU
UVT: 89.4%
UVA: 0.049/cm
Settled: 1.2 NTU
35 mg/L 9800
Filtrate 0.08 NTU
UVT: 89.7%
UVA: 0.047/cm
Settled: 1.1 NTU

## Slide 15: Jars 5-8 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9800 w/NaOCl

## Slide 16: Jars 5-8: End of 5-minute flocculation (30 RPM) duration.
2 mg/L NaOCl
20 mg/L 9800
Filtrate 0.09 NTU
UVT: 88.4%
UVA: 0.054/cm
Settled: 0.8 NTU
2 mg/L NaOCl
25 mg/L 9800
Filtrate 0.09 NTU
UVT: 89.6%
UVA: 0.048/cm
Settled: 0.8 NTU
2 mg/L NaOCl
30 mg/L 9800
Filtrate ? NTU
UVT: ? %
UVA: ?/cm
Settled: 0.8 NTU
2 mg/L NaOCl
35 mg/L 9800
Filtrate 0.06 NTU
UVT: 90.6%
UVA: 0.043/cm
Settled: 0.9 NTU

## Slide 17: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 18: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
2 mg/L NaOCl
20 mg/L 9800
Filtrate 0.09 NTU
UVT: 88.4%
UVA: 0.054/cm
Settled: 0.8 NTU
2 mg/L NaOCl
25 mg/L 9800
Filtrate 0.09 NTU
UVT: 89.6%
UVA: 0.048/cm
Settled: 0.8 NTU
2 mg/L NaOCl
30 mg/L 9800
Filtrate ? NTU
UVT: ? %
UVA: ?/cm
Settled: 0.8 NTU
2 mg/L NaOCl
35 mg/L 9800
Filtrate 0.06 NTU
UVT: 90.6%
UVA: 0.043/cm
Settled: 0.9 NTU

## Slide 19: Jars 9-12 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants 9800/9890 w/NaOCl

## Slide 20: Jars 9-12: End of 5-minute flocculation (30 RPM) duration.
2 mg/L NaOCl
20 mg/L 9800
1 mg/L 9890
Filtrate 0.05 NTU
UVT: 90.3%
UVA: 0.044/cm
Settled: 0.5 NTU
2 mg/L NaOCl
25 mg/L 9800
1.25 mg/L 9890
Filtrate 0.06 NTU
UVT: 90.6%
UVA: 0.043/cm
Settled: 0.5 NTU
2 mg/L NaOCl
30 mg/L 9800
1.5 mg/L 9890
Filtrate 0.06 NTU
UVT: 90.8%
UVA: 0.042/cm
Settled: 0.7 NTU
2 mg/L NaOCl
35 mg/L 9800
1.75 mg/L 9890
Filtrate 0.06 NTU
UVT: 90.8%
UVA: 0.042/cm
Settled: 0.7 NTU

## Slide 21: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 22: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
2 mg/L NaOCl
20 mg/L 9800
1 mg/L 9890
Filtrate 0.05 NTU
UVT: 90.3%
UVA: 0.044/cm
Settled: 0.5 NTU
2 mg/L NaOCl
25 mg/L 9800
1.25 mg/L 9890
Filtrate 0.06 NTU
UVT: 90.6%
UVA: 0.043/cm
Settled: 0.5 NTU
2 mg/L NaOCl
30 mg/L 9800
1.5 mg/L 9890
Filtrate 0.06 NTU
UVT: 90.8%
UVA: 0.042/cm
Settled: 0.7 NTU
2 mg/L NaOCl
35 mg/L 9800
1.75 mg/L 9890
Filtrate 0.06 NTU
UVT: 90.8%
UVA: 0.042/cm
Settled: 0.7 NTU

## Slide 23: Jars 13-16 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants 9800/9890 w/NaOCl

## Slide 24: Jars 13-16: End of 5-minute flocculation (30 RPM) duration.
2 mg/L NaOCl
20 mg/L 9800
2 mg/L 9890
Filtrate 0.06 NTU
UVT: 89.8%
UVA: 0.047/cm
Settled: 0.6 NTU
2 mg/L NaOCl
25 mg/L 9800
2.5 mg/L 9890
Filtrate 0.07 NTU
UVT: 90.2%
UVA: 0.045/cm
Settled: 0.7 NTU
2 mg/L NaOCl
30 mg/L 9800
3 mg/L 9890
Filtrate 0.07 NTU
UVT: 90.4%
UVA: 0.044/cm
Settled: 0.8 NTU
2 mg/L NaOCl
35 mg/L 9800
3.5 mg/L 9890
Filtrate 0.08 NTU
UVT: 90.6%
UVA: 0.043/cm
Settled: 0.8 NTU

## Slide 25: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 26: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
2 mg/L NaOCl
20 mg/L 9800
2 mg/L 9890
Filtrate 0.06 NTU
UVT: 89.8%
UVA: 0.047/cm
Settled: 0.6 NTU
2 mg/L NaOCl
25 mg/L 9800
2.5 mg/L 9890
Filtrate 0.07 NTU
UVT: 90.2%
UVA: 0.045/cm
Settled: 0.7 NTU
2 mg/L NaOCl
30 mg/L 9800
3 mg/L 9890
Filtrate 0.07 NTU
UVT: 90.4%
UVA: 0.044/cm
Settled: 0.8 NTU
2 mg/L NaOCl
35 mg/L 9800
3.5 mg/L 9890
Filtrate 0.08 NTU
UVT: 90.6%
UVA: 0.043/cm
Settled: 0.8 NTU

## Slide 27: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-60 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 28: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 29: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 30: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 31: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 32: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732