## Slide 1: Clearlake Oaks CWD CA1710001 Lake County Jar Test
by Guy Schott, P.E.
May 8, 2019

## Slide 2: Lucerne Water Co. Source Water: Clear Lake Conventional Treatment

## Slide 3: Conventional Treatment Plant

## Slide 4: Clearlake Oaks CWD.: Source Water Characteristics March 8, 2019
Source
Post Ozone Sample
Turbidity: 1.35 NTU
UVT: 90%
UVA: 0.046/cm
0.4 um Filtered
UVT: 91.1%
UVA: 0.040/cm

## Slide 5: UVT/UVA
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 6: Applied Coagulants for Jar Testing
Pro Pac 9800 (NTU Technologies)
50% Aluminum Chlorohydrate
50% Water
SG = 1.34
Pro Pac 9890 (NTU Technologies)
35-45% Aluminum Chlorohydrate
35-45% Water
SG = 1.25-1.34
7066 (Garratt Callahan)
10 – 30% Poly Aluminum Hydroxychloride Sulfate
50% Basicity
SG = 1.2
Aluminum Sulfate
48.24% Aluminum Sulfate, 8.2% Al2O3
SG = 1.34

## Slide 7: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength). Alum Sulfate is reported as Alum.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 8: Clearlake Oaks CWS: Jar Test 1-6 Results Post-Ozone Source Water
Jar | 200 RPM Flash Mix Seconds | 30 RPM Floc Duration minutes | 7066 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 25 min
J1 | 60 | 10 | 30 | 0.10 | 94.1 | 0.026 | 0.65
J2 | 60 | 10 | 40 | 0.14 | 94.6 | 0.024 | 0.60
J3 | 60 | 10 | 50 | 0.18 | 94.0 | 0.027 | 0.48
J4 | 60 | 10 | 60 | 0.13 | 94.4 | 0.025 | 0.42
J5 | 60 | 10 | 70 | 0.13 | 94.9 | 0.023 | 0.31
J6 | 60 | 10 | 80 | 0.12 | 94.9 | 0.023 | 0.31

## Slide 9: Clearlake Oaks CWS: Jar Test 7-12 Results Post-Ozone Source Water
Jar | 200 RPM Flash Mix Seconds | 30 RPM Floc Duration minutes | 9800 mg/L | 9890 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 25 min
J7 | 60 | 10 | 21 | 1.05 | 0.08 | 95.8 | 0.019 | 0.30
J8 | 60 | 10 | 21 | 2.1 | 0.07 | 95.6 | 0.020 | 0.24
J9 | 60 | 10 | 23 | 1.15 | 0.11 | 95.8 | 0.019 | 0.40
J10 | 60 | 10 | 23 | 2.3 | 0.10 | 95.3 | 0.021 | 0.39
J11 | 60 | 10 | 25 | 1.25 | 0.08 | 95.1 | 0.022 | 0.43
J12 | 60 | 10 | 25 | 2.5 | 0.11 | 95.5 | 0.020 | 0.93

## Slide 10: Clearlake Oaks CWS: Jar Test 13-16 Results Post-Ozone Source Water, Flash Mix 60 sec (200 RPM)
Jar | 30 RPM Floc Duration minutes | KMnO4 mg/L | 9800 mg/L | 9890 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 25 min
J13 | 60 | 1.0 | 21 | 1.05 | 0.10 | 94.3 | 0.026 | 0.45
J14 | 60 | 1.0 | 21 | 1.05 | 0.11 | 93.6 | 0.029 | 0.38
J15 | 60 | 2.0 | 23 | 1.15 | 0.07 | 94.3 | 0.026 | 0.23
J16 | 60 | 2.0 | 23 | 1.15 | 0.14 | 93.2 | 0.031 | 0.42

## Slide 11: Clearlake Oaks CWS: Jar Test 17-24 Results Post-Ozone Source Water, Flash Mix 60 sec (200 RPM)
Jar | 30 RPM Floc Mix minutes | Alum mg/L | 9800 mg/L | 9890 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 25 min
J17 | 5 | 0 | 23 | 1.15 | 0.08 | 94.8 | 0.023 | 0.48
J18 | 10 | 0 | 23 | 1.15 | 0.07 | 94.5 | 0.025 | 0.39
J19 | 20 | 0 | 23 | 1.15 | 0.07 | 94.9 | 0.023 | 0.30
J20 | 40 | 0 | 23 | 1.15 | 0.07 | 94.9 | 0.023 | 0.36
J21 | 5 | 16.8 | 0 | 0 | 0.15 | 92.7 | 0.033 | 1.1
J22 | 10 | 16.8 | 0 | 0 | 0.17 | 92.6 | 0.033 | 0.70
J23 | 20 | 16.8 | 0 | 0 | 0.14 | 92.8 | 0.032 | 0.54
J24 | 45 | 16.8 | 0 | 0 | 0.13 | 92.8 | 0.032 | 0.35

## Slide 12: Clearlake Oaks CWS: Jar Test 25-28 Results Post-Ozone Source Water
Jar | 200 RPM Flash Mix Seconds | 30 RPM Floc Duration minutes | 9800 mg/L | 9890 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 25 min
J25 | 0 | 5 | 23 | 1.15 | 0.07 | 94.4 | 0.025 | 0.43
J26 | 0 | 10 | 23 | 1.15 | 0.07 | 94.6 | 0.024 | 0.30
J27 | 0 | 20 | 23 | 1.15 | 0.08 | 94.6 | 0.024 | 0.22
J28 | 0 | 40 | 23 | 1.15 | 0.06 | 94.7 | 0.024 | 0.15

## Slide 13: Clearlake Oaks CWS: Jar Test 29-36 Results Post-Ozone Source Water
Jar | 200 RPM Flash Mix Seconds | 30 RPM Floc Duration minutes | Alum mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 25 min
J29 | 0 | 5 | 16.8 | 0.24 | 92.8 | 0.032 | 2.1
J30 | 0 | 10 | 16.8 | 0.17 | 92.8 | 0.032 | 0.95
J31 | 0 | 20 | 16.8 | 0.14 | 93.0 | 0.032 | 0.48
J32 | 0 | 40 | 16.8 | 0.18 | 92.7 | 0.033 | 0.29
J33 | 60 | 10 | 21 | 0.17 | 93.1 | 0.036 | 0.67
J34 | 60 | 10 | 25 | 0.15 | 92.9 | 0.032 | 0.50
J35 | 60 | 10 | 29 | 0.13 | 93.4 | 0.030 | 0.48
J36 | 60 | 10 | 33 | 0.11 | 93.6 | 0.029 | 0.39

## Slide 14: Clearlake Oaks CWS: Jar Test 37-40 Results Post-Ozone Source Water, No Flash Mix Applied
Jar | 30 RPM Floc Duration minutes | Alum mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 15 min | Settle NTU 25 min | Settle NTU 35 min
J37 | 5 | 33 | 0.12 | 93.7 | 0.028 | 1.6 | 1.1 | 0.95
J38 | 10 | 33 | 0.17 | 93.6 | 0.029 | 0.63 | 0.45 | 0.55
J39 | 20 | 33 | 0.12 | 93.6 | 0.029 | 0.58 | 0.36 | 0.38
J40 | 40 | 33 | 0.46 | 93.3 | 0.030 | 0.31 | 0.25 | 0.28

## Slide 15: Jars 1-6 Test Flash Mix 60 Sec (200 RPM) Floc Mix 10 min (30 RPM) Applied Coagulant 7066

## Slide 16: Jars 1-6: End of 10-minute flocculation (30 RPM) duration.
30 mg/L 7066
Filtrate 0.10 NTU
UVT: 94.1%
UVA: 0.026/cm
Settled: 0.65 NTU
40 mg/L 7066
Filtrate 0.14 NTU
UVT: 94.6%
UVA: 0.024/cm
Settled: 0.60 NTU
50 mg/L 7066
Filtrate 0.18 NTU
UVT: 94.0%
UVA: 0.027/cm
Settled: 0.48 NTU
60 mg/L 7066
Filtrate 0.13 NTU
UVT: 94.4%
UVA: 0.025/cm
Settled: 0.42 NTU
70 mg/L 7066
Filtrate 0.13 NTU
UVT: 94.9%
UVA: 0.023/cm
Settled: 0.31 NTU
80 mg/L 7066
Filtrate 0.12 NTU
UVT: 94.9%
UVA: 0.023/cm
Settled: 0.31 NTU

## Slide 17: Jars 1-6: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 18: Jars 1-6: After 25-minutes of settling, settled water turbidity is taken.
30 mg/L 7066
Filtrate 0.10 NTU
UVT: 94.1%
UVA: 0.026/cm
Settled: 0.65 NTU
40 mg/L 7066
Filtrate 0.14 NTU
UVT: 94.6%
UVA: 0.024/cm
Settled: 0.60 NTU
50 mg/L 7066
Filtrate 0.18 NTU
UVT: 94.0%
UVA: 0.027/cm
Settled: 0.48 NTU
60 mg/L 7066
Filtrate 0.13 NTU
UVT: 94.4%
UVA: 0.025/cm
Settled: 0.42 NTU
70 mg/L 7066
Filtrate 0.13 NTU
UVT: 94.9%
UVA: 0.023/cm
Settled: 0.31 NTU
80 mg/L 7066
Filtrate 0.12 NTU
UVT: 94.9%
UVA: 0.023/cm
Settled: 0.31 NTU

## Slide 19: Jars 7-12 Test Flash Mix 60 Sec (200 RPM) Floc Mix 10 min (30 RPM) Applied Coagulant 9800/9890

## Slide 20: Jars 7-12: End of 10-minute flocculation (30 RPM) duration.
21 mg/L 9800
1.05 mg/L 9890
Filtrate 0.08 NTU
UVT: 95.8%
UVA: 0.019/cm
Settled: 0.30 NTU
21 mg/L 9800
2.1 mg/L 9890
Filtrate 0.07 NTU
UVT: 95.6%
UVA: 0.020/cm
Settled: 0.24 NTU
23 mg/L 9800
1.15 mg/L 9890
Filtrate 0.11 NTU
UVT: 95.8%
UVA: 0.019/cm
Settled: 0.40 NTU
23 mg/L 9800
2.3 mg/L 9890
Filtrate 0.10 NTU
UVT: 95.3%
UVA: 0.021/cm
Settled: 0.39 NTU
25 mg/L 9800
1.25 mg/L 9890
Filtrate 0.08 NTU
UVT: 95.3%
UVA: 0.022/cm
Settled: 0.43 NTU
25 mg/L 9800
2.5 mg/L 9890
Filtrate 0.11 NTU
UVT: 95.5%
UVA: 0.020/cm
Settled: 0.93 NTU

## Slide 21: Jars 7-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 22: Jars 7-12: After 25-minutes of settling, settled water turbidity is taken.
21 mg/L 9800
1.05 mg/L 9890
Filtrate 0.08 NTU
UVT: 95.8%
UVA: 0.019/cm
Settled: 0.30 NTU
21 mg/L 9800
2.1 mg/L 9890
Filtrate 0.07 NTU
UVT: 95.6%
UVA: 0.020/cm
Settled: 0.24 NTU
23 mg/L 9800
1.15 mg/L 9890
Filtrate 0.11 NTU
UVT: 95.8%
UVA: 0.019/cm
Settled: 0.40 NTU
23 mg/L 9800
2.3 mg/L 9890
Filtrate 0.10 NTU
UVT: 95.3%
UVA: 0.021/cm
Settled: 0.39 NTU
25 mg/L 9800
1.25 mg/L 9890
Filtrate 0.08 NTU
UVT: 95.3%
UVA: 0.022/cm
Settled: 0.43 NTU
25 mg/L 9800
2.5 mg/L 9890
Filtrate 0.11 NTU
UVT: 95.5%
UVA: 0.020/cm
Settled: 0.93 NTU

## Slide 23: Jars 13-16 Test Flash Mix 60 Sec (200 RPM) Floc Mix 60 min (30 RPM) Applied Coagulant 9800/9890 w/KMnO4 Pre-oxidation

## Slide 24: Jars 13-16: End of 60-minute flocculation (30 RPM) duration.
1.0 mg/L KMnO4
21 mg/L 9800
1.05 mg/L 9890
Filtrate 0.10 NTU
UVT: 94.3%
UVA: 0.026/cm
Settled: 0.45 NTU
2.0 mg/L KMnO4
21 mg/L 9800
1.05 mg/L 9890
Filtrate 0.11 NTU
UVT: 93.6%
UVA: 0.029/cm
Settled: 0.38 NTU
1.0 mg/L KMnO4
23 mg/L 9800
1.15 mg/L 9890
Filtrate 0.07 NTU
UVT: 94.3%
UVA: 0.026/cm
Settled: 023 NTU
2.0 mg/L KMnO4
23 mg/L 9800
1.15 mg/L 9890
Filtrate 0.14 NTU
UVT: 93.2%
UVA: 0.031/cm
Settled: 042 NTU

## Slide 25: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 26: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
1.0 mg/L KMnO4
21 mg/L 9800
1.05 mg/L 9890
Filtrate 0.10 NTU
UVT: 94.3%
UVA: 0.026/cm
Settled: 0.45 NTU
2.0 mg/L KMnO4
21 mg/L 9800
1.05 mg/L 9890
Filtrate 0.11 NTU
UVT: 93.6%
UVA: 0.029/cm
Settled: 0.38 NTU
1.0 mg/L KMnO4
23 mg/L 9800
1.15 mg/L 9890
Filtrate 0.07 NTU
UVT: 94.3%
UVA: 0.026/cm
Settled: 023 NTU
2.0 mg/L KMnO4
23 mg/L 9800
1.15 mg/L 9890
Filtrate 0.14 NTU
UVT: 93.2%
UVA: 0.031/cm
Settled: 042 NTU

## Slide 27: Jars 17-20 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5/10/20/40 min (30 RPM) Applied Coagulant 9800/9890

## Slide 28: Jars 17: End of 5-minute flocculation (30 RPM) duration.
23 mg/L 9800
1.15 mg/L 9890
Filtrate 0.08 NTU
UVT: 94.8%
UVA: 0.023/cm
Settled: 0.48 NTU

## Slide 29: Jars 18: End of 10-minute flocculation (30 RPM) duration.
23 mg/L 9800
1.15 mg/L 9890
Filtrate 0.07 NTU
UVT: 94.5%
UVA: 0.024/cm
Settled: 0.39 NTU

## Slide 30: Jars 19: End of 20-minute flocculation (30 RPM) duration.
23 mg/L 9800
1.15 mg/L 9890
Filtrate 0.07 NTU
UVT: 94.9%
UVA: 0.023/cm
Settled: 0.30 NTU

## Slide 31: Jars 20: End of 40-minute flocculation (30 RPM) duration.
23 mg/L 9800
1.15 mg/L 9890
Filtrate 0.07 NTU
UVT: 95.1%
UVA: 0.022/cm
Settled: 0.36 NTU

## Slide 32: Jars 21-24 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5/10/20/45 min (30 RPM) Applied Coagulant Aluminum Sulfate

## Slide 33: Jars 21: End of 5-minute flocculation (30 RPM) duration.
16.8 mg/L Alum
Filtrate 0.15 NTU
UVT: 92.7%
UVA: 0.033/cm
Settled: 1.1 NTU

## Slide 34: Jars 22: End of 10-minute flocculation (30 RPM) duration.
16.8 mg/L Alum
Filtrate 0.17 NTU
UVT: 92.6%
UVA: 0.033/cm
Settled: 0.70 NTU

## Slide 35: Jars 23: End of 20-minute flocculation (30 RPM) duration.
16.8 mg/L Alum
Filtrate 0.14 NTU
UVT: 92.8%
UVA: 0.032/cm
Settled: 0.54 NTU

## Slide 36: Jars 24: End of 45-minute flocculation (30 RPM) duration.
16.8 mg/L Alum
Filtrate 0.13 NTU
UVT: 92.8%
UVA: 0.032/cm
Settled: 0.35 NTU

## Slide 37: Jars 25-28 Test No Flash Mix Floc Mix 5/10/20/40 min (30 RPM) Applied Coagulant 9800/9890

## Slide 38: Jars 25: End of 5-minute flocculation (30 RPM) duration.
23 mg/L 9800
1.15 mg/L 9890
Filtrate 0.07 NTU
UVT: 94.4%
UVA: 0.025/cm
Settled: 0.43 NTU

## Slide 39: Jars 27: End of 10-minute flocculation (30 RPM) duration.
23 mg/L 9800
1.15 mg/L 9890
Filtrate 0.07 NTU
UVT: 94.6%
UVA: 0.024/cm
Settled: 0.30 NTU

## Slide 40: Jars 27: End of 20-minute flocculation (30 RPM) duration.
23 mg/L 9800
1.15 mg/L 9890
Filtrate 0.08 NTU
UVT: 94.6%
UVA: 0.024/cm
Settled: 0.22 NTU

## Slide 41: Jars 28: End of 40-minute flocculation (30 RPM) duration.
23 mg/L 9800
1.15 mg/L 9890
Filtrate 0.06 NTU
UVT: 94.7%
UVA: 0.024/cm
Settled: 0.15 NTU

## Slide 42: Jars 29-32 Test No Flash Mix Floc Mix 5/10/20/40 min (30 RPM) Applied Coagulant Aluminum Sulfate

## Slide 43: Jars 29: End of 5-minute flocculation (30 RPM) duration.
16.8 mg/L Alum
Filtrate 0.24 NTU
UVT: 92.8%
UVA: 0.032/cm
Settled: 2.1 NTU

## Slide 44: Jars 30: End of 10-minute flocculation (30 RPM) duration.
16.8 mg/L Alum
Filtrate 0.17 NTU
UVT: 92.8%
UVA: 0.032/cm
Settled: 0.95 NTU

## Slide 45: Jars 31: End of 20-minute flocculation (30 RPM) duration.
16.8 mg/L Alum
Filtrate 0.14 NTU
UVT: 93.0%
UVA: 0.032/cm
Settled: 0.48 NTU

## Slide 46: Jars 32: End of 40-minute flocculation (30 RPM) duration.
16.8 mg/L Alum
Filtrate 0.18 NTU
UVT: 92.7%
UVA: 0.033/cm
Settled: 0.29 NTU

## Slide 47: Jars 33-36 Test Flash Mix 60 sec (200 RPM) Floc Mix 10 min (30 RPM) Applied Coagulant Aluminum Sulfate

## Slide 48: Jars 33-36: End of 10-minute flocculation (30 RPM) duration.
21 mg/L Alum
Filtrate 0.17 NTU
UVT: 93.1%
UVA: 0.036/cm
Settled: 0.67 NTU
25 mg/L Alum
Filtrate 0.15 NTU
UVT: 92.9%
UVA: 0.032/cm
Settled: 0.50 NTU
29 mg/L Alum
Filtrate 0.13 NTU
UVT: 93.4%
UVA: 0.030/cm
Settled: 0.48 NTU
33 mg/L Alum
Filtrate 0.11 NTU
UVT: 93.6%
UVA: 0.030/cm
Settled: 0.39 NTU

## Slide 49: Jars 33-36: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 50: Jars 33-36: After 25-minutes of settling, settled water turbidity is taken.
21 mg/L Alum
Filtrate 0.17 NTU
UVT: 93.1%
UVA: 0.036/cm
Settled: 0.67 NTU
25 mg/L Alum
Filtrate 0.15 NTU
UVT: 92.9%
UVA: 0.032/cm
Settled: 0.50 NTU
29 mg/L Alum
Filtrate 0.13 NTU
UVT: 93.4%
UVA: 0.030/cm
Settled: 0.48 NTU
33 mg/L Alum
Filtrate 0.11 NTU
UVT: 93.6%
UVA: 0.030/cm
Settled: 0.39 NTU

## Slide 51: Jars 37-40 Test No Flash Mix Floc Mix 5/10/20/40 min (30 RPM) Applied Coagulant Aluminum Sulfate

## Slide 52: Jars 37: End of 5-minute flocculation (30 RPM) duration.
33 mg/L Alum
Filtrate 0.12 NTU
UVT: 93.7%
UVA: 0.028/cm
Settled: 1.6 NTU (15 min)
Settled: 1.1 NTU (25 min)
Settled: 0.95 NTU (35 min)

## Slide 53: Jars 38: End of 10-minute flocculation (30 RPM) duration.
33 mg/L Alum
Filtrate 0.17 NTU
UVT: 93.6%
UVA: 0.029/cm
Settled: 0.63 NTU (15 min)
Settled: 0.45 NTU (25 min)
Settled: 0.55 NTU (35 min)

## Slide 54: Jars 39: End of 20-minute flocculation (30 RPM) duration.
33 mg/L Alum
Filtrate 0.12 NTU
UVT: 93.6%
UVA: 0.029/cm
Settled: 0.58 NTU (15 min)
Settled: 0.36 NTU (25 min)
Settled: 0.38 NTU (35 min)

## Slide 55: Jars 40: End of 40-minute flocculation (30 RPM) duration.
33 mg/L Alum
Filtrate 0.46 NTU
UVT: 93.3%
UVA: 0.029/cm
Settled: 0.31 NTU (15 min)
Settled: 0.25 NTU (25 min)
Settled: 0.28 NTU (35 min)

## Slide 56: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-60 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 57: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 58: Filter Used for This Study
Note: 1.20 um (nominal size), polypropylene hydrophobic membrane was used for this study.
Thickness: 180-250 um, Max flow rate (200 mL/min @ 10 psi)
(Tisch Scientific, Part#: SF14854, www.scienticfilters.com)

## Slide 59: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 60: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 61: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 62: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732