## Slide 1: Clearwell
Clearlake Oaks CWD CA1710001 Tracer Study Clearwell June 29, 2022
Performed by:
Guy Schott, P.E
Amy Santos

## Slide 2: Table of Contents
Clearwell Design Specifications and Tracer Sampling Points
Summary of Tracer Results and Procedures
Tracer Injection Point
Recorded Tracer Data (Tables)
Graphs: Modified Step-Dose and Normalized Step-Dose Curve to F-Curve
Purpose of a Tracer Test
Disinfection Exposure Time of Fluid in Vessel for Determining Ct10
Ct10 Value
Baffling Factor (BF), Definition
Tracer Test Method (Modified Step-Dose)
Method of Analysis and Equipment

## Slide 3: Pipeline & Tank Design Specifications PAX Mixer & Surface Water Aeration System were on for this Study

## Slide 4: Summary of Tracer Procedures
Tracer study was conducted on the newly rehabilitated 188,000-gallon clearwell installed with a PAX mixer and 2 x surface aeration (~5,000 gpm each) for TTHM reduction. For this test, the PAX mixer and surface aeration systems were on. Liquid fluoride was used as the tracer that was injected at the chlorine injection point upstream of the clearwell.
Sampling were conducted at two stations
  Station 1: Inlet to Tank 1 to determine fluoride dose (mg/L)
  Station 2: Downstream of clearwell and flow meter near high lift pump
Clearwell entry flow was 600 gpm
Clearwell exit flow was 610 gpm

## Slide 5: Tracer Test Result Summary – Transmission Line + Clearwell
Modified Step-Dose
Test Date: 6/29/22
Pipe volume from injection point to Tank 1: 1,350 gal
Clearwell operating level: 19.16-ft
Tank Diameter: 40-ft (9,400 gal/ft)
Volume of Transmission Line + Clearwell: 181,400 gallons
Flow thru Clearwell: 610 gpm
HRT: 297 minutes (181,400 gal/ 610 gpm)
t10: 36 minutes
Baffling Factor (t10/HRT): 0.12

## Slide 6: Top of Clearwell
Center Vent

## Slide 7: Clearwell Roof – Hatch Entry & Powervent
PAX Powervent headspace
ventilation unit
3,000 CFM
Inlet

## Slide 8: Clearwell Inlet and Surface Aeration (off)

## Slide 9: Clearwell Surface Aeration (on/off)

## Slide 10: Clearwell Surface Aeration

## Slide 11: Laboratory
Fluoride Analysis

## Slide 12: Clearlake Oaks CWS Tracer and Fluoride injection location
Tracer: H2SiF6, Fluoride (F)
Feed pump capacity 17.2 gal/hr set at 50% (8.6 gal/hr.) during test
Add 3 liters H2SiF6 to 20-gal H2O
Background Fluoride: 0.160 mg/L as F
Measured dose: 1.88 mg/L as F (excluding background fluoride)
Fluoride (tracer) was injected into a vault at chlorine injection point.

## Slide 13: Feed Pump and Tracer Injection
Fluoride chemical crock and pump
Fluoride Injection Point (same location of post NaOCl)

## Slide 14: Tracer Sample Point to Clearwell for Determining Fluoride Dose
Vault location of sample point
Sample collection point of tracer

## Slide 15: Clearwell Sample Tap off Booster Pump

## Slide 16: Clearwell Outlet Tracer Sample Line Station from Booster Pump

## Slide 17: Tracer Fluoride Dose, Inlet to Clearwell, Table 1
Elapsed Time minutes | *Tracer Fluoride Dose mg/L
11-15 | 1.87
16-20 | 1.87
25-30 | 1.89
31-35 | 1.94
36-40 | 1.93
41-45 | 1.94
Chart: Fluoride-Dose to Clearwell
| 13 | 18 | 27 | 33 | 38 | 43
 | 1.87 | 1.87 | 1.89 | 1.94 | 1.93 | 1.94
*Excludes background fluoride of 0.160 mg/L

## Slide 18: Tracer Dose and Background Residual
Average background fluoride concentration: 0.160 mg/L as F
Average steady-state measured fluoride concentration exiting pipeline and entering the first tank (steel): 2.04 mg/L as F
Fluoride dose: 2.04 – 0.160 = 1.88 mg/L as F
Results are based on tracer dose of 1.88 mg/L as F
10% of tracer dose is 0.188 mg/L as F

## Slide 19: Results 2

## Slide 20: Step
Chart: Step-Dose Curve - Clearwell
| 0 | 5 | 10 | 15 | 18 | 21 | 24 | 27 | 30 | 33 | 36 | 39 | 42 | 45 | 48 | 51 | 54 | 57 | 60 | 63
 | 0 | 0 | 0.025 | 0.058 | 0.074 | 0.095 | 0.119 | 0.135 | 0.161 | 0.171 | 0.192 | 0.209 | 0.223 | 0.241 | 0.264 | 0.28 | 0.298 | 0.315 | 0.334 | 0.352
Dose: 1.88 mg/L
0.188 mg/L at t10
t10: 36 min
HRT: 297 min
BF: 0.12 (t10/HRT)

## Slide 21: Step Curve tanks 1-5
Chart: Normalized F-Curve - Clearwell
| 0 | 1.6813022650724613E-2 | 3.3626045301449227E-2 | 5.0439067952173823E-2 | 6.0526881542608588E-2 | 7.0614695133043359E-2 | 8.0702508723478117E-2 | 9.0790322313912888E-2 | 0.10087813590434763 | 0.11096594949478239 | 0.12105376308521716 | 0.13114157667565193 | 0.14122939026608669 | 0.15131720385652145 | 0.16140501744695621 | 0.17149283103739096 | 0.18158064462782578 | 0.19166845821826053 | 0.20175627180869529 | 0.21184408539913016
 | 0 | 0 | 0.013319 | 0.0309 | 0.039425 | 0.050613 | 0.063399 | 0.071923 | 0.085775 | 0.091103 | 0.10229 | 0.11135 | 0.11881 | 0.1284 | 0.14065 | 0.14917 | 0.15876 | 0.16782 | 0.17794 | 0.18753
Baffling Factor (BF) = 0.12

## Slide 22: Purpose of a Tracer Study
To determine the hydraulic efficiency or disinfectant exposure time of water through one or more reactors.
The addition of known quantities of a nonreactive chemical (tracer) is added in the form of a pulse (slug) or step-input.
The time of travel or disinfectant exposure time through the reactor is related to:
  Flow rate
  Reactor water volume
  Water Depth
  Reactor configuration
  Hydraulic mixing

## Slide 23: Disinfection Exposure Time of Fluid in Vessel for Determining Ct10
C” is the disinfectant residual (mg/L) at the point of inactivation compliance.
The disinfection exposure time of water used for Ct10 calculation is the time (t10) it takes for the first 10 percent of the water entering the reactor to exit the reactor.
To determine this, a marker (nonreactive tracer) is introduced into the water and is monitored leaving the reactor.
Example: 2.7 mg/L of tracer is continuously dose during testing; t10 is that time when 0.27 mg/L of tracer concentration (10% of dose) has exited the reactor.

## Slide 24: Ct10 Value
Log inactivation is based on the Delivered Dose, “Ct10”
  “C” is the disinfectant residual (mg/L)
  “t10” is the exposure or contact time (minutes)
  Multiply them:
C • t10 = mg/L • min (delivered dose to pathogens)
The calculated Ct10 value is looked up in EPA Ct tables to determine the log inactivation based on specific monitoring parameters (pH, disinfectant residual and temperature).

## Slide 25: Baffling Factor (BF)
Baffling factor or short-circuiting factor:
  Determined from tracer study or estimated
  BF = t10/ HRT from tracer study
  HRT (hydraulic residence time) = reactor volume divided by reactor flow
Once the BF is determined, then it is applied to the operations of the reactor for determining the disinfectant exposure time.
Example:
  Total Clearwell operating volume: 180,000 gallons
  Exit flow: 620 gpm (0.892 MGD)
  BF: 0.12, from tracer study
  Calculated contact or disinfection exposure time:
    180,000 gal ÷ 620 gpm × 0.12 = 35 minutes = t10

## Slide 26: Test Method
Modified Step-Dose Method
It is a continue feed of tracer at constant rate and inlet plant flow throughout the duration of the test. The “Step-Dose” test has a duration of 3-4 HRT to achieve reactor outlet steady-state tracer concentration. The time “t10” is determined when 10% of the tracer dose concentration has exist the reactor. The “Modified Step-Dose” test allows the test to be completed in less than 1 HRT by physical measurements of the tracer inlet flow and/or channel basin concentration.

## Slide 27: Method of Analysis and Equipment
Intellical™ ISEF121 Fluoride (F-) Ion Selective Electrode (ISE)
HQ40d Portable ISE Multi-Parameter Meter
Fluoride Ionic Strength Adjustor (ISA)
Fluoride Standards (0.2 & 2.0 mg/L)
25 mL graduated cylinder
Finnpipette F2 variable volume pipette, capacity 0.5 - 5 mL
Electrode stirrer stand
50 mL beakers
Stir Bar, Magnetic, Polygon

## Slide 28: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Tracer Test Results for review
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732