## Slide 1: Lucerne Water Co., Cal Water Service CA1710005 Lake County Jar Test
by Guy Schott, P.E.
July 27, 2021

## Slide 2: Lucerne Water Co. Source Water: Clear Lake Conventional Treatment

## Slide 3: Lucerne Water Co. Characteristics July 27, 2021
Source
pH: 9.10
Turbidity: 4.8 NTU
UVT: 80.3%,
UVA: 0.095/cm
0.4 um Filtered
Turbidity: 0.44 NTU
UVT: 85.2%,
UVA: 0.069/cm

## Slide 4: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 5: Applied Coagulants for Jar Testing
Pro Pac 9800 (NTU Technologies)
50% Aluminum Chlorohydrate
50% Water
23.62% Al2O3
12.5% Al
83% Basicity
SG = 1.25-1.34
NSF limit: 250 mg/L as Product
10 mg/L as 9800 = Reduction 1.18 mg/L as CaCO3

## Slide 6: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 9.10
LCA #1:
9800: 34.8 mg/L as product
pH adjusted to 7.70 with acetic acid

## Slide 7: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 8: Source Water pH and Alkalinity Changes when H2SO4 is Added
Constituents | pH open system (measured) | *Loss of CO2 open system (calculated) | pH, no loss of CO2 closed system (calculated) | Alkalinity as CaCO3, mg/L (calculated
Source pH | 9.10 | - | - | 181
H2SO4 = 10 mg/L | 8.81 | 3.7 | 8.43 | 170.8
H2SO4 = 20 mg/L | 8.24 | 7.4 | 7.57 | 160.6
H2SO4 = 25 mg/L | 7.81 | 8.2 | 7.37 | 155.5
H2SO4 = 30 mg/L | 7.56 | 9.1 | 7.23 | 150.4
H2SO4 = 40 mg/L | 7.19 | 8.9 | 7.01 | 140.2
H2SO4 = 50 mg/L | 6.98 | 8.9 | 6.85 | 130.0 (130 measured)
*This is the calculated amount of CO2 loss from a closed system pH to calculated the measured open system pH.

## Slide 9: Lucerne Water Co., Jar Test 1 - 8 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | H2SO4 mg/L | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 0 | 35 | 0.22 | 88.9 | 0.050 | 27.5 | 0.81
J2 | 25 | 35 | 0.23 | 89.8 | 0.046 | 33.3 | 0.83
J3 | 0 | 45 | 0.20 | 89.2 | 0.049 | 29.0 | 0.61
J4 | 25 | 45 | 0.11 | 90.4 | 0.043 | 37.7 | 0.33
J5 | 0 | 50 | 0.27 | 89.5 | 0.048 | 30.4 | 0.58
J6 | 25 | 50 | 0.19 | 90.7 | 0.042 | 39.1 | 0.50
J7 | 0 | 60 | 0.15 | 89.7 | 0.047 | 31.9 | 0.44
J8 | 25 | 60 | 0.10 | 91.0 | 0.040 | 42.0 | 0.28

## Slide 10: Lucerne Water Co., Jar Test 9 - 16 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar # | H2SO4 mg/L | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 0 | 60 | 0.17 | 89.1 | 0.050 | 27.5 | 0.43
J10 | 25 | 60 | 0.14 | 90.3 | 0.044 | 36.2 | 0.40
J11 | 0 | 70 | 0.14 | 89.2 | 0.049 | 29.0 | 0.41
J12 | 25 | 70 | 0.09 | 90.7 | 0.042 | 39.1 | 0.35
J13 | 0 | 70 | 0.20 | 89.3 | 0.049 | 29.0 | 0.51
J14 | 25 | 70 | 0.15 | 91.3 | 0.039 | 43.5 | 0.36
J15 | 0 | 80 | 0.19 | 89.5 | 0.048 | 30.4 | 0.46
J16 | 25 | 80 | 0.07 | 91.7 | 0.037 | 46.4 | 0.24

## Slide 11: Lucerne Water Co., Jar Test 17 - 24 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar # | H2SO4 mg/L | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J17 | 0 | 80 | 0.16 | 89.7 | 0.046 | 33.3 | 0.37
J18 | 15 | 80 | 0.11 | 90.7 | 0.042 | 39.1 | 0.31
J19 | 25 | 80 | 0.09 | 91.4 | 0.038 | 44.9 | 0.30
J20 | 35 | 80 | 0.07 | 91.7 | 0.037 | 46.4 | 0.26
J21 | 0 | 60 | 0.19 | 89.0 | 0.050 | 19.0 | 0.52
J22 | 25 | 60 | 0.11 | 90.6 | 0.042 | 39.1 | 0.42
J23 | 35 | 60 | 0.14 | 90.8 | 0.041 | 40.6 | 0.43
J24 | 45 | 60 | 0.08 | 91.1 | 0.040 | 42.0 | 0.37

## Slide 12: Jars 1-4 Test Post KMnO4 Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Acid (H2SO4) + Applied Coagulant 9800

## Slide 13: Jars 1-4: End of 5-minute flocculation (30 RPM) duration.
0 mg/L H2SO4
35 mg/L 9800
Filtrate 0.22 NTU
UVT: 88.9%
UVA: 0.050/cm
UVA Reduction 27.5%
Settled: 0.81 NTU
25 mg/L H2SO4
35 mg/L 9800
Filtrate 0.23 NTU
UVT: 89.8%
UVA: 0.046/cm
UVA Reduction 33.3%
Settled: 0.83 NTU
0 mg/L H2SO4
45 mg/L 9800
Filtrate 0.20 NTU
UVT: 89.2%
UVA: 0.049/cm
UVA Reduction 29.0%
Settled: 0.61 NTU
25 mg/L H2SO4
45 mg/L 9800
Filtrate 0.11 NTU
UVT: 90.4%
UVA: 0.043/cm
UVA Reduction 37.7%
Settled: 0.33 NTU

## Slide 14: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 15: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L H2SO4
35 mg/L 9800
Filtrate 0.22 NTU
UVT: 88.9%
UVA: 0.050/cm
UVA Reduction 27.5%
Settled: 0.81 NTU
25 mg/L H2SO4
35 mg/L 9800
Filtrate 0.23 NTU
UVT: 89.8%
UVA: 0.046/cm
UVA Reduction 33.3%
Settled: 0.83 NTU
0 mg/L H2SO4
45 mg/L 9800
Filtrate 0.20 NTU
UVT: 89.2%
UVA: 0.049/cm
UVA Reduction 29.0%
Settled: 0.61 NTU
25 mg/L H2SO4
45 mg/L 9800
Filtrate 0.11 NTU
UVT: 90.4%
UVA: 0.043/cm
UVA Reduction 37.7%
Settled: 0.33 NTU

## Slide 16: Jars 5-8 Test Post KMnO4 Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Acid (H2SO4) + Applied Coagulant 9800

## Slide 17: Jars 5-8: End of 5-minute flocculation (30 RPM) duration.
0 mg/L H2SO4
50 mg/L 9800
Filtrate 0.27 NTU
UVT: 89.5%
UVA: 0.048/cm
UVA Reduction 30.4%
Settled: 0.58 NTU
25 mg/L H2SO4
50 mg/L 9800
Filtrate 0.19 NTU
UVT: 90.7%
UVA: 0.042/cm
UVA Reduction 39.1%
Settled: 0.50 NTU
0 mg/L H2SO4
60 mg/L 9800
Filtrate 0.15 NTU
UVT: 89.7%
UVA: 0.047/cm
UVA Reduction 31.9%
Settled: 0.44 NTU
25 mg/L H2SO4
60 mg/L 9800
Filtrate 0.10 NTU
UVT: 91.0%
UVA: 0.040/cm
UVA Reduction 42.0%
Settled: 0.28 NTU

## Slide 18: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 19: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L H2SO4
50 mg/L 9800
Filtrate 0.27 NTU
UVT: 89.5%
UVA: 0.048/cm
UVA Reduction 30.4%
Settled: 0.58 NTU
25 mg/L H2SO4
50 mg/L 9800
Filtrate 0.19 NTU
UVT: 90.7%
UVA: 0.042/cm
UVA Reduction 39.1%
Settled: 0.50 NTU
0 mg/L H2SO4
60 mg/L 9800
Filtrate 0.15 NTU
UVT: 89.7%
UVA: 0.047/cm
UVA Reduction 31.9%
Settled: 0.44 NTU
25 mg/L H2SO4
60 mg/L 9800
Filtrate 0.10 NTU
UVT: 91.0%
UVA: 0.040/cm
UVA Reduction 42.0%
Settled: 0.28 NTU

## Slide 20: Jars 9-12 Test Post KMnO4 Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Acid (H2SO4) + Applied Coagulant 9800

## Slide 21: Jars 9-12: End of 5-minute flocculation (30 RPM) duration.
0 mg/L H2SO4
60 mg/L 9800
Filtrate 0.17 NTU
UVT: 89.1%
UVA: 0.050/cm
UVA Reduction 27.5%
Settled: 0.43 NTU
25 mg/L H2SO4
60 mg/L 9800
Filtrate 0.14 NTU
UVT: 90.3%
UVA: 0.044/cm
UVA Reduction 36.2%
Settled: 0.40 NTU
0 mg/L H2SO4
70 mg/L 9800
Filtrate 0.14 NTU
UVT: 89.2%
UVA: 0.049/cm
UVA Reduction 29.0%
Settled: 0.41 NTU
25 mg/L H2SO4
70 mg/L 9800
Filtrate 0.09 NTU
UVT: 90.7%
UVA: 0.042/cm
UVA Reduction 39.1%
Settled: 0.35 NTU

## Slide 22: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 23: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L H2SO4
60 mg/L 9800
Filtrate 0.17 NTU
UVT: 89.1%
UVA: 0.050/cm
UVA Reduction 27.5%
Settled: 0.43 NTU
25 mg/L H2SO4
60 mg/L 9800
Filtrate 0.14 NTU
UVT: 90.3%
UVA: 0.044/cm
UVA Reduction 36.2%
Settled: 0.40 NTU
0 mg/L H2SO4
70 mg/L 9800
Filtrate 0.14 NTU
UVT: 89.2%
UVA: 0.049/cm
UVA Reduction 29.0%
Settled: 0.41 NTU
25 mg/L H2SO4
70 mg/L 9800
Filtrate 0.09 NTU
UVT: 90.7%
UVA: 0.042/cm
UVA Reduction 39.1%
Settled: 0.35 NTU

## Slide 24: Jars 13-16 Test Post KMnO4 Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Acid (H2SO4) + Applied Coagulant 9800

## Slide 25: Jars 13-16: End of 5-minute flocculation (30 RPM) duration.
0 mg/L H2SO4
70 mg/L 9800
Filtrate 0.20 NTU
UVT: 89.3%
UVA: 0.049/cm
UVA Reduction 29.0%
Settled: 0.43 NTU
25 mg/L H2SO4
70 mg/L 9800
Filtrate 0.15 NTU
UVT: 90.3%
UVA: 0.039/cm
UVA Reduction 43.5%
Settled: 0.40 NTU
0 mg/L H2SO4
80 mg/L 9800
Filtrate 0.19 NTU
UVT: 89.2%
UVA: 0.048/cm
UVA Reduction 30.4%
Settled: 0.41 NTU
25 mg/L H2SO4
80 mg/L 9800
Filtrate 0.07 NTU
UVT: 90.7%
UVA: 0.037/cm
UVA Reduction 46.4%
Settled: 0.35 NTU

## Slide 26: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 27: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L H2SO4
70 mg/L 9800
Filtrate 0.20 NTU
UVT: 89.3%
UVA: 0.049/cm
UVA Reduction 29.0%
Settled: 0.43 NTU
25 mg/L H2SO4
70 mg/L 9800
Filtrate 0.15 NTU
UVT: 90.3%
UVA: 0.039/cm
UVA Reduction 43.5%
Settled: 0.40 NTU
0 mg/L H2SO4
80 mg/L 9800
Filtrate 0.19 NTU
UVT: 89.2%
UVA: 0.048/cm
UVA Reduction 30.4%
Settled: 0.41 NTU
25 mg/L H2SO4
80 mg/L 9800
Filtrate 0.07 NTU
UVT: 90.7%
UVA: 0.037/cm
UVA Reduction 46.4%
Settled: 0.35 NTU

## Slide 28: Jars 17-20 Test Post KMnO4 Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Acid (H2SO4) + Applied Coagulant 9800

## Slide 29: Jars 17-20: End of 5-minute flocculation (30 RPM) duration.
0 mg/L H2SO4
80 mg/L 9800
Filtrate 0.16 NTU
UVT: 89.7%
UVA: 0.046/cm
UVA Reduction 33.3%
Settled: 0.37 NTU
15 mg/L H2SO4
80 mg/L 9800
Filtrate 0.11 NTU
UVT: 90.7%
UVA: 0.042/cm
UVA Reduction 39.1%
Settled: 0.31 NTU
25 mg/L H2SO4
80 mg/L 9800
Filtrate 0.09 NTU
UVT: 91.4%
UVA: 0.038/cm
UVA Reduction 44.9%
Settled: 0.30 NTU
35 mg/L H2SO4
80 mg/L 9800
Filtrate 0.07 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction 46.4%
Settled: 0.26 NTU

## Slide 30: Jars 17-20: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 31: Jars 17-20: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L H2SO4
80 mg/L 9800
Filtrate 0.16 NTU
UVT: 89.7%
UVA: 0.046/cm
UVA Reduction 33.3%
Settled: 0.37 NTU
15 mg/L H2SO4
80 mg/L 9800
Filtrate 0.11 NTU
UVT: 90.7%
UVA: 0.042/cm
UVA Reduction 39.1%
Settled: 0.31 NTU
25 mg/L H2SO4
80 mg/L 9800
Filtrate 0.09 NTU
UVT: 91.4%
UVA: 0.038/cm
UVA Reduction 44.9%
Settled: 0.30 NTU
35 mg/L H2SO4
80 mg/L 9800
Filtrate 0.07 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction 46.4%
Settled: 0.26 NTU

## Slide 32: Jars 21-24 Test Post KMnO4 Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Acid (H2SO4) + Applied Coagulant 9800

## Slide 33: Jars 21-24: End of 5-minute flocculation (30 RPM) duration.
0 mg/L H2SO4
60 mg/L 9800
Filtrate 0.19 NTU
UVT: 89.0%
UVA: 0.050/cm
UVA Reduction 19.0%
Settled: 0.52 NTU
25 mg/L H2SO4
60 mg/L 9800
Filtrate 0.11 NTU
UVT: 90.6%
UVA: 0.042/cm
UVA Reduction 39.1%
Settled: 0.42 NTU
35 mg/L H2SO4
60 mg/L 9800
Filtrate 0.14 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction 40.6%
Settled: 0.43 NTU
45 mg/L H2SO4
60 mg/L 9800
Filtrate 0.08 NTU
UVT: 91.1%
UVA: 0.040/cm
UVA Reduction 42.0%
Settled: 0.37 NTU

## Slide 34: Jars 21-24: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 35: Jars 21-24: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L H2SO4
60 mg/L 9800
Filtrate 0.19 NTU
UVT: 89.0%
UVA: 0.050/cm
UVA Reduction 19.0%
Settled: 0.52 NTU
25 mg/L H2SO4
60 mg/L 9800
Filtrate 0.11 NTU
UVT: 90.6%
UVA: 0.042/cm
UVA Reduction 39.1%
Settled: 0.42 NTU
35 mg/L H2SO4
60 mg/L 9800
Filtrate 0.14 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction 40.6%
Settled: 0.43 NTU
45 mg/L H2SO4
60 mg/L 9800
Filtrate 0.08 NTU
UVT: 91.1%
UVA: 0.040/cm
UVA Reduction 42.0%
Settled: 0.37 NTU

## Slide 36: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 37: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 38: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 39: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 40: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 41: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732