## Slide 1: Lucerne Water Co., Cal Water Service CA1710005 Lake County Jar Test
by Guy Schott, P.E.
July 30, 2021

## Slide 2: Lucerne Water Co. Source Water: Clear Lake Conventional Treatment

## Slide 3: Lucerne Water Co. Characteristics July 30, 2021
Source
Turbidity: 7.9 NTU
UVT: 79.7%,
UVA: 0.098/cm
0.4 um Filtered
Turbidity: 0.5 NTU
UVT: 85.4%,
UVA: 0.068/cm

## Slide 4: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 5: Applied Coagulants for Jar Testing
Pro Pac 9800 (NTU Technologies)
50% Aluminum Chlorohydrate
50% Water
23.62% Al2O3
12.5% Al
83% Basicity
SG = 1.25-1.34
NSF limit: 250 mg/L as Product
10 mg/L as 9800 = Reduction 1.18 mg/L as CaCO3

## Slide 6: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 7: Lucerne Water Co., Source: Clear Lake Summary Highlights
Jar# | KMnO4 mg/L | H2SO4 mg/L | PAC mg/L | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
1 | 0 | 0 | 0 | 80 | 0.09 | 89.3 | 0.048 | 29.4 | 0.26
2 | 0.8 | 0 | 0 | 80 | 0.09 | 89.5 | 0.047 | 30.9 | 0.34
3 | 0.8 | 0 | 0 | 80 | 0.09 | 89.8 | 0.046 | 32.4 | 0.37
4 | 0.8 | 25 | 0 | 80 | 0.08 | 90.6 | 0.042 | 38.2 | 0.37
5 | 0.8 | 25 | 0 | 80 | 0.07 | 90.8 | 0.041 | 39.7 | 0.36
6 | 0.8 | 25 | 0 | 80 | 0.06 | 91.6 | 0.037 | 45.6 | 0.32
7 | 0.8 | 0 | 20 | 80 | 0.06 | 91.7 | 0.037 | 45.6 | 0.22
8 | 0.8 | 25 | 20 | 80 | 0.07 | 92.7 | 0.032 | 52.9 | 0.31
9 | 0.8 | 25 | 20 | 80 | 0.06 | 92.7 | 0.032 | 52.9 | 0.31
10 | 0.8 | 25 | 20 | 80 | 0.06 | 93.2 | 0.030 | 55.9 | 0.39

## Slide 8: Lucerne Water Co., Jar Test 1 - 4 Results Flash Mix 200 RPM (30 sec); Floc Mix 20 RPM (15 min)
Jar# | KMnO4 mg/L | *PAC mg/L | H2SO4 mg/L | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 0 | 0 | 0 | 80 | 0.16 | 88.8 | 0.051 | 25.0 | 0.70
J2 | 0 | 10 | 0 | 80 | 0.32 | 89.1 | 0.049 | 27.9 | 0.90
J3 | 0 | 15 | 0 | 80 | 0.31 | 89.8 | 0.046 | 32.4 | 0.97
J4 | 0 | 20 | 0 | 80 | 0.28 | 89.7 | 0.046 | 32.4 | 0.72
*It is suspected that PAC was not well mixed when added resulting in poor removal of DOC
Notes:
PAC added first and then floc for 2 minutes at 20 RPM
Coagulants were added then flash mix for 30 seconds at 200 RPM
Flocculation for 15 minutes at 20 RPM

## Slide 9: Lucerne Water Co., Jar Test 5 - 8 Results Flash Mix 200 RPM (30 sec); Floc Mix 20 RPM (15 min)
Jar# | KMnO4 mg/L | H2SO4 mg/L | *PAC mg/L | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J5 | 0 | 25 | 0 | 80 | 0.12 | 90.3 | 0.044 | 35.3 | 0.40
J6 | 0 | 25 | 10 | 80 | 0.19 | 91.2 | 0.039 | 42.6 | 0.58
J7 | 0 | 25 | 15 | 80 | 0.20 | 91.0 | 0.040 | 41.2 | 0.61
J8 | 0 | 20 | 20 | 80 | 0.18 | 90.4 | 0.043 | 36.8 | 0.52
*It is suspected that PAC was not well mixed when added resulting poor removal of DOC
Notes:
H2SO4 followed by PAC were added first and then floc for 2 minutes at 20 RPM
Coagulants were added then flash mix for 30 seconds at 200 RPM
Flocculation for 15 minutes at 20 RPM

## Slide 10: Lucerne Water Co., Jar Test 9 - 12 Results Flash Mix 200 RPM (30 sec); Floc Mix 20 RPM (15 min)
Jar# | KMnO4 mg/L | H2SO4 mg/L | *PAC mg/L | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 0 | 25 | 0 | 80 | 0.13 | 90.2 | 0.044 | 35.3 | 0.38
J10 | 0 | 25 | 10 | 80 | 0.13 | 91.2 | 0.039 | 42.6 | 0.71
J11 | 0 | 25 | 15 | 80 | 0.12 | 91.7 | 0.037 | 45.6 | 0.59
J12 | 0 | 20 | 20 | 80 | 0.09 | 92.1 | 0.035 | 48.5 | 0.42
*PAC was well mixed when added compared to previous results resulting in good reduction of indirect DOC
Notes:
H2SO4 followed by PAC were added first and then floc for 2 minutes at 20 RPM
Coagulants were added then flash mix for 30 seconds at 200 RPM
Flocculation for 15 minutes at 20 RPM

## Slide 11: Lucerne Water Co., Jar Test 13 - 16 Results Flash Mix 200 RPM (30 sec); Floc Mix 20 RPM (15 min)
Jar# | KMnO4 mg/L | H2SO4 mg/L | 9800 mg/L | PAC mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J13 | 0 | 25 | 80 | 0 | 0.19 | 90.4 | 0.043 | 36.8 | 0.39
J14 | 0 | 25 | 80 | 10 | 0.12 | 91.4 | 0.039 | 42.6 | 0.90
J15 | 0 | 25 | 80 | 15 | 0.18 | 91.9 | 0.036 | 47.1 | 1.28
J16 | 0 | 20 | 80 | 20 | 0.17 | 92.0 | 0.036 | 47.1 | 1.87
Notes:
H2SO4 added first followed by coagulants then PAC
Flash mix for 30 seconds at 200 RPM
Flocculation for 15 minutes at 20 RPM

## Slide 12: Lucerne Water Co., Jar Test 17 - 20 Results Flash Mix 200 RPM (30 sec); Floc Mix 20 RPM (15 min)
Jar# | KMnO4 mg/L | H2SO4 mg/L | PAC mg/L | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J17 | 0.8 | 25 | 0 | 80 | 0.06 | 91.2 | 0.039 | 42.6 | 0.40
J18 | 0.8 | 25 | 10 | 80 | 0.07 | 92.2 | 0.035 | 48.5 | 0.33
J19 | 0.8 | 25 | 15 | 80 | 0.06 | 92.8 | 0.032 | 52.9 | 0.41
J20 | 0.8 | 20 | 20 | 80 | 0.06 | 93.2 | 0.030 | 55.9 | 0.37
Notes:
KMnO4 added first followed by flocculation for 2 minutes at 20 RPM
Added: H2SO4 followed by PAC and then coagulants
Flash mix for 30 seconds at 200 RPM
Flocculation for 15 minutes at 20 RPM

## Slide 13: Lucerne Water Co., Jar Test 21 - 24 Results Flash Mix 200 RPM (30 sec); Floc Mix 20 RPM (15 min)
Jar# | KMnO4 mg/L | H2SO4 mg/L | PAC mg/L | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J21 | 0.8 | 0 | 0 | 80 | 0.09 | 89.8 | 0.046 | 32.4 | 0.37
J22 | 0.8 | 25 | 0 | 80 | 0.06 | 91.6 | 0.037 | 45.6 | 0.32
J23 | 0.8 | 25 | 20 | 80 | 0.06 | 93.2 | 0.030 | 55.9 | 0.39
J24 | 0.8 | 20 | 20 | 80 | 0.07 | 93.1 | 0.030 | 55.9 | 0.99
Jar 24 – 9800 was added first followed by PAC. Settled water increased significantly.
Notes:
KMnO4 added first followed by flocculation for 2 minutes at 20 RPM
Added: H2SO4 to Jars 2-3, followed by PAC to Jar 3 only.
Add coagulants to Jars 1 – 4, followed by PAC to Jar 4.
Flash mix for 30 seconds at 200 RPM
Flocculation for 15 minutes at 20 RPM

## Slide 14: Lucerne Water Co., Jar Test 25 - 28 Results Flash Mix 200 RPM (30 sec); Floc Mix 20 RPM (15 min)
Jar# | KMnO4 mg/L | H2SO4 mg/L | PAC mg/L | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J25 | 0 | 0 | 0 | 80 | 0.09 | 89.3 | 0.048 | 29.4 | 0.26
J26 | 0.8 | 0 | 0 | 80 | 0.09 | 89.5 | 0.047 | 30.9 | 0.34
J27 | 0.8 | 25 | 0 | 80 | 0.08 | 90.6 | 0.042 | 38.2 | 0.37
J28 | 0.8 | 25 | 20 | 80 | 0.07 | 92.7 | 0.032 | 52.9 | 0.31
Notes:
KMnO4 added first followed by flocculation for 2 minutes at 20 RPM
Added: H2SO4 followed by PAC and then coagulants
Flash mix for 30 seconds at 200 RPM
Flocculation for 15 minutes at 20 RPM

## Slide 15: Lucerne Water Co., Jar Test 29 - 32 Results Flash Mix 200 RPM (30 sec); Floc Mix 20 RPM (15 min)
Jar# | KMnO4 mg/L | H2SO4 mg/L | PAC mg/L | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J29 | 0.8 | 25 | 0 | 80 | 0.07 | 90.8 | 0.041 | 39.7 | 0.36
J30 | 0.8 | 25 | 0 | 80 | 0.06 | 90.7 | 0.041 | 39.7 | 0.29
J31 | 0.8 | 25 | 20 | 80 | 0.06 | 92.7 | 0.032 | 52.9 | 0.31
J32 | 0.8 | 0 | 20 | 80 | 0.06 | 91.7 | 0.037 | 45.6 | 0.22
Notes:
KMnO4 added first followed by flocculation for 2 minutes at 20 RPM
Add H2SO4 to Jars 1 and 3; Add PAC to Jars 3 and 4
Add coagulant to Jars 1-4
Add H2SO4 to Jars 1
Flash mix for 30 seconds at 200 RPM; Flocculation for 15 minutes at 20 RPM

## Slide 16: Jars 1-4 Test Flash Mix 30 Sec (200 RPM) Floc Mix 15 min (20 RPM) Applied PAC + Applied Coagulant 9800

## Slide 17: Jars 1-4: End of 15-minute flocculation (20 RPM) duration.
0 mg/L KMnO4
0 mg/L H2SO4
0 mg/L PAC
80 mg/L 9800
Filtrate 0.16 NTU
UVT: 89.0%
UVA: 0.051/cm
UVA Reduction 25.0%
Settled: 0.70 NTU
0 mg/L KMnO4
0 mg/L H2SO4
10 mg/L PAC
80 mg/L 9800
Filtrate 0.32 NTU
UVT: 89.1%
UVA: 0.049/cm
UVA Reduction 27.9%
Settled: 0.90 NTU
0 mg/L KMnO4
0 mg/L H2SO4
15 mg/L PAC
80 mg/L 9800
Filtrate 0.31 NTU
UVT: 89.8%
UVA: 0.046/cm
UVA Reduction 32.4%
Settled: 0.97 NTU
0 mg/L KMnO4
0 mg/L H2SO4
20 mg/L PAC
80 mg/L 9800
Filtrate 0.28 NTU
UVT: 89.7%
UVA: 0.046/cm
UVA Reduction 32.4%
Settled: 0.72 NTU

## Slide 18: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 19: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L KMnO4
0 mg/L H2SO4
0 mg/L PAC
80 mg/L 9800
Filtrate 0.16 NTU
UVT: 89.0%
UVA: 0.051/cm
UVA Reduction 25.0%
Settled: 0.70 NTU
0 mg/L KMnO4
0 mg/L H2SO4
10 mg/L PAC
80 mg/L 9800
Filtrate 0.32 NTU
UVT: 89.1%
UVA: 0.049/cm
UVA Reduction 27.9%
Settled: 0.90 NTU
0 mg/L KMnO4
0 mg/L H2SO4
15 mg/L PAC
80 mg/L 9800
Filtrate 0.31 NTU
UVT: 89.8%
UVA: 0.046/cm
UVA Reduction 32.4%
Settled: 0.97 NTU
0 mg/L KMnO4
0 mg/L H2SO4
20 mg/L PAC
80 mg/L 9800
Filtrate 0.28 NTU
UVT: 89.7%
UVA: 0.046/cm
UVA Reduction 32.4%
Settled: 0.72 NTU

## Slide 20: Jars 5-8 Test Flash Mix 30 Sec (200 RPM) Floc Mix 15 min (20 RPM) Applied PAC + Acid (H2SO4) + Applied Coagulant 9800

## Slide 21: Jars 5-8: End of 15-minute flocculation (20 RPM) duration.
0 mg/L KMnO4
25 mg/L H2SO4
0 mg/L PAC
80 mg/L 9800
Filtrate 0.12 NTU
UVT: 90.3%
UVA: 0.044/cm
UVA Reduction 35.3%
Settled: 0.40 NTU
0 mg/L KMnO4
25 mg/L H2SO4
10 mg/L PAC
80 mg/L 9800
Filtrate 0.19 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 42.6%
Settled: 0.58 NTU
0 mg/L KMnO4
25 mg/L H2SO4
15 mg/L PAC
80 mg/L 9800
Filtrate 0.20 NTU
UVT: 91.0%
UVA: 0.040/cm
UVA Reduction 41.2%
Settled: 0.61 NTU
0 mg/L KMnO4
25 mg/L H2SO4
20 mg/L PAC
80 mg/L 9800
Filtrate 0.18 NTU
UVT: 90.4%
UVA: 0.043/cm
UVA Reduction 36.8%
Settled: 0.52 NTU

## Slide 22: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 23: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L KMnO4
25 mg/L H2SO4
0 mg/L PAC
80 mg/L 9800
Filtrate 0.12 NTU
UVT: 90.3%
UVA: 0.044/cm
UVA Reduction 35.3%
Settled: 0.40 NTU
0 mg/L KMnO4
25 mg/L H2SO4
10 mg/L PAC
80 mg/L 9800
Filtrate 0.19 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 42.6%
Settled: 0.58 NTU
0 mg/L KMnO4
25 mg/L H2SO4
15 mg/L PAC
80 mg/L 9800
Filtrate 0.20 NTU
UVT: 91.0%
UVA: 0.040/cm
UVA Reduction 41.2%
Settled: 0.61 NTU
0 mg/L KMnO4
25 mg/L H2SO4
20 mg/L PAC
80 mg/L 9800
Filtrate 0.18 NTU
UVT: 90.4%
UVA: 0.043/cm
UVA Reduction 36.8%
Settled: 0.52 NTU

## Slide 24: Jars 9-12 Test Flash Mix 30 Sec (200 RPM) Floc Mix 15 min (20 RPM) Applied PAC + Acid (H2SO4) + Applied Coagulant 9800

## Slide 25: Jars 9-12: End of 15-minute flocculation (20 RPM) duration.
0 mg/L KMnO4
25 mg/L H2SO4
0 mg/L PAC
80 mg/L 9800
Filtrate 0.13 NTU
UVT: 90.2%
UVA: 0.044/cm
UVA Reduction 35.3%
Settled: 0.38 NTU
0 mg/L KMnO4
25 mg/L H2SO4
10 mg/L PAC
80 mg/L 9800
Filtrate 0.13 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 42.6%
Settled: 0.71 NTU
0 mg/L KMnO4
25 mg/L H2SO4
15 mg/L PAC
80 mg/L 9800
Filtrate 0.12 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction 45.6%
Settled: 0.59 NTU
0 mg/L KMnO4
25 mg/L H2SO4
20 mg/L PAC
80 mg/L 9800
Filtrate 0.09 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction 48.5%
Settled: 0.42 NTU

## Slide 26: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 27: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L KMnO4
25 mg/L H2SO4
0 mg/L PAC
80 mg/L 9800
Filtrate 0.13 NTU
UVT: 90.2%
UVA: 0.044/cm
UVA Reduction 35.3%
Settled: 0.38 NTU
0 mg/L KMnO4
25 mg/L H2SO4
10 mg/L PAC
80 mg/L 9800
Filtrate 0.13 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 42.6%
Settled: 0.71 NTU
0 mg/L KMnO4
25 mg/L H2SO4
15 mg/L PAC
80 mg/L 9800
Filtrate 0.12 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction 45.6%
Settled: 0.59 NTU
0 mg/L KMnO4
25 mg/L H2SO4
20 mg/L PAC
80 mg/L 9800
Filtrate 0.09 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction 48.5%
Settled: 0.42 NTU

## Slide 28: Jars 13-16 Test Flash Mix 30 Sec (200 RPM) Floc Mix 15 min (20 RPM) Applied PAC + Acid (H2SO4) + Applied Coagulant 9800

## Slide 29: Jars 13-16: End of 15-minute flocculation (20 RPM) duration.
0 mg/L KMnO4
25 mg/L H2SO4
80 mg/L 9800
0 mg/L PAC
Filtrate 0.19 NTU
UVT: 90.4%
UVA: 0.043/cm
UVA Reduction 36.8%
Settled: 0.39 NTU
0 mg/L KMnO4
25 mg/L H2SO4
80 mg/L 9800
10 mg/L PAC
Filtrate 0.12 NTU
UVT: 91.4%
UVA: 0.039/cm
UVA Reduction 42.6%
Settled: 0.90 NTU
0 mg/L KMnO4
25 mg/L H2SO4
80 mg/L 9800
15 mg/L PAC
Filtrate 0.18 NTU
UVT: 91.8%
UVA: 0.036/cm
UVA Reduction 47.1%
Settled: 1.28 NTU
0 mg/L KMnO4
25 mg/L H2SO4
80 mg/L 9800
20 mg/L PAC
Filtrate 0.17 NTU
UVT: 92.0%
UVA: 0.035/cm
UVA Reduction 47.1%
Settled: 1.87 NTU

## Slide 30: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 31: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L KMnO4
25 mg/L H2SO4
80 mg/L 9800
0 mg/L PAC
Filtrate 0.19 NTU
UVT: 90.4%
UVA: 0.043/cm
UVA Reduction 36.8%
Settled: 0.39 NTU
0 mg/L KMnO4
25 mg/L H2SO4
80 mg/L 9800
10 mg/L PAC
Filtrate 0.12 NTU
UVT: 91.4%
UVA: 0.039/cm
UVA Reduction 42.6%
Settled: 0.90 NTU
0 mg/L KMnO4
25 mg/L H2SO4
80 mg/L 9800
15 mg/L PAC
Filtrate 0.18 NTU
UVT: 91.8%
UVA: 0.036/cm
UVA Reduction 47.1%
Settled: 1.28 NTU
0 mg/L KMnO4
25 mg/L H2SO4
80 mg/L 9800
20 mg/L PAC
Filtrate 0.17 NTU
UVT: 92.0%
UVA: 0.035/cm
UVA Reduction 47.1%
Settled: 1.87 NTU

## Slide 32: Jars 17-20 Test Flash Mix 30 Sec (200 RPM) Floc Mix 15 min (20 RPM) Applied KMnO4 + Applied PAC + Acid (H2SO4) + Applied Coagulant 9800

## Slide 33: Jars 17-20: End of 15-minute flocculation (20 RPM) duration.
0.8 mg/L KMnO4
25 mg/L H2SO4
0 mg/L PAC
80 mg/L 9800
Filtrate 0.06 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 42.6%
Settled: 0.40 NTU
0.8 mg/L KMnO4
25 mg/L H2SO4
10 mg/L PAC
80 mg/L 9800
Filtrate 0.07 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction 48.5%
Settled: 0.33 NTU
0.8 mg/L KMnO4
25 mg/L H2SO4
15 mg/L PAC
80 mg/L 9800
Filtrate 0.06 NTU
UVT: 92.8%
UVA: 0.032/cm
UVA Reduction 52.9%
Settled: 0.41 NTU
0.8 mg/L KMnO4
25 mg/L H2SO4
20 mg/L PAC
80 mg/L 9800
Filtrate 0.06 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction 55.9%
Settled: 0.37 NTU

## Slide 34: Jars 17-20: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 35: Jars 17-20: After 25-minutes of settling, settled water turbidity is taken.
0.8 mg/L KMnO4
25 mg/L H2SO4
0 mg/L PAC
80 mg/L 9800
Filtrate 0.06 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 42.6%
Settled: 0.40 NTU
0.8 mg/L KMnO4
25 mg/L H2SO4
10 mg/L PAC
80 mg/L 9800
Filtrate 0.07 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction 48.5%
Settled: 0.33 NTU
0.8 mg/L KMnO4
25 mg/L H2SO4
15 mg/L PAC
80 mg/L 9800
Filtrate 0.06 NTU
UVT: 92.8%
UVA: 0.032/cm
UVA Reduction 52.9%
Settled: 0.41 NTU
0.8 mg/L KMnO4
25 mg/L H2SO4
20 mg/L PAC
80 mg/L 9800
Filtrate 0.06 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction 55.9%
Settled: 0.37 NTU

## Slide 36: Jars 21-24 Test Flash Mix 30 Sec (200 RPM) Floc Mix 15 min (20 RPM) Applied KMnO4 + Applied PAC + Acid (H2SO4) + Applied Coagulant 9800

## Slide 37: Jars 21-24: End of 15-minute flocculation (20 RPM) duration.
0.8 mg/L KMnO4
0 mg/L H2SO4
0 mg/L PAC
80 mg/L 9800
Filtrate 0.09 NTU
UVT: 89.8%
UVA: 0.046/cm
UVA Reduction 32.4%
Settled: 0.37 NTU
0.8 mg/L KMnO4
25 mg/L H2SO4
0 mg/L PAC
80 mg/L 9800
Filtrate 0.06 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction 45.6%
Settled: 0.32 NTU
0.8 mg/L KMnO4
25 mg/L H2SO4
20 mg/L PAC
80 mg/L 9800
Filtrate 0.06 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction 55.9%
Settled: 0.39 NTU
0.8 mg/L KMnO4
25 mg/L H2SO4
80 mg/L 9800
20 mg/L PAC
Filtrate 0.07 NTU
UVT: 93.1%
UVA: 0.030/cm
UVA Reduction 55.9%
Settled: 0.99 NTU

## Slide 38: Jars 21-24: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 39: Jars 21-24: After 25-minutes of settling, settled water turbidity is taken.
0.8 mg/L KMnO4
0 mg/L H2SO4
0 mg/L PAC
80 mg/L 9800
Filtrate 0.09 NTU
UVT: 89.8%
UVA: 0.046/cm
UVA Reduction 32.4%
Settled: 0.37 NTU
0.8 mg/L KMnO4
25 mg/L H2SO4
0 mg/L PAC
80 mg/L 9800
Filtrate 0.06 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction 45.6%
Settled: 0.32 NTU
0.8 mg/L KMnO4
25 mg/L H2SO4
20 mg/L PAC
80 mg/L 9800
Filtrate 0.06 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction 55.9%
Settled: 0.39 NTU
0.8 mg/L KMnO4
25 mg/L H2SO4
80 mg/L 9800
20 mg/L PAC
Filtrate 0.07 NTU
UVT: 93.1%
UVA: 0.030/cm
UVA Reduction 55.9%
Settled: 0.99 NTU

## Slide 40: Jars 25-28 Test Flash Mix 30 Sec (200 RPM) Floc Mix 15 min (20 RPM) Applied KMnO4 + Applied PAC + Acid (H2SO4) + Applied Coagulant 9800

## Slide 41: Jars 25-28: End of 15-minute flocculation (20 RPM) duration.
0 mg/L KMnO4
0 mg/L H2SO4
0 mg/L PAC
80 mg/L 9800
Filtrate 0.09 NTU
UVT: 89.3%
UVA: 0.048/cm
UVA Reduction 29.4%
Settled: 0.26 NTU
0.8 mg/L KMnO4
0 mg/L H2SO4
0 mg/L PAC
80 mg/L 9800
Filtrate 0.09 NTU
UVT: 89.5%
UVA: 0.047/cm
UVA Reduction 30.9%
Settled: 0.34 NTU
0.8 mg/L KMnO4
25 mg/L H2SO4
0 mg/L PAC
80 mg/L 9800
Filtrate 0.08 NTU
UVT: 90.6%
UVA: 0.042/cm
UVA Reduction 38.2%
Settled: 0.37 NTU
0.8 mg/L KMnO4
25 mg/L H2SO4
20 mg/L PAC
80 mg/L 9800
Filtrate 0.07 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction 52.9%
Settled: 0.31 NTU

## Slide 42: Jars 25-28: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 43: Jars 25-28: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L KMnO4
0 mg/L H2SO4
0 mg/L PAC
80 mg/L 9800
Filtrate 0.09 NTU
UVT: 89.3%
UVA: 0.048/cm
UVA Reduction 29.4%
Settled: 0.26 NTU
0.8 mg/L KMnO4
0 mg/L H2SO4
0 mg/L PAC
80 mg/L 9800
Filtrate 0.09 NTU
UVT: 89.5%
UVA: 0.047/cm
UVA Reduction 30.9%
Settled: 0.34 NTU
0.8 mg/L KMnO4
25 mg/L H2SO4
0 mg/L PAC
80 mg/L 9800
Filtrate 0.08 NTU
UVT: 90.6%
UVA: 0.042/cm
UVA Reduction 38.2%
Settled: 0.37 NTU
0.8 mg/L KMnO4
25 mg/L H2SO4
20 mg/L PAC
80 mg/L 9800
Filtrate 0.07 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction 52.9%
Settled: 0.31 NTU

## Slide 44: Jars 29-32 Test Flash Mix 30 Sec (200 RPM) Floc Mix 15 min (20 RPM) Applied KMnO4 + Applied PAC + Acid (H2SO4) + Applied Coagulant 9800

## Slide 45: Jars 29-32: End of 15-minute flocculation (20 RPM) duration.
0.8 mg/L KMnO4
25 mg/L H2SO4
0 mg/L PAC
80 mg/L 9800
Filtrate 0.07 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction 39.7%
Settled: 0.36 NTU
0.8 mg/L KMnO4
0 mg/L PAC
80 mg/L 9800
25 mg/L H2SO4
Filtrate 0.06 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction 39.7%
Settled: 0.29 NTU
0.8 mg/L KMnO4
25 mg/L H2SO4
20 mg/L PAC
80 mg/L 9800
Filtrate 0.06 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction 52.9%
Settled: 0.31 NTU
0.8 mg/L KMnO4
0 mg/L H2SO4
20 mg/L PAC
80 mg/L 9800
Filtrate 0.06 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction 45.6%
Settled: 0.22 NTU

## Slide 46: Jars 29-32: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 47: Jars 29-32: After 25-minutes of settling, settled water turbidity is taken.
0.8 mg/L KMnO4
25 mg/L H2SO4
0 mg/L PAC
80 mg/L 9800
Filtrate 0.07 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction 39.7%
Settled: 0.36 NTU
0.8 mg/L KMnO4
0 mg/L PAC
80 mg/L 9800
25 mg/L H2SO4
Filtrate 0.06 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction 39.7%
Settled: 0.29 NTU
0.8 mg/L KMnO4
25 mg/L H2SO4
20 mg/L PAC
80 mg/L 9800
Filtrate 0.06 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction 52.9%
Settled: 0.31 NTU
0.8 mg/L KMnO4
0 mg/L H2SO4
20 mg/L PAC
80 mg/L 9800
Filtrate 0.06 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction 45.6%
Settled: 0.22 NTU

## Slide 48: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 49: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 50: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 51: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 52: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 53: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732