## Slide 1: Konocti County Water District CA1710006, Lake County, Jar Test
by Guy Schott, P.E. September 22, 2020

## Slide 2: Konocti County Water District Source Water: Clear Lake Conventional Treatment

## Slide 3: Konocti CWD, September 21, 2020 Source Water Characteristics
Source (evening)
pH: 8.62
Turbidity: 25.5 NTU
UVT: 70.68%
UVA: 0.1507/cm
0.4 um Filtered
Turbidity: 1.31 NTU
UVT: 82.378%
UVA: 0.0843/cm
Using the P300 UVT/UVA analyzer; calibrated with DI water.
0.4 um Filtered
Turbidity: 1.44 NTU
UVT: 80.9%
UVA: 0.091/cm
Using the P200 UVT/UVA analyzer; calibrated with Organic free water.

## Slide 4: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 5: Applied Coagulants for Jar Testing
Pro Pac 9800 (NTU Technologies)
50% Aluminum Chlorohydrate
50% Water
23.62% Al2O3
83% Basicity
SG = 1.34
Pro Pac 9890 (NTU Technologies)
35-45% Aluminum Chlorohydrate
20% Trade Secret
35-45% Water
SG = 1.25-1.34
BWS, Inc.
Advanced Coagulant
AdvFloc-CTC-00011
12.55% Al2O3
64.9% Basicity
SG = 1.299

## Slide 6: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 8.62
LCA #1:
9800: 68.5 mg/L as product
pH adjusted to 7.5 w/acetic acid solution

## Slide 7: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 8: Konocti CWD: Jar Test 1-4 Results Clear Lake Source Water Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 minutes)
Jar # | H2SO4 mg/L | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 0 | 69 | 0.20 | 91.86 | 0.0369 | 56.2 | 4.0
J2 | 25 | 69 | 0.12 | 92.52 | 0.0338 | 59.9 | 2.44
J3 | 0 | 75 | 0.12 | 92.47 | 0.0340 | 59.7 | 2.76
J4 | 25 | 75 | 0.13 | 92.96 | 0.0317 | 62.4 | 0.64

## Slide 9: Konocti CWD: Jar Test 5-8 Results Clear Lake Source Water Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 minutes)
Jar # | 9890 mg/L | 9800 mg/L | Adv. Coag. mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J5 | 70 | 3.5 | 0 | 0.08 | 92.24 | 0.0351 | 58.6 | 1.25
J6 | 75 | 3.75 | 0 | 0.08 | 92.20 | 0.0353 | 58.1 | 0.39
J7 | 80 | 4.0 | 0 | 0.10 | 92.32 | 0.0347 | 58.8 | 0.70
J8 | 0 | 0 | 220 | 0.18 | 92.27 | 0.0350 | 58.5 | 6.8

## Slide 10: Konocti CWD: Jar Test 9-12 Results Clear Lake Source Water Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 minutes)
Jar # | NaOCl mg/L | 9890 mg/L | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 0 | 3.5 | 70 | 0.13 | 92.13 | 0.0356 | 57.8 | 2.95
J10 | 0 | 3.75 | 75 | 0.12 | 92.01 | 0.0362 | 57.1 | 3.2
J11 | 2.0 | 3.5 | 70 | 0.12 | 90.97 | 0.0411 | 51.2 | 5.3
J12 | 2.0 | 3.75 | 75 | 0.15 | 90.99 | 0.0410 | 51.4 | 7.0

## Slide 11: Konocti CWD: Jar Test 13-15 Results Clear Lake Source Water Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 minutes) Jar 15: NaOCl = 5.0 mg/L
Jar # | Adv Coag. mg/L | 9800 mg/L | 9890 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J13 | 140 | 0 | 0 | 0.13 | 91.87 | 0.0368 | 56.3 | 4.4
J14 | 150 | 0 | 0 | 0.20 | 92.13 | 0.0356 | 57.8 | 1.5
J15 | 0 | 70 | 3.5 | 0.15 | 90.99 | 0.0410 | 51.7 | 7.0

## Slide 12: Konocti CWD: Jar Test 16-23 Results Clear Lake Source Water Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 minutes)
Jar # | 9890 mg/L | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J16 | 70 | 3.5 | 0.10 | 92.5 | 0.033 | 63.7 | 0.87
J17 | 75 | 3.75 | 0.10 | 92.4 | 0.034 | 62.6 | 0.43
J18 | 70 | 0 | 0.09 | 92.3 | 0.034 | 62.6 | 0.33
J19 | 75 | 0 | 0.09 | 92.2 | 0.034 | 62.6 | 0.31
J20 | 55 | 0 | 0.08 | 92.2 | 0.035 | 61.5 | 0.31
J21 | 60 | 0 | 0.08 | 92.1 | 0.035 | 61.5 | 0.34
J22 | 65 | 0 | 0.07 | 92.1 | 0.035 | 61.5 | 0.54
J23 | 70 | 0 | 0.08 | 92.0 | 0.036 | 60.4 | 0.66

## Slide 13: Konocti CWD: Jar Test 24-27 Results Clear Lake Source Water Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 minutes)
Jar # | NaOCl mg/L | 9890 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J24 | 0 | 45 | 0.09 | 91.9 | 0.036 | 60.4 | 0.55
J25 | 0 | 50 | 0.08 | 91.9 | 0.036 | 60.4 | 0.33
J26 | 0 | 55 | 0.08 | 92.0 | 0.035 | 61.5 | 0.39
J27 | 2.0 | 55 | 0.08 | 91.7 | 0.037 | 59.3 | 0.29

## Slide 14: No Photos Available Jars 1-4 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9800

## Slide 15: Jars 5-8 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants 9800/9890 Advanced Coagulant

## Slide 16: Jars 5-8: End of 5-minute flocculation (30 RPM) duration.
70 mg/L 9890
3.5 mg/L 9800
Filtrate 0.08 NTU
UVT: 92.24%
UVA: 0.0351/cm
UVA Reduction: 58.6%
Settled: 1.25 NTU
75 mg/L 9890
3.75 mg/L 9800
Filtrate 0.08 NTU
UVT: 92.20%
UVA: 0.0353/cm
UVA Reduction: 58.1%
Settled: 0.39 NTU
80 mg/L 9890
4.0 mg/L 9800
Filtrate 0.10 NTU
UVT: 92.32%
UVA: 0.0347/cm
UVA Reduction: 58.8%
Settled: 0.70 NTU
220 mg/L Adv. Coag.
Filtrate 0.18 NTU
UVT: 92.27%
UVA: 0.0350/cm
UVA Reduction: 58.5%
Settled: 6.8 NTU

## Slide 17: Jars 6-10: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 18: Jars 6-10: After 25-minutes of settling, settled water turbidity is taken.
70 mg/L 9890
3.5 mg/L 9800
Filtrate 0.08 NTU
UVT: 92.24%
UVA: 0.0351/cm
UVA Reduction: 58.6%
Settled: 1.25 NTU
75 mg/L 9890
3.75 mg/L 9800
Filtrate 0.08 NTU
UVT: 92.20%
UVA: 0.0353/cm
UVA Reduction: 58.1%
Settled: 0.39 NTU
80 mg/L 9890
4.0 mg/L 9800
Filtrate 0.10 NTU
UVT: 92.32%
UVA: 0.0347/cm
UVA Reduction: 58.8%
Settled: 0.70 NTU
220 mg/L Adv. Coag.
Filtrate 0.18 NTU
UVT: 92.27%
UVA: 0.0350/cm
UVA Reduction: 58.5%
Settled: 6.8 NTU

## Slide 19: Jars 9-12 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) w/NaOCl Applied Coagulants 9800/9890

## Slide 20: Jars 9-12: End of 5-minute flocculation (30 RPM) duration.
0 mg/L NaOCl
70 mg/L 9800
3.5 mg/L 9890
Filtrate 0.13 NTU
UVT: 92.13%
UVA: 0.0356/cm
UVA Reduction: 57.8%
Settled: 2.95 NTU
0 mg/L NaOCl
75 mg/L 9800
3.75 mg/L 9890
Filtrate 0.12 NTU
UVT: 92.01%
UVA: 0.0362/cm
UVA Reduction: 57.1%
Settled: 3.2 NTU
2.0 mg/L NaOCl
70 mg/L 9800
3.5 mg/L 9890
Filtrate 0.12 NTU
UVT: 90.97%
UVA: 0.0411/cm
UVA Reduction: 51.2%
Settled: 5.3 NTU
2.0 mg/L NaOCl
75 mg/L 9800
3.75 mg/L 9890
Filtrate 0.15 NTU
UVT: 90.97%
UVA: 0.0410/cm
UVA Reduction: 51.4%
Settled: 7.0 NTU

## Slide 21: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 22: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L NaOCl
70 mg/L 9800
3.5 mg/L 9890
Filtrate 0.13 NTU
UVT: 92.13%
UVA: 0.0356/cm
UVA Reduction: 57.8%
Settled: 2.95 NTU
0 mg/L NaOCl
75 mg/L 9800
3.75 mg/L 9890
Filtrate 0.12 NTU
UVT: 92.01%
UVA: 0.0362/cm
UVA Reduction: 57.1%
Settled: 3.2 NTU
2.0 mg/L NaOCl
70 mg/L 9800
3.5 mg/L 9890
Filtrate 0.12 NTU
UVT: 90.97%
UVA: 0.0411/cm
UVA Reduction: 51.2%
Settled: 5.3 NTU
2.0 mg/L NaOCl
75 mg/L 9800
3.75 mg/L 9890
Filtrate 0.15 NTU
UVT: 90.97%
UVA: 0.0410/cm
UVA Reduction: 51.4%
Settled: 7.0 NTU

## Slide 23: Jars 13-15 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) w/NaOCl Applied Coagulants Adv Coag./9800/9890

## Slide 24: Jars 13-15: End of 5-minute flocculation (30 RPM) duration.
0 mg/L NaOCl
140 mg/L Adv Coag.
Filtrate 0.13 NTU
UVT: 91.87%
UVA: 0.0368/cm
UVA Reduction: 56.3%
Settled: 4.4 NTU
5.0 mg/L NaOCl
70 mg/L 9800
3.5 mg/L 9890
Filtrate 0.10 NTU
UVT: 91.07%
UVA: 0.0407/cm
UVA Reduction: 51.7%
Settled: 1.48 NTU
0 mg/L NaOCl
150 mg/L Adv Coag.
Filtrate 0.20 NTU
UVT: 92.13%
UVA: 0.0356/cm
UVA Reduction: 57.8%
Settled: 1.5 NTU

## Slide 25: Jars 13-15: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 26: Jars 13-15: After 25-minutes of settling, settled water turbidity is taken.

## Slide 27: Jars 16-19 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants 9800/9890

## Slide 28: Jars 16-19: End of 5-minute flocculation (30 RPM) duration.
70 mg/L 9890
3.5 mg/L 9800
Filtrate 0.10 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 63.7%
Settled: 0.87 NTU
75 mg/L 9890
3.5 mg/L 9800
Filtrate 0.10 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction: 62.6%
Settled: 0.43 NTU
70 mg/L 9890
0 mg/L 9800
Filtrate 0.09 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction: 62.6%
Settled: 0.33 NTU
75 mg/L 9890
0 mg/L 9800
Filtrate 0.09 NTU
UVT: 92.2%
UVA: 0.034/cm
UVA Reduction: 62.6%
Settled: 0.31 NTU

## Slide 29: Jars 16-19: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 30: Jars 16-19: After 25-minutes of settling, settled water turbidity is taken.
70 mg/L 9890
3.5 mg/L 9800
Filtrate 0.10 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 63.7%
Settled: 0.87 NTU
75 mg/L 9890
3.5 mg/L 9800
Filtrate 0.10 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction: 62.6%
Settled: 0.43 NTU
70 mg/L 9890
0 mg/L 9800
Filtrate 0.09 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction: 62.6%
Settled: 0.33 NTU
75 mg/L 9890
0 mg/L 9800
Filtrate 0.09 NTU
UVT: 92.2%
UVA: 0.034/cm
UVA Reduction: 62.6%
Settled: 0.31 NTU

## Slide 31: Jars 20-23 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9890

## Slide 32: Jars 20-23: End of 5-minute flocculation (30 RPM) duration.
55 mg/L 9890
Filtrate 0.08 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction: 61.5%
Settled: 0.31 NTU
60 mg/L 9890
Filtrate 0.08 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction: 61.5%
Settled: 0.34 NTU
65 mg/L 9890
Filtrate 0.07 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction: 61.5%
Settled: 0.54 NTU
70 mg/L 9890
Filtrate 0.08 NTU
UVT: 92.0%
UVA: 0.036/cm
UVA Reduction: 60.4%
Settled: 0.66 NTU

## Slide 33: Jars 20-23: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 34: Jars 20-23: After 25-minutes of settling, settled water turbidity is taken.
55 mg/L 9890
Filtrate 0.08 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction: 61.5%
Settled: 0.31 NTU
60 mg/L 9890
Filtrate 0.08 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction: 61.5%
Settled: 0.34 NTU
65 mg/L 9890
Filtrate 0.07 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction: 61.5%
Settled: 0.54 NTU
70 mg/L 9890
Filtrate 0.08 NTU
UVT: 92.0%
UVA: 0.036/cm
UVA Reduction: 60.4%
Settled: 0.66 NTU

## Slide 35: Jars 24-27 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) w/NaOCl Applied Coagulant 9890

## Slide 36: Jars 24-27: End of 5-minute flocculation (30 RPM) duration.
45 mg/L 9890
Filtrate 0.09 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction: 60.4%
Settled: 0.55 NTU
50 mg/L 9890
Filtrate 0.08 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction: 60.4%
Settled: 0.33 NTU
55 mg/L 9890
Filtrate 0.08 NTU
UVT: 92.0%
UVA: 0.035/cm
UVA Reduction: 61.5%
Settled: 0.39 NTU
2.0 mg/L NaOCl
55 mg/L 9890
Filtrate 0.08 NTU
UVT: 92.0%
UVA: 0.035/cm
UVA Reduction: 61.5%
Settled: 0.39 NTU

## Slide 37: Jars 24-27: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 38: Jars 24-27: After 25-minutes of settling, settled water turbidity is taken.
45 mg/L 9890
Filtrate 0.09 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction: 60.4%
Settled: 0.55 NTU
50 mg/L 9890
Filtrate 0.08 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction: 60.4%
Settled: 0.33 NTU
55 mg/L 9890
Filtrate 0.08 NTU
UVT: 92.0%
UVA: 0.035/cm
UVA Reduction: 61.5%
Settled: 0.39 NTU
2.0 mg/L NaOCl
55 mg/L 9890
Filtrate 0.08 NTU
UVT: 92.0%
UVA: 0.035/cm
UVA Reduction: 61.5%
Settled: 0.39 NTU

## Slide 39: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate).
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 40: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 41: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 42: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 43: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 44: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732