## Slide 1: Surfwood Mutual Water Corporation CA2300590 Mendocino County Jar Test
by Guy Schott, P.E
September 19, 2019

## Slide 2: Source Water: Jack Peter’s Creek Roughing Filter followed by Multi-Media Filtration
Source Water Characteristics
Turbidity: 6.2 NTU
pH: 7.20
UVT: 65.3%, UVA: 0.185/cm
0.4 um Filtered
UVT: 70.1%, UVA: 0.154/cm
Treated Water Train 1 (7066 coagulant 61 mg/L)
Turbidity: 0.05 NTU
UVT: 97.2%, UVA: 0.012/cm
UVA Reduction: 92.2%

## Slide 3: UVT/UVA, pathlength: 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 4: Coagulant Used for Jar Testing
7066 (Garratt Callahan)
10 – 30% Poly Aluminum Hydroxychloride Sulfate
SG = 1.2

## Slide 5: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.20
LCA #1:
7066: 58.6 mg/L as product (no pH adjustment)
Final pH: 6.49

## Slide 6: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Preparation of coagulant stock solutions are generally 1.0 or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 7: Filterability and %UVT/UVA Analysis
All jars except jars 21-24, 25 mL were sampled immediately at the end of flocculation duration for filterability and %UVT/UVA. Jars 21-24, 25 mL were sampled after 5 minutes of settling.

## Slide 8: Surfwood MWC: Jar Test 1-8 Results Jar 1-8, 25 mL sampled at end of floc duration.
Jar # | 200 RPM Flash Mix sec | RPM Floc Duration 5 min | 7066 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 60 | 30 | 58 | 0.13 | 95.3 | 0.021 | 86.4 | 0.56
J2 | 60 | 30 | 61 | 0.07 | 96.3 | 0.016 | 89.6 | 0.57
J3 | 60 | 30 | 64 | 0.07 | 96.2 | 0.017 | 89.0 | 0.82
J4 | 60 | 30 | 67 | 0.08 | 96.2 | 0.017 | 89.0 | 0.59
J5 | 60 | 20 | 58 | n/a | n/a | n/a | - | 0.59
J6 | 60 | 20 | 61 | 0.09 | 96.0 | 0.018 | 88.3 | 0.49
J7 | 60 | 20 | 64 | 0.08 | 96.2 | 0.017 | 89.0 | 1.63
J8 | 60 | 20 | 67 | 0.09 | 96.1 | 0.017 | 89.0 | 0.63

## Slide 9: Surfwood MWC: Jar Test 9-16 Results Jar 9-16, 25 mL sampled at end of floc duration.
Jar # | 200 RPM Flash Mix sec | RPM Floc Duration 5 min | 7066 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 60 | 10 | 58 | 0.13 | 95.3 | 0.021 | 86.4 | 0.97
J10 | 60 | 10 | 61 | 0.09 | 96.0 | 0.018 | 88.3 | 0.77
J11 | 60 | 10 | 64 | 0.13 | 96.0 | 0.018 | 88.3 | 1.37
J12 | 60 | 10 | 67 | 0.09 | 96.1 | 0.017 | 89.0 | 0.82
J13 | 60 | 40 | 58 | 0.08 | 95.6 | 0.020 | 87.0 | 0.84
J14 | 60 | 40 | 61 | 0.13 | 95.2 | 0.021 | 86.4 | 0.79
J15 | 60 | 40 | 64 | 0.13 | 95.2 | 0.021 | 86.4 | 1.07
J16 | 60 | 40 | 67 | 0.11 | 95.7 | 0.019 | 87.7 | 0.51

## Slide 10: Surfwood MWC: Jar Test 17-20 Results Jar 17-20, 25 mL sampled at end of floc duration.
Jar # | 200 RPM Flash Mix sec | RPM Floc Duration 5 min | 7066 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J17 | 60 | 30 | 58 | 0.13 | 95.0 | 0.022 | 85.7 | 0.83
J18 | 60 | 30 | 61 | 0.13 | 95.2 | 0.021 | 86.4 | 0.58
J19 | 60 | 30 | 64 | 0.13 | 95.3 | 0.021 | 86.4 | 0.58
J20 | 60 | 30 | 67 | 0.11 | 95.6 | 0.020 | 87.0 | 0.39

## Slide 11: Surfwood MWC: Jar Test 21-24 Results Jar 21-24, 25 mL sampled after 5 min of settling.
Jar # | 200 RPM Flash Mix sec | RPM Floc Duration 5 min | 7066 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J21 | 60 | 30 | 58 | 0.22 | 93.6 | 0.029 | 81.2 | 0.72
J22 | 60 | 30 | 61 | 0.19 | 94.2 | 0.026 | 83.1 | 0.70
J23 | 60 | 30 | 64 | 0.08 | 95.6 | 0.020 | 87.0 | 0.78
J24 | 60 | 30 | 67 | 0.11 | 95.6 | 0.020 | 87.0 | 0.49

## Slide 12: Surfwood MWC: Jar Test 25-32 Results Jar 25-32, 25 mL sampled at end of floc duration.
Jar # | 200 RPM Flash Mix sec | RPM -Floc Duration 5 min | 7066 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J25 | 15 | 30 | 58 | 0.11 | 95.6 | 0.020 | 87.0 | 0.87
J26 | 15 | 30 | 61 | 0.08 | 96.2 | 0.017 | 89.0 | 0.79
J27 | 15 | 30 | 64 | n/a | n/a | n/a | n/a | 0.90
J28 | 15 | 30 | 67 | 0.06 | 96.6 | 0.015 | 90.3 | 0.78
J29 | 0 | 30 | 58 | 0.09 | 95.8 | 0.019 | 87.7 | 0.95
J30 | 0 | 30 | 61 | 0.16 | 95.0 | 0.022 | 85.7 | 1.02
J31 | 0 | 30 | 64 | 0.07 | 96.4 | 0.016 | 89.6 | 1.08
J32 | 0 | 30 | 67 | 0.06 | 96.7 | 0.015 | 90.3 | 0.84

## Slide 13: Jars 1-4 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) 25 mL sampled end of Floc Applied Coagulant 7066

## Slide 14: Jars 1-4: At End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
58 mg/L 7066
Filtrate 0.13 NTU
UVT: 95.3%
UVA: 0.021/cm
UVA Reduction: 86.4%
Settled: 0.56 NTU
61 mg/L 7066
Filtrate 0.07 NTU
UVT: 96.3%
UVA: 0.016/cm
UVA Reduction: 89.6%
Settled: 0.57 NTU
64 mg/L 7066
Filtrate 0.07 NTU
UVT: 96.2%
UVA: 0.017/cm
UVA Reduction: 89%
Settled: 0.82 NTU
67 mg/L 7066
Filtrate 0.08 NTU
UVT: 96.2%
UVA: 0.017/cm
UVA Reduction: 89%
Settled: 0.59 NTU

## Slide 15: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.

## Slide 16: Visual of Filterability of Jars 1-4
58 mg/L 7066
Filtrate 0.13 NTU
UVT: 95.3%
UVA: 0.021/cm
Settled: 0.56 NTU
61 mg/L 7066
Filtrate 0.07 NTU
UVT: 96.3%
UVA: 0.016/cm
Settled: 0.57 NTU
64 mg/L 7066
Filtrate 0.07 NTU
UVT: 96.2%
UVA: 0.017/cm
Settled: 0.82 NTU
67 mg/L 7066
Filtrate 0.08 NTU
UVT: 96.2%
UVA: 0.017/cm
Settled: 0.59 NTU

## Slide 17: Jars 5-8 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (20 RPM) 25 mL sampled end of Floc Applied Coagulant 7066

## Slide 18: Jars 5-8: At End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
58 mg/L 7066
Filtrate x NTU
UVT: x%
UVA: x/cm
Settled: 0.59 NTU
61 mg/L 7066
Filtrate 0.09 NTU
UVT: 96.0%
UVA: 0.018/cm
UVA Reduction: 88.3%
Settled: 0.49 NTU
64 mg/L 7066
Filtrate 0.08 NTU
UVT: 96.2%
UVA: 0.017/cm
UVA Reduction: 89%
Settled: 1.6 NTU
67 mg/L 7066
Filtrate 0.09 NTU
UVT: 96.1%
UVA: 0.017/cm
UVA Reduction: 89%
Settled: 0.63 NTU

## Slide 19: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.

## Slide 20: Visual of Filterability of Jars 5-8
58 mg/L 7066
Filtrate x NTU
UVT: x%
UVA: x/cm
Settled: 0.59 NTU
61 mg/L 7066
Filtrate 0.09 NTU
UVT: 96.0%
UVA: 0.018/cm
Settled: 0.49 NTU
64 mg/L 7066
Filtrate 0.08 NTU
UVT: 96.2%
UVA: 0.017/cm
Settled: 1.6 NTU
67 mg/L 7066
Filtrate 0.09 NTU
UVT: 96.1%
UVA: 0.017/cm
Settled: 0.63 NTU

## Slide 21: Jars 9-12 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (10 RPM) 25 mL sampled end of Floc Applied Coagulant 7066

## Slide 22: Jars 9-12: At End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
58 mg/L 7066
Filtrate 0.13 NTU
UVT: 95.3%
UVA: 0.021/cm
UVA Reduction: 86.4%
Settled: 0.97 NTU
61 mg/L 7066
Filtrate 0.09 NTU
UVT: 96.0%
UVA: 0.018/cm
UVA Reduction: 88.3%
Settled: 0.77 NTU
64 mg/L 7066
Filtrate 0.13 NTU
UVT: 96.0%
UVA: 0.018/cm
UVA Reduction: 88.3%
Settled: 1.37 NTU
67 mg/L 7066
Filtrate 0.09 NTU
UVT: 96.1%
UVA: 0.017/cm
UVA Reduction: 89%
Settled: 0.82 NTU

## Slide 23: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.

## Slide 24: Visual of Filterability of Jars 9-12
58 mg/L 7066
Filtrate 0.13 NTU
UVT: 95.3%
UVA: 0.021/cm
Settled: 0.97 NTU
61 mg/L 7066
Filtrate 0.09 NTU
UVT: 96.0%
UVA: 0.018/cm
Settled: 0.77 NTU
64 mg/L 7066
Filtrate 0.13 NTU
UVT: 96.0%
UVA: 0.018/cm
Settled: 1.37 NTU
67 mg/L 7066
Filtrate 0.09 NTU
UVT: 96.1%
UVA: 0.017/cm
Settled: 0.82 NTU

## Slide 25: Jars 13-16 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (40 RPM) 25 mL sampled end of Floc Applied Coagulant 7066

## Slide 26: Jars 13-16: At End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
58 mg/L 7066
Filtrate 0.08 NTU
UVT: 95.6%
UVA: 0.020/cm
UVA Reduction: 87%
Settled: 0.84 NTU
61 mg/L 7066
Filtrate 0.13 NTU
UVT: 95.2%
UVA: 0.021/cm
UVA Reduction: 86.4%
Settled: 0.79 NTU
64 mg/L 7066
Filtrate 0.13 NTU
UVT: 95.2%
UVA: 0.021/cm
UVA Reduction: 86.4%
Settled: 1.07 NTU
67 mg/L 7066
Filtrate 0.11 NTU
UVT: 95.7%
UVA: 0.019/cm
UVA Reduction: 87.7%
Settled: 0.51 NTU

## Slide 27: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.

## Slide 28: Visual of Filterability of Jars 13-16
58 mg/L 7066
Filtrate 0.08 NTU
UVT: 95.6%
UVA: 0.020/cm
Settled: 0.84 NTU
61 mg/L 7066
Filtrate 0.13 NTU
UVT: 95.2%
UVA: 0.021/cm
Settled: 0.79 NTU
61 mg/L 7066
Filtrate 0.13 NTU
UVT: 95.2%
UVA: 0.021/cm
Settled: 0.79 NTU
67 mg/L 7066
Filtrate 0.11 NTU
UVT: 95.7%
UVA: 0.019/cm
Settled: 0.51 NTU

## Slide 29: Jars 17-20 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) 25 mL sampled end of Floc Applied Coagulant 7066

## Slide 30: Jars 17-20: At End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
58 mg/L 7066
Filtrate 0.13 NTU
UVT: 95.0%
UVA: 0.022/cm
UVA Reduction: 85.7%
Settled: 0.84 NTU
61 mg/L 7066
Filtrate 0.13 NTU
UVT: 95.2%
UVA: 0.021/cm
UVA Reduction: 86.4%
Settled: 0.54 NTU
64 mg/L 7066
Filtrate 0.13 NTU
UVT: 95.3%
UVA: 0.021/cm
UVA Reduction: 86.4%
Settled: 0.58 NTU
67 mg/L 7066
Filtrate 0.11 NTU
UVT: 95.6%
UVA: 0.020/cm
UVA Reduction: 87%
Settled: 0.39 NTU

## Slide 31: Jars 17-20: After 25-minutes of settling, settled water turbidity is taken.

## Slide 32: Visual of Filterability of Jars 17-20
58 mg/L 7066
Filtrate 0.13 NTU
UVT: 95.0%
UVA: 0.022/cm
Settled: 0.84 NTU
61 mg/L 7066
Filtrate 0.13 NTU
UVT: 95.2%
UVA: 0.021/cm
Settled: 0.54 NTU
64 mg/L 7066
Filtrate 0.13 NTU
UVT: 95.3%
UVA: 0.021/cm
Settled: 0.58 NTU
67 mg/L 7066
Filtrate 0.11 NTU
UVT: 95.6%
UVA: 0.020/cm
Settled: 0.39 NTU

## Slide 33: Jars 21-24 Test Flash Mix 60 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 7066

## Slide 34: Jars 21-24: End of 5-minute flocculation (30 RPM) duration.
58 mg/L 7066
Filtrate 0.22 NTU
UVT: 93.6%
UVA: 0.029/cm
UVA Reduction: 81.2%
Settled: 0.72 NTU
61 mg/L 7066
Filtrate 0.19 NTU
UVT: 94.2%
UVA: 0.026/cm
UVA Reduction: 83.1%
Settled: 0.70 NTU
64 mg/L 7066
Filtrate 0.08 NTU
UVT: 95.6%
UVA: 0.020/cm
UVA Reduction: 87%
Settled: 0.78 NTU
67 mg/L 7066
Filtrate 0.11 NTU
UVT: 95.6%
UVA: 0.020/cm
UVA Reduction: 87%
Settled: 0.49 NTU

## Slide 35: Jars 21-24: After 5-minutes of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 36: Jars 21-24: After 25-minutes of settling, settled water turbidity is taken.
58 mg/L 7066
Filtrate 0.22 NTU
UVT: 93.6%
UVA: 0.029/cm
UVA Reduction: 81.2%
Settled: 0.72 NTU
61 mg/L 7066
Filtrate 0.19 NTU
UVT: 94.2%
UVA: 0.026/cm
UVA Reduction: 83.1%
Settled: 0.70 NTU
64 mg/L 7066
Filtrate 0.08 NTU
UVT: 95.6%
UVA: 0.020/cm
UVA Reduction: 87%
Settled: 0.78 NTU
67 mg/L 7066
Filtrate 0.11 NTU
UVT: 95.6%
UVA: 0.020/cm
UVA Reduction: 87%
Settled: 0.49 NTU

## Slide 37: Visual of Filterability of Jars 21-24
58 mg/L 7066
Filtrate 0.22 NTU
UVT: 93.6%
UVA: 0.029/cm
Settled: 0.72 NTU
61 mg/L 7066
Filtrate 0.19 NTU
UVT: 94.2%
UVA: 0.026/cm
Settled: 0.70 NTU
64 mg/L 7066
Filtrate 0.08 NTU
UVT: 95.6%
UVA: 0.020/cm
Settled: 0.78 NTU
67 mg/L 7066
Filtrate 0.11 NTU
UVT: 95.6%
UVA: 0.020/cm
Settled: 0.49 NTU

## Slide 38: Jars 25-28 Test Flash Mix 15 Sec (200 RPM) Floc Mix 5 min (30 RPM) 25 mL sampled end of Floc Applied Coagulant 7066

## Slide 39: Jars 25-28: At End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
58 mg/L 7066
Filtrate 0.11 NTU
UVT: 95.6%
UVA: 0.020/cm
UVA Reduction: 87%
Settled: 0.87 NTU
61 mg/L 7066
Filtrate 0.08 NTU
UVT: 96.2%
UVA: 0.017/cm
UVA Reduction: 89%
Settled: 0.79 NTU
64 mg/L 7066
Filtrate x NTU
UVT: x%
UVA: x/cm
Settled: 0.90 NTU
67 mg/L 7066
Filtrate 0.06 NTU
UVT: 96.6%
UVA: 0.015/cm
UVA Reduction: 90.3%
Settled: 0.78 NTU

## Slide 40: Jars 25-28: After 25-minutes of settling, settled water turbidity is taken.

## Slide 41: Visual of Filterability of Jars 25-28
58 mg/L 7066
Filtrate 0.11 NTU
UVT: 95.6%
UVA: 0.020/cm
Settled: 0.87 NTU
61 mg/L 7066
Filtrate 0.08 NTU
UVT: 96.2%
UVA: 0.017/cm
Settled: 0.79 NTU
67 mg/L 7066
Filtrate 0.06 NTU
UVT: 96.6%
UVA: 0.015/cm
Settled: 0.78 NTU

## Slide 42: Jars 29-32 Test Flash Mix 0 Sec (200 RPM) Floc Mix 5 min (30 RPM) 25 mL sampled end of Floc Applied Coagulant 7066

## Slide 43: Jars 29-32: At End of Floc Duration, 25 mL is syringed for filterability and %UVT/UVA.
58 mg/L 7066
Filtrate 0.09 NTU
UVT: 95.8%
UVA: 0.019/cm
UVA Reduction: 87.7%
Settled: 0.95 NTU
61 mg/L 7066
Filtrate 0.16 NTU
UVT: 95.0%
UVA: 0.022/cm
UVA Reduction: 85.7%
Settled: 1.02 NTU
61 mg/L 7066
Filtrate 0.07 NTU
UVT: 96.4%
UVA: 0.016/cm
UVA Reduction: 89.6%
Settled: 1.08 NTU
64 mg/L 7066
Filtrate 0.06 NTU
UVT: 96.7%
UVA: 0.015/cm
UVA Reduction: 90.3%
Settled: 0.84 NTU

## Slide 44: Jars 29-32: After 25-minutes of settling, settled water turbidity is taken.

## Slide 45: Visual of Filterability of Jars 29-32
58 mg/L 7066
Filtrate 0.09 NTU
UVT: 95.8%
UVA: 0.019/cm
Settled: 0.95 NTU
61 mg/L 7066
Filtrate 0.16 NTU
UVT: 95.0%
UVA: 0.022/cm
Settled: 1.02 NTU
61 mg/L 7066
Filtrate 0.07 NTU
UVT: 96.4%
UVA: 0.016/cm
Settled: 1.08 NTU
64 mg/L 7066
Filtrate 0.06 NTU
UVT: 96.7%
UVA: 0.015/cm
Settled: 0.84 NTU

## Slide 46: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-60 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate). For this study, sample was taken immediately at the end of flocculation process.
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 47: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 48: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 49: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 50: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 51: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732