## Slide 1: Redwood Valley County Water District CA2310008 Mendocino County Jar Test
by Guy Schott, P.E
April 30, 2020

## Slide 2: Conventional Water Treatment Plant

## Slide 3: Redwood Valley CWD Water Characteristics, April 29, 2020
Source
Turbidity: 0.40 NTU
pH: 8.9
UVT: 90.3%, UVA: 0.044/cm
Filter 1
Turbidity: 0.09 NTU
UVT: 94.9%, UVA: 0.022/cm
UVA Reduction: 50%
Filter 2
Turbidity: 0.09 NTU
UVT: 95.4%, UVA: 0.020/cm
UVA Reduction: 54.5%
Filter 3
Turbidity: 0.08 NTU
UVT: 95.6%, UVA: 0.019/cm
UVA Reduction: 56.8%

## Slide 4: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 5: Applied Coagulants for Jar Testing, Set 1
Pro Pac 9800 (NTU Technologies)
50% Aluminum Chlorohydrate (ACH)
50% Water
SG = 1.34
7066 (Garratt Callahan)
10 – 30% Poly Aluminum Hydroxychloride Sulfate
50% Basicity
SG = 1.2

## Slide 6: Applied Coagulants for Jar Testing, Set 2
Pro Pac 9810 (NTU Technologies)
45-50% Aluminum Chlorohydrate (ACH)
45-50% Water
5% Proprietary
SG = 1.25 - 1.34
Aluminum Sulfate
48.25% Alum
SG = 1.34
Advanced Coagulant
SG = 1.3

## Slide 7: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 8.9
LCA #1: 9800: 13.7 mg/L as product
pH adjusted to 7.5 with acidic acid
LCA #2: 7066: 44.5 mg/L as product
pH adjusted to 7.5 with acidic acid
LCA #3: Alum: 19.7 mg/L as product
pH adjusted to 6.6 with acidic acid
LCA #4: Advance Coag: 40 mg/L as product
pH adjusted to 7.5 with acidic acid

## Slide 8: Laboratory Charge Analyzer - Continue
LCA #3:
Added 1.0 mg/L NaOCl
7032 (ACH): 26.6 mg/L as product
pH adjusted to 7.5 with acidic acid
LCA #4:
917: 19 mg/L as product
pH adjusted to 7.5 with acidic acid

## Slide 9: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength). Aluminum sulfate is reported as Alum.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 10: Redwood Valley CWD: Jar Test 1-6 Results Floc Mix 30 RPM (5 minutes)
Jar # | 100 RPM Flash Mix seconds | 9800 mg/L | Alum mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 0 | 11.2 | 14.6 | 0.10 | 92.2 | 0.035 | 20.5 | 0.70
J2 | 0 | 11.2 | 14.6 | 0.10 | 91.9 | 0.036 | 18.2 | 0.64
J3 | 20 | 11.2 | 14.6 | 0.11 | 92.2 | 0.035 | 20.5 | 0.47
J4 | 20 | 11.2 | 14.6 | 0.11 | 92.2 | 0.035 | 22.7 | 0.46
J5 | 0 | 36.6 | 14.6 | 0.13 | 94.6 | 0.024 | 45.5 | 0.33
J6 | 20 | 36.6 | 14.6 | 0.07 | 94.7 | 0.023 | 47.7 | 0.33

## Slide 11: Redwood Valley CWD: Jar Test 7-14 Results Floc Mix 30 RPM (5 minutes)
Jar # | 200 RPM Flash Mix sec | 7066 mg/L | Adv/ Coag mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J7 | 0 | 45 | 0 | 0.13 | 91.9 | 0.036 | 18.2 | 0.46
J8 | 0 | 60 | 0 | 0.15 | 92.5 | 0.033 | 25.0 | 0.54
J9 | 20 | 45 | 0 | 0.10 | 91.8 | 0.037 | 15.9 | 0.42
J10 | 20 | 60 | 0 | 0.14 | 92.6 | 0.033 | 25.0 | 0.32
J11 | 0 | 0 | 40 | 0.09 | 92.2 | 0.035 | 20.5 | 0.42
J12 | 0 | 0 | 50 | 0.10 | 92.7 | 0.032 | 27.3 | 0.35
J13 | 20 | 0 | 40 | 0.13 | 92.1 | 0.035 | 20.5 | 0.39
J14 | 20 | 0 | 50 | 0.16 | 92.5 | 0.033 | 25.0 | 0.30

## Slide 12: Redwood Valley CWD: Jar Test 15-22 Results
Jar # | 200 RPM Flash Mix sec | 30 RPM Floc Duration minutes | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J15 | 0 | 5 | 13.5 | 0.09 | 92.5 | 0.034 | 22.7 | 0.85
J16 | 0 | 5 | 16 | 0.11 | 92.4 | 0.034 | 22.7 | 0.61
J17 | 0 | 5 | 18.5 | 0.10 | 92.6 | 0.033 | 25.0 | 0.51
J18 | 0 | 5 | 21 | 0.11 | 92.9 | 0.032 | 27.3 | 0.48
J19 | 0 | 5 | 23.5 | 0.08 | 93.3 | 0.030 | 31.8 | 0.41
J20 | 0 | 5 | 26 | 0.15 | 93.2 | 0.030 | 31.8 | 0.45
J21 | 0 | 5 | 28.5 | 0.10 | 93.4 | 0.029 | 34.1 | 0.38
J22 | 0 | 5 | 31 | 0.11 | 93.6 | 0.028 | 36.4 | 0.34

## Slide 13: Redwood Valley CWD: Jar Test 23-26 Results
Jar # | 200 RPM Flash Mix sec | 30 RPM Floc Duration minutes | Alum mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J23 | 0 | 5 | 20 | 0.18 | 91.3 | 0.039 | 11.4 | 1.11
J24 | 0 | 5 | 23 | 0.20 | 91.5 | 0.038 | 13.6 | 1.05
J25 | 0 | 5 | 26 | 0.20 | 91.6 | 0.037 | 15.9 | 0.89
J26 | 0 | 5 | 29 | 0.12 | 92.5 | 0.033 | 25.0 | 0.68

## Slide 14: Redwood Valley CWD: Jar Test 27-34 Results
Jar # | 200 RPM Flash Mix sec | 30 RPM Floc Duration minutes | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J27 | 0 | 5 | 14 | 0.08 | 93.1 | 0.030 | 31.8 | 0.47
J28 | 0 | 5 | 17 | 0.09 | 93.2 | 0.030 | 31.8 | 0.40
J29 | 0 | 5 | 20 | 0.10 | 93.3 | 0.029 | 34.1 | 0.38
J30 | 0 | 5 | 23 | 0.08 | 93.7 | 0.026 | 40.9 | 0.35
J31 | 0 | 5 | 26 | 0.10 | 93.7 | 0.028 | 36.4 | 0.27
J32 | 0 | 5 | 29 | 0.08 | 93.9 | 0.027 | 38.6 | 0.29
J33 | 0 | 5 | 33 | 0.10 | 94.0 | 0.026 | 40.9 | 0.31
J34 | 0 | 5 | 36 | 0.10 | 94.0 | 0.026 | 40.9 | 0.28

## Slide 15: Redwood Valley CWD: Jar Test 35-37 Results No Initial Flash Mixing Applied, Floc 30 RPM (5 min)
Jar # | 9800 mg/L | 9810 mg/L | Alum mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J35 | 36 | 0 | 0 | 0.14 | 93.8 | 0.027 | 38.6 | 0.35
J36 | 36 | 0 | 15 | 0.12 | 94.5 | 0.024 | 45.5 | 0.37
J37 | 0 | 36 | 15 | 0.08 | 94.5 | 0.024 | 45.5 | 0.47

## Slide 16: Jars 1-6 Test Flash Mix 0-20 Sec (100 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants 9800/Alum No Pictures to View

## Slide 17: Jars 7-10 Test Flash Mix 0-20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 7066

## Slide 18: Jars 7-10: End of 5-minute flocculation (30 RPM) duration.
45 mg/L 7066
Filtrate 0.13 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction 18.2%
Settled: 0.46 NTU
No Flash Mix
60 mg/L 7066
Filtrate 0.15 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction 25%
Settled: 0.54 NTU
No Flash Mix
45 mg/L 7066
Filtrate 0.10 NTU
UVT: 91.8%
UVA: 0.037/cm
UVA Reduction 15.9%
Settled: 0.42 NTU
Flash Mix,
20 sec (200 RPM)
60 mg/L 7066
Filtrate 0.14 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction 25%
Settled: 0.32 NTU
Flash Mix,
20 sec (200 RPM)

## Slide 19: Jars 7-10: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 20: Jars 7-10: After 25-minutes of settling, settled water turbidity is taken.
45 mg/L 7066
Filtrate 0.13 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction 18.2%
Settled: 0.46 NTU
No Flash Mix
60 mg/L 7066
Filtrate 0.15 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction 25%
Settled: 0.54 NTU
No Flash Mix
45 mg/L 7066
Filtrate 0.10 NTU
UVT: 91.8%
UVA: 0.037/cm
UVA Reduction 15.9%
Settled: 0.42 NTU
Flash Mix,
20 sec (200 RPM)
60 mg/L 7066
Filtrate 0.14 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction 25%
Settled: 0.32 NTU
Flash Mix,
20 sec (200 RPM)

## Slide 21: Jars 11-14 Test Flash Mix 0-20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant Adv Coag

## Slide 22: Jars 11-14: End of 5-minute flocculation (30 RPM) duration.
40 mg/L Adv Coag
Filtrate 0.09 NTU
UVT: 92.9%
UVA: 0.035/cm
UVA Reduction 20.5%
Settled: 0.42 NTU
No Flash Mix
50 mg/L Adv Coag
Filtrate 0.10 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction 27.3%
Settled: 0.35 NTU
No Flash Mix
40 mg/L Adv Coag
Filtrate 0.13 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction 20.5%
Settled: 0.39 NTU
Flash Mix,
20 sec (200 RPM)
50 mg/L Adv Coag
Filtrate 0.16 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction 25%
Settled: 0.30 NTU
Flash Mix,
20 sec (200 RPM)

## Slide 23: Jars 11-14: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 24: Jars 11-14: After 25-minutes of settling, settled water turbidity is taken.
40 mg/L Adv Coag
Filtrate 0.09 NTU
UVT: 92.9%
UVA: 0.035/cm
UVA Reduction 20.5%
Settled: 0.42 NTU
No Flash Mix
50 mg/L Adv Coag
Filtrate 0.10 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction 27.3%
Settled: 0.35 NTU
No Flash Mix
40 mg/L Adv Coag
Filtrate 0.13 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction 20.5%
Settled: 0.39 NTU
Flash Mix,
20 sec (200 RPM)
50 mg/L Adv Coag
Filtrate 0.16 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction 25%
Settled: 0.30 NTU
Flash Mix,
20 sec (200 RPM)

## Slide 25: Jars 15-18 Test No Flash Mix Floc Mix 5 min (30 RPM) Applied Coagulant 9800

## Slide 26: Jars 15-18: End of 5-minute flocculation (30 RPM) duration.
13.5 mg/L 9800
Filtrate 0.09 NTU
UVT: 92.5%
UVA: 0.034/cm
UVA Reduction 22.7%
Settled: 0.85 NTU
16 mg/L 9800
Filtrate 0.11 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction 22.7%
Settled: 0.61 NTU
18.5 mg/L 9800
Filtrate 0.10 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction 25%
Settled: 0.51 NTU
21 mg/L 9800
Filtrate 0.11 NTU
UVT: 92.9%
UVA: 0.032/cm
UVA Reduction 27.3%
Settled: 0.48 NTU

## Slide 27: Jars 15-18: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 28: Jars 15-18: After 25-minutes of settling, settled water turbidity is taken.
13.5 mg/L 9800
Filtrate 0.09 NTU
UVT: 92.5%
UVA: 0.034/cm
UVA Reduction 22.7%
Settled: 0.85 NTU
16 mg/L 9800
Filtrate 0.11 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction 22.7%
Settled: 0.61 NTU
18.5 mg/L 9800
Filtrate 0.10 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction 25%
Settled: 0.51 NTU
21 mg/L 9800
Filtrate 0.11 NTU
UVT: 92.9%
UVA: 0.032/cm
UVA Reduction 27.3%
Settled: 0.48 NTU

## Slide 29: Jars 19-22 Test No Flash Mix Floc Mix 5 min (30 RPM) Applied Coagulant 9800

## Slide 30: Jars 19-22: End of 5-minute flocculation (30 RPM) duration.
23.5 mg/L 9800
Filtrate 0.08 NTU
UVT: 93.3%
UVA: 0.030/cm
UVA Reduction 31.8%
Settled: 0.41 NTU
26 mg/L 9800
Filtrate 0.15 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction 31.8%
Settled: 0.45 NTU
28.5 mg/L 9800
Filtrate 0.10 NTU
UVT: 93.4%
UVA: 0.029/cm
UVA Reduction 34.1%
Settled: 0.38 NTU
31 mg/L 9800
Filtrate 0.11 NTU
UVT: 93.6%
UVA: 0.028/cm
UVA Reduction 36.4%
Settled: 0.34 NTU

## Slide 31: Jars 19-22: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 32: Jars 19-22: After 25-minutes of settling, settled water turbidity is taken.
23.5 mg/L 9800
Filtrate 0.08 NTU
UVT: 93.3%
UVA: 0.030/cm
UVA Reduction 31.8%
Settled: 0.41 NTU
26 mg/L 9800
Filtrate 0.15 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction 31.8%
Settled: 0.45 NTU
28.5 mg/L 9800
Filtrate 0.10 NTU
UVT: 93.4%
UVA: 0.029/cm
UVA Reduction 34.1%
Settled: 0.38 NTU
31 mg/L 9800
Filtrate 0.11 NTU
UVT: 93.6%
UVA: 0.028/cm
UVA Reduction 36.4%
Settled: 0.34 NTU

## Slide 33: Jars 23-26 Test No Flash Mix Floc Mix 5 min (30 RPM) Applied Coagulant Alum

## Slide 34: Jars 23-26: End of 5-minute flocculation (30 RPM) duration.
20 mg/L Alum
Filtrate 0.18 NTU
UVT: 91.3%
UVA: 0.039/cm
UVA Reduction 11.4%
Settled: 1.11 NTU
23 mg/L Alum
Filtrate 0.20 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction 13.6%
Settled: 1.05 NTU
26 mg/L Alum
Filtrate 0.20 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction 15.9%
Settled: 0.89 NTU
29 mg/L Alum
Filtrate 0.12 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction 25%
Settled: 0.68 NTU

## Slide 35: Jars 23-26: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 36: Jars 23-26: After 25-minutes of settling, settled water turbidity is taken.
20 mg/L Alum
Filtrate 0.18 NTU
UVT: 91.3%
UVA: 0.039/cm
UVA Reduction 11.4%
Settled: 1.11 NTU
23 mg/L Alum
Filtrate 0.20 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction 13.6%
Settled: 1.05 NTU
26 mg/L Alum
Filtrate 0.20 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction 15.9%
Settled: 0.89 NTU
29 mg/L Alum
Filtrate 0.12 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction 25%
Settled: 0.68 NTU

## Slide 37: Jars 27-30 Test No Flash Mix Floc Mix 5 min (30 RPM) Applied Coagulant 9810

## Slide 38: Jars 27-30: End of 5-minute flocculation (30 RPM) duration.
14 mg/L 9810
Filtrate 0.08 NTU
UVT: 93.1%
UVA: 0.030/cm
UVA Reduction 31.8%
Settled: 0.47 NTU
17 mg/L 9810
Filtrate 0.09 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction 31.8%
Settled: 0.40 NTU
20 mg/L 9810
Filtrate 0.10 NTU
UVT: 93.3%
UVA: 0.029/cm
UVA Reduction 34.1%
Settled: 0.38 NTU
23 mg/L 9810
Filtrate 0.08 NTU
UVT: 93.7%
UVA: 0.026/cm
UVA Reduction 40.9%
Settled: 0.35 NTU

## Slide 39: Jars 27-30: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 40: Jars 27-30: After 25-minutes of settling, settled water turbidity is taken.
14 mg/L 9810
Filtrate 0.08 NTU
UVT: 93.1%
UVA: 0.030/cm
UVA Reduction 31.8%
Settled: 0.47 NTU
17 mg/L 9810
Filtrate 0.09 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction 31.8%
Settled: 0.40 NTU
20 mg/L 9810
Filtrate 0.10 NTU
UVT: 93.3%
UVA: 0.029/cm
UVA Reduction 34.1%
Settled: 0.38 NTU
23 mg/L 9810
Filtrate 0.08 NTU
UVT: 93.7%
UVA: 0.026/cm
UVA Reduction 40.9%
Settled: 0.35 NTU

## Slide 41: Jars 31-34 Test No Flash Mix Floc Mix 5 min (30 RPM) Applied Coagulant 9810

## Slide 42: Jars 31-34: End of 5-minute flocculation (30 RPM) duration.
26 mg/L 9810
Filtrate 0.10 NTU
UVT: 93.7%
UVA: 0.028/cm
UVA Reduction 36.4%
Settled: 0.27 NTU
29 mg/L 9810
Filtrate 0.08 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction 38.6%
Settled: 0.29 NTU
33 mg/L 9810
Filtrate 0.10 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction 40.9%
Settled: 0.31 NTU
36 mg/L 9810
Filtrate 0.10 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction 40.9%
Settled: 0.28 NTU

## Slide 43: Jars 31-34: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 44: Jars 31-34: After 25-minutes of settling, settled water turbidity is taken.
26 mg/L 9810
Filtrate 0.10 NTU
UVT: 93.7%
UVA: 0.028/cm
UVA Reduction 36.4%
Settled: 0.27 NTU
29 mg/L 9810
Filtrate 0.08 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction 38.6%
Settled: 0.29 NTU
33 mg/L 9810
Filtrate 0.10 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction 40.9%
Settled: 0.31 NTU
36 mg/L 9810
Filtrate 0.10 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction 40.9%
Settled: 0.28 NTU

## Slide 45: Jars 35-37 Test No Flash Mix Floc Mix 5 min (30 RPM) Applied Coagulant 9800/9810/Alum

## Slide 46: Jars 35-37: End of 5-minute flocculation (30 RPM) duration.
36 mg/L 9800
0 mg/L Alum
Filtrate 0.14 NTU
UVT: 93.8%
UVA: 0.027/cm
UVA Reduction 38.6%
Settled: 0.35 NTU
36 mg/L 9800
15 mg/L Alum
Filtrate 0.12 NTU
UVT: 94.5%
UVA: 0.024/cm
UVA Reduction 45.5%
Settled: 0.37 NTU
36 mg/L 9810
15 mg/L Alum
Filtrate 0.08 NTU
UVT: 94.5%
UVA: 0.024/cm
UVA Reduction 45.5%
Settled: 0.77 NTU

## Slide 47: Jars 35-37: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 48: Jars 35-37: After 25-minutes of settling, settled water turbidity is taken.
36 mg/L 9800
0 mg/L Alum
Filtrate 0.14 NTU
UVT: 93.8%
UVA: 0.027/cm
UVA Reduction 38.6%
Settled: 0.35 NTU
36 mg/L 9800
15 mg/L Alum
Filtrate 0.12 NTU
UVT: 94.5%
UVA: 0.024/cm
UVA Reduction 45.5%
Settled: 0.37 NTU
36 mg/L 9810
15 mg/L Alum
Filtrate 0.08 NTU
UVT: 94.5%
UVA: 0.024/cm
UVA Reduction 45.5%
Settled: 0.77 NTU

## Slide 49: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-60 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 50: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 51: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 52: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 53: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 54: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732