## Slide 1: Howell Mountain MWC CA2810001, Napa County, Jar Test
by Guy Schott, P.E. September 30, 2021

## Slide 2: Treatment Plant
Office Building
Treatment Plant Building

## Slide 3: Source Waters (blend): Lake Dear/Lake Henne/Well 01
Source Water Characteristics
September 30, 2021
Turbidity: 1.69 NTU
Alkalinity: 30 mg/L as CaCO3
pH: 7.02
UVT: 73.7%, UVA: 0.133/cm
0.4 um Filtered
Turbidity: 0.56 NTU
UVT: 76.0%, UVA: 0.118/cm

## Slide 4: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (254 nm) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 5: Howell Mountain MWC Treated Water Characteristics, September 30, 2021
Plant Dose 917: 27 mg/L
Settled water turbidites: 089 – 0.93 NTU
Plant Filtrate Water (before NaOCl injection)
Turbidity: 0.12 NTU
UVT: 91.1%,
UVA: 0.040/cm
Plant Filtrate Water (after NaOCl injection)
Turbidity: 0.13 NTU
UVT: 93.5%,
UVA: 0.029/cm

## Slide 6: Applied Coagulants for Jar Testing (1)
AdvFloc-CTC-00011
Polyaluminum Hydroxy Chlorosulfate
12.55% Al2O3
6.64% Al
64.9% Basicity
SG = 1.299
NSF limit: 450 mg/L as Product
BWS, Inc.
Greg Nieckarz, Ph.D.
Greg.niekarz@bws.works
541-953-5112
Pro Pac 917 (NTU Technologies, Inc.)
10% polyamine (50% water, 50% active polyamines)
45% Aluminum Chlorohydrate (ACH)
~21.3% Al2O3
~11.3% Al
45% Water
83% Basicity
SG = 1.25-1.34
NSF limit: 100 mg/L as Product

## Slide 7: Applied Coagulants for Jar Testing (2)
Brenntag (559-485-4150)
Solenis
Praestol 186K
SG = 1.0 – 1.2
Viscosity: 60-180 centipoise
MW: 150,00 g/moles
pDADMAC (20% active, 80% H2O)
NSF limit: 50 mg/L (product)
Product dose 5 mg/L = 1 mg/L pDADMAC active

## Slide 8: Polyamine C59H108N14O10 MW: 1,173.6 g/mol

## Slide 9: Diallyldimethylammonium chloride or N-allyl-N,N-dimethylprop-2-en-1-aminium chloride pDADMAC C8H16ClN MW: 161.67 g/mol
N
+
CH3
CH3
CH2
CH
CH2
CH2
CH
CH2
Cl-

## Slide 10: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
No pH adjustment
Source pH: 7.02
LCA #1:
CTC-00011: 75 mg/L as product
Final pH: 6.51

## Slide 11: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Aluminum Sulfate doses are reported as hydrated Al2(SO4)3*14.3H20.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 12: Howell Mountain; Jar Test 1 - 8 Results Flash Mix 200 RPM (20 sec); Floc Mix 25 RPM (5 min)
Jar# | CTC-00011 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 70 | 0.07 | 89.1 | 0.049 | 58.5 | 0.34
J2 | 75 | 0.08 | 89.4 | 0.048 | 59.3 | 0.38
J3 | 80 | 0.05 | 89.5 | 0.047 | 60.2 | 0.40
J4 | 85 | 0.06 | 89.5 | 0.047 | 60.2 | 0.40
J5 | 85 | 0.06 | 89.7 | 0.047 | 60.2 | 0.46
J6 | 90 | 0.04 | 90.0 | 0.045 | 61.9 | 0.41
J7 | 95 | 0.06 | 89.9 | 0.045 | 61.9 | 0.40
J8 | 100 | 0.05 | 90.1 | 0.045 | 61.9 | 0.41

## Slide 13: Howell Mountain; Jar Test 9 - 16 Results Flash Mix 200 RPM (20 sec); Floc Mix 25 RPM (5 min)
Jar# | 917 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 27 | 0.08 | 89.6 | 0.047 | 60.2 | 0.99
J10 | 40 | 0.10 | 89.8 | 0.046 | 61.0 | 2.95
J11 | 45 | 0.06 | 90.3 | 0.044 | 62.7 | 2.79
J12 | 50 | 0.17 | 88.6 | 0.052 | 55.9 | 2.57
J13 | 21 | 0.09 | 89.3 | 0.049 | 58.5 | 0.78
J14 | 24 | 0.08 | 89.4 | 0.048 | 59.3 | 0.90
J15 | 27 | 0.09 | 89.4 | 0.048 | 59.3 | 1.19
J16 | 30 | 0.13 | 89.3 | 0.049 | 58.5 | 1.52

## Slide 14: Howell Mountain; Jar Test 17 - 24 Results Flash Mix 200 RPM (20 sec); Floc Mix 25 RPM (5 min)
Jar# | PAC mg/L | CTC-00011 mg/L | 917 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J17 | 0 | 0 | 25 | 0.07 | 90.3 | 0.044 | 62.7 | 0.80
J18 | 10 | 0 | 25 | 0.24 | 91.3 | 0.039 | 66.9 | 4.93
J19 | 15 | 0 | 25 | 0.17 | 91.4 | 0.038 | 67.8 | 7.67
J20 | 20 | 0 | 25 | 0.20 | 91.8 | 0.036 | 69.5 | 10.5
J21 | 0 | 80 | 0 | 0.05 | 91.2 | 0.039 | 66.9 | 0.77
J22 | 10 | 80 | 0 | 0.05 | 92.0 | 0.035 | 70.3 | 4.09
J23 | 15 | 80 | 0 | 0.05 | 92.5 | 0.033 | 72.0 | 6.54
J24 | 20 | 80 | 0 | 0.05 | 93.1 | 0.030 | 74.6 | 8.97

## Slide 15: Howell Mountain; Jar Test 25 - 32 Results Flash Mix 200 RPM (20 sec); Floc Mix 25 RPM (5 min)
Jar# | PAC mg/L | CTC-00011 mg/L | 186K mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J25 | 0 | 70 | 0 | 0.04 | 90.5 | 0.042 | 64.4 | 0.54
J26 | 0 | 70 | 1 | 0.04 | 90.7 | 0.042 | 64.4 | 0.58
J27 | 0 | 70 | 2 | 0.05 | 90.7 | 0.042 | 64.4 | 0.97
J28 | 0 | 70 | 3 | 0.04 | 90.8 | 0.041 | 65.3 | 0.80
J29 | 0 | 50 | 0 | 0.04 | 90.1 | 0.044 | 62.7 | 0.26
J30 | 20 | 50 | 0 | 0.05 | 90.7 | 0.037 | 68.6 | 3.76
J31 | 0 | 60 | 0 | 0.04 | 90.3 | 0.044 | 62.7 | 0.48
J32 | 20 | 60 | 0 | 0.04 | 91.9 | 0.036 | 69.5 | 2.62

## Slide 16: Jars 1-4 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (25 RPM) Applied Coagulant CTC-00011

## Slide 17: Jars 1-4: End of 5-minute flocculation (25 RPM) duration.
70 mg/L CTC-00011
Filtrate: 0.07 NTU
UVT: 89.1%
UVA: 0.049/cm
UVA Reduction: 58.5%
Settled: 0.34 NTU
75 mg/L CTC-00011
Filtrate: 0.08 NTU
UVT: 89.4%
UVA: 0.048/cm
UVA Reduction: 59.3%
Settled: 0.38 NTU
80 mg/L CTC-00011
Filtrate: 0.05 NTU
UVT: 89.4%
UVA: 0.047/cm
UVA Reduction: 60.2%
Settled: 0.40 NTU
85 mg/L CTC-00011
Filtrate: 0.06 NTU
UVT: 89.5%
UVA: 0.047/cm
UVA Reduction: 60.2%
Settled: 0.40 NTU

## Slide 18: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 19: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
70 mg/L CTC-00011
Filtrate: 0.07 NTU
UVT: 89.1%
UVA: 0.049/cm
UVA Reduction: 58.5%
Settled: 0.34 NTU
75 mg/L CTC-00011
Filtrate: 0.08 NTU
UVT: 89.4%
UVA: 0.048/cm
UVA Reduction: 59.3%
Settled: 0.38 NTU
80 mg/L CTC-00011
Filtrate: 0.05 NTU
UVT: 89.4%
UVA: 0.047/cm
UVA Reduction: 60.2%
Settled: 0.40 NTU
85 mg/L CTC-00011
Filtrate: 0.06 NTU
UVT: 89.5%
UVA: 0.047/cm
UVA Reduction: 60.2%
Settled: 0.40 NTU

## Slide 20: Jars 5-8 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (25 RPM) Applied Coagulant CTC-00011

## Slide 21: Jars 5-8: End of 5-minute flocculation (25 RPM) duration.
85 mg/L CTC-00011
Filtrate: 0.06 NTU
UVT: 89.7%
UVA: 0.047/cm
UVA Reduction: 60.2%
Settled: 0.46 NTU
90 mg/L CTC-00011
Filtrate: 0.04 NTU
UVT: 90.0%
UVA: 0.045/cm
UVA Reduction: 61.9%
Settled: 0.41 NTU
95 mg/L CTC-00011
Filtrate: 0.06 NTU
UVT: 89.9%
UVA: 0.045/cm
UVA Reduction: 61.9%
Settled: 0.40 NTU
100 mg/L CTC-00011
Filtrate: 0.05 NTU
UVT: 90.1%
UVA: 0.045/cm
UVA Reduction: 61.9%
Settled: 0.41 NTU

## Slide 22: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 23: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
85 mg/L CTC-00011
Filtrate: 0.06 NTU
UVT: 89.7%
UVA: 0.047/cm
UVA Reduction: 60.2%
Settled: 0.46 NTU
90 mg/L CTC-00011
Filtrate: 0.04 NTU
UVT: 90.0%
UVA: 0.045/cm
UVA Reduction: 61.9%
Settled: 0.41 NTU
95 mg/L CTC-00011
Filtrate: 0.06 NTU
UVT: 89.9%
UVA: 0.045/cm
UVA Reduction: 61.9%
Settled: 0.40 NTU
100 mg/L CTC-00011
Filtrate: 0.05 NTU
UVT: 90.1%
UVA: 0.045/cm
UVA Reduction: 61.9%
Settled: 0.41 NTU

## Slide 24: Jars 9-12 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (25 RPM) Applied Coagulant 917

## Slide 25: Jars 9-12: End of 5-minute flocculation (25 RPM) duration.
27 mg/L 917
Filtrate: 0.08 NTU
UVT: 89.6%
UVA: 0.047/cm
UVA Reduction: 60.2%
Settled: 0.99 NTU
40 mg/L 917
Filtrate: 0.10 NTU
UVT: 89.8%
UVA: 0.046/cm
UVA Reduction: 61.0%
Settled: 2.95 NTU
45 mg/L 917
Filtrate: 0.06 NTU
UVT: 90.3%
UVA: 0.044/cm
UVA Reduction: 62.7%
Settled: 2.79 NTU
50 mg/L 917
Filtrate: 0.17 NTU
UVT: 88.6%
UVA: 0.052/cm
UVA Reduction: 55.9%
Settled: 2.57 NTU

## Slide 26: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 27: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
27 mg/L 917
Filtrate: 0.08 NTU
UVT: 89.6%
UVA: 0.047/cm
UVA Reduction: 60.2%
Settled: 0.99 NTU
40 mg/L 917
Filtrate: 0.10 NTU
UVT: 89.8%
UVA: 0.046/cm
UVA Reduction: 61.0%
Settled: 2.95 NTU
45 mg/L 917
Filtrate: 0.06 NTU
UVT: 90.3%
UVA: 0.044/cm
UVA Reduction: 62.7%
Settled: 2.79 NTU
50 mg/L 917
Filtrate: 0.17 NTU
UVT: 88.6%
UVA: 0.052/cm
UVA Reduction: 55.9%
Settled: 2.57 NTU

## Slide 28: Jars 13-16 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (25 RPM) Applied Coagulant 917

## Slide 29: Jars 13-16: End of 5-minute flocculation (25 RPM) duration.
21 mg/L 917
Filtrate: 0.09 NTU
UVT: 89.3%
UVA: 0.049/cm
UVA Reduction: 58.5%
Settled: 0.78 NTU
24 mg/L 917
Filtrate: 0.08 NTU
UVT: 89.4%
UVA: 0.048/cm
UVA Reduction: 59.3%
Settled: 0.90 NTU
27 mg/L 917
Filtrate: 0.09 NTU
UVT: 89.4%
UVA: 0.048/cm
UVA Reduction: 59.3%
Settled: 1.19 NTU
30 mg/L 917
Filtrate: 0.13 NTU
UVT: 89.3%
UVA: 0.049/cm
UVA Reduction: 58.5%
Settled: 1.52 NTU

## Slide 30: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 31: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
21 mg/L 917
Filtrate: 0.09 NTU
UVT: 89.3%
UVA: 0.049/cm
UVA Reduction: 58.5%
Settled: 0.78 NTU
24 mg/L 917
Filtrate: 0.08 NTU
UVT: 89.4%
UVA: 0.048/cm
UVA Reduction: 59.3%
Settled: 0.90 NTU
27 mg/L 917
Filtrate: 0.09 NTU
UVT: 89.4%
UVA: 0.048/cm
UVA Reduction: 59.3%
Settled: 1.19 NTU
30 mg/L 917
Filtrate: 0.13 NTU
UVT: 89.3%
UVA: 0.049/cm
UVA Reduction: 58.5%
Settled: 1.52 NTU

## Slide 32: Jars 17-20 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) PAC with Applied Coagulant 917

## Slide 33: Jars 17-20: End of 5-minute flocculation (25 RPM) duration.
0 mg/L PAC
25 mg/L 917
Filtrate: 0.07 NTU
UVT: 90.3%
UVA: 0.044/cm
UVA Reduction: 62.7%
Settled: 0.80 NTU
10 mg/L PAC
25 mg/L 917
Filtrate: 0.24 NTU
UVT: 91.3%
UVA: 0.039/cm
UVA Reduction: 66.9%
Settled: 4.93 NTU
15 mg/L PAC
25 mg/L 917
Filtrate: 0.17 NTU
UVT: 91.4%
UVA: 0.038/cm
UVA Reduction: 67.8%
Settled: 7.67 NTU
20 mg/L PAC
25 mg/L 917
Filtrate: 0.20 NTU
UVT: 91.8%
UVA: 0.036/cm
UVA Reduction: 69.5%
Settled: 10.5 NTU

## Slide 34: Jars 17-20: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 35: Jars 17-20: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L PAC
25 mg/L 917
Filtrate: 0.07 NTU
UVT: 90.3%
UVA: 0.044/cm
UVA Reduction: 62.7%
Settled: 0.80 NTU
10 mg/L PAC
25 mg/L 917
Filtrate: 0.24 NTU
UVT: 91.3%
UVA: 0.039/cm
UVA Reduction: 66.9%
Settled: 4.93 NTU
15 mg/L PAC
25 mg/L 917
Filtrate: 0.17 NTU
UVT: 91.4%
UVA: 0.038/cm
UVA Reduction: 67.8%
Settled: 7.67 NTU
20 mg/L PAC
25 mg/L 917
Filtrate: 0.20 NTU
UVT: 91.8%
UVA: 0.036/cm
UVA Reduction: 69.5%
Settled: 10.5 NTU

## Slide 36: Jars 21-24 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) PAC with Applied Coagulants CTC-00011

## Slide 37: Jars 21-24: End of 5-minute flocculation (25 RPM) duration.
0 mg/L PAC
80 mg/L CTC-00011
Filtrate: 0.05 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction: 66.9%
Settled: 0.77 NTU
10 mg/L PAC
80 mg/L CTC-00011
Filtrate: 0.05 NTU
UVT: 92.0%
UVA: 0.035/cm
UVA Reduction: 70.3%
Settled: 4.09 NTU
15 mg/L PAC
80 mg/L CTC-00011
Filtrate: 0.05 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 72.0%
Settled: 6.54 NTU
20 mg/L PAC
80 mg/L CTC-00011
Filtrate: 0.05 NTU
UVT: 93.1%
UVA: 0.030/cm
UVA Reduction: 74.6%
Settled: 8.97 NTU

## Slide 38: Jars 21-24: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L PAC
80 mg/L CTC-00011
Filtrate: 0.05 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction: 66.9%
Settled: 0.77 NTU
10 mg/L PAC
80 mg/L CTC-00011
Filtrate: 0.05 NTU
UVT: 92.0%
UVA: 0.035/cm
UVA Reduction: 70.3%
Settled: 4.09 NTU
15 mg/L PAC
80 mg/L CTC-00011
Filtrate: 0.05 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 72.0%
Settled: 6.54 NTU
20 mg/L PAC
80 mg/L CTC-00011
Filtrate: 0.05 NTU
UVT: 93.1%
UVA: 0.030/cm
UVA Reduction: 74.6%
Settled: 8.97 NTU

## Slide 39: Jars 25-28 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (25 RPM) Applied Coagulants CTC-00011/186K

## Slide 40: Jars 25-28: End of 5-minute flocculation (25 RPM) duration.
70 mg/L CTC-00011
0 mg/L 186K
Filtrate: 0.04 NTU
UVT: 90.5%
UVA: 0.042/cm
UVA Reduction: 64.4%
Settled: 0.54 NTU
70 mg/L CTC-00011
1 mg/L 186K
Filtrate: 0.04 NTU
UVT: 90.7%
UVA: 0.042/cm
UVA Reduction: 64.4%
Settled: 0.58 NTU
70 mg/L CTC-00011
2 mg/L 186K
Filtrate: 0.05 NTU
UVT: 90.7%
UVA: 0.042/cm
UVA Reduction: 64.4%
Settled: 0.97 NTU
70 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.04 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction: 65.3%
Settled: 0.80 NTU

## Slide 41: Jars 25-28: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 42: Jars 25-28: After 25-minutes of settling, settled water turbidity is taken.
70 mg/L CTC-00011
0 mg/L 186K
Filtrate: 0.04 NTU
UVT: 90.5%
UVA: 0.042/cm
UVA Reduction: 64.4%
Settled: 0.54 NTU
70 mg/L CTC-00011
1 mg/L 186K
Filtrate: 0.04 NTU
UVT: 90.7%
UVA: 0.042/cm
UVA Reduction: 64.4%
Settled: 0.58 NTU
70 mg/L CTC-00011
2 mg/L 186K
Filtrate: 0.05 NTU
UVT: 90.7%
UVA: 0.042/cm
UVA Reduction: 64.4%
Settled: 0.97 NTU
70 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.04 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction: 65.3%
Settled: 0.80 NTU

## Slide 43: Jars 28-32 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (25 RPM) PAC with Applied Coagulant CTC-00011

## Slide 44: Jars 29-32: End of 5-minute flocculation (25 RPM) duration.
0 mg/L PAC
50 mg/L CTC-00011
Filtrate: 0.04 NTU
UVT: 90.1%
UVA: 0.044/cm
UVA Reduction: 62.7%
Settled: 0.26 NTU
20 mg/L PAC
50 mg/L CTC-00011
Filtrate: 0.05 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction: 68.6%
Settled: 3.76 NTU
0 mg/L PAC
60 mg/L CTC-00011
Filtrate: 0.04 NTU
UVT: 90.3%
UVA: 0.044/cm
UVA Reduction: 62.7%
Settled: 0.48 NTU
20 mg/L PAC
60 mg/L CTC-00011
Filtrate: 0.04 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction: 69.5%
Settled: 2.62 NTU

## Slide 45: Jars 29-32: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 46: Jars 29-32: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L PAC
50 mg/L CTC-00011
Filtrate: 0.04 NTU
UVT: 90.1%
UVA: 0.044/cm
UVA Reduction: 62.7%
Settled: 0.26 NTU
20 mg/L PAC
50 mg/L CTC-00011
Filtrate: 0.05 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction: 68.6%
Settled: 3.76 NTU
0 mg/L PAC
60 mg/L CTC-00011
Filtrate: 0.04 NTU
UVT: 90.3%
UVA: 0.044/cm
UVA Reduction: 62.7%
Settled: 0.48 NTU
20 mg/L PAC
60 mg/L CTC-00011
Filtrate: 0.04 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction: 69.5%
Settled: 2.62 NTU

## Slide 47: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 48: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 49: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 50: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 51: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 52: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732