## Slide 1: City of Calistoga CA2810002 Napa County Jar Test
by Guy Schott, P.E.
February 3, 2020

## Slide 2: City of Calistoga Source Water: Kimball Reservoir

## Slide 3: City of Calistoga, February 3, 2020 Kimball Reservoir and Treated Water Characteristics
Source
Turbidity: 5.4 NTU
pH: 7.52
UVT: 75.1%, UVA: 0.124/cm
0.4 um Filtered
Turbidity: 0.3 NTU
UVT: 80.3%, UVA: 0.095/cm
Media Filter
Turbidity: 0.07 NTU
UVT: 95.6%, UVA: 0.019/cm
UVA Reduction: 80%
Post Cl2:
Turbidity: 0.09 NTU
UVT: 95.6%, UVA: 0.019/cm
UVA Reduction: 80%

## Slide 4: UVT/UVA
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 5: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.52
LCA #1:
JC 1600: 28.4 mg/L as product (no pH adjustment)
Final pH: 7.42
LCA #2:
JC 1720: 36 mg/L as product (no pH adjustment)
Final pH: 7.34
LCA #3:
7066: 134.6 mg/L as product (no pH adjustment)
Final pH: 6.95

## Slide 6: Coagulants Used for Jar Testing
JC 1600 (Jenfitch, LLC)
45-50% Aluminum Chlorohydrate
50% Water
SG = 1.34
JC 1720 (Jenfitch, LLC)
Polyaluminum Hydroxychlorosulfate
SG = 1.29
Basicity (70%)
JC 9450 (Jenfitch, LLC)
Has advanced reactive oxygen species (ROS)
SG = 1.14-1.22
7066 (Garratt Callahan)
10 – 30% Poly Aluminum Hydroxychloride Sulfate
50% Basicity
SG = 1.2
AH-423 (Garratt Callahan)
2.5 – 50% Aluminum Chlorohydrate
2.5-50% Polydimethyldiallylammonium Chloride
SG = 1.14 – 1.35

## Slide 7: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 8: City of Calistoga, Jar Test 1-8 Results Flash Mix 200 RPM (30 sec)
Jar # | 30 RPM Floc Mix Minutes | JC 1600 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 5 | 28 | 0.28 | 91.8 | 0.037 | 61.2 | 2.04
J2 | 5 | 31 | 0.11 | 92.5 | 0.033 | 65.4 | 2.39
J3 | 5 | 34 | 0.17 | 92.2 | 0.035 | 63.3 | 2.39
J4 | 5 | 37 | 0.11 | 92.9 | 0.032 | 66.4 | 2.21
J5 | 5 | 37 | 0.32 | 91.7 | 0.037 | 61.2 | 2.26
J6 | 5 | 40 | 0.40 | 91.6 | 0.038 | 60.1 | 2.46
J7 | 5 | 43 | 0.41 | 91.6 | 0.038 | 60.1 | 2.61
J8 | 5 | 47 | 0.44 | 91.3 | 0.039 | 59.1 | 2.51

## Slide 9: City of Calistoga, Jar Test 9-12 Results Flash Mix 200 RPM (30 sec), Floc Mix 30 RPM (5 min)
Jar # | JC 1600 mg/L | JC 1720 mg/L | 7066 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 31 | 3.1 | 0 | 0.13 | 92.3 | 0.034 | 64.3 | 1.33
J10 | 31 | 6.2 | 0 | 0.25 | 91.8 | 0.037 | 61.2 | 1.26
J11 | 37.7 | 36.6 | 0 | 0.13 | 93.4 | 0.030 | 68.5 | 1.07
J12 | 37 | 0 | 140 | 0.07 | 93.2 | 0.030 | 68.5 | 0.39

## Slide 10: City of Calistoga, Jar Test 13-16 Results Flash Mix 200 RPM (30 sec), Floc Mix 30 RPM (5 min)
Jar # | JC 1600 mg/L | JC 1720 mg/L | 7066 mg/L | JC 9450 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J13 | 37.7 | 36.6 | 0 | 0 | 0.06 | 94.7 | 0.023 | 75.9 | 0.60
J14 | 37.7 | 36.6 | 0 | 19.2 | 0.06 | 94.7 | 0.023 | 75.9 | 0.62
J15 | 0 | 0 | 140 | 0 | 0.06 | 93.7 | 0.028 | 70.6 | 0.35
J16 | 46 | 0 | 140 | 19.2 | 0.06 | 93.9 | 0.027 | 71.7 | 0.33

## Slide 11: City of Calistoga, Jar Test 17-20 Results Flash Mix 200 RPM (30 sec)
Jar # | 30 RPM Floc Mix min | JC 1600 mg/L | JC 1720 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J17 | 3 | 37.7 | 36.6 | 0.06 | 94.5 | 0.024 | 74.8 | 1.87
J18 | 5 | 37.7 | 36.6 | 0.07 | 94.3 | 0.025 | 73.8 | 1.07
J19 | 10 | 37.7 | 36.6 | 0.06 | 94.4 | 0.024 | 74.8 | 0.82
J20 | 15 | 37.7 | 36.6 | 0.09 | 94.3 | 0.025 | 73.8 | 0.39

## Slide 12: City of Calistoga, Jar Test 21-24 Results Flash Mix 200 RPM (30 sec)
Jar # | 30 RPM Floc Mix Minutes | JC 1720 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J21 | 5 | 36 | 0.07 | 92.5 | 0.033 | 65.4 | 1.08
J22 | 5 | 39 | 0.07 | 92.3 | 0.034 | 64.3 | 1.15
J23 | 5 | 42 | 0.10 | 92.4 | 0.034 | 64.3 | 1.07
J24 | 5 | 45 | 0.07 | 92.5 | 0.033 | 65.4 | 1.03

## Slide 13: City of Calistoga, Jar Test 25-28 Results No Flash Mix for Jars 25-28
Jar # | 30 RPM Floc Mix Minutes | JC 1600 mg/L | JC 1720 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J25 | 3 | 37.7 | 36.6 | 0.07 | 94.3 | 0.025 | 73.8 | 2.51
J26 | 5 | 37.7 | 36.6 | 0.12 | 94.0 | 0.026 | 72.7 | 1.53
J27 | 10 | 37.7 | 36.6 | 0.15 | 93.9 | 0.027 | 71.7 | 0.75
J28 | 15 | 37.7 | 36.6 | 0.10 | 94.0 | 0.026 | 72.7 | 0.43

## Slide 14: City of Calistoga, Jar Test 29-32 Results Flash Mix 200 RPM (30 Sec)
Jar # | 30 RPM Floc Mix Minutes | AH 423 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J29 | 5 | 35 | 0.23 | 92.6 | 0.033 | 65.3 | 1.04
J30 | 5 | 38 | 0.09 | 93.1 | 0.030 | 68.4 | 1.50
J31 | 5 | 41 | 0.24 | 92.5 | 0.033 | 65.3 | 1.31
J32 | 5 | 44 | 0.28 | n/a | n/a | n/a | 1.11

## Slide 15: Jars 1-4 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant JC 1600

## Slide 16: Jars 1-4: End of 5-minute flocculation (30 RPM) duration.
28 mg/L JC 1600
Filtrate 0.28 NTU
UVT: 91.8%
UVA: 0.037/cm
UVA Reduction: 61.2%
Settled: 2.04 NTU
31 mg/L JC 1600
Filtrate 0.11 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 65.4%
Settled: 2.39 NTU
34 mg/L JC 1600
Filtrate 0.17 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction: 63.3%
Settled: 2.39 NTU
37 mg/L JC 1600
Filtrate 0.11 NTU
UVT: 92.9%
UVA: 0.032/cm
UVA Reduction: 66.4%
Settled: 2.21 NTU

## Slide 17: Jars 1-4: After 5 min of settling, 25 mL is decanted for filterability and %UVT/UVA.

## Slide 18: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
28 mg/L JC 1600
Filtrate 0.28 NTU
UVT: 91.8%
UVA: 0.037/cm
UVA Reduction: 61.2%
Settled: 2.04 NTU
31 mg/L JC 1600
Filtrate 0.11 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 65.4%
Settled: 2.39 NTU
34 mg/L JC 1600
Filtrate 0.17 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction: 63.3%
Settled: 2.39 NTU
37 mg/L JC 1600
Filtrate 0.11 NTU
UVT: 92.9%
UVA: 0.032/cm
UVA Reduction: 66.4%
Settled: 2.21 NTU

## Slide 19: Jars 5-8 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant JC 1600

## Slide 20: Jars 5-8: End of 5-minute flocculation (30 RPM) duration.
37 mg/L JC 1600
Filtrate 0.32 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction: 61.2%
Settled: 2.26 NTU
40 mg/L JC 1600
Filtrate 0.40 NTU
UVT: 91.6%
UVA: 0.038/cm
UVA Reduction: 60.1%
Settled: 2.46 NTU
43 mg/L JC 1600
Filtrate 0.41 NTU
UVT: 91.6%
UVA: 0.038/cm
UVA Reduction: 60.1%
Settled: 2.61 NTU
47 mg/L JC 1600
Filtrate 0.44 NTU
UVT: 91.3%
UVA: 0.039/cm
UVA Reduction: 59.1%
Settled: 2.51 NTU

## Slide 21: Jars 5-8: After 5 min of settling, 25 mL is decanted for filterability and %UVT/UVA.

## Slide 22: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
37 mg/L JC 1600
Filtrate 0.32 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction: 61.2%
Settled: 2.26 NTU
40 mg/L JC 1600
Filtrate 0.40 NTU
UVT: 91.6%
UVA: 0.038/cm
UVA Reduction: 60.1%
Settled: 2.46 NTU
43 mg/L JC 1600
Filtrate 0.41 NTU
UVT: 91.6%
UVA: 0.038/cm
UVA Reduction: 60.1%
Settled: 2.61 NTU
47 mg/L JC 1600
Filtrate 0.44 NTU
UVT: 91.3%
UVA: 0.039/cm
UVA Reduction: 59.1%
Settled: 2.51 NTU

## Slide 23: Jars 9-12 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants JC 1600 JC 1720 7066

## Slide 24: Jars 9-12 Test: End of 5-minute flocculation (30 RPM) duration.
31 mg/L JC 1600
3.1 mg/L JC 1720
Filtrate 0.13 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction: 64.3%
Settled: 1.33 NTU
31 mg/L JC 1600
6.2 mg/L JC 1720
Filtrate 0.25 NTU
UVT: 91.8%
UVA: 0.037/cm
UVA Reduction: 61.2%
Settled: 1.26 NTU
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.13 NTU
UVT: 93.4%
UVA: 0.030/cm
UVA Reduction: 68.5%
Settled: 1.07 NTU
140 mg/L 7066
Filtrate 0.07 NTU
UVT: 93.2%
UVA: 0.031/cm
UVA Reduction: 68.5%
Settled: 0.39 NTU

## Slide 25: Jars 9-12: After 5 min of settling, 25 mL is decanted for filterability and %UVT/UVA.

## Slide 26: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
31 mg/L JC 1600
3.1 mg/L JC 1720
Filtrate 0.13 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction: 64.3%
Settled: 1.33 NTU
31 mg/L JC 1600
6.2 mg/L JC 1720
Filtrate 0.25 NTU
UVT: 91.8%
UVA: 0.037/cm
UVA Reduction: 61.2%
Settled: 1.26 NTU
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.13 NTU
UVT: 93.4%
UVA: 0.030/cm
UVA Reduction: 68.5%
Settled: 1.07 NTU
140 mg/L 7066
Filtrate 0.07 NTU
UVT: 93.2%
UVA: 0.031/cm
UVA Reduction: 68.5%
Settled: 0.39 NTU

## Slide 27: Jars 13-16 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants JC 1600 JC 1720 JC 9450 7066

## Slide 28: Jars 13-16: End of 5-minute flocculation (30 RPM) duration.
37.7 mg/L JC 1600
36.6 mg/L JC 1720
0 mg/L JC 9450
Filtrate 0.06 NTU
UVT: 94.7%
UVA: 0.023/cm
UVA Reduction: 75.9%
Settled: 0.60 NTU
37.7 mg/L JC 1600
36.6 mg/L JC 1720
19.2 mg/L JC 9450
Filtrate 0.06 NTU
UVT: 94.7%
UVA: 0.023/cm
UVA Reduction: 75.9%
Settled: 0.62 NTU
140 mg/L 7066
0 mg/L JC 9450
Filtrate 0.06 NTU
UVT: 93.7%
UVA: 0.028/cm
UVA Reduction: 70.6%
Settled: 0.35 NTU
140 mg/L 7066
19.2 mg/L JC 9450
Filtrate 0.06 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction: 71.7%
Settled: 0.33 NTU

## Slide 29: Jars 13-16: After 5 min of settling, 25 mL is decanted for filterability and %UVT/UVA.

## Slide 30: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
37.7 mg/L JC 1600
36.6 mg/L JC 1720
0 mg/L JC 9450
Filtrate 0.06 NTU
UVT: 94.7%
UVA: 0.023/cm
UVA Reduction: 75.9%
Settled: 0.60 NTU
37.7 mg/L JC 1600
36.6 mg/L JC 1720
19.2 mg/L JC 9450
Filtrate 0.06 NTU
UVT: 94.7%
UVA: 0.023/cm
UVA Reduction: 75.9%
Settled: 0.62 NTU
140 mg/L 7066
0 mg/L JC 9450
Filtrate 0.06 NTU
UVT: 93.7%
UVA: 0.028/cm
UVA Reduction: 70.6%
Settled: 0.35 NTU
140 mg/L 7066
19.2 mg/L JC 9450
Filtrate 0.06 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction: 71.7%
Settled: 0.33 NTU

## Slide 31: Jars 17-20 Test Flash Mix 30 Sec (200 RPM) Floc Mix 3/5/10/15 min (30 RPM) No Pictures Applied Coagulants JC 1600 JC 1720

## Slide 32: Jars 21-24 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant JC 1720

## Slide 33: Jars 21-24: End of 5-minute flocculation (30 RPM) duration.
36 mg/L JC 1720
Filtrate 0.07 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 65.4%
Settled: 1.08 NTU
39 mg/L JC 1720
Filtrate 0.07 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction: 65.4%
Settled: 1.15 NTU
42 mg/L JC 1720
Filtrate 0.10 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction: 64.3%
Settled: 1.07 NTU
45 mg/L JC 1720
Filtrate 0.07 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 65.4%
Settled: 1.03 NTU

## Slide 34: Jars 21-24: After 5 min of settling, 25 mL is decanted for filterability and %UVT/UVA.

## Slide 35: Jars 21-24: After 25-minutes of settling, settled water turbidity is taken.
36 mg/L JC 1720
Filtrate 0.07 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 65.4%
Settled: 1.08 NTU
39 mg/L JC 1720
Filtrate 0.07 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction: 65.4%
Settled: 1.15 NTU
42 mg/L JC 1720
Filtrate 0.10 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction: 64.3%
Settled: 1.07 NTU
45 mg/L JC 1720
Filtrate 0.07 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 65.4%
Settled: 1.03 NTU

## Slide 36: Jars 25-28 Test No Flash Mixing Floc Mix 3/5/10/15 min (30 RPM) Applied Coagulants JC 1600 JC 1720

## Slide 37: Jars 25-28 Test: End of 3-minute flocculation (30 RPM) duration for Jar 1.
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.07 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction: 73.8%
Settled: 2.51 NTU
Floc: 3 minutes
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.12 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 72.7%
Settled: 1.53 NTU
Floc: 5 minutes
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.15 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction: 71.7%
Settled: 0.75 NTU
Floc: 10 minutes
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.10 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 72.7%
Settled: 0.43 NTU
Floc: 15 minutes

## Slide 38: Jars 25-28 Test: End of 5-minute flocculation (30 RPM) duration for Jar 2.
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.07 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction: 73.8%
Settled: 2.51 NTU
Floc: 3 minutes
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.12 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 72.7%
Settled: 1.53 NTU
Floc: 5 minutes
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.15 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction: 71.7%
Settled: 0.75 NTU
Floc: 10 minutes
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.10 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 72.7%
Settled: 0.43 NTU
Floc: 15 minutes

## Slide 39: Jars 25-28 Test: End of 10-minute flocculation (30 RPM) duration for Jar 3.
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.07 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction: 73.8%
Settled: 2.51 NTU
Floc: 3 minutes
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.12 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 72.7%
Settled: 1.53 NTU
Floc: 5 minutes
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.15 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction: 71.7%
Settled: 0.75 NTU
Floc: 10 minutes
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.10 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 72.7%
Settled: 0.43 NTU
Floc: 15 minutes

## Slide 40: Jars 25-28: End of 15-minute flocculation (30 RPM) duration for Jar 4.
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.07 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction: 73.8%
Settled: 2.51 NTU
Floc: 3 minutes
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.12 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 72.7%
Settled: 1.53 NTU
Floc: 5 minutes
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.15 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction: 71.7%
Settled: 0.75 NTU
Floc: 10 minutes
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.10 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 72.7%
Settled: 0.43 NTU
Floc: 15 minutes

## Slide 41: Jars 21-24 Test: After 25-minutes of settling for Jar 4, settled water turbidity is taken.
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.07 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction: 73.8%
Settled: 2.51 NTU
Floc: 3 minutes
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.12 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 72.7%
Settled: 1.53 NTU
Floc: 5 minutes
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.15 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction: 71.7%
Settled: 0.75 NTU
Floc: 10 minutes
37.7 mg/L JC 1600
36.6 mg/L JC 1720
Filtrate 0.10 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 72.7%
Settled: 0.43 NTU
Floc: 15 minutes

## Slide 42: Jars 28-32 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant AH-423

## Slide 43: Jars 28-32: End of 5-minute flocculation (30 RPM) duration.
35 mg/L AH-423
Filtrate 0.23 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction: 65.3%
Settled: 1.04 NTU
38 mg/L AH-423
Filtrate 0.09 NTU
UVT: 93.1%
UVA: 0.030/cm
UVA Reduction: 68.4%
Settled: 1.50 NTU
41 mg/L AH-423
Filtrate 0.24 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 65.3%
Settled: 1.31 NTU
44 mg/L AH-423
Filtrate 0.28 NTU
UVT: -%
UVA: -/cm
Settled: 1.11 NTU

## Slide 44: Jars 28-32: After 5 min of settling, 25 mL is decanted for filterability and %UVT/UVA.

## Slide 45: Jars 28-32 Test: After 25-minutes of settling, settled water turbidity is taken.
35 mg/L AH-423
Filtrate 0.23 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction: 65.3%
Settled: 1.04 NTU
38 mg/L AH-423
Filtrate 0.09 NTU
UVT: 93.1%
UVA: 0.030/cm
UVA Reduction: 68.4%
Settled: 1.50 NTU
41 mg/L AH-423
Filtrate 0.24 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 65.3%
Settled: 1.31 NTU
44 mg/L AH-423
Filtrate 0.28 NTU
UVT: -%
UVA: -/cm
Settled: 1.11 NTU

## Slide 46: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-60 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 47: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 48: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 49: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 50: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 51: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732