## Slide 1: City of St. Helena CA2810004 Napa County Jar Test
by Guy Schott, P.E.
September 18, 2024

## Slide 2: Source Water: Bell Canyon Reservoir
Source Water Characteristics
Turbidity: 3.23 NTU
pH: 7.13
Alkalinity: 33.2 mg/L CaCO3
Fe: 0.40 mg/L
UVT: 67.35%
UVA: 0.1715/cm
0.4 um Filtered
UVT: 70.02%
UVA: 0.1548/cm

## Slide 3: Flocculation/Sedimentation Basins

## Slide 4: Bell Canyon Reservoir Source & Treated Water Characteristics, September 18, 2024
Source – Bell Canyon Reservoir
pH: 7.13
Alkalinity: 33.2 mg/L as CaCO3
Turbidity: 3.23 NTU
Fe: 0.40 mg/L
UVT: 67.3%,
UVA: 0.1715/cm
0.4 um Filtered
Turbidity: 1.03 NTU
UVT: 70.02%,
UVA: 0.1548/cm
Filter 1 Water
pH: 6.19
Alkalinity: 10.6 mg/L as CaCO3
Turbidity: 0.06 NTU
Fe: 0.0 mg/L
UVT: 90.66%, UVA: 0.0426/cm
Clearwell Water
pH: 7.30
Alkalinity: 30.6 mg/L as CaCO3
0.12 NTU
Fe: 0.0 mg/L
UVT: 92.32%, UVA: 0.0348/cm

## Slide 5: UVT/UVA, pathlength 40 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 6: Applied Coagulants for Jar Testing
Aluminum Sulfate (Product)
Al2(SO4)3*14.3H20 (Liquid)
47.47% Aluminum Sulfate
52% Water
8.08% Al2O3
0% Basicity
SG = 1.325
NSF max use: 400 mg/L (product)
As hydrated Al2(SO4)3*14.3H20
17% Al2O3
Ferric Sulfate
50% Ferric Sulfate
50% Water
SG = 1.40-1.51
NSF limit: 600 mg/L as Product
NTU Technologies
Zeta Floc 20, Organic Polymer
20% pDADMAC
80% Water
SG = 1.07
NSF limit: 50 mg/L as Product

## Slide 7: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.13
LCA #1
FeSO4: 65 mg/L as FeSO4
No pH adjustment.

## Slide 8: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength). Aluminum sulfate is reported as Alum.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 9: City of St. Helena : Jar Test Summary - Results
Jar # | NaOCl mg/L | Alum mg/L | FeSO4 mg/L | Zeta Floc 20 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Improved Reduction* | pH | Fe mg/L
JA | 0 | 50 | - | - | 0.05 | 88.56 | 0.0528 | 0 | 6.06 | -
JB | 2.0 | 50 | - | - | 0.05 | 88.37 | 0.0537 | 0 | 6.10 | -
JC | 2.0 | 50 | - | - | 0.04 | 88.36 | 0.0538 | 0 | - | -
JD | 0 | - | 70 | - | 0.05 | 91.78 | 0.0365 | 31.6 | 5.33 | -
JH | 0 | - | 70 | 1.0 | 0.04 | 92.95 | 0.0318 | 40.4 | 5.18 | 0.060
JE | 2.0 | - | 70 | - | 0.05 | 91.34 | 0.0394 | 26.2 | 5.37 | 0.022
JF | 2.0 | - | 70 | 1.0 | 0.04 | 92.24 | 0.0351 | 34.3 | - | 0.002
JG | 2.0 | - | 70 | 1.0 | 0.03 | 91.83 | 0.0371 | 30.5 | 5.41 | 0.010
JI | 2.0 | - | 70 | 1.0 | 0.04 | 92.56 | 0.0336 | 37.1 | 5.25 | 0.003
*The FeSO4 %UVA is the relative improvement from the average UVA/cm for the Alum dose of 50 mg/L.

## Slide 10: City of St. Helena : Jar Test 1-8 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar # | NaOCl mg/L | Alum mg/L | FeSO4 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min | pH
J1 | - | 50 | - | 0.05 | 88.56 | 0.0528 | 65.9 | 0.44 | 6.06
J2 | - | - | 60 | 0.14 | 89.82 | 0.0467 | 69.8 | 1.02 | 5.69
J3 | - | - | 65 | 0.10 | 90.90 | 0.0415 | 73.2 | 0.98 | 5.55
J4 | - | - | 70 | 0.05 | 91.94 | 0.0365 | 76.4 | 0.88 | 5.33
J5 | 2.0 | 50 | - | 0.05 | 88.37 | 0.0537 | 65.3 | 0.38 | 6.10
J6 | 2.0 | - | 60 | 0.16 | 88.65 | 0.0524 | 66.1 | 1.15 | 5.87
J7 | 2.0 | - | 65 | 0.08 | 90.71 | 0.0424 | 72.6 | 0.79 | 5.59
J8 | 2.0 | - | 70 | 0.05 | 91.34 | 0.0394 | 74.5 | 0.77 | 5.37
Source water jar testing was taken after Post NaMnO4

## Slide 11: City of St. Helena : Jar Test 9-12 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar # | NaOCl mg/L | Alum mg/L | FeSO4 mg/L | Zeta Floc 20 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 2.0 | 50 | - | - | 0.04 | 88.36 | 0.0538 | 65.2 | 0.30
J10 | 2.0 | - | 60 | 1.0 | 0.04 | 91.03 | 0.0408 | 73.6 | 0.64
J11 | 2.0 | - | 65 | 1.0 | 0.03 | 91.55 | 0.0384 | 75.2 | 0.66
J12 | 2.0 | - | 70 | 1.0 | 0.04 | 92.24 | 0.0351 | 77.3 | 0.69
Source water jar testing was taken after Post NaMnO4

## Slide 12: City of St. Helena : Jar Test 13-18 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar # | NaOCl mg/L | Alum mg/L | FeSO4 mg/L | Zeta Floc 20 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min | pH
J13 | 2.0 | 50 | - | - | 0.04 | 88.76 | 0.0518 | 66.5 | 0.40 | 6.13
J14 | 0.0 | - | 70 | 0 | 0.06 | 92.13 | 0.0356 | 77.0 | 0.57 | 5.30
J15 | 2.0 | - | 75 | 0 | 0.07 | 91.40 | 0.0391 | 74.7 | 0.74 | 5.39
J16 | 2.0 | - | 70 | 1.0 | 0.03 | 91.83 | 0.0371 | 76.0 | 0.61 | 5.41
J17 | 0.0 | - | 70 | 1.0 | 0.04 | 92.95 | 0.0318 | 79.5 | 0.96 | 5.18
J18 | 2.0 | - | 70 | 1.0 | 0.04 | 92.56 | 0.0336 | 78.3 | 0.38 | 5.25
Source water jar testing was taken after Post NaMnO4

## Slide 13: Jars 1-4 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post NaMnO4 Applied Coagulants Alum/FeSO4

## Slide 14: Jars 1-4: End of 5-minute flocculation (30 RPM) duration.
50 mg/L Alum
Filtrate: 0.05 NTU
UVT: 88.56%
UVA: 0.0528/cm
UVA Reduction: 65.9%
Settled: 0.44 NTU
pH: 6.06
60 mg/L FeSO4
Filtrate: 0.14 NTU
UVT: 89.82%
UVA: 0.0467/cm
UVA Reduction: 65.9%
Settled: 1.02 NTU
pH: 5.69
65 mg/L FeSO4
Filtrate: 0.10 NTU
UVT: 90.90%
UVA: 0.0415/cm
UVA Reduction: 65.9%
Settled: 0.98 NTU
pH: 5.55
70 mg/L FeSO4
Filtrate: 0.05 NTU
UVT: 91.78%
UVA: 0.0365/cm
UVA Reduction: 76.4%
Settled: 0.88 NTU
pH: 5.33

## Slide 15: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 16: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
50 mg/L Alum
Filtrate: 0.05 NTU
UVT: 88.56%
UVA: 0.0528/cm
UVA Reduction: 65.9%
Settled: 0.44 NTU
pH: 6.06
60 mg/L FeSO4
Filtrate: 0.14 NTU
UVT: 89.82%
UVA: 0.0467/cm
UVA Reduction: 65.9%
Settled: 1.02 NTU
pH: 5.69
65 mg/L FeSO4
Filtrate: 0.10 NTU
UVT: 90.90%
UVA: 0.0415/cm
UVA Reduction: 65.9%
Settled: 0.98 NTU
pH: 5.55
70 mg/L FeSO4
Filtrate: 0.05 NTU
UVT: 91.78%
UVA: 0.0365/cm
UVA Reduction: 76.4%
Settled: 0.88 NTU
pH: 5.33

## Slide 17: Jars 5-8 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post NaMnO4 Applied Coagulants Alum/FeSO4

## Slide 18: Jars 5-8: End of 5-minute flocculation (30 RPM) duration.
2.0 mg/L NaOCl
50 mg/L Alum
Filtrate: 0.05 NTU
UVT: 88.37%
UVA: 0.0537/cm
UVA Reduction: 65.3%
Settled: 0.38 NTU
pH: 6.10
2.0 mg/L NaOCl
60 mg/L FeSO4
Filtrate: 0.16 NTU
UVT: 89.65%
UVA: 0.0524/cm
UVA Reduction: 66.1%
Settled: 1.15 NTU
pH: 5.87
2.0 mg/L NaOCl
65 mg/L FeSO4
Filtrate: 0.08 NTU
UVT: 90.54%
UVA: 0.0424/cm
UVA Reduction: 72.6%
Settled: 0.79 NTU
pH: 5.59
2.0 mg/L NaOCl
70 mg/L FeSO4
Filtrate: 0.05 NTU
UVT: 91.20%
UVA: 0.0394/cm
UVA Reduction: 74.5%
Settled: 0.77 NTU
pH: 5.37, Fe: 0.022 mg/L

## Slide 19: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 20: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
2.0 mg/L NaOCl
50 mg/L Alum
Filtrate: 0.05 NTU
UVT: 88.37%
UVA: 0.0537/cm
UVA Reduction: 65.3%
Settled: 0.38 NTU
pH: 6.10
2.0 mg/L NaOCl
60 mg/L FeSO4
Filtrate: 0.16 NTU
UVT: 89.65%
UVA: 0.0524/cm
UVA Reduction: 66.1%
Settled: 1.15 NTU
pH: 5.87
2.0 mg/L NaOCl
65 mg/L FeSO4
Filtrate: 0.08 NTU
UVT: 90.54%
UVA: 0.0424/cm
UVA Reduction: 72.6%
Settled: 0.79 NTU
pH: 5.59
2.0 mg/L NaOCl
70 mg/L FeSO4
Filtrate: 0.05 NTU
UVT: 91.20%
UVA: 0.0394/cm
UVA Reduction: 74.5%
Settled: 0.77 NTU
pH: 5.37, Fe: 0.022 mg/L

## Slide 21: Jars 9-12 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post NaMnO4 Applied Coagulants Alum/FeSO4

## Slide 22: Jars 9-12: End of 5-minute flocculation (30 RPM) duration.
2.0 mg/L NaOCl
50 mg/L Alum
Filtrate: 0.04 NTU
UVT: 88.36%
UVA: 0.0538/cm
UVA Reduction: 65.2%
Settled: 0.30 NTU
2.0 mg/L NaOCl
60 mg/L FeSO4
1.0 mg/L ZetaFloc 20
Filtrate: 0.04 NTU
UVT: 91.03%
UVA: 0.0408/cm
UVA Reduction: 73.6%
Settled: 0.64 NTU
2.0 mg/L NaOCl
65 mg/L FeSO4
1.0 mg/L ZetaFloc 20
Filtrate: 0.03 NTU
UVT: 91.55%
UVA: 0.0384/cm
UVA Reduction: 75.2%
Settled: 0.66 NTU
2.0 mg/L NaOCl
70 mg/L FeSO4
1.0 mg/L ZetaFloc 20
Filtrate: 0.04 NTU
UVT: 92.24%
UVA: 0.0351/cm
UVA Reduction: 77.3%
Settled: 0.69 NTU

## Slide 23: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 24: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
2.0 mg/L NaOCl
50 mg/L Alum
Filtrate: 0.04 NTU
UVT: 88.36%
UVA: 0.0538/cm
UVA Reduction: 65.2%
Settled: 0.30 NTU
2.0 mg/L NaOCl
60 mg/L FeSO4
1.0 mg/L ZetaFloc 20
Filtrate: 0.04 NTU
UVT: 91.03%
UVA: 0.0408/cm
UVA Reduction: 73.6%
Settled: 0.64 NTU
2.0 mg/L NaOCl
65 mg/L FeSO4
1.0 mg/L ZetaFloc 20
Filtrate: 0.03 NTU
UVT: 91.55%
UVA: 0.0384/cm
UVA Reduction: 75.2%
Settled: 0.66 NTU
2.0 mg/L NaOCl
70 mg/L FeSO4
1.0 mg/L ZetaFloc 20
Filtrate: 0.04 NTU
UVT: 92.24%
UVA: 0.0351/cm
UVA Reduction: 77.3%
Settled: 0.69 NTU

## Slide 25: Jars 13-16 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post NaMnO4 Applied Coagulants Alum/FeSO4

## Slide 26: Jars 13-16: End of 5-minute flocculation (30 RPM) duration.
2.0 mg/L NaOCl
50 mg/L Alum
Filtrate: 0.04 NTU
UVT: 88.76%
UVA: 0.0518/cm
UVA Reduction: 66.5%
Settled: 0.40 NTU
pH: 6.13
2.0 mg/L NaOCl
70 mg/L FeSO4
Filtrate: 0.04 NTU
UVT: 91.03%
UVA: 0.0408/cm
UVA Reduction: 73.6%
Settled: 0.64 NTU
pH: 5.30, Fe: 0.055 mg/L
2.0 mg/L NaOCl
70 mg/L FeSO4
1.0 mg/L ZetaFloc 20
Filtrate: 0.03 NTU
UVT: 91.83%
UVA: 0.0371/cm
UVA Reduction: 76.0%
Settled: 0.61 NTU
pH: 5.41, Fe: 0.010 mg/L
2.0 mg/L NaOCl
70 mg/L FeSO4
Filtrate: 0.07 NTU
UVT: 91.4%
UVA: 0.0391/cm
UVA Reduction: 74.7%
Settled: 0.74 NTU
pH: 5.39, Fe: 0.003 mg/L

## Slide 27: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 28: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
2.0 mg/L NaOCl
50 mg/L Alum
Filtrate: 0.04 NTU
UVT: 88.76%
UVA: 0.0518/cm
UVA Reduction: 66.5%
Settled: 0.40 NTU
pH: 6.13
2.0 mg/L NaOCl
70 mg/L FeSO4
Filtrate: 0.04 NTU
UVT: 91.03%
UVA: 0.0408/cm
UVA Reduction: 73.6%
Settled: 0.64 NTU
pH: 5.30, Fe: 0.055 mg/L
2.0 mg/L NaOCl
70 mg/L FeSO4
1.0 mg/L ZetaFloc 20
Filtrate: 0.03 NTU
UVT: 91.83%
UVA: 0.0371/cm
UVA Reduction: 76.0%
Settled: 0.61 NTU
pH: 5.41, Fe: 0.010 mg/L
2.0 mg/L NaOCl
70 mg/L FeSO4
Filtrate: 0.07 NTU
UVT: 91.4%
UVA: 0.0391/cm
UVA Reduction: 74.7%
Settled: 0.74 NTU
pH: 5.39, Fe: 0.003 mg/L

## Slide 29: Jars 17-18 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Post NaMnO4 Applied Coagulants Alum/FeSO4

## Slide 30: Jars 17-18: End of 5-minute flocculation (30 RPM) duration.
0 mg/L NaOCl
70 mg/L FeSO4
Filtrate: 0.04 NTU
UVT: 92.95%
UVA: 0.0318/cm
UVA Reduction: 79.5%
Settled: 0.96 NTU
pH: 5.18, Fe: 0.060 mg/L
2.0 mg/L NaOCl
70 mg/L FeSO4
Filtrate: 0.04 NTU
UVT: 92.56%
UVA: 0.0408/cm
UVA Reduction: 78.3%
Settled: 0.38 NTU
pH: 5.25, Fe: 0.003 mg/L

## Slide 31: Jars 17-18: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 32: Jars 17-18: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L NaOCl
70 mg/L FeSO4
Filtrate: 0.04 NTU
UVT: 92.95%
UVA: 0.0318/cm
UVA Reduction: 79.5%
Settled: 0.96 NTU
pH: 5.18, Fe: 0.060 mg/L
2.0 mg/L NaOCl
70 mg/L FeSO4
Filtrate: 0.04 NTU
UVT: 92.56%
UVA: 0.0408/cm
UVA Reduction: 78.3%
Settled: 0.38 NTU
pH: 5.25, Fe: 0.003 mg/L

## Slide 33: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-60 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 34: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 35: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 36: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 37: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 38: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Jar Testing Done Right training video: https://www.youtube.com/watch?v=aGByyxhelkI
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732