## Slide 1: City of St. Helena CA2810004 Napa County Jar Test
by Guy Schott, P.E.
September 5, 2024

## Slide 2: Source Water: Bell Canyon Reservoir
Source Water Characteristics
Turbidity: 8.94 NTU
pH: 7.21
UVT: 69.21%
UVA: 0.1599
0.4 um Filtered
UVT: 73.46%
UVA: 0.1340

## Slide 3: Flocculation/Sedimentation Basins

## Slide 4: Bell Canyon Reservoir Source & Treated Water Characteristics, September 5, 2024
Source – Bell Canyon Reservoir
pH: 7.21
Alkalinity: 32 mg/L as CaCO3
Turbidity: 8.94 NTU
UVT: 69.21%,
UVA: 0.1599/cm
0.4 um Filtered
Turbidity: 0.74 NTU
UVT: 73.46%,
UVA: 0.1340/cm
Plant Filtrate Water
pH: 6.31
Alkalinity: 11.7 mg/L as CaCO3
0.08 NTU
UVT: 90.37%,
UVA: 0.0440/cm

## Slide 5: UVT/UVA, pathlength 40 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 6: Applied Coagulants for Jar Testing (1)
Aluminum Sulfate (Product)
Al2(SO4)3*14.3H20 (Liquid)
47.47% Aluminum Sulfate
52% Water
8.08% Al2O3
0% Basicity
SG = 1.325
NSF max use: 400 mg/L (product)
As hydrated Al2(SO4)3*14.3H20
17% Al2O3
Ferric Chloride
42.4% Ferric Chloride
47.6% Water
SG = 1.44
NSF limit: 250 mg/L as Product

## Slide 7: Applied Coagulants for Jar Testing (2)
Pro Pac 917 (NTU Technologies, Inc.)
10% polyamine (50% water, 50% active polyamines)
45% Aluminum Chlorohydrate (ACH)
~21.3% Al2O3
~11.3% Al
45% Water
83% Basicity
SG = 1.25-1.34
NSF limit: 100 mg/L as Product
NTU Technologies
Pro Pac 9810
45-50% Aluminum Chlorohydrate
45-50% Water
~22.4% Al2O3
~11.9% Al
83% Basicity
5% polyamine (50% water, 50% active polyamines)
SG = 1.25-1.34
NSF Max Use: 200 mg/L as Product;

## Slide 8: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.21
LCA #1
917: 18.7 mg/L as product
No pH adjustment.
LCA #2:
Aluminum Sulfate: 49.9 mg/L as Alum
pH adjusted to 6.6
Aluminum Sulfate: 67.6 mg/L as Alum
No pH adjustment

## Slide 9: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength). Aluminum sulfate is reported as Alum.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 10: City of St. Helena : Jar Test 1-4 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (7 min)
Jar # | Alum mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min | pH | Alk mg/L CaCO3
J1 | 45 | 0.06 | 88.35 | 0.0538 | 59.8 | 0.26 | 6.15 | 13.5
J2 | 50 | 0.05 | 89.41 | 0.0487 | 63.7 | 0.33 | 6.06 | 11.5
J3 | 55 | 0.05 | 89.63 | 0.0476 | 64.5 | 0.25 | 5.93 | 10.4
J4 | 60 | 0.07 | 89.82 | 0.0467 | 65.2 | 0.28 | 5.83 | 8.3
Source water jar testing was taken after Post NaMnO4

## Slide 11: City of St. Helena : Jar Test 5-8 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (9 min)
Jar # | 917 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min | pH | Alk mg/L CaCO3
J5 | 18 | 0.06 | 86.33 | 0.0639 | 52.3 | 0.47 | 7.16 | 32.2
J6 | 22 | 0.05 | 87.38 | 0.0586 | 56.3 | 0.25 | 7.13 | 30.8
J7 | 26 | 0.05 | 88.11 | 0.0586 | 58.3 | 0.22 | 7.12 | 31.0
J8 | 30 | 0.06 | 88.66 | 0.0523 | 61.0 | 0.44 | 7.10 | 30.9
Source water jar testing was taken after Post NaMnO4

## Slide 12: City of St. Helena : Jar Test 9-12 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (9 min)
Jar # | 917 mg/L | Alum mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min | pH | Alk mg/L CaCO3
J9 | 20 | 0 | 0.06 | 55.4 | 0.0597 | 55.4 | 0.25 | 7.15 | 31.3
J10 | 20 | 10 | 0.06 | 56.5 | 0.0583 | 56.5 | 0.24 | 6.86 | 26.8
J11 | 20 | 20 | 0.05 | 59.3 | 0.0546 | 59.3 | 0.25 | 6.63 | 22.2
J12 | 20 | 30 | 0.06 | 61.4 | 0.0517 | 61.4 | 0.40 | 6.42 | 18.3
Source water jar testing was taken after Post NaMnO4

## Slide 13: City of St. Helena : Jar Test 13-16 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (9 min)
Jar # | 917 mg/L | Alum mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min | pH | Alk mg/L CaCO3
J13 | 20 | 35 | 0.05 | 89.90 | 0.0463 | 65.4 | 0.30 | 6.31 | 16.5
J14 | 20 | 40 | 0.05 | 90.01 | 0.0457 | 65.9 | 0.46 | 6.20 | 14.0
J15 | 20 | 45 | 0.05 | 90.39 | 0.0439 | 67.2 | 0.49 | 6.11 | 13.0
J16 | 20 | 50 | 0.05 | 92.00 | 0.0448 | 66.6 | 0.46 | 6.00 | 10.5
Source water jar testing was taken after Post NaMnO4

## Slide 14: City of St. Helena : Jar Test 17-20 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (9 min)
Jar # | 9810 mg/L | Alum mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min | pH | Alk mg/L CaCO3
J17 | 24 | 0 | 0.05 | 88.04 | 0.0554 | 58.7 | 0.20 | 7.20 | 30.7
J18 | 24 | 20 | 0.05 | 88.83 | 0.0513 | 61.7 | 0.17 | 6.63 | 22.0
J19 | 24 | 25 | 0.05 | 89.01 | 0.0506 | 62.2 | 0.20 | 6.54 | 19.9
J20 | 24 | 30 | 0.05 | 89.22 | 0.0496 | 63.0 | 0.24 | 6.42 | 18.0
Source water jar testing was taken after Post NaMnO4

## Slide 15: City of St. Helena : Jar Test 21-24 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (9 min)
Jar # | 9810 mg/L | Alum mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min | pH | Alk mg/L CaCO3
J21 | 0 | 50 | 0.05 | 89.77 | 0.0469 | 65.0 | 0.26 | 6.05 | 11.9
J22 | 28 | 25 | 0.06 | 89.57 | 0.0478 | 64.3 | 0.34 | 6.48 | 20.0
J23 | 32 | 25 | 0.08 | 89.74 | 0.0470 | 64.9 | 0.45 | 6.45 | 19.8
J24 | 36 | 25 | 0.08 | 89.83 | 0.0466 | 65.2 | 0.47 | 6.44 | 20.5
Source water jar testing was taken after Post NaMnO4

## Slide 16: City of St. Helena : Jar Test 25-28 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (7 min)
Jar # | 9810 mg/L | FeCl3 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min | pH | Alk mg/L CaCO3
J25 | 0 | 27 | 0.08 | 88.92 | 0.0510 | 61.9 | 0.50 | 6.19 | 13.2
J26 | 24 | 10 | 0.05 | 89.48 | 0.0473 | 64.7 | 0.42 | 6.74 | 23.4
J27 | 24 | 15 | 0.05 | 90.46 | 0.0430 | 67.9 | 0.42 | 6.53 | 19.9
J28 | 24 | 20 | 0.05 | 91.30 | 0.0395 | 70.5 | 0.66 | 6.35 | 16.7
J29 | 0 | 35 | 0.05 | 92.63 | 0.0333 | 75.1 | 0.35 | 5.79 | 7.4
J30 | 24 | 25 | 0.05 | 91.76 | 0.0374 | 72.1 | 1.79 | 6.14 | -
Source water jar testing was taken after Post NaMnO4

## Slide 17: Jars 1-4 Test Flash Mix 20 Sec (200 RPM) Floc Mix 7 min (30 RPM) Post NaMnO4 Applied Coagulant Alum

## Slide 18: Jars 1-4: End of 7-minute flocculation (30 RPM) duration.
45 mg/L Alum
Filtrate: 0.06 NTU
UVT: 88.35%
UVA: 0.0538/cm
UVA Reduction: 59.9%
Settled: 0.26 NTU
pH: 6.15, Alk: 13.5 mg/L
50 mg/L Alum
Filtrate: 0.05 NTU
UVT: 89.41%
UVA: 0.0487/cm
UVA Reduction: 63.7%
Settled: 0.33 NTU
pH: 6.06, Alk: 11.5 mg/L
55 mg/L Alum
Filtrate: 0.05 NTU
UVT: 89. 63%
UVA: 0.0476/cm
UVA Reduction: 64.5%
Settled: 0.25 NTU
pH: 5.93, Alk: 10.4 mg/L
60 mg/L Alum
Filtrate: 0.07 NTU
UVT: 89. 82%
UVA: 0.0467/cm
UVA Reduction: 65.2%
Settled: 0.28 NTU
pH: 5.83, Alk: 8.3 mg/L

## Slide 19: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 20: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
45 mg/L Alum
Filtrate: 0.06 NTU
UVT: 88.35%
UVA: 0.0538/cm
UVA Reduction: 59.9%
Settled: 0.26 NTU
pH: 6.15, Alk: 13.5 mg/L
50 mg/L Alum
Filtrate: 0.05 NTU
UVT: 89.41%
UVA: 0.0487/cm
UVA Reduction: 63.7%
Settled: 0.33 NTU
pH: 6.06, Alk: 11.5 mg/L
55 mg/L Alum
Filtrate: 0.05 NTU
UVT: 89. 63%
UVA: 0.0476/cm
UVA Reduction: 64.5%
Settled: 0.25 NTU
pH: 5.93, Alk: 10.4 mg/L
60 mg/L Alum
Filtrate: 0.07 NTU
UVT: 89. 82%
UVA: 0.0467/cm
UVA Reduction: 65.2%
Settled: 0.28 NTU
pH: 5.83, Alk: 8.3 mg/L

## Slide 21: Jars 5-8 Test Flash Mix 20 Sec (200 RPM) Floc Mix 9 min (30 RPM) Post NaMnO4 Applied Coagulant 917

## Slide 22: Jars 5-8: End of 9-minute flocculation (30 RPM) duration.
18 mg/L 917
Filtrate: 0.06 NTU
UVT: 86.4%
UVA: 0.0639/cm
UVA Reduction: 52.3%
Settled: 0.47 NTU
pH: 7.16, Alk: 32.2 mg/L
22 mg/L 917
Filtrate: 0.05 NTU
UVT: 87.4%
UVA: 0.0586/cm
UVA Reduction: 56.3%
Settled: 0.25 NTU
pH: 7.13, Alk: 30.8 mg/L
26 mg/L 917
Filtrate: 0.05 NTU
UVT: 88.1%
UVA: 0.0550/cm
UVA Reduction: 59.0%
Settled: 0.22 NTU
pH: 7.12, Alk: 31.0 mg/L
30 mg/L 917
Filtrate: 0.05 NTU
UVT: 88.7%
UVA: 0.0523/cm
UVA Reduction: 61.0%
Settled: 0.44 NTU
pH: 7.10, Alk: 30.9 mg/L

## Slide 23: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 24: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
18 mg/L 917
Filtrate: 0.06 NTU
UVT: 86.4%
UVA: 0.0639/cm
UVA Reduction: 52.3%
Settled: 0.47 NTU
pH: 7.16, Alk: 32.2 mg/L
22 mg/L 917
Filtrate: 0.05 NTU
UVT: 87.4%
UVA: 0.0586/cm
UVA Reduction: 56.3%
Settled: 0.25 NTU
pH: 7.13, Alk: 30.8 mg/L
26 mg/L 917
Filtrate: 0.05 NTU
UVT: 88.1%
UVA: 0.0550/cm
UVA Reduction: 59.0%
Settled: 0.22 NTU
pH: 7.12, Alk: 31.0 mg/L
30 mg/L 917
Filtrate: 0.05 NTU
UVT: 88.7%
UVA: 0.0523/cm
UVA Reduction: 61.0%
Settled: 0.44 NTU
pH: 7.10, Alk: 30.9 mg/L

## Slide 25: Jars 9-12 Test Flash Mix 20 Sec (200 RPM) Floc Mix 8 min (30 RPM) Post NaMnO4 Applied Coagulant 917 Alum

## Slide 26: Jars 9-12: End of 8-minute flocculation (30 RPM) duration.
20 mg/L 917
0 mg/L Alum
Filtrate: 0.06 NTU
UVT: 87.2%
UVA: 0.0597/cm
UVA Reduction: 55.4%
Settled: 0.25 NTU
pH: 7.15, Alk: 31.3 mg/L
20 mg/L 917
10 mg/L Alum
Filtrate: 0.06 NTU
UVT: 87.4%
UVA: 0.0583/cm
UVA Reduction: 56.5%
Settled: 0.23 NTU
pH: 6.86, Alk: 23.8 mg/L
20 mg/L 917
20 mg/L Alum
Filtrate: 0.05 NTU
UVT: 88.2%
UVA: 0.0546/cm
UVA Reduction: 59.3%
Settled: 0.25 NTU
pH: 6.63, Alk: 22.2 mg/L
20 mg/L 917
30 mg/L Alum
Filtrate: 0.06 NTU
UVT: 88.8%
UVA: 0.0517/cm
UVA Reduction: 61.4%
Settled: 0.40 NTU
pH: 6.42, Alk: 18.3 mg/L

## Slide 27: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 28: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
20 mg/L 917
0 mg/L Alum
Filtrate: 0.06 NTU
UVT: 87.2%
UVA: 0.0597/cm
UVA Reduction: 55.4%
Settled: 0.25 NTU
pH: 7.15, Alk: 31.3 mg/L
20 mg/L 917
10 mg/L Alum
Filtrate: 0.06 NTU
UVT: 87.4%
UVA: 0.0583/cm
UVA Reduction: 56.5%
Settled: 0.23 NTU
pH: 6.86, Alk: 23.8 mg/L
20 mg/L 917
20 mg/L Alum
Filtrate: 0.05 NTU
UVT: 88.2%
UVA: 0.0546/cm
UVA Reduction: 59.3%
Settled: 0.25 NTU
pH: 6.63, Alk: 22.2 mg/L
20 mg/L 917
30 mg/L Alum
Filtrate: 0.06 NTU
UVT: 88.8%
UVA: 0.0517/cm
UVA Reduction: 61.4%
Settled: 0.40 NTU
pH: 6.42, Alk: 18.3 mg/L

## Slide 29: Jars 13-16 Test Flash Mix 30 Sec (200 RPM) Floc Mix 9 min (30 RPM) Post NaMnO4 Applied Coagulants 917 Alum

## Slide 30: Jars 13-16: End of 9-minute flocculation (30 RPM) duration.
20 mg/L 917
35 mg/L Alum
Filtrate: 0.05 NTU
UVT: 89.90%
UVA: 0.0463/cm
UVA Reduction: 65.4%
Settled: 0.30 NTU
pH: 6.31, Alk: 16.5 mg/L
20 mg/L 917
40 mg/L Alum
Filtrate: 0.05 NTU
UVT: 90.01%
UVA: 0.0457/cm
UVA Reduction: 65.9%
Settled: 0.46 NTU
pH: 6.20, Alk: 14.0 mg/L
20 mg/L 917
45 mg/L Alum
Filtrate: 0.05 NTU
UVT: 90.39%
UVA: 0.0439/cm
UVA Reduction: 67.2%
Settled: 0.49 NTU
pH: 6.11, Alk: 13.0 mg/L
20 mg/L 917
50 mg/L Alum
Filtrate: 0.05 NTU
UVT: 90.20%
UVA: 0.0448/cm
UVA Reduction: 66.6%
Settled: 0.46 NTU
pH: 6.00, Alk: 10.5 mg/L

## Slide 31: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 32: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
20 mg/L 917
35 mg/L Alum
Filtrate: 0.05 NTU
UVT: 89.90%
UVA: 0.0463/cm
UVA Reduction: 65.4%
Settled: 0.30 NTU
pH: 6.31, Alk: 16.5 mg/L
20 mg/L 917
40 mg/L Alum
Filtrate: 0.05 NTU
UVT: 90.01%
UVA: 0.0457/cm
UVA Reduction: 65.9%
Settled: 0.46 NTU
pH: 6.20, Alk: 14.0 mg/L
20 mg/L 917
45 mg/L Alum
Filtrate: 0.05 NTU
UVT: 90.39%
UVA: 0.0439/cm
UVA Reduction: 67.2%
Settled: 0.49 NTU
pH: 6.11, Alk: 13.0 mg/L
20 mg/L 917
50 mg/L Alum
Filtrate: 0.05 NTU
UVT: 90.20%
UVA: 0.0448/cm
UVA Reduction: 66.6%
Settled: 0.46 NTU
pH: 6.00, Alk: 10.5 mg/L

## Slide 33: Jars 17-20 Test Flash Mix 30 Sec (200 RPM) Floc Mix 8 min (30 RPM) Post NaMnO4 Applied Coagulants 9810 Alum

## Slide 34: Jars 17-20: End of 8-minute flocculation (30 RPM) duration.
24 mg/L 9810
0 mg/L Alum
Filtrate: 0.05 NTU
UVT: 89.04%
UVA: 0.0554/cm
UVA Reduction: 58.7%
Settled: 0.20 NTU
pH: 7.20, Alk: 30.7 mg/L
24 mg/L 9810
20 mg/L Alum
Filtrate: 0.05 NTU
UVT: 89.83%
UVA: 0.0513/cm
UVA Reduction: 61.7%
Settled: 0.17 NTU
pH: 6.63, Alk: 22 mg/L
24 mg/L 9810
25 mg/L Alum
Filtrate: 0.05 NTU
UVT: 89.01%
UVA: 0.0506/cm
UVA Reduction: 62.2%
Settled: 0.20 NTU
pH: 6.54, Alk: 19.9 mg/L
24 mg/L 9810
30 mg/L Alum
Filtrate: 0.05 NTU
UVT: 89.22%
UVA: 0.0496/cm
UVA Reduction: 63.0%
Settled: 0.24 NTU
pH: 6.42, Alk: 18.0 mg/L

## Slide 35: Jars 17-20: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 36: Jars 17-20: After 25-minutes of settling, settled water turbidity is taken.
24 mg/L 9810
0 mg/L Alum
Filtrate: 0.05 NTU
UVT: 89.04%
UVA: 0.0554/cm
UVA Reduction: 58.7%
Settled: 0.20 NTU
pH: 7.20, Alk: 30.7 mg/L
24 mg/L 9810
20 mg/L Alum
Filtrate: 0.05 NTU
UVT: 89.83%
UVA: 0.0513/cm
UVA Reduction: 61.7%
Settled: 0.17 NTU
pH: 6.63, Alk: 22 mg/L
24 mg/L 9810
25 mg/L Alum
Filtrate: 0.05 NTU
UVT: 89.01%
UVA: 0.0506/cm
UVA Reduction: 62.2%
Settled: 0.20 NTU
pH: 6.54, Alk: 19.9 mg/L
24 mg/L 9810
30 mg/L Alum
Filtrate: 0.05 NTU
UVT: 89.22%
UVA: 0.0496/cm
UVA Reduction: 63.0%
Settled: 0.24 NTU
pH: 6.42, Alk: 18.0 mg/L

## Slide 37: Jars 21-24 Test Flash Mix 20 Sec (200 RPM) Floc Mix 9 min (30 RPM) Post NaMnO4 Applied Coagulants Alum/9810

## Slide 38: Jars 21-24: End of 9-minute flocculation (30 RPM) duration.
0mg/L 9810
50 mg/L Alum
Filtrate: 0.05 NTU
UVT: 89.8%
UVA: 0.0469/cm
UVA Reduction: 65.0%
Settled: 0.26 NTU
pH: 6.05, Alk: 11.9 mg/L
28 mg/L 9810
25 mg/L Alum
Filtrate: 0.06 NTU
UVT: 89.6%
UVA: 0.0478/cm
UVA Reduction: 64.3%
Settled: 0.34 NTU
pH: 6.48, Alk: 20.0 mg/L
32 mg/L 9810
25 mg/L Alum
Filtrate: 0.08 NTU
UVT: 89.7%
UVA: 0.0470/cm
UVA Reduction: 64.9%
Settled: 0.45 NTU
pH: 6.45, Alk: 19.8 mg/L
36 mg/L 9810
25 mg/L Alum
Filtrate: 0.08 NTU
UVT: 89.8%
UVA: 0.0466/cm
UVA Reduction: 89.8%
Settled: 0.47 NTU
pH: 6.44, Alk: 20.5 mg/L

## Slide 39: Jars 21-24: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 40: Jars 21-24: After 25-minutes of settling, settled water turbidity is taken.
0mg/L 9810
50 mg/L Alum
Filtrate: 0.05 NTU
UVT: 89.8%
UVA: 0.0469/cm
UVA Reduction: 65.0%
Settled: 0.26 NTU
pH: 6.05, Alk: 11.9 mg/L
28 mg/L 9810
25 mg/L Alum
Filtrate: 0.06 NTU
UVT: 89.6%
UVA: 0.0478/cm
UVA Reduction: 64.3%
Settled: 0.34 NTU
pH: 6.48, Alk: 20.0 mg/L
32 mg/L 9810
25 mg/L Alum
Filtrate: 0.08 NTU
UVT: 89.7%
UVA: 0.0470/cm
UVA Reduction: 64.9%
Settled: 0.45 NTU
pH: 6.45, Alk: 19.8 mg/L
36 mg/L 9810
25 mg/L Alum
Filtrate: 0.08 NTU
UVT: 89.8%
UVA: 0.0466/cm
UVA Reduction: 89.8%
Settled: 0.47 NTU
pH: 6.44, Alk: 20.5 mg/L

## Slide 41: Jars 25-28 Test Flash Mix 20 Sec (200 RPM) Floc Mix 7 min (30 RPM) Pre-NaMnO4 Applied Coagulants FeCl3/9810

## Slide 42: Jars 25-28: End of 10-minute flocculation (30 RPM) duration.
0 mg/L 9810
27 mg/L FeCl3
Filtrate: 0.08 NTU
UVT: 88.92%
UVA: 0.0510/cm
UVA Reduction: 61.9%
Settled: 0.50 NTU
pH: 6.19, Alk: 13.2 mg/L
24 mg/L 9810
10 mg/L FeCl3
Filtrate: 0.05 NTU
UVT: 89.5%
UVA: 0.0473/cm
UVA Reduction: 64.7%
Settled: 0.50 NTU
pH: 6.74, Alk: 23.4 mg/L
24 mg/L 9810
15 mg/L FeCl3
Filtrate: 0.05 NTU
UVT: 90.5%
UVA: 0.0436/cm
UVA Reduction: 67.9%
Settled: 0.42 NTU
pH: 6.53, Alk: 19.9 mg/L
24 mg/L 9810
20 mg/L FeCl3
Filtrate: 0.05 NTU
UVT: 91.3%
UVA: 0.0395/cm
UVA Reduction: 70.5%
Settled: 0.66 NTU
pH: 6.35, Alk: 16.7 mg/L

## Slide 43: Jars 25-28: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 44: Jars 25-28: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L 9810
27 mg/L FeCl3
Filtrate: 0.08 NTU
UVT: 88.92%
UVA: 0.0510/cm
UVA Reduction: 61.9%
Settled: 0.50 NTU
pH: 6.19, Alk: 13.2 mg/L
24 mg/L 9810
10 mg/L FeCl3
Filtrate: 0.05 NTU
UVT: 89.5%
UVA: 0.0473/cm
UVA Reduction: 64.7%
Settled: 0.50 NTU
pH: 6.74, Alk: 23.4 mg/L
24 mg/L 9810
15 mg/L FeCl3
Filtrate: 0.05 NTU
UVT: 90.5%
UVA: 0.0436/cm
UVA Reduction: 67.9%
Settled: 0.42 NTU
pH: 6.53, Alk: 19.9 mg/L
24 mg/L 9810
20 mg/L FeCl3
Filtrate: 0.05 NTU
UVT: 91.3%
UVA: 0.0395/cm
UVA Reduction: 70.5%
Settled: 0.66 NTU
pH: 6.35, Alk: 16.7 mg/L

## Slide 45: Jars 29-31 Test Flash Mix 60 Sec (200 RPM) Floc Mix 10 min (30 RPM) Pre-NaMnO4 Applied Coagulant 926

## Slide 46: Jars 29-31: End of 10-minute flocculation (30 RPM) duration.
35 mg/L FeCl3
Filtrate: 0.05 NTU
UVT: 92.5%
UVA: 0.0333/cm
UVA Reduction: 75.1%
Settled: 0.35 NTU
pH: 5.79, Alk: 7.4 mg/L
Invalidate
24 mg/L 9810
25 mg/L FeCl3
Filtrate: 0.05 NTU
UVT: 91.6%
UVA: 0.0374/cm
UVA Reduction: 72.1%
Settled: 1.79 NTU
pH: 6.14, Alk: x mg/L

## Slide 47: Jars 29-31: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA

## Slide 48: Jars 29-31: After 25-minutes of settling, settled water turbidity is taken.
35 mg/L FeCl3
Filtrate: 0.05 NTU
UVT: 92.5%
UVA: 0.0333/cm
UVA Reduction: 75.1%
Settled: 0.35 NTU
pH: 5.79, Alk: 7.4 mg/L
24 mg/L 9810
25 mg/L FeCl3
Filtrate: 0.05 NTU
UVT: 91.6%
UVA: 0.0374/cm
UVA Reduction: 72.1%
Settled: 1.79 NTU
pH: 6.14, Alk: x mg/L
Invalidate

## Slide 49: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-60 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 50: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 51: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 52: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 53: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 54: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Jar Testing Done Right training video: https://www.youtube.com/watch?v=aGByyxhelkI
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732