## Slide 1: City of American Canyon CA2810005, Napa County, Jar Test
by Guy Schott, P.E. September 24, 2021

## Slide 2: Conventional and Membrane Treatment Plants

## Slide 3: City of American Canyon Source & Treated Water Characteristics, September 24, 2021
Source – North Bay Aqueduct
pH: 7.65 – 7.73
Alkalinity: 100 mg/L as CaCO3
Turbidity: 11.1 NTU
UVT: 63.4%,
UVA: 0.197/cm
0.4 um Filtered
Turbidity: 0.18 NTU
UVT: 75.9%,
UVA: 0.119/cm
Plant Filtrate Water
0.15 NTU
UVT: 92.6%,
UVA: 0.033/cm

## Slide 4: Applied Coagulants for Jar Testing (1)
AdvFloc-CTC-00011
Polyaluminum Hydroxy Chlorosulfate
12.55% Al2O3
6.64% Al
64.9% Basicity
SG = 1.299
NSF limit: 450 mg/L as Product
BWS, Inc.
Greg Nieckarz, Ph.D.
Greg.niekarz@bws.works
541-953-5112
7% Acid Alum
36.47% Alum
3.25% Al
6.2% Al2O3
7% H2SO4
SG = 1.28

## Slide 5: Applied Coagulants for Jar Testing (2)
Brenntag (559-485-4150)
Solenis
Praestol 186K
SG = 1.0 – 1.2
Viscosity: 60-180 centipoise
MW: 150,00 g/moles
pDADMAC (20% active, 80% H2O)
NSF limit: 50 mg/L (product)
Product dose 5 mg/L = 1 mg/L pDADMAC active
AdvFloc-CTC-00017
SG = 1.0 – 1.2
pDADMAC (40% active, 60% H2O)
NSF limit: 25 mg/L (product)
Product dose 2.5 mg/L = 1 mg/L pDADMAC active
BWS, Inc.
Greg Nieckarz, Ph.D.
Greg.niekarz@bws.works
541-953-5112

## Slide 6: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (254 nm) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 7: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
No pH adjustment
Source pH: 7.65
LCA #1:
CTC-00011: 148 mg/L as product
LCA #2:
pH adjusted to 6.8 w/acidic acid
7%Acid Alum: 65 mg/L as product

## Slide 8: Diallyldimethylammonium chloride or N-allyl-N,N-dimethylprop-2-en-1-aminium chloride pDADMAC C8H16ClN MW: 161.67 g/mol
N
+
CH3
CH3
CH2
CH
CH2
CH2
CH
CH2
Cl-

## Slide 9: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Aluminum Sulfate doses are reported as hydrated Al2(SO4)3*14.3H20.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 10: American Canyon: Source: North Bay Aqueduct Summary of Optimum Dose/Coagulants for Filtrate Jars
Jar# | PAC mg/L | 7% Acid Alum mg/L | CTC- 00011 mg/L | 186K pDADMAC mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
A | 0 | 0 | 160 | 0 | 0.08 | 91.7 | 0.037 | 68.9 | 0.44
B | 0 | 0 | 160 | 0 | 0.05 | 92.0 | 0.035 | 70.6 | 0.32
C | 0 | 0 | 150 | 3 | 0.05 | 92.5 | 0.033 | 72.3 | 0.59
D | 0 | 0 | 150 | 3 | 0.05 | 91.8 | 0.037 | 68.9 | 0.78
E | 20 | 0 | 150 | 0 | 0.05 | 93.2 | 0.030 | 74.8 | 0.34
F | 20 | 0 | 150 | 3 | 0.06 | 93.2 | 0.030 | 74.8 | 0.78
G | 0 | 65 | 0 | 0 | 0.05 | 91.5 | 0.038 | 68.1 | 1.07
H | 20 | 65 | 0 | 0 | 0.05 | 92.9 | 0.031 | 73.9 | 1.17
I | 20 | 65 | 0 | 3 | 0.05 | 93.3 | 0.029 | 75.6 | 1.62

## Slide 11: American Canyon; Jar Test 1 - 8 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | CTC-00011 mg/L | 186K mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 140 | 0 | 0.14 | 90.4 | 0.043 | 63.9 | 0.49
J2 | 150 | 0 | 0.08 | 91.4 | 0.038 | 68.1 | 0.57
J3 | 160 | 0 | 0.08 | 91.7 | 0.037 | 68.9 | 0.44
J4 | 170 | 0 | 0.08 | 91.7 | 0.037 | 68.9 | 0.67
J5 | 150 | 0 | 0.11 | 91.7 | 0.037 | 68.9 | 0.62
J6 | 150 | 3 | 0.05 | 92.5 | 0.033 | 72.3 | 0.59
J7 | 150 | 6 | 0.12 | 92.7 | 0.032 | 73.1 | 0.80
J8 | 150 | 9 | 0.12 | 92.3 | 0.034 | 71.4 | 1.12

## Slide 12: American Canyon; Jar Test 9 - 16 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | PAC mg/L | CTC-00011 mg/L | 186K mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 0 | 150 | 0 | 0.08 | 91.6 | 0.037 | 68.9 | 0.63
J10 | 0 | 150 | 1 | 0.10 | 91.5 | 0.038 | 68.1 | 0.57
J11 | 0 | 150 | 2 | 0.07 | 91.9 | 0.036 | 69.7 | 0.74
J12 | 0 | 150 | 3 | 0.05 | 91.8 | 0.037 | 68.9 | 0.78
J13 | 0 | 150 | 3 | 0.06 | 92.3 | 0.034 | 71.4 | 0.64
J14 | 10 | 150 | 3 | 0.06 | 92.9 | 0.031 | 73.9 | 0.63
J15 | 15 | 150 | 3 | 0.05 | 93.3 | 0.029 | 75.6 | 0.66
J16 | 20 | 150 | 3 | 0.05 | 93.4 | 0.029 | 75.6 | 0.77

## Slide 13: American Canyon; Jar Test 17 - 24 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | PAC mg/L | CTC-00011 mg/L | 186K mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J17 | 0 | 150 | 0 | 0.09 | 91.7 | 0.037 | 68.9 | 0.50
J18 | 10 | 150 | 0 | 0.08 | 92.5 | 0.033 | 72.3 | 0.60
J19 | 15 | 150 | 0 | 0.07 | 92.9 | 0.032 | 73.1 | 0.50
J20 | 20 | 150 | 0 | 0.05 | 93.2 | 0.030 | 74.8 | 0.34
J21 | 0 | 150 | 0 | 0.09 | 91.7 | 0.037 | 68.9 | 0.38
J22 | 20 | 150 | 0 | 0.06 | 93.0 | 0.031 | 73.9 | 0.56
J23 | 0 | 150 | 3 | 0.05 | 92.2 | 0.035 | 70.6 | 0.70
J24 | 20 | 150 | 3 | 0.06 | 93.2 | 0.030 | 74.8 | 0.78

## Slide 14: American Canyon; Jar Test 25 - 28 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (10 min)
Jar# | PAC mg/L | CTC-00011 mg/L | 186K mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J25 | 0 | 150 | 0 | 0.07 | 91.4 | 0.038 | 68.1 | 0.44
J26 | 20 | 150 | 0 | 0.08 | 92.4 | 0.034 | 71.4 | 0.31
J27 | 0 | 150 | 3 | 0.05 | 91.8 | 0.036 | 69.7 | 0.50
J28 | 20 | 150 | 3 | 0.05 | 93.6 | 0.028 | 76.5 | 0.51

## Slide 15: American Canyon; Jar Test 29 - 36 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | PAC mg/L | 7% Acid Alum mg/L | 186K mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J29 | 0 | 60 | 0 | 0.11 | 91.1 | 0.040 | 66.4 | 1.03
J30 | 0 | 65 | 0 | 0.06 | 91.5 | 0.038 | 68.1 | 1.21
J31 | 0 | 70 | 0 | 0.07 | 91.7 | 0.037 | 68.9 | 1.15
J32 | 0 | 75 | 0 | 0.09 | 91.8 | 0.037 | 68.9 | 0.96
J33 | 0 | 65 | 0 | 0.05 | 91.5 | 0.038 | 68.1 | 1.07
J34 | 20 | 65 | 0 | 0.05 | 92.9 | 0.031 | 73.9 | 1.17
J35 | 0 | 65 | 3 | 0.05 | 92.0 | 0.036 | 69.7 | 1.50
J36 | 20 | 65 | 3 | 0.05 | 93.3 | 0.029 | 75.6 | 1.62

## Slide 16: American Canyon; Jar Test 37 - 40 Results Flash Mix 200 RPM (20 sec); Floc Mix 20 RPM (30 min)
Jar# | KMnO4 mg/L | 7% Acid Alum mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J37 | 0 | 65 | 0.08 | 91.2 | 0.039 | 67.2 | 0.46
J38 | 1.5 | 65 | 0.10 | 85.9 | 0.065 | 45.4 | 0.84
J39 | 3.0 | 65 | 0.10 | 78.2 | 0.106 | 10.9 | 0.87
J40 | 5.0 | 65 | 0.08 | 69.0 | 0.160 | - | 0.78
Note: KMnO4 was overdosed for Jars 38-40.

## Slide 17: American Canyon; Jar Test 41 - 44 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | CTC-00011 mg/L | CTC-00017 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J41 | 160 | 0 | 0.05 | 92.0 | 0.035 | 70.6 | 0.32
J42 | 160 | 1 | 0.05 | 92.2 | 0.035 | 70.6 | 0.41
J43 | 160 | 1.5 | 0.05 | 92.2 | 0.034 | 71.4 | 0.41
J44 | 160 | 2 | 0.04 | 92.4 | 0.034 | 71.4 | 0.44

## Slide 18: Jars 1-4 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant CTC-00011

## Slide 19: Jars 1-4: End of 5-minute flocculation (30 RPM) duration.
140 mg/L CTC-00011
Filtrate: 0.14 NTU
UVT: 90.4%
UVA: 0.043/cm
UVA Reduction: 63.9%
Settled: 0.49 NTU
150 mg/L CTC-00011
Filtrate: 0.08 NTU
UVT: 91.4%
UVA: 0.038/cm
UVA Reduction: 68.1%
Settled: 0.57 NTU
160 mg/L CTC-00011
Filtrate: 0.08 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction: 68.9%
Settled: 0.44 NTU
170 mg/L CTC-00011
Filtrate: 0.08 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction: 68.9%
Settled: 0.67 NTU

## Slide 20: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 21: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
140 mg/L CTC-00011
Filtrate: 0.14 NTU
UVT: 90.4%
UVA: 0.043/cm
UVA Reduction: 63.9%
Settled: 0.49 NTU
150 mg/L CTC-00011
Filtrate: 0.08 NTU
UVT: 91.4%
UVA: 0.038/cm
UVA Reduction: 68.1%
Settled: 0.57 NTU
160 mg/L CTC-00011
Filtrate: 0.08 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction: 68.9%
Settled: 0.44 NTU
170 mg/L CTC-00011
Filtrate: 0.08 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction: 68.9%
Settled: 0.67 NTU

## Slide 22: Jars 5-8 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants CTC-00011/186K

## Slide 23: Jars 5-8: End of 5-minute flocculation (30 RPM) duration.
150 mg/L CTC-00011
0 mg/L 186K
Filtrate: 0.11 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction: 68.9%
Settled: 0.62 NTU
150 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.05 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 72.3%
Settled: 0.59 NTU
150 mg/L CTC-00011
6 mg/L 186K
Filtrate: 0.12 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction: 73.1%
Settled: 0.80 NTU
150 mg/L CTC-00011
9 mg/L 186K
Filtrate: 0.12 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction: 71.4%
Settled: 1.12 NTU

## Slide 24: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 25: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
150 mg/L CTC-00011
0 mg/L 186K
Filtrate: 0.11 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction: 68.9%
Settled: 0.62 NTU
150 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.05 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 72.3%
Settled: 0.59 NTU
150 mg/L CTC-00011
6 mg/L 186K
Filtrate: 0.12 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction: 73.1%
Settled: 0.80 NTU
150 mg/L CTC-00011
9 mg/L 186K
Filtrate: 0.12 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction: 71.4%
Settled: 1.12 NTU

## Slide 26: Jars 9-12 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants CTC-00011/186K

## Slide 27: Jars 9-12: End of 5-minute flocculation (30 RPM) duration.
150 mg/L CTC-00011
0 mg/L 186K
Filtrate: 0.08 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction: 68.9%
Settled: 0.63 NTU
150 mg/L CTC-00011
1 mg/L 186K
Filtrate: 0.10 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction: 68.1%
Settled: 0.57 NTU
150 mg/L CTC-00011
2 mg/L 186K
Filtrate: 0.07 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction: 69.7%
Settled: 0.74 NTU
150 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.05 NTU
UVT: 91.8%
UVA: 0.037/cm
UVA Reduction: 68.9%
Settled: 0.78 NTU

## Slide 28: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 29: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
150 mg/L CTC-00011
0 mg/L 186K
Filtrate: 0.08 NTU
UVT: 91.6%
UVA: 0.037/cm
UVA Reduction: 68.9%
Settled: 0.63 NTU
150 mg/L CTC-00011
1 mg/L 186K
Filtrate: 0.10 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction: 68.1%
Settled: 0.57 NTU
150 mg/L CTC-00011
2 mg/L 186K
Filtrate: 0.07 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction: 69.7%
Settled: 0.74 NTU
150 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.05 NTU
UVT: 91.8%
UVA: 0.037/cm
UVA Reduction: 68.9%
Settled: 0.78 NTU

## Slide 30: Jars 13-16 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) PAC with Applied Coagulants CTC-00011/186K

## Slide 31: Jars 13-16: End of 5-minute flocculation (30 RPM) duration.
0 mg/L PAC
150 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.06 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction: 71.4%
Settled: 0.64 NTU
10 mg/L PAC
150 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.06 NTU
UVT: 92.9%
UVA: 0.031/cm
UVA Reduction: 73.9%
Settled: 0.63 NTU
15 mg/L PAC
150 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.05 NTU
UVT: 93.3%
UVA: 0.029/cm
UVA Reduction: 75.6%
Settled: 0.66 NTU
20 mg/L PAC
150 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.05 NTU
UVT: 93.4%
UVA: 0.029/cm
UVA Reduction: 75.6%
Settled: 0.77 NTU

## Slide 32: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 33: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L PAC
150 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.06 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction: 71.4%
Settled: 0.64 NTU
10 mg/L PAC
150 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.06 NTU
UVT: 92.9%
UVA: 0.031/cm
UVA Reduction: 73.9%
Settled: 0.63 NTU
15 mg/L PAC
150 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.05 NTU
UVT: 93.3%
UVA: 0.029/cm
UVA Reduction: 75.6%
Settled: 0.66 NTU
20 mg/L PAC
150 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.05 NTU
UVT: 93.4%
UVA: 0.029/cm
UVA Reduction: 75.6%
Settled: 0.77 NTU

## Slide 34: Jars 17-20 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) PAC with Applied Coagulants CTC-00011

## Slide 35: Jars 17-20: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 36: Jars 17-20: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L PAC
150 mg/L CTC-00011
Filtrate: 0.09 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction: 68.9%
Settled: 0.50 NTU
10 mg/L PAC
150 mg/L CTC-00011
Filtrate: 0.08 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 72.3%
Settled: 0.60 NTU
15 mg/L PAC
150 mg/L CTC-00011
Filtrate: 0.07 NTU
UVT: 92.9%
UVA: 0.032/cm
UVA Reduction: 73.1%
Settled: 0.50 NTU
20 mg/L PAC
150 mg/L CTC-00011
Filtrate: 0.05 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction: 74.8%
Settled: 0.34 NTU

## Slide 37: Jars 21-24 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) PAC with Applied Coagulants CTC-00011

## Slide 38: Jars 21-24: End of 5-minute flocculation (30 RPM) duration.
0 mg/L PAC
150 mg/L CTC-00011
0 mg/L 186K
Filtrate: 0.09 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction: 68.9%
Settled: 0.38 NTU
20 mg/L PAC
150 mg/L CTC-00011
0 mg/L 186K
Filtrate: 0.06 NTU
UVT: 93.0%
UVA: 0.031/cm
UVA Reduction: 73.9%
Settled: 0.56 NTU
0 mg/L PAC
150 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.05 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction: 70.6%
Settled: 0.70 NTU
20 mg/L PAC
150 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.06 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction: 74.0%
Settled: 0.78 NTU

## Slide 39: Jars 21-24: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 40: Jars 21-24: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L PAC
150 mg/L CTC-00011
0 mg/L 186K
Filtrate: 0.09 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction: 68.9%
Settled: 0.38 NTU
20 mg/L PAC
150 mg/L CTC-00011
0 mg/L 186K
Filtrate: 0.06 NTU
UVT: 93.0%
UVA: 0.031/cm
UVA Reduction: 73.9%
Settled: 0.56 NTU
0 mg/L PAC
150 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.05 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction: 70.6%
Settled: 0.70 NTU
20 mg/L PAC
150 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.06 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction: 74.0%
Settled: 0.78 NTU

## Slide 41: Jars 25-28 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) PAC with Applied Coagulants CTC-00011

## Slide 42: Jars 25-28: End of 5-minute flocculation (30 RPM) duration.
0 mg/L PAC
150 mg/L CTC-00011
0 mg/L 186K
Filtrate: 0.07 NTU
UVT: 91.4%
UVA: 0.038/cm
UVA Reduction: 68.1%
Settled: 0.44 NTU
20 mg/L PAC
150 mg/L CTC-00011
0 mg/L 186K
Filtrate: 0.08 NTU
UVT: 92.4%
UVA: 0.031/cm
UVA Reduction: 71.4%
Settled: 0.31 NTU
0 mg/L PAC
150 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.05 NTU
UVT: 91.8%
UVA: 0.036/cm
UVA Reduction: 69.7%
Settled: 0.50 NTU
20 mg/L PAC
150 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.05 NTU
UVT: 93.6%
UVA: 0.028/cm
UVA Reduction: 76.5%
Settled: 0.51 NTU

## Slide 43: Jars 25-28: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 44: Jars 25-28: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L PAC
150 mg/L CTC-00011
0 mg/L 186K
Filtrate: 0.07 NTU
UVT: 91.4%
UVA: 0.038/cm
UVA Reduction: 68.1%
Settled: 0.44 NTU
20 mg/L PAC
150 mg/L CTC-00011
0 mg/L 186K
Filtrate: 0.08 NTU
UVT: 92.4%
UVA: 0.031/cm
UVA Reduction: 71.4%
Settled: 0.31 NTU
0 mg/L PAC
150 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.05 NTU
UVT: 91.8%
UVA: 0.036/cm
UVA Reduction: 69.7%
Settled: 0.50 NTU
20 mg/L PAC
150 mg/L CTC-00011
3 mg/L 186K
Filtrate: 0.05 NTU
UVT: 93.6%
UVA: 0.028/cm
UVA Reduction: 76.5%
Settled: 0.51 NTU

## Slide 45: Jars 29-32 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 7% Acid Alum

## Slide 46: Jars 29-32: End of 5-minute flocculation (30 RPM) duration.
60 mg/L 7%Acid Alum
Filtrate: 0.11 NTU
UVT: 91.1%
UVA: 0.040/cm
UVA Reduction: 66.4%
Settled: 1.03 NTU
65 mg/L 7%Acid Alum
Filtrate: 0.06 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction: 68.1%
Settled: 1.21 NTU
70 mg/L 7%Acid Alum
Filtrate: 0.07 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction: 68.9%
Settled: 1.15 NTU
75 mg/L 7%Acid Alum
Filtrate: 0.09 NTU
UVT: 91.8%
UVA: 0.037/cm
UVA Reduction: 68.9%
Settled: 0.96 NTU

## Slide 47: Jars 29-32: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 48: Jars 29-32: After 25-minutes of settling, settled water turbidity is taken.
60 mg/L 7%Acid Alum
Filtrate: 0.11 NTU
UVT: 91.1%
UVA: 0.040/cm
UVA Reduction: 66.4%
Settled: 1.03 NTU
65 mg/L 7%Acid Alum
Filtrate: 0.06 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction: 68.1%
Settled: 1.21 NTU
70 mg/L 7%Acid Alum
Filtrate: 0.07 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction: 68.9%
Settled: 1.15 NTU
75 mg/L 7%Acid Alum
Filtrate: 0.09 NTU
UVT: 91.8%
UVA: 0.037/cm
UVA Reduction: 68.9%
Settled: 0.96 NTU

## Slide 49: Jars 33-36 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) PAC + Applied Coagulant 7% Acid Alum

## Slide 50: Jars 33-36: End of 5-minute flocculation (30 RPM) duration.
0 mg/L PACE
65 mg/L 7%Acid Alum
Filtrate: 0.05 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction: 68.1%
Settled: 1.07 NTU
20 mg/L PACE
65 mg/L 7%Acid Alum
Filtrate: 0.05 NTU
UVT: 92.9%
UVA: 0.031/cm
UVA Reduction: 73.9%
Settled: 1.17 NTU
0 mg/L PACE
65 mg/L 7%Acid Alum
3 mg/L 186K
Filtrate: 0.05 NTU
UVT: 92.0%
UVA: 0.036/cm
UVA Reduction: 69.7%
Settled: 1.50 NTU
20 mg/L PACE
65 mg/L 7%Acid Alum
3 mg/L 186K
Filtrate: 0.04 NTU
UVT: 93.3%
UVA: 0.029/cm
UVA Reduction: 75.6%
Settled: 1.62 NTU

## Slide 51: Jars 33-36: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 52: Jars 33-36: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L PACE
65 mg/L 7%Acid Alum
Filtrate: 0.05 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction: 68.1%
Settled: 1.07 NTU
20 mg/L PACE
65 mg/L 7%Acid Alum
Filtrate: 0.05 NTU
UVT: 92.9%
UVA: 0.031/cm
UVA Reduction: 73.9%
Settled: 1.17 NTU
0 mg/L PACE
65 mg/L 7%Acid Alum
3 mg/L 186K
Filtrate: 0.05 NTU
UVT: 92.0%
UVA: 0.036/cm
UVA Reduction: 69.7%
Settled: 1.50 NTU
20 mg/L PACE
65 mg/L 7%Acid Alum
3 mg/L 186K
Filtrate: 0.04 NTU
UVT: 93.3%
UVA: 0.029/cm
UVA Reduction: 75.6%
Settled: 1.62 NTU

## Slide 53: Jars 37-40 Test Flash Mix 20 Sec (200 RPM) Floc Mix 30 min (20 RPM) KMnO4 + Applied Coagulant 7% Acid Alum

## Slide 54: Jars 37-40: End of 30-minute flocculation (30 RPM) duration.
0 mg/L KMnO4
65 mg/L 7%Acid Alum
Filtrate: 0.08 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction: 67.2%
Settled: 0.46 NTU
1.5 mg/L KMnO4
65 mg/L 7%Acid Alum
Filtrate: 0.10 NTU
UVT: 85.9%
UVA: 0.065/cm
UVA Reduction: 45.4%
Settled: 0.84 NTU
3.0 mg/L KMnO4
65 mg/L 7%Acid Alum
Filtrate: 0.10 NTU
UVT: 78.2%
UVA: 0.106/cm
UVA Reduction: 10.9%
Settled: 0.87 NTU
5.0 mg/L KMnO4
65 mg/L 7%Acid Alum
Filtrate: 0.08 NTU
UVT: 69.0%
UVA: 0.160/cm
UVA Reduction: -%
Settled: 0.78 NTU

## Slide 55: Jars 37-40: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 56: Jars 37-40: After 25-minutes of settling, settled water turbidity is taken.
0 mg/L KMnO4
65 mg/L 7%Acid Alum
Filtrate: 0.08 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction: 67.2%
Settled: 0.46 NTU
1.5 mg/L KMnO4
65 mg/L 7%Acid Alum
Filtrate: 0.10 NTU
UVT: 85.9%
UVA: 0.065/cm
UVA Reduction: 45.4%
Settled: 0.84 NTU
3.0 mg/L KMnO4
65 mg/L 7%Acid Alum
Filtrate: 0.10 NTU
UVT: 78.2%
UVA: 0.106/cm
UVA Reduction: 10.9%
Settled: 0.87 NTU
5.0 mg/L KMnO4
65 mg/L 7%Acid Alum
Filtrate: 0.08 NTU
UVT: 69.0%
UVA: 0.160/cm
UVA Reduction: -%
Settled: 0.78 NTU

## Slide 57: Jars 41-44 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants CTC-00011/CTC-00017

## Slide 58: Jars 41-44: End of 5-minute flocculation (30 RPM) duration.
160 mg/L CTC-00011
0 mg/L CTC-00017
Filtrate: 0.05 NTU
UVT: 92.0%
UVA: 0.035/cm
UVA Reduction: 70.6%
Settled: 0.32 NTU
160 mg/L CTC-00011
1 mg/L CTC-00017
Filtrate: 0.05 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction: 70.6%
Settled: 0.41 NTU
160 mg/L CTC-00011
1.5 mg/L CTC-00017
Filtrate: 0.05 NTU
UVT: 92.2%
UVA: 0.034/cm
UVA Reduction: 71.4%
Settled: 0.41 NTU
160 mg/L CTC-00011
2 mg/L CTC-00017
Filtrate: 0.05 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction: 71.4%
Settled: 0.44 NTU

## Slide 59: Jars 41-44: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 60: Jars 41-44: After 25-minutes of settling, settled water turbidity is taken.
160 mg/L CTC-00011
0 mg/L CTC-00017
Filtrate: 0.05 NTU
UVT: 92.0%
UVA: 0.035/cm
UVA Reduction: 70.6%
Settled: 0.32 NTU
160 mg/L CTC-00011
1 mg/L CTC-00017
Filtrate: 0.05 NTU
UVT: 92.2%
UVA: 0.035/cm
UVA Reduction: 70.6%
Settled: 0.41 NTU
160 mg/L CTC-00011
1.5 mg/L CTC-00017
Filtrate: 0.05 NTU
UVT: 92.2%
UVA: 0.034/cm
UVA Reduction: 71.4%
Settled: 0.41 NTU
160 mg/L CTC-00011
2 mg/L CTC-00017
Filtrate: 0.05 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction: 71.4%
Settled: 0.44 NTU

## Slide 61: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 62: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 63: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 64: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 65: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 66: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732