## Slide 1: Benicia, City of CA4810001 Solano County Jar Test
by Guy Schott, P.E.
February 12, 2021

## Slide 2: Source Water: North Bay Aqueduct

## Slide 3: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (254 nm) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 4: City of Benicia WTP Water Characteristics February 12, 2021
Source
pH: 7.5-7.7
Alkalinity: 86 mg/L as CaCO3
Turbidity: 6.06 NTU
UVT: 72.2%,
UVA: 0.141/cm
0.4 um Filtered
Turbidity: 0.37 NTU
UVT: 77.5%,
UVA: 0.110/cm
Plant Coagulant Dose:
5% Acid Alum: 46 mg/L
Clarifloc C-378: 0.5 mg/L
Filtrate Water (pre-chlorine)
Alkalinity: 56 mg/L as CaCO3
Turbidity: 0.28 NTU
UVT: 92.3%,
UVA: 0.034/cm
Filtrate Water (post-Chlorine)
Turbidity: 0.05 NTU
UVT: 94.5%,
UVA: 0.024/cm

## Slide 5: %UVA Reduction via Source Water Pre-Chlorination
Chart: %UVA Reduction Over Time Pre-Chlorination (2.0 mg/L)
| 0 | 9 | 38 | 85 | 124
 | 0 | 0.087 | 0.123 | 0.181 | 0.188

## Slide 6: Filtrate Water (Jar Test) Plant Coagulant Dose vs. Optimum Coagulant Dose
Chart: Chlorine Residual Over Time
| 0 | 4.0999999999999996 | 16 | 21 | 27 | 37 | 50 | 62 | 74 | 84.5 | 96 | 107.5 | 121.5 | 134
Acid Alum: 46 mg/L, CatFloc C-378: 2.1 mg/L, UVA: 0.038/cm | 1.39 | 0.72 | 0.42 | 0.36 | 0.29 | 0.2 | 0.13 | 0.08 | 0.04 | 0.03 | 0.01 | 0 | 0 | 0
Acid Alum: 85 mg/L, CatFloc C-378: 3.1 mg/L, UVA: 0.029/cm | 1.3 | 0.9 | 0.65 | 0.59 | 0.53 | 0.44 | 0.38 | 0.32 | 0.28 | 0.24 | 0.21 | 0.16 | 0.12 | 0.09

## Slide 7: Filtrate Water (Jar Test) Plant Coagulant Dose vs. Optimum Coagulant Dose/PAC
Chart: Chlorine Residual Over Time
| 0 | 4 | 7 | 11 | 22.4 | 36.4 | 48.9 | 60.9 | 71.900000000000006 | 83.9 | 97 | 108.2 | 119.4 | 132 | 144.5
Acid Alum: 46 mg/L, CatFloc C-378: 2.2 mg/L, UVA: 0.041/cm | 1.28 | 0.72 | 0.6 | 0.5 | 0.34 | 0.21 | 0.14 | 0.1 | 0.08 | 0.04 | 0.02 | 0 | 0 | 0 | 0
Acid Alum: 43 mg/L, CatFloc C-378: 3.2 mg/L, PAC: 30 mg/L, UVA: 0.024/cm | 1.38 | 0.8 | 0.7 | 0.61 | 0.5 | 0.37 | 0.3 | 0.27 | 0.21 | 0.18 | 0.13 | 0.11 | 0.09 | 0.07 | 0.03

## Slide 8: Applied Coagulants for Jar Testing (1)
5% Acid Aluminum Sulfate (Product)
Al2(SO4)3*14.3H20 (Liquid)
40% Aluminum Sulfate
5% H2SO4
55% Water
6.8% Al2O3
3.6% Al
0% Basicity
SG = 1.29
NSF limit: 400 mg/L (product)
As hydrated Al2(SO4)3*14.3H20
17% Al2O3
Polydyne Incorporated
Clarifloc C-378
SG = 1.0 – 1.2
pDADMAC (20% active, 80% H2O)
NSF limit: 50 mg/L (product)
Product dose 5 mg/L = 1 mg/L pDADMAC active

## Slide 9: Applied Coagulants for Jar Testing (2)
Pro Pac 9810 (NTU Technologies)
45-50% Aluminum Chlorohydrate
45-50% Water
~22.4% Al2O3
~11.9% Al
83% Basicity
5% polyamine (50% water, 50% active polyamines)
SG = 1.25-1.34
NSF limit: 200 mg/L as Product;
Product dose 40 mg/L = 1 mg/L polyamines active
BWS, Inc.
AdvFloc-CTC-00011
Polyaluminum Hydroxy Chlorosulfate
12.55% Al2O3
6.64% Al
64.9% Basicity
SG = 1.299
NSF limit: 250 mg/L as Product

## Slide 10: Polyamine C59H108N14O10 MW: 1,173.6 g/mol

## Slide 11: Diallyldimethylammonium chloride or N-allyl-N,N-dimethylprop-2-en-1-aminium chloride pDADMAC C8H16ClN MW: 161.67 g/mol
N
+
CH3
CH3
CH2
CH
CH2
CH2
CH
CH2
Cl-

## Slide 12: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.72
LCA #1: 5% Acid Alum: 36.7 mg/L as hydrated
pH adjusted to 6.6 with acetic acid
LCA #2: 9810: 32.9 mg/L
pH adjusted to 7.5 with acetic acid
LCA #3: AdvFloc CTC-00011: 126 mg/L
pH adjusted to 7.5 with acetic acid

## Slide 13: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Aluminum Sulfate doses are reported as hydrated Al2(SO4)3*14.3H20.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 14: Alkalinity (mg/L as CaCO3) Consumed based on Coagulant and Dose
Dose, mg/L | 5% Acid Alum (dry) | AdvFloc (product) | 9810 (product)
10 | 6.29 | 1.3 | 1.12
30 | 18.9 | 3.9 | 3.4
46 | 28.9 | 6.0 | 5.2
85 | 53.4 | 11 | 9.5
100 | 62.9 | 13 | 11.3
180 | 113 | 23.4 | 20.2

## Slide 15: City of Benicia WTP; Source NBA; Summary of Plant Coagulant/Dose Jar vs. Best Jars
Jar# | 5% Acid Alum mg/L | AdvFloc CTC-0011 mg/L | CatFloc C-378 mg/L | 9810 mg/L | PAC mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
A | 46 | 0 | 2.0 | 0 | 0 | 0.06 | 91.4 | 0.038 | 65.5 | 1.12
vs. |  |  |  |  |  |  |  |  |  | 
B | 85 | 0 | 3.1 | 0 | 0 | 0.04 | 93.4 | 0.029 | 73.6 | 1.84
C | 46 | 0 | 3.2 | 0 | 30 | 0.06 | 94.5 | 0.024 | 78.2 | 5.69
D | 0 | 180 | 4.0 | 0 | 0 | 0.04 | 93.6 | 0.028 | 74.5 | 0.49
E | 0 | 0 | 0 | 45 | 0 | 0.12 | 91.9 | 0.036 | 67.3 | 1.38

## Slide 16: City of Benicia WTP; Source NBA; Jar Test 1 - 8 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | 5% Acid Alum mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 25 | 0.18 | 87.2 | 0.059 | 46.4 | 3.93
J2 | 30 | 0.17 | 88.1 | 0.055 | 50.0 | 2.93
J3 | 35 | 0.17 | 88.9 | 0.051 | 53.6 | 2.48
J4 | 40 | 0.07 | 90.4 | 0.043 | 60.9 | 1.17
J5 | 40 | 0.15 | 89.9 | 0.046 | 58.2 | 1.40
J6 | 45 | 0.14 | 90.5 | 0.043 | 60.9 | 1.22
J7 | 50 | 0.20 | 90.4 | 0.043 | 60.9 | 1.37
J8 | 55 | 0.10 | 91.2 | 0.039 | 64.5 | 1.40

## Slide 17: City of Benicia WTP; Source NBA; Jar Test 9 - 16 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 30 | 0.15 | 89.9 | 0.046 | 58.2 | 1.47
J10 | 33 | 0.15 | 90.0 | 0.045 | 59.1 | 1.20
J11 | 36 | 0.15 | 90.6 | 0.042 | 61.8 | 1.41
J12 | 39 | 0.15 | 90.8 | 0.041 | 62.7 | 1.64
J13 | 42 | 0.12 | 91.5 | 0.038 | 65.5 | 1.12
J14 | 45 | 0.12 | 91.9 | 0.036 | 67.3 | 1.38
J15 | 48 | 0.13 | 91.8 | 0.036 | 67.3 | 1.30
J16 | 51 | 0.17 | 91.9 | 0.036 | 67.3 | 1.45

## Slide 18: City of Benicia WTP; Source NBA; Jar Test 17 - 24 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | AdvFloc CTC-0011 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J17 | 120 | 0.08 | 92.1 | 0.035 | 68.2 | N/A
J18 | 130 | 0.07 | 92.5 | 0.033 | 70.0 | N/A
J19 | 140 | 0.06 | 92.7 | 0.032 | 70.9 | N/A
J20 | 150 | 0.06 | 92.9 | 0.031 | 71.8 | N/A
J21 | 140 | 0.09 | 92.0 | 0.036 | 67.3 | 0.35
J22 | 150 | 0.06 | 92.3 | 0.034 | 69.1 | 0.35
J23 | 160 | 0.06 | 92.5 | 0.033 | 70.0 | 0.29
J24 | 170 | 0.05 | 92.5 | 0.032 | 70.9 | 0.26

## Slide 19: City of Benicia WTP; Source NBA; Jar Test 25 - 32 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | 5% Acid Alum mg/L | CatFloc C-378 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J25 | 46 | 0 | 0.13 | 90.6 | 0.042 | 61.8 | 1.02
J26 | 46 | 0.5 | 0.12 | 90.7 | 0.042 | 61.8 | 1.22
J27 | 46 | 1.0 | 0.11 | 90.9 | 0.041 | 62.7 | 1.30
J28 | 46 | 1.5 | 0.08 | 91.2 | 0.039 | 64.5 | 1.30
J29 | 46 | 1.5 | 0.08 | 91.2 | 0.039 | 64.5 | 0.95
J30 | 46 | 2.0 | 0.05 | 91.2 | 0.039 | 64.5 | 1.16
J31 | 56 | 1.5 | 0.05 | 91.9 | 0.036 | 67.3 | 1.15
J32 | 56 | 2.0 | 0.05 | 92.0 | 0.035 | 68.2 | 1.30

## Slide 20: City of Benicia WTP; Source NBA; Jar Test 33 - 36 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | 5% Acid Alum mg/L | CatFloc C-378 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J33 | 55 | 2.0 | 0.05 | 92.1 | 0.035 | 68.2 | 1.39
J34 | 65 | 2.4 | 0.05 | 92.7 | 0.032 | 70.9 | 1.60
J35 | 75 | 2.7 | 0.04 | 93.0 | 0.031 | 71.8 | 1.94
J36 | 85 | 3.1 | 0.04 | 93.3 | 0.029 | 73.6 | 1.62

## Slide 21: City of Benicia WTP; Source NBA; Jar Test 37 - 40 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | AdvFloc CTC-0011 mg/L | CatFloc C-378 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J37 | 180 | 0.0 | 0.06 | 93.0 | 0.031 | 71.8 | 0.37
J38 | 180 | 2.0 | 0.04 | 93.4 | 0.029 | 73.6 | 0.40
J39 | 180 | 3.0 | 0.04 | 93.7 | 0.028 | 74.5 | 0.39
J40 | 180 | 4.0 | 0.04 | 93.8 | 0.027 | 75.5 | 0.48

## Slide 22: City of Benicia WTP; Source NBA; Jar Test 41 - 44 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (5 min)
Jar# | 5% Acid Alum mg/L | AdvFloc CTC-0011 mg/L | CatFloc C-378 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduct | Settle NTU 25 min
J41 | 46 | 0 | 0 | 0.12 | 90.6 | 0.042 | 61.8 | 0.89
J42 | 46 | 0 | 2.0 | 0.06 | 91.4 | 0.038 | 65.5 | 1.12
J43 | 85 | 0 | 3.1 | 0.04 | 93.4 | 0.029 | 73.6 | 1.84
J44 | 0 | 180 | 4.0 | 0.04 | 93.6 | 0.028 | 74.5 | 0.49

## Slide 23: City of Benicia WTP; Source NBA; Jar Test 45 - 52 Results Flash Mix 200 RPM (30 sec); Floc Mix 30 RPM (15 min)
Jar# | 5% Acid Alum mg/L | CatFloc C-378 mg/L | PAC mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J45 | 46 | 2.2 | 0 | 0.08 | 91.0 | 0.040 | 63.6 | 0.51
J46 | 46 | 2.2 | 20 | 0.11 | 93.2 | 0.030 | 72.7 | 3.01
J47 | 46 | 2.2 | 30 | 0.11 | 93.9 | 0.027 | 75.7 | 5.06
J48 | 46 | 2.2 | 40 | 0.16 | 93.9 | 0.027 | 75.7 | 5.74
J49 | 46 | 2.2 | 0 | 0.05 | 90.9 | 0.041 | 62.7 | 0.48
J50 | 46 | 2.2 | 30 | 0.10 | 93.7 | 0.028 | 74.5 | 4.72
J51 | 46 | 3.2 | 30 | 0.06 | 94.5 | 0.024 | 78.2 | 5.69
J52 | 46 | 4.2 | 30 | 0.05 | 93.9 | 0.027 | 75.5 | 6.10

## Slide 24: Jars 1-4 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 5% Acid Alum

## Slide 25: Jars 1-4: End of 5-minute flocculation (30 RPM) duration.
25 mg/L 5% Acid Alum
Filtrate 0.18 NTU
UVT: 87.2%
UVA: 0.059/cm
UVA Reduction 46.4%
Settled: 3.91 NTU
30 mg/L 5% Acid Alum
Filtrate 0.17 NTU
UVT: 88.1%
UVA: 0.055/cm
UVA Reduction 50.0%
Settled: 2.93 NTU
35 mg/L 5% Acid Alum
Filtrate 0.17 NTU
UVT: 88.9%
UVA: 0.051/cm
UVA Reduction 53.6%
Settled: 2.48 NTU
40 mg/L 5% Acid Alum
Filtrate 0.07 NTU
UVT: 90.4%
UVA: 0.043/cm
UVA Reduction 60.9%
Settled: 1.17 NTU

## Slide 26: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 27: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
25 mg/L 5% Acid Alum
Filtrate 0.18 NTU
UVT: 87.2%
UVA: 0.059/cm
UVA Reduction 46.4%
Settled: 3.91 NTU
30 mg/L 5% Acid Alum
Filtrate 0.17 NTU
UVT: 88.1%
UVA: 0.055/cm
UVA Reduction 50.0%
Settled: 2.93 NTU
35 mg/L 5% Acid Alum
Filtrate 0.17 NTU
UVT: 88.9%
UVA: 0.051/cm
UVA Reduction 53.6%
Settled: 2.48 NTU
40 mg/L 5% Acid Alum
Filtrate 0.07 NTU
UVT: 90.4%
UVA: 0.043/cm
UVA Reduction 60.9%
Settled: 1.17 NTU

## Slide 28: Jars 5-8 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 5% Acid Alum

## Slide 29: Jars 5-8: End of 5-minute flocculation (30 RPM) duration.
40 mg/L 5% Acid Alum
Filtrate 0.15 NTU
UVT: 89.9%
UVA: 0.046/cm
UVA Reduction 58.2%
Settled: 1.40 NTU
45 mg/L 5% Acid Alum
Filtrate 0.14 NTU
UVT: 90.5%
UVA: 0.043/cm
UVA Reduction 60.9%
Settled: 1.22 NTU
50 mg/L 5% Acid Alum
Filtrate 0.20 NTU
UVT: 90.4%
UVA: 0.043/cm
UVA Reduction 60.9%
Settled: 1.37 NTU
55 mg/L 5% Acid Alum
Filtrate 0.10 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 64.5%
Settled: 1.40 NTU

## Slide 30: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 31: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
40 mg/L 5% Acid Alum
Filtrate 0.15 NTU
UVT: 89.9%
UVA: 0.046/cm
UVA Reduction 58.2%
Settled: 1.40 NTU
45 mg/L 5% Acid Alum
Filtrate 0.14 NTU
UVT: 90.5%
UVA: 0.043/cm
UVA Reduction 60.9%
Settled: 1.22 NTU
50 mg/L 5% Acid Alum
Filtrate 0.20 NTU
UVT: 90.4%
UVA: 0.043/cm
UVA Reduction 60.9%
Settled: 1.37 NTU
55 mg/L 5% Acid Alum
Filtrate 0.10 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 64.5%
Settled: 1.40 NTU

## Slide 32: Jars 9-12 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9810

## Slide 33: Jars 9-12: End of 5-minute flocculation (30 RPM) duration.
30 mg/L 9810
Filtrate 0.15 NTU
UVT: 89.9%
UVA: 0.046/cm
UVA Reduction 58.2%
Settled: 1.47 NTU
33 mg/L 9810
Filtrate 0.15 NTU
UVT: 90.0%
UVA: 0.045/cm
UVA Reduction 59.1%
Settled: 1.20 NTU
36 mg/L 9810
Filtrate 0.15 NTU
UVT: 90.6%
UVA: 0.042/cm
UVA Reduction 61.8%
Settled: 1.41 NTU
39 mg/L 9810
Filtrate 0.15 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction 62.7%
Settled: 1.64 NTU

## Slide 34: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 35: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
30 mg/L 9810
Filtrate 0.15 NTU
UVT: 89.9%
UVA: 0.046/cm
UVA Reduction 58.2%
Settled: 1.47 NTU
33 mg/L 9810
Filtrate 0.15 NTU
UVT: 90.0%
UVA: 0.045/cm
UVA Reduction 59.1%
Settled: 1.20 NTU
36 mg/L 9810
Filtrate 0.15 NTU
UVT: 90.6%
UVA: 0.042/cm
UVA Reduction 61.8%
Settled: 1.41 NTU
39 mg/L 9810
Filtrate 0.15 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction 62.7%
Settled: 1.64 NTU

## Slide 36: Jars 13-16 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9810

## Slide 37: Jars 13-16: End of 5-minute flocculation (30 RPM) duration.
42 mg/L 9810
Filtrate 0.12 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction 65.5%
Settled: 1.12 NTU
45 mg/L 9810
Filtrate 0.12 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction 67.3%
Settled: 1.38 NTU
48 mg/L 9810
Filtrate 0.13 NTU
UVT: 91.8%
UVA: 0.036/cm
UVA Reduction 67.3%
Settled: 1.30 NTU
51 mg/L 9810
Filtrate 0.17 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction 67.3%
Settled: 1.45 NTU

## Slide 38: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 39: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
42 mg/L 9810
Filtrate 0.12 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction 65.5%
Settled: 1.12 NTU
45 mg/L 9810
Filtrate 0.12 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction 67.3%
Settled: 1.38 NTU
48 mg/L 9810
Filtrate 0.13 NTU
UVT: 91.8%
UVA: 0.036/cm
UVA Reduction 67.3%
Settled: 1.30 NTU
51 mg/L 9810
Filtrate 0.17 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction 67.3%
Settled: 1.45 NTU

## Slide 40: Jars 17-20 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant AdvFloc CTC-00011

## Slide 41: Jars 17-20: End of 5-minute flocculation (30 RPM) duration.
120 mg/L AdvFloc
Filtrate 0.08 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction 68.2%
Settled: N/A NTU
130 mg/L AdvFloc
Filtrate 0.07 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction 70.0%
Settled: N/A NTU
140 mg/L AdvFloc
Filtrate 0.06 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction 7.8%
Settled: N/A NTU
150 mg/L AdvFloc
Filtrate 0.06 NTU
UVT: 92.9%
UVA: 0.031/cm
UVA Reduction 71.8%
Settled: N/A NTU

## Slide 42: Jars 17-20: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 43: Jars 17-20: After 25-minutes of settling, settled water turbidity is taken.
120 mg/L AdvFloc
Filtrate 0.08 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction 68.2%
Settled: N/A NTU
130 mg/L AdvFloc
Filtrate 0.07 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction 70.0%
Settled: N/A NTU
140 mg/L AdvFloc
Filtrate 0.06 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction 7.8%
Settled: N/A NTU
150 mg/L AdvFloc
Filtrate 0.06 NTU
UVT: 92.9%
UVA: 0.031/cm
UVA Reduction 71.8%
Settled: N/A NTU

## Slide 44: Jars 21-24 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant AdvFloc CTC-00011

## Slide 45: Jars 21-24: End of 5-minute flocculation (30 RPM) duration.
140 mg/L AdvFloc
Filtrate 0.09 NTU
UVT: 92.0%
UVA: 0.036/cm
UVA Reduction 67.3%
Settled: 0.35 NTU
150 mg/L AdvFloc
Filtrate 0.06 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction 69.1%
Settled: 0.35 NTU
160 mg/L AdvFloc
Filtrate 0.06 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction 70.0%
Settled: 0.29 NTU
170 mg/L AdvFloc
Filtrate 0.05 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction 70.9%
Settled: 0.26 NTU

## Slide 46: Jars 21-24: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 47: Jars 21-24: After 25-minutes of settling, settled water turbidity is taken.
140 mg/L AdvFloc
Filtrate 0.09 NTU
UVT: 92.0%
UVA: 0.036/cm
UVA Reduction 67.3%
Settled: 0.35 NTU
150 mg/L AdvFloc
Filtrate 0.06 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction 69.1%
Settled: 0.35 NTU
160 mg/L AdvFloc
Filtrate 0.06 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction 70.0%
Settled: 0.29 NTU
170 mg/L AdvFloc
Filtrate 0.05 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction 70.9%
Settled: 0.26 NTU

## Slide 48: Jars 25-28 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants 5% Acid Alum/CatFloc C-378

## Slide 49: Jars 25-28: End of 5-minute flocculation (30 RPM) duration.
46 mg/L 5% Acid Alum
0 mg/L C-378
Filtrate 0.13 NTU
UVT: 90.6%
UVA: 0.042/cm
UVA Reduction 61.8%
Settled: 1.02 NTU
46 mg/L 5% Acid Alum
0.5 mg/L C-378
Filtrate 0.12 NTU
UVT: 87.2%
UVA: 0.042/cm
UVA Reduction 61.8%
Settled: 1.22 NTU
46 mg/L 5% Acid Alum
1.0 mg/L C-378
Filtrate 0.11 NTU
UVT: 90.9%
UVA: 0.041/cm
UVA Reduction 62.7%
Settled: 1.30 NTU
46 mg/L 5% Acid Alum
1.5 mg/L C-378
Filtrate 0.08 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 64.5%
Settled: 1.30 NTU

## Slide 50: Jars 25-28: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 51: Jars 25-28: After 25-minutes of settling, settled water turbidity is taken.
46 mg/L 5% Acid Alum
0 mg/L C-378
Filtrate 0.13 NTU
UVT: 90.6%
UVA: 0.042/cm
UVA Reduction 61.8%
Settled: 1.02 NTU
46 mg/L 5% Acid Alum
0.5 mg/L C-378
Filtrate 0.12 NTU
UVT: 87.2%
UVA: 0.042/cm
UVA Reduction 61.8%
Settled: 1.22 NTU
46 mg/L 5% Acid Alum
1.0 mg/L C-378
Filtrate 0.11 NTU
UVT: 90.9%
UVA: 0.041/cm
UVA Reduction 62.7%
Settled: 1.30 NTU
46 mg/L 5% Acid Alum
1.5 mg/L C-378
Filtrate 0.08 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 64.5%
Settled: 1.30 NTU

## Slide 52: Jars 29-32 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants 5% Acid Alum/CatFloc C-378

## Slide 53: Jars 29-32: End of 5-minute flocculation (30 RPM) duration.
46 mg/L 5% Acid Alum
1.5 mg/L C-378
Filtrate 0.08 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 64.5%
Settled: 0.95 NTU
46 mg/L 5% Acid Alum
2.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 64.5%
Settled: 1.16 NTU
56 mg/L 5% Acid Alum
1.5 mg/L C-378
Filtrate 0.05 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction 67.3%
Settled: 1.15 NTU
56 mg/L 5% Acid Alum
2.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 92.0%
UVA: 0.035/cm
UVA Reduction 68.2%
Settled: 1.30 NTU

## Slide 54: Jars 29-32: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 55: Jars 29-32: After 25-minutes of settling, settled water turbidity is taken.
46 mg/L 5% Acid Alum
1.5 mg/L C-378
Filtrate 0.08 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 64.5%
Settled: 0.95 NTU
46 mg/L 5% Acid Alum
2.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction 64.5%
Settled: 1.16 NTU
56 mg/L 5% Acid Alum
1.5 mg/L C-378
Filtrate 0.05 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction 67.3%
Settled: 1.15 NTU
56 mg/L 5% Acid Alum
2.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 92.0%
UVA: 0.035/cm
UVA Reduction 68.2%
Settled: 1.30 NTU

## Slide 56: Jars 33-36 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants 5% Acid Alum/CatFloc C-378

## Slide 57: Jars 33-36: End of 5-minute flocculation (30 RPM) duration.
55 mg/L 5% Acid Alum
2.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction 68.2%
Settled: 1.39 NTU
65 mg/L 5% Acid Alum
2.4 mg/L C-378
Filtrate 0.05 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction 70.9%
Settled: 1.60 NTU
75 mg/L 5% Acid Alum
2.7 mg/L C-378
Filtrate 0.04 NTU
UVT: 93.0%
UVA: 0.031/cm
UVA Reduction 71.8%
Settled: 1.94 NTU
85 mg/L 5% Acid Alum
3.1 mg/L C-378
Filtrate 0.04 NTU
UVT: 93.3%
UVA: 0.029/cm
UVA Reduction 73.6%
Settled: 1.62 NTU

## Slide 58: Jars 33-36: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 59: Jars 33-36: After 25-minutes of settling, settled water turbidity is taken.
55 mg/L 5% Acid Alum
2.0 mg/L C-378
Filtrate 0.05 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction 68.2%
Settled: 1.39 NTU
65 mg/L 5% Acid Alum
2.4 mg/L C-378
Filtrate 0.05 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction 70.9%
Settled: 1.60 NTU
75 mg/L 5% Acid Alum
2.7 mg/L C-378
Filtrate 0.04 NTU
UVT: 93.0%
UVA: 0.031/cm
UVA Reduction 71.8%
Settled: 1.94 NTU
85 mg/L 5% Acid Alum
3.1 mg/L C-378
Filtrate 0.04 NTU
UVT: 93.3%
UVA: 0.029/cm
UVA Reduction 73.6%
Settled: 1.62 NTU

## Slide 60: Jars 37-40 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants AdvFloc CTC-00011 /CatFloc C-378

## Slide 61: Jars 37-40: End of 5-minute flocculation (30 RPM) duration.
180 mg/L AdvFloc
0 mg/L C-378
Filtrate 0.06 NTU
UVT: 93.0%
UVA: 0.031/cm
UVA Reduction 71.8%
Settled: 0.37 NTU
180 mg/L AdvFloc
2.0 mg/L C-378
Filtrate 0.04 NTU
UVT: 93.4%
UVA: 0.029/cm
UVA Reduction 73.6%
Settled: 0.40 NTU
180 mg/L AdvFloc
3.0 mg/L C-378
Filtrate 0.04 NTU
UVT: 93.7%
UVA: 0.028/cm
UVA Reduction 74.5%
Settled: 0.39 NTU
180 mg/L AdvFloc
4.0 mg/L C-378
Filtrate 0.04 NTU
UVT: 93.8%
UVA: 0.027/cm
UVA Reduction 75.5%
Settled: 0.48 NTU

## Slide 62: Jars 37-40: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 63: Jars 37-40: After 25-minutes of settling, settled water turbidity is taken.
180 mg/L AdvFloc
0 mg/L C-378
Filtrate 0.06 NTU
UVT: 93.0%
UVA: 0.031/cm
UVA Reduction 71.8%
Settled: 0.37 NTU
180 mg/L AdvFloc
2.0 mg/L C-378
Filtrate 0.04 NTU
UVT: 93.4%
UVA: 0.029/cm
UVA Reduction 73.6%
Settled: 0.40 NTU
180 mg/L AdvFloc
3.0 mg/L C-378
Filtrate 0.04 NTU
UVT: 93.7%
UVA: 0.028/cm
UVA Reduction 74.5%
Settled: 0.39 NTU
180 mg/L AdvFloc
4.0 mg/L C-378
Filtrate 0.04 NTU
UVT: 93.8%
UVA: 0.027/cm
UVA Reduction 75.5%
Settled: 0.48 NTU

## Slide 64: Jars 41-44 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants 5% Acid Alum/ AdvFloc CTC-00011 /CatFloc C-378

## Slide 65: Jars 41-44: End of 5-minute flocculation (30 RPM) duration.
46 mg/L 5% Acid Alum
0 mg/L C-378
Filtrate 0.12 NTU
UVT: 90.6%
UVA: 0.042/cm
UVA Reduction 61.8%
Settled: 0.89 NTU
180 mg/L AdvFloc
4.0 mg/L C-378
Filtrate 0.04 NTU
UVT: 93.6%
UVA: 0.028/cm
UVA Reduction 74.5%
Settled: 0.49 NTU
46 mg/L 5% Acid Alum
2.0 mg/L C-378
Filtrate 0.06 NTU
UVT: 91.4%
UVA: 0.038/cm
UVA Reduction 65.4%
Settled: 1.12 NTU
85 mg/L 5% Acid Alum
3.1 mg/L C-378
Filtrate 0.04 NTU
UVT: 93.4%
UVA: 0.029/cm
UVA Reduction 73.6%
Settled: 1.84 NTU

## Slide 66: Jars 41-44: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 67: Jars 41-44: After 25-minutes of settling, settled water turbidity is taken.
46 mg/L 5% Acid Alum
0 mg/L C-378
Filtrate 0.12 NTU
UVT: 90.6%
UVA: 0.042/cm
UVA Reduction 61.8%
Settled: 0.89 NTU
180 mg/L AdvFloc
4.0 mg/L C-378
Filtrate 0.04 NTU
UVT: 93.6%
UVA: 0.028/cm
UVA Reduction 74.5%
Settled: 0.49 NTU
46 mg/L 5% Acid Alum
2.0 mg/L C-378
Filtrate 0.06 NTU
UVT: 91.4%
UVA: 0.038/cm
UVA Reduction 65.4%
Settled: 1.12 NTU
85 mg/L 5% Acid Alum
3.1 mg/L C-378
Filtrate 0.04 NTU
UVT: 93.4%
UVA: 0.029/cm
UVA Reduction 73.6%
Settled: 1.84 NTU

## Slide 68: Jars 45-48 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants 5% Acid Alum/CatFloc C-378 + Powder Activated Carbon (PAC)

## Slide 69: Jars 45-48: End of 5-minute flocculation (30 RPM) duration.
46 mg/L 5% Acid Alum
2.2 mg/L C-378
0 mg/L PAC
Filtrate 0.08 NTU
UVT: 91.0%
UVA: 0.040/cm
UVA Reduction 63.6%
Settled: 0.51 NTU
46 mg/L 5% Acid Alum
2.2 mg/L C-378
20 mg/L PAC
Filtrate 0.11 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction 72.7%
Settled: 3.01 NTU
46 mg/L 5% Acid Alum
2.2 mg/L C-378
30 mg/L PAC
Filtrate 0.11 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction 75.7%
Settled: 5.06 NTU
46 mg/L 5% Acid Alum
2.2 mg/L C-378
40 mg/L PAC
Filtrate 0.16 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction 75.7%
Settled: 5.74 NTU

## Slide 70: Jars 45-48: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 71: Jars 45-48: After 25-minutes of settling, settled water turbidity is taken.
46 mg/L 5% Acid Alum
2.2 mg/L C-378
0 mg/L PAC
Filtrate 0.08 NTU
UVT: 91.0%
UVA: 0.040/cm
UVA Reduction 63.6%
Settled: 0.51 NTU
46 mg/L 5% Acid Alum
2.2 mg/L C-378
20 mg/L PAC
Filtrate 0.11 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction 72.7%
Settled: 3.01 NTU
46 mg/L 5% Acid Alum
2.2 mg/L C-378
30 mg/L PAC
Filtrate 0.11 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction 75.7%
Settled: 5.06 NTU
46 mg/L 5% Acid Alum
2.2 mg/L C-378
40 mg/L PAC
Filtrate 0.16 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction 75.7%
Settled: 5.74 NTU

## Slide 72: Jars 49-52 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants 5% Acid Alum/CatFloc C-378 + Powder Activated Carbon (PAC)

## Slide 73: Jars 49-52: End of 5-minute flocculation (30 RPM) duration.
46 mg/L 5% Acid Alum
2.2 mg/L C-378
0 mg/L PAC
Filtrate 0.05 NTU
UVT: 91.0%
UVA: 0.041/cm
UVA Reduction 62.7%
Settled: 0.48 NTU
46 mg/L 5% Acid Alum
2.2 mg/L C-378
30 mg/L PAC
Filtrate 0.10 NTU
UVT: 93.7%
UVA: 0.028/cm
UVA Reduction 74.5%
Settled: 4.72 NTU
46 mg/L 5% Acid Alum
3.2 mg/L C-378
30 mg/L PAC
Filtrate 0.06 NTU
UVT: 94.5%
UVA: 0.024/cm
UVA Reduction 78.2%
Settled: 5.69 NTU
46 mg/L 5% Acid Alum
4.2 mg/L C-378
30 mg/L PAC
Filtrate 0.05 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction 75.5%
Settled: 6.10 NTU

## Slide 74: Jars 49-52: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 75: Jars 49-52: After 25-minutes of settling, settled water turbidity is taken.
46 mg/L 5% Acid Alum
2.2 mg/L C-378
0 mg/L PAC
Filtrate 0.05 NTU
UVT: 91.0%
UVA: 0.041/cm
UVA Reduction 62.7%
Settled: 0.48 NTU
46 mg/L 5% Acid Alum
2.2 mg/L C-378
30 mg/L PAC
Filtrate 0.10 NTU
UVT: 93.7%
UVA: 0.028/cm
UVA Reduction 74.5%
Settled: 4.72 NTU
46 mg/L 5% Acid Alum
3.2 mg/L C-378
30 mg/L PAC
Filtrate 0.06 NTU
UVT: 94.5%
UVA: 0.024/cm
UVA Reduction 78.2%
Settled: 5.69 NTU
46 mg/L 5% Acid Alum
4.2 mg/L C-378
30 mg/L PAC
Filtrate 0.05 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction 75.5%
Settled: 6.10 NTU

## Slide 76: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 77: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 78: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 79: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 80: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 81: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732