{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["CT Data","GiardiaGraph","ViruseGraph"],"not_rendered":{"charts":4,"images":1,"macros":0,"external_links":0,"defined_names":6,"comments":1,"pivot_tables":0},"unopened":[{"sheet":"GiardiaGraph","index":1,"reason":"not_a_worksheet"},{"sheet":"ViruseGraph","index":2,"reason":"not_a_worksheet"}],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"CT Data","index":0,"n_rows":56,"n_cols":93,"rows_kept":56,"cut":false,"hidden":false,"merged":[[9,8,9,9],[8,8,8,9],[55,9,55,12],[54,3,54,12],[55,3,55,7]]}
[null,"Author:  Guy Schott, guy.schott@waterboards.ca.gov, 707-576-2732"]
[null,"CT Compliance for "]
[null,"Viruses"]
[null,"by Chlorine Dioxide Disinfection"]
[]
[null,"Input Parameters:"]
[null,"Water System Name:",null,null,null,null,null,null,"Enter Name"]
[null,"Number of Service Connections:",null,null,null,null,null,null,"Enter number"]
[null,"System Number:",null,null,null,null,null,null,"Enter number"]
[null,"Month and Year:",null,null,null,null,null,null,"2017-07-01"]
[null,"Clearwell(s) - Volume per Foot:",null,null,null,null,null,null,50000,"Gallons/Ft"]
[null,"Short-Circuiting Factor for Clearwell(s):",null,null,null,null,null,null,0.2,"t10/T"]
[null,"Transmission Pipe - Volume",null,null,null,null,null,null,1000,"Gallons"]
[null,"Short-Circuiting Factor for Transmission Pipe:",null,null,null,null,null,null,0.9,"t10/T"]
[]
[null,null,"Data inputs should be based on when plant is on-line and flow leaving clearwell",null,null,null,null,null,null,null,null,null,"Results",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"DATE(AY17,AZ17,AZ16)","v":"2017-07-01"},1]
[null,null,"Clearwell & Transmission Data for Peak Hourly Flow (for waters with pH = 6.0-9.0)",null,null,null,null,null,null,null,"Crypto","Giardia ","Viruses",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"YEAR(I10)","v":2017},{"$f":"MONTH($I$10)","v":7},null,null,null,null,null,null,null,null,"Virus Table for 4 log",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Giardia "]
[null,"Date","Flow Rate, \ngpm","Lowest \nLevel, ft","Temp, \noC","ClO2\nResidual, \nmg/L","ClO2-\nResidual, \nmg/L","Effective \nVolume, \ngal","Effective \nContact Time, \nminutes","CT10\nmg/L∙min","Log \nInactivation","Log \nInactivation","Log \nInactivation",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Log\nVirus","CT\nVirus",1,2,null,"1-5, Log",1,2,null,"5-20, Log",1,2,null,"20-25, Log",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,null,null,"Required Log Inactivation:",0.5,3.5,null,null,"Log \nInactivation"]
[null,{"$f":"AY19&\"-\"&AZ19","v":"Sat-1"},1200,5,5,0.8,0.5,{"$f":"IF(AND(D19=0,$I$13=0),\"-\",IF(C19<=0,\"-\",$I$11*D19*$I$12+$I$13*$I$14))","v":50900},{"$f":"IF(C19=0,\"-\",H19/(C19))","v":42.416666666666664},{"$f":"IF(OR($C19=0,$F19<=0),\"-\",I19*F19)","v":33.93333333333333},{"$f":"IF(OR($D19=0,$C19=0,$F19<=0),\"-\", (0.001506*(1.09116^E19)*J19))","v":7.9048508647990068E-2},{"$f":"IF(OR($D19=0,$C19=0,$F19<=0),\"-\", IF(CO19>8,\">8.0\",CO19))","v":3.8914373088685008},{"$f":"IF(OR($C19<=0,E19<=0,$F19<=0),\"-\",IF(J19>AF19,\">4.0\",IF(E19<=5,AJ19,IF(E19<=20,AN19,AR19))))","v":">4.0"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(OR($C19=0,E19<=0,$F19<=0),\"-\", 4*J19/AF19)","v":4.0638722554890219},{"$f":"IF(E19<1,\"-\",HLOOKUP(E19,$BI$18:$CG$19,2))","v":33.4},{"$f":"-0.00001929*E19^2-0.00000929*E19-0.000392","v":-9.2069999999999999E-4},{"$f":"0.00093714*E19^2+0.00328714*E19+0.068062","v":0.1079262},1.4244000000000001,{"$f":"IF(C19<=0,\"-\",AG19*$J19^2+AH19*$J19+AI19)","v":4.0265362680000001},{"$f":"-0.00000004*E19^4+0.00000159*E19^3-0.00004328*E19^2+0.00030334*E19-0.00156149","v":-9.5304000000000016E-4},{"$f":"-0.00002*E19^3+0.001177*E19^2-0.007005*E19+0.117161","v":0.10906100000000001},1.4248000000000001,{"$f":"IF(C19<=0,\"-\",AK19*$J19^2+AL19*$J19+AM19)","v":4.0282052389333334},{"$f":"-0.000171*E19^2+0.006151*E19-0.061302","v":-3.4822000000000006E-2},{"$f":"0.002057*E19^2-0.065201*E19+0.770529","v":0.49594900000000003},1.426585,{"$f":"IF(C19<=0,\"-\",AO19*$J19^2+AP19*$J19+AQ19)","v":-21.840739297777784},null,null,null,null,null,null,{"$f":"IF(ISBLANK($AY$16),\"\",TEXT(AY16,\"ddd\"))","v":"Sat"},1,null,0.5,0.5,null,null,{"$f":"$BF$53","v":3.8914373088685008},{"$f":"$BG$53","v":"-"},null,50.1,45.9,41.8,37.6,33.4,31.7,30.1,28.4,26.8,25.1,23.4,21.7,20.100000000000001,18.399999999999999,16.7,15.9,15,14.2,13.3,12.5,11.7,10.9,10,9.1999999999999993,8.4,null,null,null,null,null,null,null,{"$f":"IF(OR($D19=0,$C19=0,$F19<=0),\"-\",IF(E19<=5,J19/(-3.07*E19+24.07),J19/(-0.2561*E19+10.137)))","v":3.8914373088685008}]
[null,"Sun-2",1200,5,5,0.8,0.2,{"$f":"IF(AND(D20=0,$I$13=0),\"-\",IF(C20<=0,\"-\",$I$11*D20*$I$12+$I$13*$I$14))","v":50900},{"$f":"IF(C20=0,\"-\",H20/(C20))","v":42.416666666666664},{"$f":"IF(OR($C20=0,$F20<=0),\"-\",I20*F20)","v":33.93333333333333},{"$f":"IF(OR($D20=0,$C20=0,$F20<=0),\"-\", (0.001506*(1.09116^E20)*J20))","v":7.9048508647990068E-2},{"$f":"IF(OR($D20=0,$C20=0,$F20<=0),\"-\", IF(CO20>8,\">8.0\",CO20))","v":3.8914373088685008},{"$f":"IF(OR($C20<=0,E20<=0,$F20<=0),\"-\",IF(J20>AF20,\">4.0\",IF(E20<=5,AJ20,IF(E20<=20,AN20,AR20))))","v":">4.0"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(OR($C20=0,E20<=0,$F20<=0),\"-\", 4*J20/AF20)","v":4.0638722554890219},33.4,-9.2069999999999999E-4,0.1079262,1.4244000000000001,4.0265362680000001,-9.5304000000000016E-4,0.10906100000000001,1.4248000000000001,4.0282052389333334,-3.4822000000000006E-2,0.49594900000000003,1.426585,-21.840739297777784,null,null,null,null,null,null,{"$f":"IF(ISBLANK($AY$16),\"\",TEXT($AVO$16+AZ19,\"ddd\"))","v":"Sun"},2,null,1,1,null,null,3.8914373088685008,"-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.8914373088685008]
[null,"Mon-3",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,{"$f":"IF(ISBLANK($AY$16),\"\",TEXT($AVO$16+AZ20,\"ddd\"))","v":"Mon"},{"$f":"AZ20+1","v":3},null,1.5,1.5,null,null,3.8914373088685008,"-",null,"Temp",2,3,4,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Tue-4",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Tue",{"$f":"AZ21+1","v":4},null,2,2,null,null,3.8914373088685008,"-",null,1,8.4,25.6,50.1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Wed-5",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Wed",5,null,2.5,2.5,null,null,3.8914373088685008,"-",null,2,7.7,23.5,45.9,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Thu-6",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Thu",6,null,3,3,null,null,3.8914373088685008,"-",null,3,7,21.4,41.8,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Fri-7",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Fri",7,null,null,3.5,null,null,3.8914373088685008,"-",null,4,6.3,19.2,37.6,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Sat-8",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Sat",8,null,null,4,null,null,3.8914373088685008,"-",null,5,5.6,17.100000000000001,33.4,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,{"$f":"AY27&\"-\"&AZ27","v":"Sun-9"},null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Sun",{"$f":"AZ26+1","v":9},null,null,null,null,null,3.8914373088685008,"-",null,6,5.3,16.2,31.7,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Mon-10",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Mon",10,null,null,null,null,null,3.8914373088685008,"-",null,7,5,15.4,30.1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Tue-11",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Tue",11,null,null,null,null,null,3.8914373088685008,"-",null,8,4.8,14.5,28.4,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Wed-12",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Wed",12,null,null,null,null,null,3.8914373088685008,"-",null,9,4.5,13.7,26.8,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Thu-13",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Thu",13,null,null,null,null,null,3.8914373088685008,"-",null,10,4.2,12.8,25.1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Fri-14",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Fri",14,null,null,null,null,null,3.8914373088685008,"-",null,11,3.9,12,23.4,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Sat-15",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Sat",15,null,null,null,null,null,3.8914373088685008,"-",null,12,3.6,11.1,21.7,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Sun-16",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Sun",16,null,null,null,null,null,3.8914373088685008,"-",null,13,3.4,10.3,20.100000000000001,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Mon-17",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Mon",17,null,null,null,null,null,3.8914373088685008,"-",null,14,3.1,9.4,18.399999999999999,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Tue-18",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Tue",18,null,null,null,null,null,3.8914373088685008,"-",null,15,2.8,8.6,16.7,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Wed-19",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Wed",19,null,null,null,null,null,3.8914373088685008,"-",null,16,2.7,8.1999999999999993,15.9,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Thu-20",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Thu",20,null,null,null,null,null,3.8914373088685008,"-",null,17,2.5,7.7,15,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Fri-21",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Fri",21,null,null,null,null,null,3.8914373088685008,"-",null,18,2.4,7.3,14.2,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Sat-22",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Sat",22,null,null,null,null,null,3.8914373088685008,"-",null,19,2.2000000000000002,6.8,13.3,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Sun-23",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Sun",23,null,null,null,null,null,3.8914373088685008,"-",null,20,2.1,6.4,12.5,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Mon-24",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Mon",24,null,null,null,null,null,3.8914373088685008,"-",null,21,2,6,11.7,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Tue-25",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Tue",25,null,null,null,null,null,3.8914373088685008,"-",null,22,1.8,5.6,10.9,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Wed-26",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Wed",26,null,null,null,null,null,3.8914373088685008,"-",null,23,1.7,5.0999999999999996,10,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Thu-27",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Thu",27,null,null,null,null,null,3.8914373088685008,"-",null,24,1.5,4.7,9.1999999999999993,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Fri-28",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Fri",28,null,null,null,null,null,3.8914373088685008,"-",null,25,1.4,4.3,8.4,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Sat-29",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Sat",29,null,null,null,null,null,3.8914373088685008,"-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Sun-30",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Sun",30,null,null,null,null,null,3.8914373088685008,"-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Mon-31",null,null,null,null,null,"-","-","-","-","-","-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-","-",-3.9199999999999999E-4,6.8061999999999998E-2,1.4244000000000001,"-",-1.56149E-3,0.117161,1.4248000000000001,"-",-6.1302000000000002E-2,0.77052900000000002,1.426585,"-",null,null,null,null,null,null,"Mon",31,null,null,null,null,null,3.8914373088685008,"-",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"-"]
[null,"Min",{"$f":"MIN(C19:C49)","v":1200},5,5,0.8,{"$f":"MIN(G19:G49)","v":0.2},50900,42.416666666666664,{"$f":"MIN(J19:J49)","v":33.93333333333333},{"$f":"MIN(K19:K49)","v":7.9048508647990068E-2},{"$f":"MIN(L19:L49)","v":3.8914373088685008},{"$f":"IF(AND(MIN(M19:M49) = 0,M51=\">4.0\"),\">4.0\",MIN(M19:M49))","v":">4.0"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"MIN(CO19:CO49)","v":3.8914373088685008}]
[null,"Median",{"$f":"IF(SUM(C19:C49)<=0,0,MEDIAN(C19:C49))","v":1200},{"$f":"IF(SUM(D19:D49)<=0,0,MEDIAN(D19:D49))","v":5},{"$f":"IF(SUM(E19:E49)<=0,0,MEDIAN(E19:E49))","v":5},{"$f":"IF(SUM(F19:F49)<=0,0,MEDIAN(F19:F49))","v":0.8},{"$f":"IF(SUM(G19:G49)<=0,0,MEDIAN(G19:G49))","v":0.35},{"$f":"IF(SUM(H19:H49)<=0,0,MEDIAN(H19:H49))","v":50900},{"$f":"IF(SUM(I19:I49)<=0,0,MEDIAN(I19:I49))","v":42.416666666666664},33.93333333333333,{"$f":"IF(SUM(K19:K49)<=0,\"-\",MEDIAN(K19:K49))","v":7.9048508647990068E-2},{"$f":"IF(SUM(L19:L49)<=0,\"-\",MEDIAN(L19:L49))","v":3.8914373088685008},{"$f":"IF(SUM(AE19:AE49)<=0,\"-\",IF(MEDIAN(AE19:AE49)>4,\">4.0\",MEDIAN(AE19:AE49)))","v":">4.0"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"IF(SUM(CO19:CO49)<=0,0,MEDIAN(CO19:CO49))","v":3.8914373088685008}]
[null,"Max",{"$f":"MAX(C19:C49)","v":1200},{"$f":"MAX(D19:D49)","v":5},{"$f":"MAX(E19:E49)","v":5},{"$f":"MAX(F19:F49)","v":0.8},{"$f":"MAX(G19:G49)","v":0.5},{"$f":"MAX(H19:H49)","v":50900},{"$f":"MAX(I19:I49)","v":42.416666666666664},33.93333333333333,{"$f":"MAX(K19:K49)","v":7.9048508647990068E-2},{"$f":"IF(MAX(CO19:CO49)>8,\">8.0\",MAX(CO18:CO49))","v":3.8914373088685008},{"$f":"IF(MAX(AE19:AE49)>4,\">4.0\",MAX(AE19:AE49))","v":">4.0"},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"MAX(CO19:CO49)","v":3.8914373088685008}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Average:",{"$f":"IF(SUM(CO19:CO49)=0,\"-\",AVERAGE(CO19:CO49))","v":3.8914373088685008},{"$f":"IF(SUM(M19:M49)=0,\"-\",AVERAGE(M19:M49))","v":"-"}]
[]
[null,"Print Name:"]
[null,"Signature:",null,null,null,null,null,null,"Date:"]