## Slide 1: Title
March 23-24, 2021

## Slide 2: CA-NV AWWA Operator Symposium March 24, 2021 1. Coagulants/Identification 2. Stock Solution Prep 3. Dose Calculations 4. CT Concept
By
Guy Schott, P.E.

## Slide 3: Common Inorganic Coagulants
Inorganic coagulants – Metal Salts
  [AL] Aluminum Sulfate, Al2(SO4)3 * 14.3H2O
  [AL] Aluminum Chlorohydrate (ACH), Al2Cl(OH)5
  [AL] Polyaluminum Chloride (PACl), AlnCl3n-m(OH)m
  [AL] Polyaluminum Chlorosulfate (PACS) , Ala(OH)b(Cl)c(SO4)d
  Ferric Chloride, FeCl3
  Ferric Sulfate, Fe2(SO4)3*8.8H20
  When inorganic coagulants hydrolyze, hydrogen ions (H+) are released that react with the alkalinity of the water.

## Slide 4: %Basicity of a Coagulant
In the formation of PACl/PACS coagulants, some of the acid (H+) that would have been released is neutralized with base (OH-) when coagulant is manufactured. The degree to which the hydrogen ions that would be released by hydrolysis are preneutralized is known as the basicity of the product.
Example:
ACH, Al2Cl(OH)5; there are 5 moles of [OH] and 2 moles of [Al]
[5]
3[2]
Basicity, % =
X 100% = 83%
[OH]
3[Al]
X 100% =
This means that 83% of the formed hydrogen ions (H+) are pre-neutralized.

## Slide 5: Alkalinity Consumption of Inorganic Coagulants 1 mg/L Aluminum base Coagulants
2.945 x [%Al2O3/100] x [1 - %Basicity/100] = x mg/L as CaCO3
or
5.56 x [%Al+3/100] x [1 - %Basicity/100] = x mg/L as CaCO3
1 mg/L of Coagulant | %Al2O3 | %Basicity | mg/L Alkalinity as CaCO3 Reduced
Alum, Al2(SO4)3*14.3H20 | 8.2 | 0 | 2.945 x 8.2/100 x (1 - 0/100) = 0.241
Al2(SO4)3*14.3H20 (dry/hydrated) | 17 | 0 | 2.945 x 17/100 x (1 – 0/100) = 0.501
ACH, Al2Cl(OH)5 | 23.62 | 83 | 2.945 x 23.62/100 x (1 – 83/100) = 0.118
PACl, Al10Cl3(OH)27 | 10.01 | 90 | 2.945 x 10.01/100 x (1 – 90/100) = 0.029
PACl, Al5Cl3(OH)12 | 32.5 | 80 | 2.945 x 32.5/100 x (1 – 80/100) = 0.191
PACl, Al10Cl21(OH)9 | 10.01 | 30 | 2.945 x 10.01/100 x (1 – 30/100) = 0.206
PACS, Al2(OH)3(Cl)(SO4) | 10.01 | 50 | 2.945 x 10.01/100 x (1 – 50/100) = 0.147
Notes: 1 mg Al+3/26.9815 * 3 *100/2 = 5.56 as CaCO3

## Slide 6: Common Organic Coagulants
Organic coagulants are long-chained, medium to high-molecular-weight polymers (sticky) used for bridging floc, improve settleability, filterability, filter-run-time and organic reduction.
  [PY] Polyamine (max dose 5 mg/L as active PY)
  [pDADMAC] Polydialyldimethylammonium chloride (max dose 10 mg/L as active pDADMAC)
  [PC] Polyacrylamide, dry or emulsion (max dose 1 mg/L as active PC)
    Shelf-life 6-9 month as an emulsion; once mixed with water, use within 2-3 days.
    Shelf-life years for dry; once mixed with water, use within 7 days.

## Slide 7: Polyamine C59H108N14O10 MW: 1,173.6 g/mol

## Slide 8: Diallyldimethylammonium chloride or N-allyl-N,N-dimethylprop-2-en-1-aminium chloride pDADMAC C8H16ClN MW: 161.67 g/mol Low to high viscosity (LV, HV, VHV)
CH3
N
+
CH3
CH2
CH
CH2
CH2
CH
CH2
Cl-

## Slide 9: Polyacrylamide (C3H5NO)n Acrylamide C3H5NO or CH2=CH-CONH2 MW: 71.08 g/mol Cationic to Anionic Charge
C
H
CH
N
H
O
CH2
Acrylamide subunit (monomer) of Polyacrylamide
It increases the viscosity of water and facilitates the flocculation of particles present in water

## Slide 10: Information on your Coagulant (C-102xyz)
Safety Data Sheet | Certificate of Analysis/Company | NSF Listing (Product #/ Name)
% Strength of Inorganic Coagulant (range) or no information | Manufacture of Chemical and Location | Name of Company, Manufacture of Chemical and Location
% Water (range) | %Al2O3, %Al, %Fe %H2SO4 (Acid Alum/Fe) | Inorganic & Organic Coagulants
% Trade Secret or Proprietary Compound | %Basicity? (ask vendor) Specific Gravity | Blended Coagulants
Specific Gravity (range) | Shipping Date/Lot# | Product Max Dose (mg/L)

## Slide 11: NSF Certified Drinking Water Treatment Chemicals
Go to NSF Certified Drinking Water Treatment Chemicals website to determine coagulant type for selected chemical products.
  http://info.nsf.org/Certified/PwsChemicals/
Example headings listed in NSF for different products:
  [AL] Aluminum base coagulants; (inorganic)
  [PY] Polyamines; (organic)
  [Al] [PY] Blends; (inorganic/organic blends)
  Poly (Diallyldimethylammonium Chloride) (pDADMAC); (organic)
[AL, PY, pDADMAC, PC] NSF symbols for type of coagulants

## Slide 12: Stock Solution Preparation for Jar Testing
(Vp, mL) x (Product % Strength) x (SGp) = (Vs, mL) x (Stock % Strength) x (SGs)
Pipettes (0.5 - 5 mL &
100 – 1000 uL)
Volumetric
Flask
Chemical
Product
Don’t use syringes

## Slide 13: Stock Solution: % Strength for Jar Testing
1-Liter Jars | 2-Liters Jars
1% Solution by Weight: 1.0 mL = 10. mg chemical Injection into 1-liter jar 1.0 mL = 10. mg/L dose 0.1% Solution by Weight: 1.0 mL = 1.0 mg Injection into 1-liter jar 1.0 mL = 1.0 mg/L dose | 2% Solution by Weight: 1.0 mL = 20. mg chemical Injection into 2-liter jar 1.0 mL = 10. mg/L dose 0.2% Solution by Weight: 1.0 mL = 2.0 mg Injection into 2-liter jar 1.0 mL = 1.0 mg/L dose
1% solution strength = 1,000 g/1,000 mL x 0.01 = 10 g/1000 mL = 10,000 mg/1,000 mL
= 10 mg/mL; 1 mL = 10 mg

## Slide 14: Stock Solution Preparation/Calculation
(vp, mL) x (100% strength) x (1.34) = (200 mL) x (1.0% strength) x (1.0)
Solve
Vp (mL) = (200 mL)(1.0%)(1) = 1.5 mL
(100%)(1.34)
(Assume SG ~ 1.0 for <3% strengths)
100%
Product
SG: 1.34
(Vp, mL) x (Product % Strength) x (SGp) = (Vs, mL) x (Stock % Strength) x (SGs)
1.0% Sol.
200 mL
SG: 1.
Pipettes

## Slide 15: Further Dilution/Calculation (1.0% to 0.1%)
(v1, mL) x (1.0% strength) x (1.0) = (100 mL) x (0.10% strength) x (1)
Solve
V2 (mL) = (100 mL)(0.10%)(1) = 10. mL
(1.0%)(1)
(V1, mL) x (Stock1 % Strength) x (SG1) = (V2, mL) x (Stock2 % Strength) x (SG2)
1.0% Sol.
200 mL
SG: 1.
0.10% Sol.
100 mL
SG: 1.
Pipettes (0.5 - 5 mL &
100 – 1000 uL)
Don’t use syringes

## Slide 16: Chemical Dose Setup/Calculations
Chemical Dose (mg/L) = =
mass
vol
20 mg
L
x-Vol (x mass)
1-liter
H2O
1-liter
H2O
20 mg
or
vol
L
Convert “vol” to mass chemical

## Slide 17: Chemical Dose Setup/Calculation
Chemical Dose (mg/L) = =
Chemical feed rate: mL/min, L/min, L/day, gal/hr, gal/day, lbs/day
Flow rate: gallons per min (gpm), million gallons per day (MGD), L/min
Chemical Feed Rate (vol/time = mass/time)
Plant Flow
(vol/time)
Chemical Feed Rate (vol/time or mass/time )
Flow Rate (vol/time)
mass
vol

## Slide 18: Dimensional Analysis – For Solving Dose Problems
Dimensional Analysis – a method used to convert one unit to a different unit by using conversion factors.
1 Gallon = 3.785 Liters
1 Liter = 1,000 mL
1 Day = 1,440 minutes
1 gram = 1,000 mg
1 lb = 454 grams (g) = 454,000 mg
1 mL (water) = 1 g = 1,000 mg
1 gallon (water) = 8.337 lbs
Specific gravity (SG): Relative density, which is the ratio of the density of a chemical product to that of a standard substance (water).

## Slide 19: Chemical Dose Setup/Calculation – Ex1
Chemical Dose (mg/L) = =
=
Chemical Dose (mg/L) = 40 mg/L as product, CC-9805
Note: Dose reported as Product: Accounts for 100% (water, inorganic, organic coagulants).
Chemical Feed Rate 56.5 mL/min, injected as neat.
SG = 1.34, 100% strength wt/wt as product (CC-9805)
Plant Flow
500 gpm
56.5 mL x 1340 mg/mL
1892.5 L
56.5 mL/min x 1000 mg/mL x 1.34 x 1
500 gal/min x 3.785 L/gal
Chemical Feed Rate
Flow Rate

## Slide 20: Chemical Dose Setup/Calculation – Ex2
Chemical Dose (mg/L) = =
Chemical Dose (mg/L) = 19.4 mg/L as Alum (dry)
Note: Dose reported as Active: Only accounts for the designated active substance within the product (i.e., hydrated Alum and FeCl3).
Chemical Feed Rate 56.5 mL/min,
SG = 1.34, 48.5% strength wt/wt as active (Alum)
Plant Flow
500 gpm
56.5 mL/min x 1000 mg/mL x 1.34 x 0.485
500 gal/min x 3.785 L/gal
56.5 mL x 649.9 mg/mL
1892.5 L

## Slide 21: Chemical Dose Setup/Calculation – Ex3
Chemical Dose (mg/L) =
Chemical Dose (mg/L) = =
Chemical Dose (mg/L) = 19.4 mg/L as Alum (dry)
Chemical Feed Rate 56.5 mL/min,
SG = 1.34, 48.5% strength wt/wt as active (Alum)
Plant Flow
0.72 MGD (MG/day)
56.5 mL/min x 1000 mg/mL x 1.34 x 0.485
0.72 MG/day x 1 day/1440 min x 1,000,000 gal/MG x 3.785 L/gal
56.5 mL/min x 1000 mg/mL x 1.34 x 0.485
500 gal/min x 3.785 L/gal
56.5 mL x 649.9 mg/mL
1892.5 L

## Slide 22: Chemical Dose Setup/Calculation – Ex4
Chemical Dose (mg/L) =
Chemical Dose (mg/L) = =
Chemical Dose (mg/L) = 19.4 mg/L as Alum (dry)
Chemical Feed Rate 21.5 gal/day,
SG = 1.34, 48.5% strength wt/wt as active (Alum)
Plant Flow
500 gpm
56.5 mL/min x 1000 mg/mL x 1.34 x 0.485
500 gal/min x 3.785 L/gal
56.5 mL x 649.9 mg/mL
1892.5 L
21.5 gal/day x 1 day/1440 min x 3.785 L/gal x 1000 mL/L x 1000 mg/mL x 1.34 x 0.485
500 gal/min x 3.785 L/gal

## Slide 23: Chemical Dose Setup/Calculation – Ex5
Chemical Dose (mg/L) =
Chemical Dose (mg/L) =
Chemical Dose (mg/L) = 1.67 mg/L as Cl2
Chemical Feed Rate
10 lbs./day, Chlorine (gas)
Plant Flow
500 gpm
3,153 mg
1,892.5 L
10 lbs./day x 1 day/1,440 min x 454,000 mg/lb.
500 gal/min x 3.785 L/gal

## Slide 24: Chemical Dose Setup/Calculation – Ex6
Chemical Dose (mg/L) =
Chemical Dose (mg/L) = 1.52 mg/L as NaOCl
Chemical Dose (mg/L) = 1.52 mg/L as NaOCl x 0.95 Cl2/NaOCl = 1.44 mg/L as Cl2
Chemical Feed Rate – injected as diluted
30 mL/min, SG = 1.13, 8% strength NaOCl
Plant Flow
500 gpm
30 mL/min x 1000 mg/mL x 1.13 x 0.08
500 gal/min x 3.785 L/gal

## Slide 25: Chemical Feed Rate Setup/Calculation – Ex7
50 mg/L = ; Solve for mL/min (algebra)
mL/min = = =
Chemical Feed Rate (mL/min) = 177 mL/min as Alum
Based on jar testing, the plant dose is to be set at 50 mg/L. What is the chemical feed rate setting (mL/min)?
Plant flow is 600 gpm.
Chemical characteristics: SG = 1.34, 48% strength wt/wt as Alum
Plant Flow
600 gpm
50 mg/L x 600 gal/min x 3.785 L/gal
1000 mg/mL x 1.34 x 0.48
113,550 mg/min
643 mg/mL
? mL/min x 1000 mg/mL x 1.34 x 0.48
600 gal/min x 3.785 L/gal
113,550 mL/min
643

## Slide 26: CT – Concept It’s the delivered disinfection dose to pathogens
  Pathogens: Giardia cyst, viruses, Cryptosporidium
  CT
  “C” is the disinfection residual (mg/L)
  “T” is the disinfection exposure or contact time (minutes)
  C x T = mg/L * min, delivered dose to pathogen
Duty of Operator/Engineer: To ensure the disinfection process provides adequate CT (delivered dose) for pathogen inactivation.
CT values are lookup in EPA CT tables (temperature, pH, residual) to determine log inactivation of selected pathogen.

## Slide 27: CT – Delivered Disinfection Dose
The disinfection residual “C” is measured before the first water customer via grab sampling or online monitoring.
More complicated parameter to quantify is the disinfection exposure time “T”.

## Slide 28: Water Age Distribution – Leaving Clearwell

## Slide 29: Age of Water in a Clearwell (Reactor)
The volume of water entering the vessel can be broken down into fluid elements.
Each of those fluid elements can have different flow paths through the reactor.
Depending on the reactor design, water temperature and mixing energy, some fluid elements can take the shortest flow path from the inlet to outlet while other elements take longer routes.

## Slide 30: What Percent of Water Age is Used?
Environmental Protection Agency (EPA) decided that the time it takes for the first 10% of the total fluid elements entering the vessel to exit the vessel will be used as the disinfection compliant exposure time.
This value is called the T10 value that has units of minutes.
The rest of water elements (90%) will have a water age greater than T10.

## Slide 31: T10 is Determined via Tracer Study
The disinfectant exposure time at T10 is determined by conducting a tracer study.
A non-reactive tracer is added to the water in the same vicinity where the disinfectant is applied.
You may think of each fluid element tagged with a measurable non-decaying tracer marker.
As the fluid elements exits the reactor vessel, the markers are measured.

## Slide 32: Baffling Factor (BF) Determined from Tracer Study or Estimated
Baffling factor or short-circuiting factor:
  BF = T10/ HRT
    where HRT: Operating Volume divided by Flow leaving reactor
Once BF is determined, it’s applied to the operations of the reactor for determining the disinfectant exposure time (T10).
Example:
  Clearwell operating volume: 100,000 gallons
  Exit flow: 600 gpm
  HRT: 100,000 gal/600 gpm = 167 minutes
  BF: 0.3 (from tracer study or assigned by State)
  Calculated disinfection exposure time:
  T10 = HRT x BF = 167 minutes × 0.3 = 50 minutes

## Slide 33: Log Inactivation from CT
Once T10 value is determined from a tracer study, “baffling factor (BF)” is calculated and applied to the daily operations of the disinfection CT reactor tank.
Daily CT values are looked up into EPA CT tables to determine log inactivation for selected pathogen.
If Clearwell chlorine residual is 1.2 mg/L and T10 is 50 minutes
CT10: 1.2 mg/L x 50 min = 60 mg/L * min (lookup in EPA CT tables)

## Slide 34: Contact and Links
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Jar Test Results/Chemical Dosages/Stock Solution for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732