## Slide 1: City of Fairfield Solano County, CA Contact Time (t10) Tracer Study May 8, 2017
by Guy Schott, P.E.
Amy Little, P.E.
Water Resources Control Board,
Division of Drinking Water
Guy.schott@waterboards.ca.gov
707-576-2732

## Slide 2
Chlorine Contact Basin - Clearwell
Pipeline volume: 9,400 gallons (100-ft linear, 4-Diam.)
Influent weir & channel volume: 8,528 gallons
Clearwell basin volume/ft: 10,800 gal/ft
Total working volume during tracer study: 206,960 gallons

## Slide 3: Final Results
Test Date: May 8, 2017
Test by: Water Resources Control Board, Division of Drinking Water
Tracer Test Method: Step-Dose using Fluoride
Clearwell Flow (inlet/outlet): 11 MGD (7,639 gpm)
Clearwell Operating Water Level: 17.5 feet
Operating Volume (Pipe, Weir, Clearwell): 206,960 gallons
HRT: 27.1 minutes
t10: 8.6 minutes
Baffling Factor: 0.32 (t10/HRT)

## Slide 4: Tracer Study – Overview 1
A tracer study was conducted at the City of Fairfield, Public Works Waterman WTP to determine the “t10” disinfection contact time and baffling factor for the combined pipeline, influent weir and concrete-squared clearwell. The “t10” is the time is takes for 10% of the added tracer mass to exit the reactor. The baffling factor is t10/HRT where HRT is the hydraulic residence time of the clearwell during the time of the tracer study.

## Slide 5: Tracer Study – Overview 2
Tracer Method: Step-Dose
Injection Point: Combined Filter Effluent (CFE) 4-ft Dia. pipeline to weir channel
Sample Points: Influence weir channel and discharge side of clearwell from 4-ft Dia. pipeline
Tracer Analysis: Ion Selective Fluoride Probe
Sampler: Amy Little
Analysis by: Guy Schott

## Slide 6: Tracer Material Overview
Tracer Material: Hydrofluorosillicic Acid (H2SiF6)
Tracer Bulk Density: 10.13 lbs/gal
Tracer Product Strength: 24.07% as H2SiF6
Molecular Weight: 144.09 g/mole (H2SiF6)
Fluoride Concentration: 79.11% (144 g/mole)
H2SiF6 Tracer Feed Rate: ~425 mL/min
Flow: 11 MGD (7,639 gpm)
Tracer Dose: 4.03 mg/L as F
Method of Injection: Steady-State.

## Slide 7: Tracer Field Results
Flow – 11 MGD (7,639 gpm); 210,000 gallon Clearwell
HRT: 27.1 minutes
Tracer Dose– 4.03 mg/L as F
t10: 8.6 minutes
Total working volume: 206,960 gallons @ 17.5 ft operating level
Calculated baffling factor: 0.32 t10/HRT

## Slide 8
Working Volume: 206,960 gallons
Average Flow: 11 MGD (7,639 gpm)
Clearwell Water Level: 17.5 ft
HRT: 27.1 minutes
t10: 8.6 minutes
Baffling factor 0.32 (t10/HRT)

## Slide 9
Clearwell and Effluent Pumps
270,000 gallon (max) clearwell - underground

## Slide 10
Injection Points before Clearwell
Fluoride
Caustic
NaOCl