## Slide 1: Garberville Sanitary District CA1210008 Tracer Study October 30-31, 2018
Tracer Study:
Reactor: Pressure Vessel
Volume: 20,000 Gallons
Diameter: 10 ft
Length: 36 ft
Baffled Tank (over/under)
Inlet/Outlet Full Perforated Baffles
Performed by:
Guy Schott, P.E.
CA Division of Drinking Water

## Slide 2: Table of Content
Summary of Tracer Results
Reactor Design
Tracer Sample Locations
Graph 1: Slug-Dose Curve
Graph 2: Normalized Slug-Dose Curve to F-Curve
Graph 3: Modified Step-Dose Curve
Graph 4: Normalized Modified Step-Dose Curve to F-Curve
Purpose of a Tracer Test
Disinfection Exposure Time of Fluid in Vessel for Determining Ct10
Ct10 Value
Baffling Factor (BF)
Tracer Test Methods
Method of Analysis and Equipment

## Slide 3: Garberville SD Tracer Test Results
Slug-Dose Method
Test Date: 9/30/18
*Baffling Factor (t10/HRT): 0.45
Modal Baffling Factor (tmod/HRT): 0.67
t50/HRT: 0.84
Morril Index, t90/t10: 3.37
Average Flow: 210 gpm
HRT: 95 minutes
t10: 43 minutes
t50: 80 minutes
t90: 145 minutes
Tracer Added: Fluoride (126.5 grams)
Tracer Recovered: Fluoride (120.3 grams)
Sample Frequency Outlet:
  0 – 10 min (5 min)
  10 – 130 min (2 min)
  130 – 160 min (3 min)
  160 – 210 min (5 min)
  210 – 330 min (10 min)
Modified Step-Dose
Test Date: 9/31/18
Baffling Factor (t10/HRT): 0.49
Average Flow: 213 gpm
HRT: 94 minutes
t10: 46.5 minutes
Tracer: Fluoride (2.72 mg/L)
Sample Frequency Inlet:
  5 gallon bucket (fill duration 3-5 min)
  8 samples (10 – 59 min range)
Sample Frequency Outlet:
  0 – 10 min (5 min)
  10 – 6 min (2 min)
  36 – 52 min (1 min)
HRT: Hydraulic Residence Time (reactor volume/flow)
*Note: Calculations are based on tracer mass recovery.

## Slide 4
Horizontal Pressure Clearwell Design

## Slide 5: Tracer Sample Locations
Inlet
Outlet

## Slide 6: Garberville SD – Slug-Dose Curve
Chart: Slug-Dose Curve
Baffling Factor = 0.45
t10: 43 min
HRT: 95 min

## Slide 7: Garberville SD – Slug-Dose Curve Normalized to F-Curve
Chart: Slug-Dose Normalized to F-Curve
Baffling Factor = 0.45

## Slide 8: Garberville SD – Modified Step-Dose Curve
Chart: Modified Step-Dose Curve
| 0 | 4 | 9 | 11 | 13 | 15 | 17 | 19 | 21 | 23 | 25 | 27 | 29 | 31 | 33 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51
 | 0 | 0 | 0 | 0.0032 | 0.0022 | 0.0011 | 0.0026 | 0.0013 | 0.0013 | 0.0073 | 0.017 | 0.024 | 0.034 | 0.045 | 0.068 | 0.087 | 0.096 | 0.124 | 0.13 | 0.147 | 0.157 | 0.166 | 0.184 | 0.193 | 0.216 | 0.245 | 0.259 | 0.285 | 0.3 | 0.323 | 0.341 | 0.366
t10: 46.5 min
HRT: 94 min
t10/HRT = 0.49
Dosage: 2.72 mg/L
0.27 mg/L at t10

## Slide 9: Garberville SD – Modified Step-Dose Curve Normalized to F-Curve
Chart: Normalized F-Curve
| 0 | 4.2519999999999995E-2 | 9.5670000000000005E-2 | 0.11692999999999999 | 0.13818999999999998 | 0.15944999999999998 | 0.18070999999999995 | 0.20196999999999996 | 0.22322999999999996 | 0.24448999999999996 | 0.26574999999999993 | 0.28700999999999993 | 0.30826999999999993 | 0.32952999999999993 | 0.35078999999999988 | 0.37204999999999988 | 0.38267999999999991 | 0.39330999999999994 | 0.40393999999999997 | 0.41456999999999999 | 0.42519999999999997 | 0.43583000000000005 | 0.44646000000000002 | 0.45709000000000005 | 0.46772000000000002 | 0.47835000000000011 | 0.48898000000000014 | 0.49961000000000011 | 0.51024000000000014 | 0.52087000000000017 | 0.53150000000000019 | 0.54213000000000022
 | 0 | 0 | 0 | 0.0011765 | 0.00080882 | 0.00040441 | 0.00095588 | 0.00047794 | 0.00047794 | 0.0026838 | 0.00625 | 0.0088235 | 0.0125 | 0.016544 | 0.025 | 0.031985 | 0.035294 | 0.045588 | 0.047794 | 0.054044 | 0.057721 | 0.061029 | 0.067647 | 0.070956 | 0.079412 | 0.090074 | 0.095221 | 0.10478 | 0.11029 | 0.11875 | 0.12537 | 0.13456
Baffling Factor = 0.49

## Slide 10: Purpose a Tracer Study?
To determine the hydraulic efficiency or disinfectant exposure time of water through one or more reactors.
The addition of known quantities of a nonreactive chemical (tracer) is added in the form of a pulse (slug) or step-input.
The time of travel or disinfectant exposure time through the reactor is related to:
  Flow rate
  Reactor water volume
  Water Depth
  Reactor configuration

## Slide 11: Disinfection Exposure Time of Fluid in Vessel for Determining Ct10
“C” is the disinfectant residual (mg/L) at the point of inactivation compliance.
The disinfection exposure time of water used for Ct10 calculation is the time (t10) it takes for 10 percent of the water entering the reactor to exit the reactor.
To determine this, a marker (nonreactive tracer) is introduced into the water and is monitored leaving the reactor.
Example: 1.0 Kg of tracer is slug-dose; t10 is that time when 0.1 Kg of tracer material (10%) has exit the reactor.

## Slide 12: Ct10 Value
- Log inactivation is based on the Delivered Dose, “Ct10”
  “C” is the disinfectant residual (mg/L)
  “t10” is the exposure or contact time (minutes)
  Multiply them:
C • t10 = mg/L • min (delivered dose)
The calculated Ct10 value is looked up in EPA Ct tables to determine the log inactivation based on specific monitoring parameters (pH, disinfectant residual and/or temperature).

## Slide 13: Baffling Factor (BF)
Baffling factor or short-circuiting factor:
  Determined from tracer study or estimated
  BF = t10/ HRT from tracer study
  HRT (hydraulic residence time) = reactor volume divided by reactor flow
Once the BF is determined, then it is applied to the operations of the reactor for determining the disinfectant exposure time.
Example:
  Clearwell operating volume: 20,000 gallons
  Exit flow: 200 gpm
  BF: 0.44, from tracer study
  Calculated contact or disinfection exposure time:
    20,000 gal ÷ 200 gpm × 0.44 = 44 minutes = t10

## Slide 14: Test Methods
Slug-Dose or Pulse-Input Method
Adding the entire amount of tracer at the beginning of test. The reactor outlet tracer concentration is monitored for 3-4 HRT to determine mass recovery and the time (t10) it takes for 10% of the tracer mass to exit the reactor.
Modified Step-Dose Method
It is a continue feed of tracer at constant rate and plant flow throughout the duration of the test. The “Step-Dose” test is run to 3-4 HRT to achieve reactor outlet steady-state tracer concentration. The time “t10” is determined when 10% of the tracer dose concentration has exist the reactor. The “Modified Step-Dose” test allows the test to be completed in less than 1 HRT by physical measurements of the tracer inlet flow concentration to verify dosage.

## Slide 15: Method of Analysis and Equipment
Intellical™ ISEF121 Fluoride (F-) Ion Selective Electrode (ISE)
HQ40d Portable ISE Multi-Parameter Meter
Fluoride Ionic Strength Adjustor (ISA)
Fluoride Standards (0.2/2.0 & 0.5/ 5.0 mg/L)
50 mL graduated cylinder
Finnpipette F2 variable volume pipette, capacity 0.5 - 5 mL
Electrode stirrer stand
50 mL beakers
Stir Bar, Magnetic, Polygon

## Slide 16: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Guy.Schott@waterboards.ca.gov
707-576-2732