## Slide 1: Graton Community Services District SN 4990011 Wastewater Treatment Plant Sonoma County, CA Modal Contact Time (Tmod) Tracer Study #1 May 30, 2018
by Guy Schott, P.E.
Water Resources Control Board,
Division of Drinking Water
Guy.schott@waterboards.ca.gov
707-576-2732
Revised on July 30, 2018; basin volume.

## Slide 2
Chlorine Contact Reactors in Series
Graton Community Services District
250 Ross Ln, Sebastopol, CA 95472
707-823-1542
Revised Contact Rectangular Basin from 10,800 to 12,000 gallons

## Slide 3: Final Results
Test Date: May 30, 2018
Test by: GCSD & WRCB, Division of Drinking Water
Tracer Test Method: Slug-Dose using Fluoride
Reactors Tested: Purge Tank, pipeline & Serpentine Contact Basin (in series)
Total Operating Volume: 15,080 gallons
Operational Flow: 120 gpm (steady-state)
HRT: 126 minutes (hydraulic residence time)
Tmod: 112 minutes (Modal Contact Time)
Modal Baffling Factor: 0.89 (Tmod/HRT)

## Slide 4: Operating Parameters Based on Tracer Test

## Slide 5: Tracer Study – Overview 1
On May 30, 2018 a single tracer study was conducted at the Graton CSD WWTP. This test was to evaluate the modal contact time for the 3,000 gallon purge tank and 12,000 gallon serpentine concrete basin operated in series including pipe volume between the two reactors. The modal contact value (Tmod) is that time at which the slug-dose curve is at its peak concentration.
The modal contact time was 112 minutes.
The HRT was 126 minutes.

## Slide 6: Tracer Study – Overview 2
Tracer Method: Slug-Dose
Injection Point of Tracer: Pipeline to Purge Tank
Sample Point: Overflow weir at end of serpentine contact basin.
Tracer Analysis: Ion Selective Fluoride Probe
Sampler: Graton CSD Operators
Analyses by: Guy Schott, Division of Drinking Water

## Slide 7: Tracer Material Overview
Tracer Material: Hydrofluorosillicic Acid (H2SiF6)
Tracer Bulk Density: 10.3 lbs/gal
Tracer Product Strength: 24% as H2SiF6
Molecular Weight: 144.09 g/mole (H2SiF6)
Fluoride Concentration: 79.11% (144 g/mole)
H2SiF6 Tracer Added: 406 mL (neat)
Fluoride (F) Tracer Added: 94 grams
Method of Injection: Slug-Dose (< 20 sec)

## Slide 8
3,000 Gal Purge Tank
Tracer Injection Point
Inlet
Outlet
Inlet
Tracer
to 12,000 gallon chlorine contact basin

## Slide 9: 12,000 Gal Contact Basin
Sample

## Slide 10: Tracer Field Results