## Slide 1: Howell Mountain Mutual Water Napa County, CA PAX Clearwell Mixer Tracer Studies, July, Sept, Oct 2015
by Guy Schott, P.E.
Guy.schott@waterboards.ca.gov
707-576-2732

## Slide 2: Clearwell – 488,000 Gal Max Capacity
Figure 1:
Test 1 – 4 (July 2015)
PAX location 1

## Slide 3: Clearwell – 488,000 Gal Max Capacity
Figure 2:
Test 5 – 6 (Sept-Oct 2015)
PAX location 2

## Slide 4: Tracer Test Overview for 488,000 Gal Max Capacity Clearwell
PAX Mixer ON |  | PAX Mixer ON | 
Figure 1 PAX Location |  | Figure 2 PAX Location | 
Inlet Configuration | Baffling Factor | Inlet Configuration | Baffling Factor
Bottom to Bottom | 0.033 | Bottom to Bottom | 0.058
Top to Bottom | 0.063 | Top to Bottom | 0.084
PAX Mixer Off |  | PAX Mixer Off | 
Inlet Configuration | Baffling Factor | Inlet Configuration | Baffling Factor
Bottom to Bottom | 0.049 | Top to Bottom | 0.091
Clearwell: No baffles
Inlet flow: 250-280 gpm
Outlet flow varied: 114-142 gpm
Clearwell Level: 19 – 23.2 ft
Clearwell Operating Volume: 325,500 – 397,500 gal
Tracer Test Type: Modified Step-Dose/Volume10 (V10) combination methods

## Slide 5: Test 1 & 2 Figure 1 for PAX location in Clearwell
PAX Mixer ON |  | PAX Mixer Off | 
Test 1: Bottom to Bottom (inlet/outlet) July 7, 2015 |  | Test 2: Bottom to Bottom (inlet/outlet) July 14, 2015 | 
Baffling factor (t10/T) | 0.033 | Baffling factor (t10/T) | 0.049
Avg tank level | 22.2 ft | Avg tank level | 23.2 ft
Avg tank volume | 379,000 gal | Avg tank volume | 401,000 gal
Inlet Flow | 255 gpm | Inlet Flow | 250 gpm
Avg outlet flow | 139 gpm | Avg outlet flow | 114 gpm
Hydraulic Retention Time | 2,727 min | Hydraulic Retention Time | 3,518 min
*Accumulated exit volume | 12,500 gal | *Accumulated exit volume | 19,500 gal
*Accumulated exit volume is the total volume that exit the Clearwell when 10% of tracer mass has exited the Clearwell.
Clearwell: 17,132 Gal/ft (Diameter: 54-ft)

## Slide 6
Baffling factor: 0.033 t10/T
Accumulated exit volume: 12,500 gallons at 10% of tracer mass
Average operating volume: 379,000 gallons
Inlet/Outlet Configuration: Bottom to Bottom

## Slide 7
Baffling factor: 0.049 t10/T
Accumulated exit volume: 19,500 gallons at 10% of tracer mass
Average operating volume: 401,000 gallons
Inlet/Outlet Configuration: Bottom to Bottom

## Slide 8: Test 3 & 4 Figure 1 for PAX location in Clearwell
PAX Mixer ON |  | PAX Mixer Off | 
Test 3: Top to Bottom (inlet/outlet) July 23, 2015 |  | Test 4: Top to Bottom (inlet/outlet) July 28, 2015 | 
Baffling factor (t10/T) | 0.063 | Baffling factor (t10/T) | 0.091
Avg tank level | 19.0 ft | Avg tank level | 21.6 ft
Avg tank volume | 321,000 gal | Avg tank volume | 370,500 gal
Inlet Flow | 255 gpm | Inlet Flow | 260 gpm
Avg outlet flow | 131 gpm | Avg outlet flow | 142 gpm
Hydraulic Retention Time | 2,360 min | Hydraulic Retention Time | 2,609 min
*Accumulated exit volume | 20,200 gal | *Accumulated exit volume | 33,800 gal
*Accumulated exit volume is the total volume that exit the Clearwell when 10% of tracer mass has exited the Clearwell.
Clearwell: 17,132 Gal/ft (Diameter: 54-ft)

## Slide 9
Baffling factor: 0.063 t10/T
Accumulated exit volume: 20,200 gallons at 10% of tracer mass
Average operating volume: 321,000 gallons
Inlet/Outlet Configuration: Top to Bottom

## Slide 10
Baffling factor: 0.091 t10/T
Accumulated exit volume: 33,800 gallons at 10% of tracer mass
Average operating volume: 370,500 gallons
Inlet/Outlet Configuration: Top to Bottom

## Slide 11: Test 5 & 6 Figure 2 for PAX location in Clearwell
PAX Mixer ON |  | PAX Mixer ON | 
Test 5: Top to Bottom (inlet/outlet) September 29, 2015 |  | Test 6: Bottom to Bottom (inlet/outlet) October 13, 2015 | 
Baffling factor (t10/T) | 0.084 | Baffling factor (t10/T) | 0.058
Avg tank level | 21.0 ft | Avg tank level | 23.1 ft
Avg tank volume | 360,700 gal | Avg tank volume | 395,600 gal
Inlet Flow | 259 gpm | Inlet Flow | 280 gpm
Avg outlet flow | 138 gpm | Avg outlet flow | 115 gpm
Hydraulic Retention Time | 2,610 min | Hydraulic Retention Time | 3,440 min
*Accumulated exit volume | 30,230 gal | *Accumulated exit volume | 23,000 gal
*Accumulated exit volume is the total volume that exit the Clearwell when 10% of tracer mass has exited the Clearwell.
Clearwell: 17,132 Gal/ft (Diameter: 54-ft)

## Slide 12
Baffling factor: 0.084 t10/T
Accumulated exit volume: 30,230 gallons at 10% of tracer mass
Average operating volume: 360,700 gallons
Inlet/Outlet Configuration: Top to Bottom

## Slide 13
Baffling factor: 0.058 t10/T
Accumulated exit volume: 23,000 gallons at 10% of tracer mass
Average operating volume: 395,600 gallons
Inlet/Outlet Configuration: Bottom to Bottom

## Slide 14
488,000 Gal Clearwell
Inlet (bottom or Top)
Outlet (bottom)

## Slide 15
Outlet (bottom)

## Slide 16
Inlet (bottom or top)

## Slide 17
Inlet (Top)
Deflector Plate

## Slide 18
Inlet (Top)

## Slide 19
Fluoride Injection System

## Slide 20
Fluoride Dosage Sampling Point

## Slide 21
Fluoride sampling point
(after clearwell)

## Slide 22
SCADA Info on Plant and Distribution Flows

## Slide 23
Fluoride Analysis

## Slide 24
Fluoride Analysis

## Slide 25
Modified
Step-Dose Method
Similar to Step-Dose Test
Differences:
  Shorter test duration: tracer is discontinued when >10% of mass has exit reactor (< Theoretical Detention Time)
  Allows for higher dosage (i.e., 4 to 10 mg/L of F-)
  Ion selective probes response better and faster at higher salt concentration (i.e. 10% of dosage)
Test Application – suitable for long test duration or when operating conditions up to 3Ƭ is impractical.
Presented at the CA-NV AWWA Oct 25, 2007

## Slide 26
Volume10 (V10)
Method
V10: Is the recorded total volume of water that has exited the reactor from to to t10 when 10% of the tracer mass has exited the reactor.
For non-steady-state flows