## Slide 1: Title
March 23-24, 2021

## Slide 2: JAR TESTING MADE EASY CA-NV AWWA OPERATOR SYMPOSIUM
by Guy Schott, P.E.
March 24, 2021

## Slide 3: Presentation Overview
Topics
Jar Testing – Application, Research & Assistance
Jar Testing Equipment/Tools
Filterability, UVT/UVA & Settleability Analysis
Jar Test Protocol
Laboratory Charged Analyzer (LCA)
Case Studies
Coagulant Overdosing
Coagulant Under Dosing
Performance with/without Acid
With/without Pre-Oxidation (Ozone/NaOCl/KMnO4)
Pre-cursor Reduction Optimization (TTHM/HAA5)
Filtrate Chlorine Decay Rate

## Slide 4: Settleability - don’t use as the sole source of data to determine optimum coagulant/dose
Why?
No supporting data on floc strength and filterability
No supporting data on indirect DOC reduction (UVA surrogate)
Not all treatment plants have settling
Likely Outcome - underdosing coagulant and DBP issues
Settleability only provides data on floc size and settling performance as it relates to flocculation duration

## Slide 5: Jar Testing – What’s Important
Timely, Efficient & Straightforward - (don’t make is complicated)
Completed within 1 hour (prep, testing and analysis)
One set of procedures, methods and analysis that can be applied to most treatment plants
Results that clearly depict which Coagulant(s) and dose that provides optimum
Filterability (NTU, floc strength)
Indirect dissolved organic carbon reduction (UVT/UVA suragate)
Settleability (NTU)
Confidence in your jar testing data that is transferable to plant operations

## Slide 6: New Jar Testing Procedures & Analysis Application/Research/Assistance (2018-2021)
16 Counties (California)
45 Public Surface Water Treatment Plants
Plant Size from 30 gpm – 50 MGD
>2,000 Jars
Training

## Slide 7: Applied Jar Test Procedures, Methods & Analysis for Various Treatment Plants
(22) Conventional Treatment Plants
with
Media Filtration &
Membrane Filtration
(3) Direct Filtration Plants
with
Media Filtration &
Membrane Filtration
(2) Dissolved Air Flotation (DAF) with
Media Filtration &
Membrane Filtration
(8) Trident & Roberts
Absorption/Contact
Media Filtration
(2) Actiflo
(ballast sand)
with
Media Filtration
(8) Alternative Technologies Roughing Contact Clarifier/Media Filtration &
Inline Filtration

## Slide 8: Lab

## Slide 9: Filterability Analysis - New
Developed technique and analysis for predicting full-scale media filtration
Material Requires:
  30 mL Syringe w/Luer-Lock Tip
  Filter holder
  1.2 um absolute Isopore membrane filter
Samples collected at end of flocculation period to assess floc strength
Filtration and Analysis: 4 minutes per Jar to complete and record

## Slide 10: Filterability Sensitivity Performance – Plant ID: COB (4 min/Jar)
Jar# | Primary Coagulant mg/L | CatFloc mg/L | Filtrate NTU | Floc Strength
J1 | 46 | 0 | 0.13 | Fair
J2 | 46 | 0 | 0.12 | Fair
J3 | 46 | 0.5 | 0.12 | Fair
J4 | 46 | 1.0 | 0.11 | Fair
J5 | 46 | 1.5 | 0.08 | Good
J6 | 46 | 1.5 | 0.08 | Good
J7 | 46 | 2.0 | 0.06 | Strong
J8 | 46 | 2.0 | 0.05 | Strong

## Slide 11: Filterability Sensitivity Performance – Plant ID: HRCSD (4 min/Jar)
Jar# | Primary Coagulant mg/L | CatFloc mg/L | Filtrate NTU | Floc Strength
J1 | 35 | 0 | 1.06 | Very Weak
J2 | 45 | 0 | 0.66 | Very Weak
J3 | 50 | 0 | 0.28 | Weak
J4 | 55 | 0 | 0.27 | Weak
J5 | 35 | 6.0 | 0.08 | Good
J6 | 45 | 6.0 | 0.05 | Strong
J7 | 50 | 6.0 | 0.04 | Strong
J8 | 55 | 6.0 | 0.05 | Strong

## Slide 12: UVT/UVA Instrument, pathlength 10 or 40 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (254 nm) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 13: UV-Absorption Analysis
Surrogate for predicting indirect DOC reduction
Compares different jar testing coagulants and doses for best indirect DOC reduction
Systems with DPB issues, UVA measures are critical for determining optimum coagulant and dose
UVA measurements:
  Source (0.4 um Isopore filter)
  Filtrate water from each tested jar (1.2 um Isopore filter)
UVA Analysis: 1 minutes per Jar to complete and record

## Slide 14: Chart – Indirect DOC Reduction
Chart: Indirect DOC Reduction (Source to Treated)
| 0 | 1.8181818181818198E-2 | 3.6363636363636397E-2 | 5.4545454545454591E-2 | 7.2727272727272793E-2 | 9.090909090909087E-2 | 0.10909090909090906 | 0.12727272727272726 | 0.14545454545454545 | 0.16363636363636366 | 0.18181818181818185 | 0.20000000000000004 | 0.21818181818181825 | 0.23636363636363633 | 0.25454545454545452 | 0.27272727272727271 | 0.29090909090909089 | 0.30909090909090914 | 0.32727272727272733 | 0.34545454545454551 | 0.36363636363636359 | 0.38181818181818178 | 0.39999999999999997 | 0.41818181818181815 | 0.4363636363636364 | 0.45454545454545459 | 0.47272727272727272 | 0.49090909090909091 | 0.50909090909090915 | 0.52727272727272823 | 0.54545454545454641 | 0.5636363636363646 | 0.58181818181818268 | 0.60000000000000087 | 0.61818181818181905 | 0.63636363636363735 | 0.65454545454545543 | 0.67272727272727362 | 0.69090909090909181 | 0.70909090909090999 | 0.72727272727272818 | 0.74545454545454637 | 0.76363636363636456 | 0.78181818181818274 | 0.80000000000000093 | 0.81818181818181912
 | 0.11 | 0.108 | 0.106 | 0.104 | 0.102 | 0.1 | 0.098 | 0.096 | 0.094 | 0.092 | 0.09 | 0.088 | 0.086 | 0.084 | 0.082 | 0.08 | 0.078 | 0.076 | 0.074 | 0.072 | 0.07 | 0.068 | 0.066 | 0.064 | 0.062 | 0.06 | 0.058 | 0.056 | 0.054 | 0.052 | 0.05 | 0.048 | 0.046 | 0.044 | 0.042 | 0.04 | 0.038 | 0.036 | 0.034 | 0.032 | 0.03 | 0.028 | 0.026 | 0.024 | 0.022 | 0.02

## Slide 15: Settleability Analysis
Analysis conducted for plants with settling
Relative performance measurements between each jar based on coagulant type, dose and flocculation duration
Samples collected 25 minutes from the end of the flocculation period
Settleability Analysis: 1 minutes per Jar to sample, complete and record

## Slide 16: Jar Testing Procedures and Analysis
1. Flash Mix 200 RPM (20-30 sec) | 2. Flocculation 20-30 RPM (5 min) | 3. Filterability & Filtrate %UVT/UVA Analysis | 4. Settleability Analysis
Pipette coagulant into each jar. | Floc for 5 minutes. Lift paddles and lock. | Sample at end of flocculation period for plants without settling. Wait 5 minutes for plants with settling. | After 25 minutes of settling, measure settled water turbidity.

## Slide 17: Jar Testing for a Four-Jar Mixer
35 minutes to complete jar testing and analysis
5 ½ minutes of jar testing (20-30 sec, 200 RPM; 5 min, 20-30 RPM)
5-minute wait before 25 mL of water is drawn from each jar
20 minutes Analysis:
  Filtrate Turbidity
  Filtrate %UVT/UVA
  %UVA Reduction (source to treated, calc.)
4 minutes: Settled Water sampled from each jar and turbidity measurements

## Slide 18: Jars 1-4: End of 5-minute flocculation (30 RPM) duration

## Slide 19: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 20: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
60 mg/L coagulant
Filtrate 0.18 NTU
UVT: 91.4%
UVA: 0.039/cm
UVA Reduction: 75.9%
Settled: 0.84 NTU
70 mg/L coagulant
Filtrate 0.14 NTU
UVT: 92.9%
UVA: 0.032/cm
UVA Reduction: 80.2%
Settled: 0.42 NTU
80 mg/L coagulant
Filtrate 0.07 NTU
UVT: 94.1%
UVA: 0.026/cm
UVA Reduction: 84.0%
Settled: 0.32 NTU
90 mg/L coagulant
Filtrate 0.06 NTU
UVT: 94.7%
UVA: 0.024/cm
UVA Reduction: 87.7%
Settled: 0.37 NTU

## Slide 21: Filterability (25 mL syringed)

## Slide 22: Filterability and UVT/UVA Analysis
Flocculated water is pushed through a 1.2 um absolute Isopore membrane (drip-rate) and measured for turbidity.
Water from cuvette is transferred to UVT/UVA cuvette for measurements.

## Slide 23: Settleability Test

## Slide 24: Jar Test - Flash and Flocculation RPM & Durations
20-30 sec
Flash Mix
(200 RPM)
5 minutes
Floc Mix
(20-30 RPM)

## Slide 25: Impact of Flash Mixing – Jar Testing
Inadequate flash mixing can
  negatively impact settleability performance
  May affect filterability in some cases (site specific)
  No affect on indirect DOC reduction
Jar testing: 20-30 seconds (200 RPM) is adequate for dispersing coagulant

## Slide 26: Flash Mix Duration (0 – 60 seconds)
Plant ID | 200 RPM Flash, sec | 30 RPM Floc mix min | Coag mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settled NTU 25 min
SW | 0 | 5 | 54 | 0.09 | 95.4 | 0.020 | 0.90
SW | 30 | 5 | 54 | 0.08 | 95.8 | 0.019 | 0.53
CW | 0 | 5 | 18 | 0.06 | 89.4 | 0.049 | 0.28
CW | 15 | 5 | 18 | 0.06 | 89.2 | 0.050 | 0.34
CW | 30 | 5 | 18 | 0.07 | 89.3 | 0.049 | 0.36
CW | 60 | 5 | 18 | 0.07 | 89.2 | 0.050 | 0.26
GTD | 0 | 5 | 1.5 | 0.11 | 97.8 | 0.010 | 1.8
GTD | 60 | 5 | 1.5 | 0.08 | 97.2 | 0.012 | 1.4
SC41 | 0 | 5 | 8.0 | 0.13 | 96.8 | 0.014 | 7.0
SC41 | 60 | 5 | 8.0 | 0.10 | 96.6 | 0.015 | 4.8

## Slide 27: Impact of Flocculation Duration
Flocculation duration only impacts settleability performance
Filterability and Indirect DOC reduction are not affected by flocculation duration
Jar testing: 5 minutes (20 - 30 RPM) is adequate for floc formation

## Slide 28: Variable Flocculation Duration (3 – 40 minutes)
Plant ID | 200 RPM Flash, sec | RPM Floc Speed | Floc Mix min | Coag/ Aid mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settled NTU 25 min
COC | 30 | 30 | 3 | 38/37 | 0.06 | 94.5 | 0.024 | 1.87
COC | 30 | 30 | 5 | 38/37 | 0.07 | 94.3 | 0.025 | 1.07
COC | 30 | 30 | 10 | 38/37 | 0.06 | 94.4 | 0.024 | 0.82
COC | 30 | 30 | 15 | 38/37 | 0.09 | 94.3 | 0.025 | 0.39
GS | 30 | 30 | 5 | 29/2.9 | 0.08 | 91.7 | 0.038 | 0.38
GS | 30 | 30 | 10 | 29/2.9 | 0.09 | 91.8 | 0.037 | 0.22
GS | 30 | 30 | 20 | 29/2.9 | 0.08 | 91.8 | 0.037 | 0.30
CLO | 60 | 30 | 5 | 23 | 0.08 | 94.8 | 0.023 | 0.48
CLO | 60 | 30 | 10 | 23 | 0.07 | 94.5 | 0.025 | 0.39
CLO | 60 | 30 | 20 | 23 | 0.07 | 94.9 | 0.023 | 0.30
CLO | 60 | 30 | 40 | 23 | 0.07 | 94.9 | 0.023 | 0.36

## Slide 29: Seasonal Shift in Primary Source Water
Uneventful
Algal Bloom
(Microcystin)
Rain
Event
Algal Bloom (Lyngbya)

## Slide 30: Laboratory Charge Analyzer
Used to determine coagulant demand of a source water entering the treatment plant.
1 Liter of source water
Automatic titrates coagulant to charge neutralization
Tool used for determining starting coagulant dose range for jar testing

## Slide 31: Table of LCA coagulant vs. Jar Test Coagulant
Plant ID | LCA Coagulant mg/L | Best Jar Coagulant mg/L | Plant ID | LCA Coagulants mg/L | Best Jar Coagulants mg/L
MK | 27 | 35 | LP | 90 | 90
BHP | 31 | 32.5 | SW | 54 | 54
KCW | 38 | 38 | NMW | 31.8 | 30
HMW | 23.2 | 28 | GS | 28 | 26/2.6
CLO | 31.9 | 35 | CW | 19 | 23
VH | 15 | 16 | CF | 76/5 | 76/5
HV | 29 | 29 | LP | 90 | 90
CW | 19 | 23 | RV | 14 | 14
KC | 35 | 35 | HM | 18.8 | 23
GSD | 12.3 | 12 | SFG | 38.4/4 | 40/4
GTD | 1.6 | 1.5 | PV | 25 | 30
FSP | 8.7 | 9.0 | KsC | 14.5 | 14.5
HH | 101 | 105 | SH | 32 | 34
COC | 36 | 36 | AC | 192 | 190
MID | 9.45 | 9.5 | SC41 | 7.5 | 8.0

## Slide 32: Jar Test Cases
Coagulant Overdosing
Coagulant Under Dosing
With/without Pre-Oxidation (NaOCl/Ozone/KMnO4)
With/without Acid
Pre-cursor Reduction Optimization (TTHM/HAA5)
Filtrate Chlorine Decay Rate

## Slide 33: Case 1. Coagulant Overdosing – Storm Event
Source turbidity: 126 NTU, storm event
50% of plant off-line for filter media change out
Plant settled water turbidity > 11 NTU
Filter backwashing once per hour
Plant filtrate turbidity: 0.27 NTU
Operator overwhelmed/not enough sleep
Operator doubles coagulant dose: 110 mg/L

## Slide 34: Case 1. Jar Test Results vs Plant (coagulant overdosing, 110 mg/L)
Jar # | Coagulant mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settled NTU
J1 | 45 | 0.50 | 89.3 | 0.049 | 2.2
J2 | 55 | 0.35 | 90.7 | 0.042 | 1.9
J3 | 65 | 0.18 | 91.6 | 0.038 | 2.4
J4 | 75 | 0.05 | 91.7 | 0.039 | 2.8
J5 | 85 | 0.14 | 91.4 | 0.039 | 3.2
J6 | 110 | 0.20 | 92.6 | 0.033 | 7.0

## Slide 35: Case 1. Jar Test Results versus Adjusted Plant Coagulant Dose
Jar Test Results
Coagulant Dose: 75 mg/L
Filtrate: 0.05 NTU
Settled: 2.8 NTU
Plant Results
Coagulant Dose: 75 mg/L
Filtrate: 0.05 NTU
Settled: 2.0 NTU
Filter Run time (increased from 1 to 6 hrs.)

## Slide 36: Case 2. Coagulant Under dosing
Source turbidity: 7.8 NTU
Plant settled water turbidity ~ 1 NTU
Plant filtrate turbidity: 0.09 NTU
Has aeration for TTHMs reduction
%TOC Reduction not being met
Plant dose (Coag 1 = 3.4 mg/L, Coag 2 = 3.0 mg/L)

## Slide 37: Case 2. Jar Test Results versus Plant (coagulant under dosing, 3.4/3 mg/L)
Jar # | Coag 1 mg/L | Coag 2 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 3.4 | 3.0 | 0.23 | 89.1 | 0.050 | 15.3 | 1.06
J2 | 24 | 0 | 0.10 | 92.6 | 0.033 | 44.1 | 0.33
J3 | 23 | 1.0 | 0.10 | 92.6 | 0.033 | 44.1 | 0.31
J4 | 22 | 2.0 | 0.12 | 92.5 | 0.033 | 44.1 | 0.33
J5 | 21 | 3.0 | 0.07 | 92.8 | 0.032 | 45.8 | 0.33

## Slide 38: Case 3. Pre-Oxidation
Ozone – Chlorine – KMnO4
Improve coagulation process
Improve settleability
Improve filtrate turbidity
Improve indirect DOC reduction
Longer filter runs
Reduce sludge production

## Slide 39: Case 3.1. Pre-Oxidation – with & without Ozone
Jar # | Ozone added | Coag mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settled NTU
1 | No | 35 | 0.12 | 87.4 | 0.058 | 36.2 | 0.7
2 | No | 40 | 0.08 | 88.2 | 0.055 | 39.6 | 0.65
3 | No | 45 | 0.09 | 88.6 | 0.053 | 41.8 | 1.0
4 | No | 50 | 0.09 | 88.7 | 0.052 | 42.9 | 1.2
5 | Yes | 18 | 0.11 | 92.5 | 0.034 | 62.6 | 0.85
6 | Yes | 23 | 0.07 | 92.4 | 0.034 | 62.6 | 0.65
7 | Yes | 28 | 0.05 | 93.2 | 0.031 | 65.9 | 0.80
8 | Yes | 33 | 0.09 | 93.1 | 0.031 | 65.9 | 1.0

## Slide 40: Case 3.2. Pre-Oxidation – with & without KMnO4 Same Source – Constant dose/compares two coagulants
Jar # | KMnO4 Added | Coag #1 mg/L | Coag #2 mg/L | CatFloc mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | Settle NTU 25 min
J1 | No | 70 | 0 | 6.0 | 0.08 | 87.0 | 0.060 | 6.45
J2 | Yes | 70 | 0 | 6.0 | 0.05 | 90.7 | 0.042 | 3.14
J3 | No | 0 | 160 | 6.0 | 0.10 | 90.8 | 0.041 | 3.69
J4 | Yes | 0 | 160 | 6.0 | 0.05 | 92.1 | 0.035 | 0.93

## Slide 41: Note on Chlorine Pre-Oxidation
Generally:
For a given coagulant dose, there will be an increase in %UVT or decrease in UVA when chlorine is added. It is believed that some of the DOC is converted to disinfection by-products giving a false indication of improved DOC reduction via coagulation.

## Slide 42: %UVA Reduction via Source Water Pre-Chlorination
Chart: Pre-Chlorination (2.0 mg/L) %UVA Reduction
| 0 | 9 | 38 | 85 | 124
 | 0 | 8.7 | 12.3 | 18.1 | 18.8

## Slide 43: Case 4: Conventional Treatment with Pressure Driven Membrane Filtration
Goals:
Optimize indirect DOC reduction (UVA surrogate)
Optimize solids loading to membrane filters (settleability)
pH adjustment via acid addition to optimize the coagulation process.

## Slide 44: Case 4. Performance – with/without Acid Source pH: 8.92, Alk: 158 mg/L CaCO3
Jar # | H2SO4 mg/L | Coag. mg/L | pH Unit | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 0 | 40 | 8.6 | 89.5 | 0.047 | 40.5 | 0.40
J3 | 0 | 60 | 8.4 | 90.1 | 0.045 | 43.0 | 0.40
J2 | 30 | 40 | 7.0 | 91.1 | 0.040 | 49.4 | 0.47
J4 | 30 | 60 | 6.95 | 92.0 | 0.036 | 54.4 | 0.38

## Slide 45: Case 5. Out of Compliance with TTHMs/HAA5s
Jar tested source water over a 12-month period (12 coagulants)
Compare coagulants/doses to filterability and %UVT/UVA
Selected best performing coagulant
Conducted side-by-side study (Treatment Trains 1 & 2)
Compare Filtrate turbidity and %UVT/UVA
Spike filtrate samples with 2.0 mg/L NaOCl
Held for 7-days
Tested TTHMs/HAA5s

## Slide 46: Case 5. Trains 1 and 2, On-site Study – *Results 1-liter filtrate samples were taken from each treatment train and spiked with 2.0 mg/L NaOCl and held for 7-days, TTHMs/HAA5s analyzed.
Train # | Coagulant | Filtrate NTU | %UVT | UVA/cm | %UVA Reduction | *TTHMs ug/L | *HAA5s ug/L
1 | New Coagulant | 0.06 | 97.2 | 0.012 | 91.1 | 43 | 9.9
2 | Original Coagulant | 0.07 | 90.8 | 0.042 | 68.9 | 110 | 49

## Slide 47: Case: 6 Jar Test – Filtrate Water Spiked with 2.2 mg/L NaOCl Plant Coagulant Dose vs. Optimum Dose and Coagulant
Chart: Chlorine Residual Over Time
| 0 | 8.1999999999999993 | 20.299999999999997 | 32.199999999999996 | 44.5 | 56.8 | 68.8 | 92 | 116
Alum: 35 mg/L, CatFloc C-378: 6.0 mg/L, UVA: 0.061/cm | 0.78 | 0.43 | 0.22 | 0.17 | 0.1 | 0.08 | 0.07 | 0.06 | 0.04
Alum: 70 mg/L, CatFloc C-378: 6.0 mg/L, UVA: 0.042/cm | 0.82 | 0.65 | 0.49 | 0.37 | 0.3 | 0.25 | 0.2 | 0.13 | 0.07
AdvFloc: 160 mg/L, CatFloc C-378: 6.0 mg/L, UVA: 0.036/cm | 1 | 0.67 | 0.53 | 0.42 | 0.35 | 0.27 | 0.23 | 0.15 | 0.13

## Slide 48: Jar Testing Made Easy – Recap
Keep it Simple
Don’t obsess in trying to model jar testing with plant mixing energies and contact times
Goal is to mix the chemical and form a floc (fast/slow mixing)
Measurements
Filtrate NTU
Filtrate %UVT/UVA Settled NTU
Don’t rely on visual floc formation and settleability as optimum dose
Evaluate
Evaluate results and determine next course of action
Repeat
Once optimum dose is found, repeat test for confirmation.

## Slide 49: Practice – Practice – Practice (minimum of 100 hours of practice)
Jar testing should be performed regularly during non-water quality events to develop and maintain the necessary skills and confidence to be able to confront real water quality changes.
Initial skill and confidence building will require several hours (~100 hours) of jar testing and practice.

## Slide 50: Thank you for attending! Contact and Links
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Jar Test Results/Procedures for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732