## Slide 1: Lake County CSA 2 – Spring Valley Clearlake Oaks, CA GridBee TTHM Aeration Tracer Studies, August 2015
by Guy Schott, P.E.
Guy.schott@waterboards.ca.gov
707-576-2732

## Slide 2: Tracer Test Overview for 384,9000 Gal Max Capacity Clearwell
Tank configuration – inlet at top; outlet at bottom 180 degrees from inlet. No baffles.
Tracer Test 1: GridBee spray aeration on (229 gpm).
Tracer Test 2: GridBee spray aeration off (0 gpm).
Inlet constant flow of 123 gpm
Outlet constant flow 270 gpm
Tracer Test Type: Modified Step-Dose

## Slide 3: Clearwell – 384,900 Gal Max Capacity

## Slide 4: Tracer Study – Clearwell 12,432 Gal/ft (Diam – 46-ft)
Test 1:
GridBee On – August 13, 2015
Baffling factor: 0.30 (t10/T)*
Avg tank level: 26.2
Avg tank vol: 325,700 gal
Aeration flow: 229 gpm
Inlet flow: 123 gpm
Outlet flow: 269 gpm
*Note: Test 1 was cut short; the predicted Baffling factor was 0.37 (t10/T) based on tracer trending.
Test 2:
GridBee Off – August 25, 2015
Baffling factor: 0.28 (t10/T)*
Avg tank level: 23.8
Avg tank vol: 295,880 gal
Aeration flow: 0 gpm
Inlet flow: 123 gpm
Outlet flow: 271 gpm
*Note: Tracer mass for Test 2 was seen much earlier than Test 1. There was a comparable difference in tracer trending between both tests.

## Slide 5
Minimum baffling factor: 0.30 t10/T
Predicted baffling factor: 0.37 t10/T

## Slide 6
Baffling factor: 0.28 t10/T

## Slide 7
Tracer Injection Point
Transfer pump vault
(123 gpm)

## Slide 8
Tracer Injection Point
Suction Pipe to
transfer pumps

## Slide 9
384,900 Gal Clearwell

## Slide 10
Top of Clearwell

## Slide 11
8-inch outlet pipe
on Clearwell

## Slide 12
6-inch inlet pipe
on Clearwell –
goes to top of tank

## Slide 13
Blower Pump
2 HP (750 CFM)

## Slide 14
Fluoride Analysis
Distribution
Pumps (270 gpm)

## Slide 15
Fluoride Analysis

## Slide 16
Fluoride Analysis

## Slide 17
Blower Intake

## Slide 18
GridBee - off
Inlet Flow – 123 gpm

## Slide 19
GridBee – On – 229 gpm (5HP)