## Slide 1: Jar Testing – Simple and Effective
Jar Testing – Simple and Effective
10/19/22
By Guy Schott, P.E.
CA State Water Resources Control Board
Division of Drinking Water

## Slide 2: Presentation Overview
Jar Testing – Application
Lab Equipment/Materials
Analysis (Filterability, Filtrate UVT/UVA & Settleability)
Case Studies – Jar Testing
  Coagulant overdosing (Filtrate NTU issues)
  Kenya (Tenwek Hospital) – New Surface Water Treatment Facility – Jar Testing/Training for Plant Optimization

## Slide 3: Applied Jar Testing - California
Conventional Treatment Plants
with
Media Filtration &
Membrane Filtration
Direct Filtration Plants
with
Media Filtration &
Membrane Filtration
Dissolved Air Flotation (DAF) with
Media Filtration &
Membrane Filtration
Trident & Roberts
Absorption/Contact
Media Filtration
Actiflo
(ballast sand)
with
Media Filtration
Alternative Technologies Roughing Contact Clarifier/Media Filtration &
Inline Filtration

## Slide 4: Jar Testing - What’s Important
Simple and effective that provides supporting data - Don’t make it complicated
One set of procedures, methods and analysis that can be applied to most treatment plant technologies
Results that clearly reveal which pre-oxidant, coagulant(s) and dose that provides supporting data on
Filterability (floc strength, turbidity, and perceived head loss)
Dissolved organic carbon reduction (UVA surrogate)
Settleability (turbidity)
Confidence in your jar testing data that is transferable to full-scale plant operations

## Slide 5: Lab
UVA/%UVT
Turbidity
Cuvettes
Stock
Solutions
Pipettes
Filters
(1.2 um absolute
Isopore membrane)
Syringes
4-Jar Tester

## Slide 6: 1. Filterability Analysis
Technique and analysis for predicting full-scale media filtration
Materials:
  30 mL Syringe w/Luer-Lock Tip
  Filter holder
  1.2 um absolute Isopore membrane filter
Samples collected at end of flocculation period (post 0-5 minutes) to assess floc strength
Filtration and Analysis: 4 minutes per Jar to complete and record

## Slide 7: 2. UV-Absorption (UVA) Analysis
Surrogate for predicting indirect DOC reduction
Compares different jar testing coagulants and doses for best filtrate UVA
Systems with DBP issues, UVA measurements are critical for determining optimum coagulant and dose
Filtrate UVA Analysis: 1 minute per Jar to complete and record

## Slide 8: 3. Settleability Analysis
Relative performance measurement between jars based on coagulant type, dose and flocculation duration
Samples are collected 25 minutes from the end of the flocculation period for a 4-jar tester
Settleability Analysis: 1 minute per Jar to sample, complete and record
Note: Do not use settleability as the sole source of data to determine optimum coagulant/dose
  No supporting data on filterability and DOC reduction

## Slide 9: Sensitivity Performance Analysis Plant ID: HRCSD; Plant dose (Alum: 35 mg/L, pDADMAC: 6.0 mg/L)
Jar# | Alum (dry) mg/L | pDADMAC mg/L | Filtrate NTU | Floc Strength | Filtrate UVA/cm | Settle NTU
J1 | 35 | 0 | 1.06 | Very Weak | 0.084 | 13.3
J2 | 45 | 0 | 0.66 | Very Weak | 0.075 | 11.4
J3 | 55 | 0 | 0.27 | Weak | 0.059 | 8.7
J4 | 65 | 0 | 0.26 | Weak | 0.052 | 3.8
J5 | 35 | 6.0 | 0.10 | Good | 0.061 | 3.2
J6 | 45 | 6.0 | 0.05 | Strong | 0.049 | 2.7
J7 | 55 | 6.0 | 0.04 | Strong | 0.044 | 3.9
J8 | 65 | 6.0 | 0.05 | Strong | 0.041 | 3.6

## Slide 10: UVA Application – Plant ID: NWC
Chart: Source to Treated (Jar Testing)
| 1 | 0.92592592592592582 | 0.88888888888888895 | 0.85185185185185186 | 0.81481481481481488 | 0.77777777777777779 | 0.7407407407407407 | 0.70370370370370372 | 0.66666666666666674 | 0.62962962962962965 | 0.59259259259259267 | 0.55555555555555558 | 0.51851851851851849 | 0.48148148148148145 | 0.44444444444444448 | 0.40740740740740744 | 0.37037037037037035 | 0.33333333333333343 | 0.29629629629629634 | 0.25925925925925924 | 0.22222222222222229 | 0.18518518518518523 | 0.14814814814814817 | 0.1111111111111112 | 7.4074074074074139E-2 | 3.703703703703707E-2 | 0
 | 0 | 0.01 | 0.015 | 0.02 | 0.025 | 0.03 | 0.035 | 0.04 | 0.045 | 0.05 | 0.055 | 0.06 | 0.065 | 0.07 | 0.075 | 0.08 | 0.085 | 0.09 | 0.095 | 0.1 | 0.105 | 0.11 | 0.115 | 0.12 | 0.125 | 0.13 | 0.135
90 ug/L TTHMs
63 ug/L HAA5
Filtrate: 0.04 NTU
Filtrate UVA: 0.046/cm
Settled: 2.0 NTU
59 ug/L TTHMs
40 ug/L HAA5
Filtrate: 0.04 NTU
Filtrate UVA: 0.030/cm
Settled: 2.0 NTU
35% UVA
Reduction

## Slide 11: Audience Engagement Slide
Filterability and UVA analysis in jar testing provides information on
Coagulant underdosing
Coagulant overdosing
Floc strength
DOC reduction (UVA surrogate)
Potential disinfection by-product issues
All above
Answer (F) – All above

## Slide 12: Jar Testing Procedures and Analysis
Flash Mix, 200 RPM (20-30 sec) | 2. Flocculation, 20-30 RPM (5 min) | 3. Filterability & Filtrate UVA Analysis | 4. Settleability Analysis
Set 20-30 RPM Pipette coagulant(s) into each jar Start flash mix. | *Floc for 5 minutes. Lift paddles and lock | Sample at end of flocculation period for plants w/out settling. Wait 5 minutes for plants w/settling. | After 25 minutes of settling, sample and measure settled water turbidity.
35 minutes to complete jar testing and analysis
*Note: Floc mixing duration longer than 5 minutes has no significant impact on filterability and filtrate UVA results.

## Slide 13: Case Studies
Coagulant overdosing (Filtrate NTU issues)
Kenya (Tenwek Hospital) – New Surface Water Treatment Facility – Jar Testing/Training for Plant Optimization

## Slide 14: Case 1: Filterability Analysis Coagulant Overdosing – Storm Event
50% of plant off-line for filter media change out
Source turbidity: 126 NTU, storm event
Operator doubles coagulant dose from 55 mg/L to: 110 mg/L
Plant settled water turbidity > 11 NTU
Plant filtrate turbidity: 0.20 - 0.26 NTU
Filter backwashing once per hour
Operator overwhelmed/not enough sleep

## Slide 15: Case 1: Jar Test Results vs Plant
Jar # | ACH Product mg/L | Filtrate NTU | Settled NTU
J1 | 45 | 0.50 | 2.2
J2 | 55 | 0.35 | 1.9
J3 | 65 | 0.18 | 2.4
J4 | 75 | 0.05 | 2.8
J5 | 85 | 0.14 | 3.2
J6 | 110 | 0.20 | 7.0
Plant Operations before Jar Testing:
Coagulant dose: 110 mg/L
Filtrate turbidity: 0.20 - 0.26 NTU
Settled water turbidity: >11 NTU
Plant Operations after Jar Testing:
Coagulant dose: 75 mg/L
Filtrate turbidity: 0.05 NTU
Settled water turbidity: 2 NTU

## Slide 16: Kenya, Tenwek Hospital - Surface Water Treatment Plant
Mission:
  Optimize the chemical and operations of the new surface water treatment facility.
  Train and work with the operators
Case 2:

## Slide 17: River Mara
Source Water
  River Mara
  Alkalinity: 12 mg/L CaCO3
  Turbidity: 100 – 800 NTU
  Source 0.4 um Filtered:
  UVA: 0.170/cm
  UVT: 67.6 %
Available Chemicals
  Dry Alum
  Dry Soda Ash
  Dry Calcium Hypochlorite

## Slide 18: Treatment Plan
Sludge
Drying Beds
Clean Water
Backwash Tank
Lab
Bld
Office
Bld
Chemical
Storage
Bld
Mix
Chemical
Solutions
Gravity
Chemical
Feeders
Clarifier
& Filter
Clearwell
Booster
Pump
Bld
Backwash Lagoon/
Filter-to-waste/
Clarifier Desludging

## Slide 19: Clarifier/Filter
Sand
Filter

## Slide 20: Case 2. Jar Testing/Training for New Treatment Plant in Kenya (Tenwek Hospital)
Upon arrival (April 2022) at Tenwek Hospital
  Alum/Soda Ash added at front of treatment plant
  Filtrate turbidity >1 NTUs; Kenya’s turbidity standard: <=5 NTUs
Jar testing results showed Na2CO3 had negative impact on filterability
  Moved Na2CO3 to post filtration
  Optimized Alum dose via jar testing
  Results:
    Filtrate turbidity <0.1 NTU
    Filtrate UVA: 0.008/cm
    Filtrate UVT: 98%

## Slide 21: Kenya, Tenwek Hospital, Jar Testing for Optimization

## Slide 22: Thank you for attending! Contact and Links
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water, Santa Rosa, CA
Go to Jar Test Results/Procedures for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Jar Testing Done Right video training https://youtu.be/aGByyxhelkI
Email: Guy Schott - Guy.Schott@waterboards.ca.gov