## CT Data
Version 1.2; Author: Guy Schott, guy.schott@waterboards.ca.gov, 707-576-2732
CT Compliance for
Viruses and Giardia Lamblia Cysts by Free Chlorine
Input Parameters:
Water System Name: | [5 empty] | Enter Name
Number of Service Connections: | [5 empty] | Enter Number
System Number: | [5 empty] | Enter Number
Month and Year: | [5 empty] | 2018-02-01
Clearwell(s) - Volume per Foot: | [5 empty] | 0 | Gallons/Ft
Short-Circuiting Factor for Clearwell(s): | [5 empty] | 0.1 | t10/T
Transmission Pipe - Volume | [5 empty] | 50000 | Gallons
Short-Circuiting Factor for Transmission Pipe: | [5 empty] | 0.9 | t10/T
| Data inputs should be based on when plant is on-line | [7 empty] | Inactivation Results |  |  |  |  | 2018-02-01 | 1
| Transmission Data for Peak Hourly Flow (for pH = 6.0-9.0) | [7 empty] | Viruses | Giardia |  |  |  | 2018 | 2
Date | Flow Rate, gpm | Clearwell Lowest Level, ft | Temp, oC | Chlorine Residual, mg/L | pH (Giardia) | Pipeline Effective Volume, gal | Effective Contact Time, minutes | Ct10 mg/L∙min | Log Inactivation | Log Inactivation | Virus | Required CT
Thu-1 | 3000 |  | 10 | 1 | 8 | 45000 | 15 | 15 | >8.0 | 0.27778 | 10 | 54 | 0.27778 | Thu | 1
Fri-2 | 2000 |  | 15 | 0.2 | 6 | 45000 | 22.5 | 4.5 | 4.5 | 0.28125 | 4.5 | 16 | 0.28125 | Fri | 2
Sat-3 | [5 empty] | - | - | - | - | - | - | - | - | Sat | 3
Sun-4 | [5 empty] | - | - | - | - | - | - | - | - | Sun | 4
Mon-5 | [5 empty] | - | - | - | - | - | - | - | - | Mon | 5
Tue-6 | [5 empty] | - | - | - | - | - | - | - | - | Tue | 6
Wed-7 | [5 empty] | - | - | - | - | - | - | - | - | Wed | 7
Thu-8 | [5 empty] | - | - | - | - | - | - | - | - | Thu | 8
Fri-9 | [5 empty] | - | - | - | - | - | - | - | - | Fri | 9
Sat-10 | [5 empty] | - | - | - | - | - | - | - | - | Sat | 10
Sun-11 | [5 empty] | - | - | - | - | - | - | - | - | Sun | 11
Mon-12 | [5 empty] | - | - | - | - | - | - | - | - | Mon | 12
Tue-13 | [5 empty] | - | - | - | - | - | - | - | - | Tue | 13
Wed-14 | [5 empty] | - | - | - | - | - | - | - | - | Wed | 14
Thu-15 | [5 empty] | - | - | - | - | - | - | - | - | Thu | 15
Fri-16 | [5 empty] | - | - | - | - | - | - | - | - | Fri | 16
Sat-17 | [5 empty] | - | - | - | - | - | - | - | - | Sat | 17
Sun-18 | [5 empty] | - | - | - | - | - | - | - | - | Sun | 18
Mon-19 | [5 empty] | - | - | - | - | - | - | - | - | Mon | 19
Tue-20 | [5 empty] | - | - | - | - | - | - | - | - | Tue | 20
Wed-21 | [5 empty] | - | - | - | - | - | - | - | - | Wed | 21
Thu-22 | [5 empty] | - | - | - | - | - | - | - | - | Thu | 22
Fri-23 | [5 empty] | - | - | - | - | - | - | - | - | Fri | 23
Sat-24 | [5 empty] | - | - | - | - | - | - | - | - | Sat | 24
Sun-25 | [5 empty] | - | - | - | - | - | - | - | - | Sun | 25
Mon-26 | [5 empty] | - | - | - | - | - | - | - | - | Mon | 26
Tue-27 | [5 empty] | - | - | - | - | - | - | - | - | Tue | 27
Wed-28 | [5 empty] | - | - | - | - | - | - | - | - | Wed | 28
Thu-29 | [5 empty] | - | - | - | - | - | - | - | - | Thu | 29
Fri-30 | [5 empty] | - | - | - | - | - | - | - | - | Fri | 30
Sat-31 | [5 empty] | - | - | - | - | - | - | - | - | Sat | 31
Min | 2000 | 0 | 10 | 0.2 | 6 | 45000 | 15 | 4.5 | 4.5 | 0.27778
Median | 2500 | 0 | 12.5 | 0.6 | 7 | 45000 | 18.75 | 9.75 | 7.25 | 0.27951
Max | 3000 | 0 | 15 | 1 | 8 | 45000 | 22.5 | 15 | >8.0 | 0.28125
Print Name:
Signature: | [7 empty] | Date:
Note on H9: Type in the following format: January 2018
Note on K16: Maximum table log inactivation for viruses is 4.0.
Note on E17: Temperature is restricted between 1 and 24C.