## Modified Method (hidden)
25%
CSTFR | t10/T | Dose | DPEC
1.7 | 0.2 | 10 | 2.87 |  | 10.6569 | 9.7263
2.4 | 0.3 | 10 | 3.71 |  | 9.5714 | 10.0407
3.5 | 0.4 | 8.4 | 4 |  | 7.9699 | 8.6452
5.1 | 0.5 | 6.79 | 4 |  | 6.5226 | 6.9039
8 | 0.6 | 5.47 | 4 |  | 5.5374 | 5.5134
16 | 0.7 | 4.53 | 4 |  | 4.8215 | 4.4029
CSTFR | t10/T | Dose | DPEC | DPEC
1.7 | 0.2 | 13.95 | 4 | 10 | 33.8897
2.4 | 0.3 | 10.78 | 4 | 4 | 10.8256
3.5 | 0.4 | 8.4 | 4 | 20 | 43.2258
5.1 | 0.5 | 6.79 | 4 | 4 | 6.9039
8 | 0.6 | 5.47 | 4 | 4 | 5.5134
16 | 0.7 | 4.53 | 4 | 4 | 4.4029

## Main Menu
Copyright © 2001-2017 State Water Resources Control Board, Divison of Drinking Water, all rights reserved. (707/576-2732), guy.schott@waterboards.ca.gov
Main Menu
#VALUE!
Chlorine Contact Chamber Design and Flow Evaluation
Version 1.20
Displays different contact tanks with and without baffles
and related flow parameters.
Graph plot: Length-to-Width (L:W) ratio vs. t10/HRT (baffle factor, BF).
Individual data points are associated to a tracer study.
It may be used to predict t10/HRT based on L:W ratio and to develop a
best-fit curve for individual data points.
Graph plot: Length-to-Width ratio vs. t10/HRT. Individual data points
are not associated to the person or company that conducted the test.
This graph may be used to develop the best-fit curve.
Graph plot: Length-to-Width ratio vs. t10/HRT for all data points
excluding Marske and Boyle results.
This graph may be used to develop the best-fit curve.
Graph plot: Length-to-Width ratio vs. t10/HRT for under-and-over flow
configurations.
Graph plot: Log (Length-to-Width ratio * horizontal velocity)
vs. t10/HRT.
The short-circuiting index t10/HRT is calculated for different L:W ratios
based on data points as a whole and data points from test conducted by
individual person(s) or Company.
New: predicted baffling factor (t10/HRT) when considering horizontal velocity.
Defines performance parameters commonly used in conventional
analysis of contact basins
List the references of person(s) or company that conducted the tracer
studies listed in this data base.
| For questions and | Guy Schott, P.E.
| comments, you may | Associate Civil Engineer
| contact: | Mendocino District
50 D Street, Suite 200
Santa Rosa, CA 95404
707-576-2732, email: guy.schott@waterboards.ca.gov
Tracer Database
Length-Width Graph
Length-Width Graph2
Predicted t10/HRT
Definition
Reference
Length-Width Graph3
Length-Width Graph4
BF vs Velocity

## CalsL_W (hidden)
| Yuba City | [6 empty] | Demare |  |  | Brooktrails |  |  | Cal Water |  |  | Brooktrails
| Degrees | 180 | 24 |  |  | 180 | 24 | Degrees | 180 | 40 | Degrees | 180 | 30 | Degrees | 180 | 30 | Degrees | 180 | 30
| Diameter | 194 | 194 |  |  | 100 | 100 | Diameter | 10 | 10 | Diameter | 190 | 190 | Diameter | 45 | 45 | Diameter | 25 | 25
| N Baffles | 1 | [5 empty] | N Baffles | 2 |  | N Baffles | 2 |  | N Baffles | 3 |  | N Baffles | 5
| Cal Area | 14779.6226 |  |  |  | 3926.9908 |  | Cal Area | 26.1799 | 23.5619 | Cal Area | 9450.9579 | 8505.8621 | Cal Area | 397.6078 | 357.847 | Cal Area | 81.8123 | 73.6311
| Cal width | 76.1836 |  |  |  | 39.2699 |  | Cal width | 2.618 | 2.618 | Cal width | 49.7419 | 49.7419 | Cal width | 8.8357 | 8.8357 | Cal width | 3.2725 | 3.2725
| Curcoference |  | 609.469 |  |  |  | 314.1593 | Curcoference |  | 31.4159 | Curcoference |  | 596.9026 | Curcoference |  | 141.3717 | Curcoference |  | 78.5398
|  |  | 568.8377 |  |  |  | 293.2153 |  |  | 27.9253 |  |  | 547.1607 |  |  | 129.5907 | L (total) | 150.7 | 71.9948
| L:W | 7.4667 |  |  |  | 7.4667 |  | L:W | 10.6667 |  | L:W | 11 |  | L:W | 14.6667 |  | L:W | 46.0505
|  | 8 |  |  |  | 8 |  |  | 12 |  |  | 12 |  |  | 16 |  |  | 24
[17 empty] | surface area | 490.8739
| Flow | 12 | MGD | 12.1 | MGD | 24.9 | MGD | Flow | 0.0288 | MGD | Flow | 0.0288 | MGD | Flow | 1.44 | MGD | Flow | 1.44 | MGD
| Flow | 8333.3333 | gpm | 8402.7778 | gpm | 17291.6667 | gpm | Flow | 20 | gpm | Flow | 5556 | gpm | Flow | 1000 | gpm | Flow | 1000 | gpm
| Flow | 1114.0075 | ft3/min | 1123.2909 | ft3/min | 2311.5656 | ft3/min | Flow | 2.6736 | ft3/min | Flow | 742.7311 | ft3/min | Flow | 133.6809 | ft3/min | Flow | 133.6809 | ft3/min
| Diameter | 194 | ft | 194 | ft | 194 | ft | Diameter | 10 | ft | Diameter | 190 | ft | Diameter | 45 | ft | Diameter | 25 | ft
| Gal/ft | 221117.9343 |  | 221117.9343 |  | 221117.9343 |  | Gal/ft | 587.5171 |  | Gal/ft | 212093.6717 |  | Gal/ft | 11897.2212 |  | Gal/ft | 3671.9819
| Max Ht | 18 |  | 18 |  | 18 |  | Max Ht | 8.2 |  | Max Ht | 14.14 |  | Max Ht | 13.5 |  | Max Ht | 13.5
| Max Vol | 3980122.8174 | gal | 3980122.8174 | gal | 3980122.8174 | gal | Max Vol | 4817.6402 | gal | Max Vol | 2999004.5179 | gal | Max Vol | 160612.4862 | gal | Max Vol | 49571.755 | gal
Run 1, 38% HT | % of Ht | 0.38 |  | 0.9 |  | 0.9 |  | % of Ht | 1 |  | % of Ht | 0.4135 |  | % of Ht | 0.825 |  | % of Ht | 0.825
| Tank Level | 6.84 | water level | 16.2 | water level | 16.2 | water level | Tank Level | 8.2 | water level | Tank Level | 5.8469 | water level | Tank Level | 11.1375 | water level | Tank Level | 11.1375 | water level
| Working Vol | 1512446.6706 | gallons | 3582110.5356 | gallons | 3582110.5356 | gallons | Working Vol | 4817.6402 | gallons | Working Vol | 1240088.3681 | gallons | Working Vol | 132505.3011 | gallons | Working Vol | 40896.6979 | gallons
| Avg section | 521.096 | ft2 | 1234.1747 | ft2 | 1234.1747 | ft2 | Avg section | 21.4675 | ft2 | Avg section | 290.8353 | ft2 | Avg section | 98.4079 | ft2 | Avg section | 36.4474 | ft2
| Avg ft/min | 2.1378 |  | 0.91016 |  | 1.873 |  | Avg ft/min | 0.12454 |  | Avg ft/min | 2.5538 |  | Avg ft/min | 1.3584 |  | Avg ft/min | 3.6678
| LW * ft/min | 17.1025 |  | 7.2812 |  | 14.9837 |  | LW * ft/min | 1.4945 |  | LW * ft/min | 30.6454 |  | LW * ft/min | 21.735 |  | LW * ft/min | 88.0267
| T | 181.4936 | min |  |  |  |  | T | 240.882 | min | T | 223.1981 | min | T | 132.5053 | min | T | 40.8967 | min
|  | 0.0055098 | [6 empty] | 0.0041514 | [7 empty] | For 5 baffles, it covers 276 degrees in length
|  | 0.062532 | 1.0694 | [5 empty] | 1.0734 | 1.6042
L:W should be 38
width is 3.938

## Tracer Database
Copyright © 2001-2017 State Water Resources Control Board, Divison of Drinking Water, all rights reserved. (707/576-2732), guy.schott@waterboards.ca.gov
Plate No. | Configuration - Plan View | Brief Description |  | Plant Flow (MGD) | Date of Test | L/W | Ave Velocity ft/min | Log of (L:W * Vel) | HRT min | t10/HRT | t50/HRT | Morril Index t90/t10 | Dispersion Index d | Type of Inlet | Type of Outlet | Tracer | Reference
1 |  |  |  | 11 | 5/8/17 | 1 | 1.5356 | 0.18628 | 27.1 | 0.32 | 0.87 | 2.95 |  | Horizontal overflow weir | pumped | Fluoride | 39
7,639 gpm
Pipeline volume: 9,400 gallons (100-ft linear, 4-Diam.)
Influent weir & channel volume: 8,528 gallons
Clearwell basin volume/ft: 10,800 gal/ft
Total working volume during tracer study: 206,960 gallons
17.5 ft operating level
|  |  |  | 0.7 | 3/21/70 | 24.4 |  |  | 44 | 0.61 | 0.91 | 2.15 | 0.072 | Unbaffled Pipe Entrance | 90o V-Notch Weirs | Rhodamine B Dye | 1
|  | Cross Baffled |  | 486 gpm
2 |  | Serpentine Basin |  | 1.1 | 4/21/71 | 21.7 |  |  | 50 | 0.55 | 0.82 | 2.19 | 0.065 | Unbaffled Pipe Entrance | Sharpcrested Weir | Rhodamine B Dye | 1
764 gpm
|  |  |  | 0.5 | 5/27/70 | 12.5 |  |  | 28 | 0.51 | 0.82 | 2.7 | 0.118 | Unbaffled Pipe Entrance | 90o V-Notch Weirs | Rhodamine B Dye | 1
347 gpm
|  | Baffled |  | 2 | 10/29/97 | 9 | 1.6 | 1.1584 | 69 | 0.31 | 0.78 | 5.1 | 0.2039 | Baffled pipe entrance | Unbaffled pipe outlet | Fluoride | 7
|  | Serpentine Basin |  | 1,389 gpm
3 |  | Water depth 10 ft
95.8K gallons operating volume
Tracer Test: Step-Dose
4 |  | Single Baffle Basin |  | 16 | Pre 1993 | 6.9 | 0.84 | 0.76313 | 35 | 0.27 | ? | 5.59 | 0.29 | Unbaffled Pipe Entrance | Unbaffled pipe outlet | Fluoride | 2
|  | Water depth 15 ft |  | 11,111 gpm | [9 empty] | 90o vertical bend upward | about midway of basin
near top
Baffled
Serpentine Basin
|  | Length: 52.7 ft |  | 4.032 | 9/15/01 | 16.5 | 0.84 | 1.1418 | 28 | 0.39 | 0.71 | 3.8 | 0.09482 | Unbaffled pipe entrance | Unbaffled pipe outlet | Zinc | 14
5 |  | Depth: 8.45 ft water |  | 2,800 gpm
Width: 23.5 ft
8, 6.8 & 3.7 ft channels
78,260 gal operating volume
Tracer Test: Step-Dose
Baffled Serpentine Basin
|  | Test 1: 8.8 MG Vol, 12.2 ft Depth |  | 34.9 | 5/1/14 | 21 | 3.58 | 1.8761 | 364 | 0.59 | - | - | - | Unbaffled pipe entrance | Unbaffled pipe outlet | Fluoride | 32
6 |  | Test 2: 7.9 MG Vol, 11 ft Depth |  | 50 | 2014-06-24 | 21 | 5.1289 | 2.0322 | 223 | 0.53
|  | Test 3: 11.2 MG Vol, 15.5 ft Depth |  | 65 | 2014-09-09 | 21 | 4.654 | 1.99 | 241 | 0.66
Tracer Test: Modified Step-Dose
Tanks in Series
Baffled followed by
none baffled tank
7 |  | Test 1: 12.2 & 20.3 ft depths |  | 34.9 | 5/1/14 | - | - | - | 706 | 0.55 | - | - | - | Unbaffled pipe entrance | Unbaffled pipe outlet | Fluoride | 32
|  | Test 2: 11 & 18.5 ft depths |  | 50 | 2014-06-24 |  |  |  | 442 | 0.55
|  | Test 3: 15.5 & 23 ft depths |  | 65 | 2014-09-09 |  |  |  | 457 | 0.59
Tracer Test: Modified Step-Dose
|  | Longitudinal Baffled |  | 1.5 | 5/15/70 | 70 |  |  | 83 | 0.63 | 0.76 | 1.43 | 0.019 | Unbaffled pipe entrance | Sharpcrested Weir | Rhodamine B Dye | 1
8 |  | Serpentine Basin |  | 1,042 gpm
|  |  |  | 1.5 | 5/16/70 | 70 |  |  | 83 | 0.57 | 0.71 | 1.52 | 0.024 | Unbaffled pipe entrance | Sharpcrested Weir | Rhodamine B Dye | 1
1,042 gpm
|  | Baffled Concrete |  | 4.32 | 2007-10-09 | 76 | 6.26 | 2.6774 | 35.4 | 0.7 | 0.83 | 1.8 |  | 24-in Diameter |  | Fluoride | 24
|  | Serpentine Basin |  | 3,000 gpm | [9 empty] | water splashes against wall
|  | 1st channel 4.5-ft wide |  | 4.32 | 2007-10-09 | 76 |  |  | 35.4 | 0.69 | [5 empty] | Fluoride | 24
9 |  | 2nd & 3rd channels are 3-ft wide |  | 3,000 gpm
4th channel is 10-ft wide
Length: 77-ft; Width: 23.5-ft
11,942 Gal/Ft (12.5 ft operating level)
Tracer Test: Modified Step-Dose
Baffled
10 |  | Serpentine Basin |  | ? | 1997 | 56 |  |  | ? | 0.73 | ? | ? | ? | Unbaffled Pipe Entrance | Unbaffled pipe outlet | NaCl | 8
[14 empty] | 3-inches off floor | 6-inches off floor
|  | Baffled |  | 26 | 3/20/98 | 27 | 5.2 | 2.1139 | 220 | 0.53 | 1.05 | 4.4 | 0.21613 |  |  | Lithium | 12
|  | Serpentine Basin |  | 18,056 gpm |  | 25 |  |  |  | 0.59
11 |  | Water depth: 8.6 ft
4.0 MG operating volume
210' x 270'
[7 empty] | Basin | HRT | Modal |  | Modal
[7 empty] | # | minutes | Contact time |  | BF
|  | Chlorine contact basin |  |  |  |  | 1 | 166 | 130 |  | 0.78
|  | for wastewater. |  |  |  |  | 2 | 167 | 135 |  | 0.81
|  | 6.5-ft channel width & baffle opening. |  | 2.256 | 8/23/2016 | 42 | 3 | 168 | 155 |  | 0.93 |  |  |  |  | Fluoride | 38
12 |  | 130-ft channel length; |  | 1,567 gpm |  |  | Combined 1-3: | 166 | 145 |  | 0.87 |  |  |  |  | Sluge Dose
Basin L:W - 42:1
82,170 gallons/basin
6.5-ft water depth
Rectangular
13 |  | Secondary |  | 30.2 | 3/7/70 | 7.5 |  |  | 37 | 0.67 | 0.95 | 2.25 | 0.081 | Unbaffled ports | V-Notch Weirs | Rhodamine B Dye | 1
|  | Clarifier |  | 20,972 gpm | [9 empty] | Across face of inlet
|  | Rectangular |  | 18.6 | 7/8/99 | - |  |  | 105 | 0.64 | 0.95 | - | - | Unbaffled ports for | V-Notch Weirs | Lithium | 13
14 |  | Floculation/Sedimentation |  | 12,917 gpm | [9 empty] | each Flocculator
Basin
Test Test: Slug-Dose
15 |  | Floculation Basins |  | 18.6 | 7/8/99 | - |  |  | 22.7 | 0.46 | 1.08 | - | - | Unbaffled ports for | Unbaffled ports | Lithium | 13
|  |  |  | 12,917 gpm | [9 empty] | each Flocculator
Test Test: Slug-Dose
|  |  |  | 1.9 | 5/2/70 | 3 |  |  | 63 | 0.39 | 0.72 | 3.68 | 0.254 | Target baffled Ports | Cipolleti Weir | Rhodamine B Dye | 1
|  |  |  | 1,319 gpm | [9 empty] | Across Face of Inlet
|  | Rectangular |  | 1.9 | 5/9/70 | 3 |  |  | 68 | 0.49 | 0.81 | 2.97 | 0.147 | Target baffled Ports | Sharpcrested Weir | Rhodamine B Dye | 1
16 |  | Concrete |  | 1,319 gpm | [9 empty] | Across Face of Inlet
|  | Basin |  | 3.6 | 4/24/71 | 3 |  |  | 35 | 0.39 | 0.63 | 3.21 | 0.149 | Target baffled Ports | Sharpcrested Weir | Rhodamine B Dye | 1
|  |  |  | 2,500 gpm | [9 empty] | Across Face of Inlet
|  |  |  | 0.3 | 4/20/71 | 9 |  |  | 107 | 0.31 | 0.58 | 3.83 | 0.252 | Target baffled Pipe | Sharpcrested Weir | Rhodamine B Dye | 1
|  |  |  | 208 gpm | [9 empty] | Entrance
Long, Narrow and
|  | Shallow Gunite |  | 3.5 | 1970-02-21 | 21 |  |  | 49 | 0.59 | 0.85 | 2.14 | 0.077 | Unbaffled pipe entrance | Sharpcrested Weir | Rhodamine B Dye | 1
17 |  | Lined Channel |  | 3.4 | 1970-03-20 | 21 |  |  | 50 | 0.62 | 0.78 | 2.07 | 0.084 | Unbaffled pipe entrance | Sharpcrested Weir | Rhodamine B Dye | 1
3-ft deep; 16-ft wide; 335-ft long
Serpentine - long rectangular
|  | channel; 16.8 ft deep; 7.5 ft wide |  | 18.6 | 7/8/99 | 36 | 13.7 | 2.693 | 22.3 | 0.8 | 1.18 | 2 | 0.07 | Baffled pipe entrance | Baffled Outlet | Fluoride | 13
18 |  | channel; 272 ft long |  | 12,917 gpm
Test Test: Slug-Dose
19 |  | Unbaffled Basin |  | 1.44 | 11/20/97 | - |  |  | ? | 0.19 | ? | ? | ? | Unbaffled pipe entrance | Unbaffled pipe outlet | Fluoride | 4
|  |  |  | 1,000 gpm | [9 empty] | 3-inches off floor | 6-inches off floor
|  | Unbaffled Basin |  | 0.26 | 4/12/16 | - | - | - | 1540 | 0.08 | - | - | - | top | bottom | Fluoride | 37
|  | Inlet/out 180o |  | 181 gpm
20
Unbaffled Basin
test with/without PAX on
Test inlet (bottom/top)
21
|  | Test 1 (22 ft avg opt level); PAX on; inlet bottom; |  |  | 7/7/15 | - |  |  | 2727 | 0.033 |  |  |  | bottom (PAX on) | bottom | Fluoride | 33
139 gpm avg outlet; 255 gpm inlet; 379,000 gal avg volume
|  | Test 2 (23.2 ft avg opt level); PAX off; inlet bottom; |  |  | 7/14/15 | - |  |  | 3518 | 0.049 |  |  |  | bottom (PAX off) | bottom | Fluoride | 33
114 gpm avg outlet; 255 gpm inlet; 401,000 gal avg volume
|  | Test 3 (18.7 ft avg opt level); PAX on, inlet top; |  |  | 7/16/15 | - |  |  | 2360 | 0.063 |  |  |  | top (PAX on) | bottom | Fluoride | 33
136 gpm avg outlet; 255 gpm inlet; 321,000 gal avg volume
|  | Test 4 (21.6 ft avg opt level); PAX off, inlet top |  |  | 7/28/15 | - |  |  | 2609 | 0.091 |  |  |  | top (PAX off) | bottom | Fluoride | 33
142 gpm avg outlet; 255 gpm inlet; 370,500 gal avg volume
Unbaffled Basin
test with PAX on
Test inlet (top/bottom)
22
|  | Test 1 (21 ft avg opt level); PAX on; inlet top; |  |  | 2015-09-29 | - |  |  | 2610 | 0.084 |  |  |  | top (PAX on) | bottom | Fluoride | 33
138 gpm avg outlet; 259 gpm inlet flow
|  | 360,700 gal avg volume | [11 empty] | bottom (PAX on) | bottom | Fluoride | 33
|  | Test 2 (23.1 ft avg opt level); PAX on; inlet bottom; |  |  | 2015-10-13 |  |  |  | 3440 | 0.058
115 gpm avg outlet; 280 gpm inlet flow
395,600 gal avg volume
Note: PAX was moved to different location from what is
seen in Plate 18.
|  | Test 1 (26.2 ft avg opt level); Spray Aeration On; |  |  | 8/13/15 | - |  |  | 1210 | 0.30* |  |  |  | Top (SolarBee Spray on) | bottom | Fluoride | 34
Spray Aeration (229 gpm); 123 gpm intlet flow;
269 gpm outlet; 325,700 gal avg volume
6 hour test
*test was cut short. The 0.3 is minimum value.
Predicted baffling factor is 0.37.
23
|  | Test 2 (23.8 ft avg opt level); Spray Aeration Off; |  |  | 8/25/15 |  |  |  | 1100 | 0.28 |  |  |  | Top (SolarBee Spray off) | bottom | Fluoride | 34
Spray Aeration (229 gpm); 123 gpm intlet flow;
271 gpm outlet; 295,880 gal avg volume
5.5 hour test
Tracer was injected in small clearwell channel next to
transfer pump suction line to large clearwell.
24 |  | Unbaffled Basin |  | 2.52 | 2/9/96 | - | - | - | 50 | 0.22 | 0.74 | 9.4 | - | 90 degree bend top of Tank | Bottom of tank | Zinc | 3
|  |  |  | 1,750 gpm | [10 empty] | 180o from inlet
25 |  | Unbaffled Basin |  | 3.67 | 5/23/06 | - |  |  | 322 | 0.15 | - | - | - | Flow in both directions | Unbaffled pipe outlet | Fluoride | 21
|  | Flow at top of tank |  | 2,549 gpm | [9 empty] | 31-ft off floor. | 7-inches off floor | Step-Dose
|  | Outlet at bottom | [11 empty] | 14" diameter pipes | 16" diameter pipes
|  | Unbaffled Tank |  | 0.69 | 11/1/06 | - |  |  | 250 | 0.1 | - | - | - | Perforated | Perforated | Fluoride | 22
|  | 12" PVC Inlet/outlet |  | 479 gpm | [9 empty] | Riser (14-ft) | Riser (14-ft) | Step-Dose (SV)
26 |  | Risers (14-ft)
Tracer Test: Modified Step-Dose
|  |  | Tanks in series | 2.52 | 2/9/96 | - |  |  | 128 | 0.34 | 0.92 | 5.4 | - | Tank1: 90 degree bend top | Tank 1: Bottom of tank | Zinc | 3
27 |  |  |  | 1,750 gpm | [9 empty] | of tank.
[14 empty] | Tank2: 90 degree bend top | Tank 2: Bottom of tank.
|  |  | Test Test: Step-Dose | [10 empty] | of tank.
28 |  | 4.0 MG Concrete Underground |  | 12.0a | 11/20/07 | 8 | 2.14 | 1.2335 | 187 | 0.57a | - | - | - | Rectangle | Rectangle | Fluoride | 26
|  | Clearwell; |  | 12.1b | 2/26/08 | 8 | 0.91 | 0.86213 | 433 | 0.42b | - | - | - | 7.5 x 7.5-ft (8-ft above floor) | 7.5 x 7.5-ft (flush to floor) |  | 27
|  | Diameter: 194-ft |  | 24.9b | 8/19/08 | 8 | 1.87 | 1.1749 | 206 | 0.49b | - | - | - |  |  |  | 27
Max Water Level: 18-ft
Inlet: 7.5 x 7.5-ft (8-ft above floor)
Outlet: 7.5 x 7.5-ft (flush on bottom floor)
One Hypalon Baffle: 163.6-ft
Baffle Openning: 30.4-ft
aTracer Test Volume (38%): 1.5 MG
bTracer Test Volume (90%): 3.6 MG
Tracer Test: Modified Step-Dose
|  | Test 1: 31.8 ft operating level. |  | 0.288 | 2/10/16 | 8 |  |  | 867 | 0.13 |  |  |  | Rise, 12 ft off bottom | bottom flush | Fluoride
29 |  | Even flows (inlet/outlet) |  | 200 gpm
|  | Test 2: 33.4 ft operating level. |  | 0.292 | 5/8/17 | 8 |  |  | 871 | 0.14 |  |  |  | Rise, 12 ft off bottom | bottom flush | Fluoride
|  | Even flows (inlet/outlet) |  | 203 gpm
Inlet/outlet separated by a single baffle.
1st Test: It was determined that there were
major gaps between floor and wall baffle curtain.
2nd Test: Gaps between floor and wall
were filled with a type of epoxy. However, it
does not appeared to hold based on test results.
|  |  |  | 0.576 | May 8, 2017 | 11 | 0.74 | 0.91062 | 87 | 0.37 | - | - | - | 8-in Inlet 2.8-ft off bottom | 8-in, Outlet 2-in off bottom | Fluoride | 40
|  |  |  | 400 gpm | [9 empty] | angled 30o up
Clearwell volume/ft: 2,844 gal/ft
Working volume during tracer study: 34,000 gallons
30 |  | 12-ft operating level during tracer study
Inlet 2.8-ft off bottom angled 30o up
Outlet 2-in off bottom
L:W ratio: 11
Has spray aeration for TTHM reduction pumped
from outlet pipe back into tank top in last channel.
31 |  | Baffled |  | 0.0288 | 9/11/2003 | 12 | 0.125 | 0.17609 | 240 | 0.39 | 0.94 | 5.43 | 0.23701 | 4-ft length perforated PVC | PVC pipe located at top | Fluoride | 16
|  | Serpentine Basin |  | 20 gpm | [9 empty] | located at bottom of tank | of tank
constant tank level
4,800 gallon storage
Test Test: Slug-Dose
|  | Baffled |  | 8 | 9/11/2007 | 11.5 | 2.554 | 1.4679 | 223 | 0.35 | - | - | - | 24-inch diameter | 20-inch diameter | Fluoride | 23
|  | Serpentine Basin |  | 5,556 gpm | [9 empty] | At top/Vertical | At bottom/Vertical
tank level may vary
Diameter: 190-ft
32 |  | 3 Million Gallon Tank
Test ran at 1.24 MG full
33 |  | Baffled |  | 1.44 | 11/20/97 | 16 | 1.36 | 1.3377 | 132.6 | 0.5 | 1.16 | 4.77 | 0.1562 | Unbaffled pipe entrance | Unbaffled pipe outlet | Fluoride | 9
|  | Serpentine Basin |  | 1,000 gpm | [9 empty] | 3-inches off floor | 6-inches off floor
Tracer Test: Step-Dose
|  | Baffled |  | 14.3 | 2005-04-07 | 16.6 | 1.9 | 1.4989 |  | 0.45 | 0.92 | 2 | - | Unbaffled pipe entrance | Unbaffled pipe outlet | Fluoride | 19
|  | Serpentine Basin |  | 9,931 gpm
34 |  | Inlet/Outlet located at bottom
Diam: 137-ft
Ht: 22.7 ft to overflow
|  | Baffled Tank |  | 0.7 | 11/1/06 | 34 | 1.19 | 1.607 | 103 | 0.5 | - | - | - | Perforated | Non-perforated | Fluoride | 22
35 |  | 12" PVC Inlet/outlet |  | 486 gpm | [9 empty] | Riser (14-ft) | Riser (14-ft) | Step-Dose (SV)
Risers (14-ft)
50,000 gal operating volume
Tracer Test: Modified Step-Dose
|  | 3.0 MG Concrete |  | 9.95 | 10/29/13 | 24 | 2.8 | 1.8274 | 187 | 0.7 | 1 | 1.98 |  | Stand Pipe | Bottom flush | Fluoride (NaF) | 31
|  | Clearwell; |  | 6,910 gpm | [11 empty] | Slug Dose
36 |  | Diameter: 130-ft
Test Water Level: 13-ft
Inlet: Stand Pipe (31.1-ft above floor)
Outlet: 7.5 x 7.5-ft (flush on bottom floor)
Tracer Test Volume (43%): 1.3 MG
Baffled
37 |  | Serpentine Basin |  | 1.44 | 8/9/96 | 81 | 4.15 | 2.5265 | 47.4 | 0.78 | 1.03 | 1.73 | 0.07719 | Unbaffled pipe entrance | Outlet Weir Box | Fluoride | 5
|  | 25-ft Diameter |  | 1,000 gpm | [9 empty] | 5 feet off floor | 10 feet off floor
47,370 gal operating volume
12.9-ft water level
Tracer Test: Step-Dose
Alvarado East Clearwell
38 |  | Circular Baffled Basin |  | 111.9 | 9/24/97 | 37 | 8.08 | 2.4756 | 168 | 0.52 | 0.79 | 2.2 | 0.00712 | Unbaffled pipe entrance | Unbaffled pipe outlet | Lithium | 10
77,708 gpm
13.058 MG operating volume
25-ft water level
72-in Dia outlet/inlet
Tracer Test: Slug-Dose
|  | 50-ft diameter |  | 2.016 | 2005-03-08 | - |  |  | 126 | 0.29 | 0.78 | 9.2 | - | Baffle pipe entrance | Baffle pipe outlet | Fluoride | 18
|  | Inlet/Outlet Baffles |  | 0.9677 | 2005-06-08 |  |  |  | 262 | 0.14 | 0.36 | 8.5
39 |  | 13.5-ft Height |  | 0.7128 | 2005-06-09 |  |  |  | 356 | 0.2 | 0.65 | 8.4
14-inch inlet/outlet
Outlet pipe is 12-ft standpipe.
Operated at 12-ft
during tracer test.
|  | Outter shell diamter: 12-ft |  | 0.086 | 2007-10-19 | - |  |  | 230 | 0.23 | - | - | - | 2-inch pipe | Overflow circular weir | Fluoride | 25
|  | Inner shell diameter: 6-ft |  | 60 gpm
40 |  | Inlet pipe height/diam.: 10-ft/2-in
Inlet velocity: 6.1 ft/sec
Perforation diam.: 7/8-inch
Height of perforations: 6-ft
Volume to top of
overflow weir: 13,790 Gal
Tracer Test: Modified Step-Dose
41 |  | Serpentine long rectangular |  | 16.8 | 7/8/99 | - |  |  | 337 | 0.16 | 0.68 | 5.5 | 1.26 | Unbaffled pipe entrance | Unbaffled pipe outlet | Fluoride | 13
|  | channel followed by two |  | 11,667 gpm | [9 empty] | top corner of basin | on bottom
unbaffled bay tanks
operated in parallel
Tracer Test: Slug-Dose
10.5 MG
|  | Unbaffled concrete |  | 35 | 10/9/97 | - |  |  | 235 | 0.39 | 0.88 | 4.5 | 0.1657 | Unbaffled pipe entrance | Unbaffled pipe outlet | Lithium | 6
42 |  | undeground tank; |  | 40 | 9/18/97 | - |  |  | 209 | 0.31 | 0.74 | 5 | 0.17986 | Unbaffled pipe entrance | Unbaffled pipe outlet | Lithium | 6
|  | inlet top corner; |  | 45 | 9/4/97 | - |  |  | 184 | 0.34 | 0.81 | 5.2 | 0.18227 | Unbaffled pipe entrance | Unbaffled pipe outlet | Lithium | 6
|  | outlet bottom center |  | 45 | 4/22/08 | - |  |  | 160 | 0.31 | 0.74 | 5.6 | - | Unbaffled pipe entrance | Unbaffled pipe outlet | Fluoride | 28
|  | Max water level: 25-ft |  | 52 | 5/6/08 | - |  |  | 158 | 0.3 | 0.74 | 5.9 | - | Unbaffled pipe entrance | Unbaffled pipe outlet | Fluoride | 28
|  | 15-17-ft normal operating level |  | 60 | 6/17/08 | - |  |  | 160 | 0.3 | 0.75 | 6.2 | - | Unbaffled pipe entrance | Unbaffled pipe outlet | Fluoride | 28
13-ft (4/22/08)
14.5-ft (5/6/08)
16.5-ft (6/17/08)
Baffled Tank
|  | 30-ft between baffles |  | 20 | 2004-03-17 | 37.6 |  |  | 108 | 0.59 | 0.86 | 2.2 | - | Unbaffled pipe entrance | Unbaffled pipe outlet | Fluoride | 17
43 |  | Note: Width in the L:W ratio |  | 41.5 | 2004-07-21 | 37.6 |  |  | 52 | 0.67 | 1 | 2.8 | -
was decreased to account
for tank slope.
Operated at 60% full during test.
Water L:W was 262:111 ft
Baffle Length: 210
Approximately 100,000 gallon of
inlet/out pipeline included in study.
Total Tank + Pipe Vol. = 1.5 MG
Normal operating level ranges
|  | from 18 to 22 feet. Test level |  | 22.24 | 2012-08-30 | 70 | 1.79 | 2.098 | 741 | 0.73 | - | - | - | Two separate pipe inlets | Rectangle drain box | Fluoride | 30
|  | average 21.13 feet. |  | 15,444 gpm | [10 empty] | 13 feet above floor
|  | Average test vol: 11.45 MG | [12 empty] | Connects to 54-in outlet
44 |  | Floor has 20% incline at wall | [12 empty] | pipe.
|  | Old clarifier converted |  | 0.216 | 10/10/98 | - |  |  | 179 | 0.09 | 0.55 | 20.3 | 1.72 | Circular weir entrance | Perforated piping on | Fluoride | 11
45 |  | to clearwell; circular |  | 150 gpm | [9 empty] | submerge | bottom of tank
v-notch weir left in.
Tracer Test: Step-Dose
Over and under configuration
46 |  |  | Station 1 | 13.5 | 2005-10-20 | 4.4 | 12.8 | 1.7507 | 3.46 | 0.62 | 1.1 | 2.1 | 0.29525 | Baffle pipe entrance | Unbaffled pipe outlet | Fluoride | 20
|  |  | Station 3 | 13.5 | 2005-10-20 | 16.8 | 12.8 | 2.3325 | 14.06 | 0.82 | 1.2 | 3.4 | 0.15422
|  |  | Station 2 | 13.5 | 2005-10-21 | 8 | 12.8 | 2.0103 | 6.58 | 0.63 | 1 | 2.65 | 0.1119
|  |  | Station 1 | 10.6 | 2005-10-21 | 4.4 | 10 | 1.6435 | 4.39 | 0.56 | 1 | 3.3 | 0.0238
|  |  | Station 3 | 10.6 | 2005-10-21 | 16.8 | 10 | 2.2253 | 17.8 | 0.75 | 1.1 | 2.2 | 0.1569
Tracer Test: Slug-Dose
[6 empty] | L/D |  |  | HRT, sec
|  |  | Station 2 | 8 | 2016-02-22 | 45 | 47 | 3.3253 | 262 | 0.95 |  |  | - |  |  | Fluoride | 36
|  |  | Station 2 | 15 | 2016-02-22 | 45 | 87 | 3.5927 | 140 | 0.95 |  |  | -
| Tracer Test: Step-Dose |  | Station 2 | 15 | 2016-02-23 | 45 | 87 | 3.5927 | 140 | 1 |  |  | -
|  |  | Station 2 | 20 | 2016-02-23 | 45 | 117 | 3.7214 | 105 | 1 |  |  | -
47 |  |  | Station 2 | 25 | 2016-02-23 | 45 | 146 | 3.8176 | 84 | 1 |  |  | -
|  |  | Station 4 | 8 | 2016-02-22 | 90 | 47 | 3.6263 | 524 | 0.95 |  |  | -
|  |  | Station 4 | 15 | 2016-02-22 | 90 | 87 | 3.8938 | 280 | 0.95 |  |  | -
|  |  | Station 4 | 15 | 2016-02-23 | 90 | 87 | 3.8938 | 280 | 1 |  |  | -
| 54-in diameter ozone pipeline (straight) |  | Station 4 | 20 | 2016-02-23 | 90 | 117 | 4.0224 | 210 | 1 |  |  | -
| 204-ft between Stations 0 & 2 (24,270 gal) |  | Station 4 | 25 | 2016-02-23 | 90 | 146 | 4.1186 | 168 | 0.95 |  |  | -
204-ft between Stations 2 & 4 (24,270 gal)
Reynolds Number: 383,000 - 965,000 (Turbulent)
L/D
|  |  |  | 58 gpm | 2017-05-15 | 57 | 0.617 | 1.5462 | 370 | 0.18 |  |  |  | Vertical Manhole | Vertical Manhole | Fluoride | 41
|  |  |  | 43 gpm | 2017-07-20 | 57 | 0.457 | 1.4158 | 370 | 0.2
48 | Modal contact time: 90 min
Pipeline volume: 21,500 gallons; Pipeline diameter: 48-inches (4 feet)
Pipeline length: 229 feet; Material: concrete (buried)
Temperature entering/exit (18 & 17.7o C); Temperature profile was conducted - results: Temperature gradient inside pipeline (warmer at upper portions of pipeline).
Modal baffling factor: 0.24 for treated wastewater treatment plant. It is expected that warmer water is short-circuiting at upper portion of pipeline.
Reynolds Number: 2,669 - 3,600 (Critical zone, between Laminar and Transition zones)
L/D
49 |  |  |  | 63 gpm | 2017-08-09 | 57 | 0.67 | 1.5819 | 340 | 0.47 |  |  |  | Vertical Manhole | Vertical Manhole | Fluoride | 42
Pipeline volume: 21,500 gallons; Pipeline diameter: 48-inches (4 feet)
Pipeline length: 229 feet; Material: concrete (buried)
Orifice pipeline: 1.5" PVC, 80-ft, 1/8" holes spaced 18 inches (added for third tracer study to increase mixing energy)
Serpentine Pipeline
L/D
50 |  |  | Station 1 | 0.513 | 2003-01-30 | 76 | 3.79 | 2.4595 | 79.8 | 0.82 | 0.96 | 1.5 | - | Unbaffled pipe entrance | Unbaffled pipe outlet | Fluoride | 15
|  |  | Station 2 | 0.513 | 2003-01-30 | 114 | 3.79 | 2.6355 | 121 | 0.84 | 0.93 | 1.3 | -
|  |  | Station 3 | 0.513 | 2003-01-30 | 153 | 3.79 | 2.7633 | 162 | 0.85 | 0.93 | 1.2 | -
|  |  | Station 4 | 0.513 | 2003-01-30 | 192 | 3.79 | 2.8619 | 202 | 0.82 | 0.89 | 1.2 | -
|  |  | Station 5 | 0.513 | 2003-01-30 | 422 | 3.79 | 3.204 | 446 | 0.96 | 1 | 1.2 | -
Tracer Test: Slug-Dose
356 gpm test flow
Reynolds Number: 22,000 (critical zone)
|  |  |  | Flow - varied | 2008-11-19 | - |  |  |  | 0.17 | - | - | - | Top of Tank | Bottom of Tank | Fluoride | 30
|  |  |  | Booster Pump | Winter | [9 empty] | same side of inlet
Distribution Flow
51
[5 empty] | 2008-11-20 |  |  |  |  | 0.14 | - | - | -
Summer
Distribution Flow
Tracer Method: Cummulative Volume (VC10); for non-steady-state flows;
t10 is based on volume of water discharged to distribution system and not on time.
|  |  |  | Flow - varied | 2008-11-20 |  |  |  |  | 0.14 | - | - | - | Top of Tank | Bottom of Tank | Fluoride | 30
|  |  |  | Booster Pump | Winter | [9 empty] | same side of inlet
Distribution Flow
52
[5 empty] | 2008-11-21 |  |  |  |  | 0.09
Summer
Distribution Flow
Tracer Method: Cummulative Volume (VC10); for non-steady-state flows;
t10 is based on volume of water discharged to distribution system and not on time.
|  |  |  | Flow - varied | 2008-11-19 |  |  |  |  | 0.16 |  | - | - | Top of Tanks | Bottom of Tank | Fluoride | 30
|  |  |  | Booster Pump | Winter
53 |  |  |  |  | Distribution Flow
[5 empty] | 2008-11-21 |  |  |  |  | 0.14
Summer
Distribution Flow
Tracer Method: Cummulative Volume (VC10); for non-steady-state flows;
t10 is based on volume of water discharged to distribution system and not on time.
Main Menu
Influent channel
width: 2.5-ft
Influent weir width: 3.5-ft
Station 2
Station 4
Station 0
Modal contact time: 210 minutes

## BF vs vel
Main Menu

## Length-WidthGraph
Main Menu
Rectangular and Circular Baffled Tanks

## Length-WidthGraph2
Main Menu
Rectangular and Circular Baffled Tanks - Based on all Test Data

## Length-WidthGraph3
Main Menu
Rectangular and Circular Baffled Tanks

## Length-WidthGraph4
Main Menu
Flow - Under and Over (Rectangular Ozone Basin)

## Predicted t10
Baffled Tanks
Predicted t10/HRT based on
the following data
| Set 1 | Set 2 | Set 3 | Set 4 | New | Set 5 | Set 1 | Set 3
| R2 = 0.78 | R2 = 0.92 | R2 = 0.80 | R2 = 0.83 | Log(L:W * Vel) | R2 = 0.69 | R2 = 0.76 | R2 = 0.76
| n = 28 | n = 8 | n = 22 | n = 7 |  | n = 26 |  | n = 3
L//W | t10/HRT | t10/HRT | t10/HRT | t10/HRT |  | t10/HRT | T10/T | t10/T
4 | 0.28351 | 0.25292 | 0.25744 | 0.33474 | 0.7 | 0.32338 | 0.27165 | 0.24776
6 | 0.32353 | 0.29236 | 0.30011 | 0.37898 | 0.75 | 0.33475 | 0.32943 | 0.32066
8 | 0.35532 | 0.32402 | 0.33461 | 0.41037 | 0.8 | 0.34612 | 0.37042 | 0.37238
10 | 0.3821 | 0.35092 | 0.36407 | 0.43471 | 0.85 | 0.35749 | 0.40222 | 0.4125
12 | 0.40548 | 0.37454 | 0.39006 | 0.4546 | 0.9 | 0.36886 | 0.4282 | 0.44529
14 | 0.42635 | 0.39576 | 0.41348 | 0.47142 | 0.95 | 0.38023 | 0.45017 | 0.473
16 | 0.44531 | 0.4151 | 0.43489 | 0.48599 | 1 | 0.3916 | 0.46919 | 0.49701
18 | 0.46272 | 0.43295 | 0.4547 | 0.49884 | 1.05 | 0.40297 | 0.48598 | 0.51819
20 | 0.47888 | 0.44956 | 0.47319 | 0.51033 | 1.1 | 0.41434 | 0.50099 | 0.53713
22 | 0.49397 | 0.46514 | 0.49056 | 0.52073 | 1.15 | 0.42571 | 0.51457 | 0.55427
24 | 0.50817 | 0.47983 | 0.50697 | 0.53023 | 1.2 | 0.43708 | 0.52697 | 0.56991
26 | 0.5216 | 0.49376 | 0.52255 | 0.53896 | 1.25 | 0.44845 | 0.53838 | 0.58431
28 | 0.53434 | 0.50701 | 0.5374 | 0.54704 | 1.3 | 0.45982 | 0.54894 | 0.59763
30 | 0.54648 | 0.51967 | 0.55161 | 0.55457 | 1.35 | 0.47119 | 0.55877 | 0.61004
32 | 0.55809 | 0.53179 | 0.56524 | 0.56161 | 1.4 | 0.48256 | 0.56797 | 0.62164
34 | 0.56922 | 0.54344 | 0.57835 | 0.56823 | 1.45 | 0.49393 | 0.57661 | 0.63254
36 | 0.57992 | 0.55466 | 0.59099 | 0.57446 | 1.5 | 0.5053 | 0.58475 | 0.64282
38 | 0.59022 | 0.56548 | 0.6032 | 0.58036 | 1.55 | 0.51667 | 0.59246 | 0.65254
40 | 0.60016 | 0.57594 | 0.61501 | 0.58596 | 1.6 | 0.52804 | 0.59977 | 0.66176
42 | 0.60977 | 0.58607 | 0.62647 | 0.59128 | 1.65 | 0.53941 | 0.60672 | 0.67053
44 | 0.61908 | 0.5959 | 0.63759 | 0.59636 | 1.7 | 0.55078 | 0.61335 | 0.6789
46 | 0.62811 | 0.60544 | 0.6484 | 0.6012 | 1.75 | 0.56215 | 0.61968 | 0.68689
48 | 0.63688 | 0.61472 | 0.65892 | 0.60585 | 1.8 | 0.57352 | 0.62575 | 0.69454
50 | 0.6454 | 0.62376 | 0.66917 | 0.6103 | 1.85 | 0.58489 | 0.63156 | 0.70188
52 | 0.6537 | 0.63256 | 0.67917 | 0.61458 | 1.9 | 0.59626 | 0.63715 | 0.70893
54 | 0.66179 | 0.64115 | 0.68893 | 0.6187 | 1.95 | 0.60763 | 0.64253 | 0.71572
56 | 0.66967 | 0.64954 | 0.69847 | 0.62267 | 2 | 0.619 | 0.64771 | 0.72226
58 | 0.67737 | 0.65774 | 0.7078 | 0.62649 | 2.05 | 0.63037 | 0.65271 | 0.72857
60 | 0.68489 | 0.66575 | 0.71694 | 0.63019 | 2.1 | 0.64174 | 0.65754 | 0.73466
62 | 0.69224 | 0.6736 | 0.72588 | 0.63377 | 2.15 | 0.65311 | 0.66222 | 0.74056
64 | 0.69944 | 0.68129 | 0.73465 | 0.63723 | 2.2 | 0.66448 | 0.66674 | 0.74627
66 | 0.70648 | 0.68882 | 0.74325 | 0.64059 | 2.25 | 0.67585 | 0.67113 | 0.7518
68 | 0.71339 | 0.69621 | 0.75169 | 0.64385 | 2.3 | 0.68722 | 0.67538 | 0.75717
70 | 0.72015 | 0.70346 | 0.75998 | 0.64701 | 2.35 | 0.69859 | 0.67951 | 0.76238
72 | 0.72679 | 0.71058 | 0.76812 | 0.65008 | 2.4 | 0.70996 | 0.68352 | 0.76744
74 | 0.73331 | 0.71757 | 0.77612 | 0.65307 | 2.45 | 0.72133 | 0.68743 | 0.77237
76 | 0.7397 | 0.72444 | 0.78399 | 0.65598 | 2.5 | 0.7327 | 0.69123 | 0.77717
78 | 0.74599 | 0.7312 | 0.79173 | 0.65882 | 2.55 | 0.74407 | 0.69493 | 0.78184
80 | 0.75217 | 0.73785 | 0.79934 | 0.66158 | 2.6 | 0.75544 | 0.69854 | 0.78639
82 | 0.75824 | 0.74439 | 0.80684 | 0.66427 | 2.65 | 0.76681 | 0.70206 | 0.79083
Set 1:
Results based on all tracer studies in this data base that have
one or more baffles ( (narrow or long channel basins and under-and-over flow basin (ozone basins) are excluded).
n = 28 data points; R2 = 0.78
Set 2:
Results based on tracer studies conducted by Santa Rosa District that have one or more baffles (narrow or long channel are excluded).
n = 8 data points; R2 = 0.92
Set 3:
Results based on all tracer studies (excluding results from Marske & Boyle) that have one or more baffles (narrow or long channel basins are excluded).
n = 22 data points; R2 = 0.80
Set 4:
Results based on tracer studies conducted by Marske & Boyle that have one or more baffles (narrow or long channel basins are excluded).
n = 7 data points; R2 = 0.83
Set 5:
Take the log of the velocity profile (feet/minute) times the L:W ratio. For a given L:W, the higher velocity profile will tend to achieve a higher baffling factor.
Main Menu
When using L:W, recommend using (green area) for predicting t10/HRT.

## Definition
Performance parameters commonly used in conventional
conventional analysis of contact basins.
Parameter | Definition
HRT | Hydraulic Residence Time (HRTor T)
t10, t50, t90 | Time for 10, 50, and 90 percent of the tracer to
pass through the reactor.
t10/HRT | Index of short-circuiting
t50/HRT | Index of mean detention time
t90/t10 | Morril dispersion index, indicates degree of
mixing, as t90/t10 increases the degree of mixing
increases. Likewise, as t90/t10 approaches 1.0
plug flow conditions are observed.
d | Dispersion index, indicates degree of tracer
dispersion. Under ideal plug flow conditions,
the value of d should approach zero.
The dispersion index calculation includes all points
of the dispersion curve.
L/W | Length to width ratio of flow. Length is the total
flow travel in the baffled channel divided by the
width of the channel.
Main Menu

## Reference
References
| 1. | Marske, M. Donald & Boyle, D. Jerry. Chlorine Contact Chamber Design - A Field Evaluation.
Water and Sewage Works, 120:1:70 (Jan. 1973).
| 2. | Bishop, M. Mark; Morgan, M; Cornwell, Brendon & Jamison, K. Donald. Improving the Disinfection
Detention Time of a Water Plant Clearwell. Jour. AWWA, 85:3:68 (March 1993).
| 3. | Schott, J. Guy & Rezvani, R. Ali. Department of Health Services,
Drinking Water Field Operations Branch, Santa Rosa, CA.
Millview County Water District, Water Treatment Plant Tracer Study, (February 1996).
| 4. | California Cities Water Company, Sonoma Water Treatment Plant Tracer Study, (1996).
| 5. | Schott, J. Guy & Rezvani, R. Ali. Department of Health Services,
Drinking Water Field Operations Branch, Santa Rosa, CA.
City of Cloverdale, Water Treatment Plant Tracer Study, (August 1996).
| 6. | Montgomery Watson. Stockton East Water District Tracer Study, (September 1997).
| 7. | Schott, J. Guy; Zensius, David & Crevistion, Stacy. Department of Health Services,
Drinking Water Field Operations Branch, Santa Rosa, CA.
City of American Canyon Tracer Study, (October 1997).
| 8. | Fleege, Niles. City of Fairfield Water Treatment Plant
Tracer Study, (1997).
| 9. | Schott, J. Guy & Lambeth, Debra. Department of Health Services,
Drinking Water Field Operations Branch, Santa Rosa, CA.
California Cities Water Company, Sonoma Water Treatment Plant Tracer Study, (November 1997).
| 10. | City of San Diego. Clearwell Tracer Study for the Alvarado, Otay and Miramar
Water Treatment Plants, (November 1997).
| 11. | Schott, J. Guy & Rezvani, R. Ali. Department of Health Services,
Drinking Water Field Operations Branch, Santa Rosa, CA.
Konocti Harbor Resort & Spa, Water Treatment Plant Tracer Study, (October 1998).
| 12. | Carollo Engineers. Sweetwater Authority, Robert Perdue WTP Clear Well
Tracer Study, (January 1999).
| 13. | Schott, J. Guy; Rezvani, R. Ali & Oakley, Janice. Department of Health Services,
Drinking Water Field Operations Branch, Santa Rosa, CA.
City of Napa, Hennessey Water Treatment Plant Tracer Study, (July 1999).
| 14. | Schott, J. Guy; Gjestland, Wendy & Watada, Marianne. Department of Health Services,
Drinking Water Field Operations Branch, Santa Rosa, CA.
Veterans Home of California Tracer Study, (September 2001).
| 15. | Schott, J. Guy; Gjestland, Wendy & Burton, H. Bruce. Department of Health Services,
Drinking Water Field Operations Branch, Santa Rosa, CA.
Murphys Sanitary District Tracer Study, (January 30, 2003).
| 16. | Schott, J. Guy, Watada, Marianne & Carter, Chris. Department of Health Services,
Drinking Water Field Operations Branch, Santa Rosa, CA.
Sereno Del Mar Water Treatment Plant Tracer Study, (September 11, 2003).
4,800 Gallon Clearwell Tracer Study
` | 17. | Kern County Water Agency. Clearwell Tracer Study For Impovement District No. 4
Henry C. Garnett Water Purification Plant, (March 17 & July 21, 2004).
| 18. | Western Hills Water District. Diablo Grande Water Supply and
Treatment Facilities Tracer Study, (March 8 and June 8 & 9, 2005).
| 19. | Hagen Enginering International, Inc.,
City of Clovis Public Utilites Department, (April 7, 2005).
| 20. | Schott, J. Guy & Burton, H. Bruce. Department of Health Services,
Drinking Water Field Operations Branch, Santa Rosa, CA.
Robert Moorhead & Glenn Knapp, City of Fresno, CA.
City of Fresno Ozone Tracer Study, (October 20 & 21, 2005).
| 21. | Seldon, Brenda & Tuolumne Utilities District Staff.
Sonora, CA
Tuolumne Utilities District Tracer Study, (May 23, 2006).
| 22. | Schott, J. Guy, Little, Amy & Frederich, Michelle. Department of Health Services,
Drinking Water Field Operations Branch, Santa Rosa, CA.
Melluish, Robert, Brooktrails Township CSD Tracer Study, (November 1, 2006).
50,000 & 160,000 Gallon Clearwells Tracer Study
| 23. | Black & Veatch
3 MG Clearwell Tracer Study
Northwest Bakersfield Water Treatment Plant, (September 11, 2007).
| 24. | Schott, J. Guy & Kroll, Wendy Jo. California Department of Public of Health,
Drinking Water Field Operations Branch, Santa Rosa, CA.
Jamison, Alan, City of Ukiah Tracer Study, (October 10, 2007).
119,000 Gallon Clearwell (at 10-ft level) Tracer Study
| 25. | Schott, J. Guy & Amy Little. California Department of Public of Health,
Drinking Water Field Operations Branch, Santa Rosa, CA.
Berryessa Pines Tracer Study, (October 19, 2007).
13,790 Gallon Clearwell Tracer Study
| 26. | HDR. City of Yuba City Tracer Study, (November 20, 2007).
4 MG Clearwell Tracer Study
| 27. | Schott, J. Guy, Bruce Burton & Reese Crenshaw. California Department of Public of Health,
Drinking Water Field Operations Branch, Santa Rosa, CA.
City of Yuba City Tracer Study, (February 26 & October 19, 2008).
4 MG Clearwell Tracer Study
| 28. | HDR. Stockton East Water District Tracer Study, (June 2008 Report).
10.5 MG Clearwell Tracer Study
| 29. | Schott, J. Guy. California Department of Public of Health,
Drinking Water Field Operations Branch, Santa Rosa, CA.
Five Points Tracer Studies, (November 19-21, 2008).
| 30. | WQTS. R.E. Badger Water Filtration Plant Tracer Study, (June 29 2012 Report).
12 MG Clearwell Tracer Study
| 31. | Carollo Engineers. City of Lodi 3.0 MG Clearwell Tracer Study, (October 2013 Report).
| 32. | Black & Veatch Corporation. SEWD - WTP Clearwells in Series Tracer Study,
(May 1, 2014, June 24, 2014, September 9, 2014).
| 33. | Schott, J. Guy. State Water Resources Control Board
Division of Drinking Water, Santa Rosa, CA.
Howell Moutain MWC Tracer Study, (July 7, 14, 23 & 28, Sept 29 and Oct 13, 2015).
500,000 Gallon Clearwell Tracer Study
| 34. | Schott, J. Guy. State Water Resources Control Board, Eval Luu (intern) & Hector Cazares
Division of Drinking Water, Santa Rosa, CA.
Lake County CSA 2 - Spring Valley Tracer Study, (August 13 & 25, 2015).
384,900 Gallon Clearwell Tracer Study - Modified Step-Dose
| 35. | Schott, J. Guy. & Stufkosky, Karen, State Water Resources Control Board
Division of Drinking Water, Santa Rosa, CA.
Buckingham Water District (Lake County)- Tracer Study, (Feb 10, 2016 & May 8, 2017).
200,000 Gallon Single Baffled Clearwell Tracer Study - Modified Step-Dose
| 36. | Schott, J. Guy. State Water Resources Control Board
Division of Drinking Water, Santa Rosa, CA.
City of Stockton (Lodi Membrane Plant)- Tracer Study, (Feb 22 & 23, 2016).
48,540 Gallon Ozone Pipeline Tracer Study - Modified Step-Dose
| 37. | Schott, J. Guy. State Water Resources Control Board
Division of Drinking Water, Santa Rosa, CA.
Harris Farms/Horse Barn Tracer Study, (April 10, 2016).
274,700 Gallon Operating Level Clearwell Tracer Study
| 38. | Schott, J. Guy. & Stufkosky, Karen, State Water Resources Control Board
Division of Drinking Water, Santa Rosa, CA.
Airport-Larkfield-Wiliup Sanitation Tracer Study, Sonoma County (August 23, 2016).
Serpentine Chlorine Contact Basin for determining Modal Contact Time.
Tracer Study - Sludge-Dose
| 39. | Schott, J. Guy. & Little, Amy, State Water Resources Control Board
Division of Drinking Water, Santa Rosa, CA.
City of Fairfield Tracer Study, Solano County (May 8, 2017).
Tracer Study - Step-Dose
| 40. | Schott, J. Guy. & Little, Amy, State Water Resources Control Board
Division of Drinking Water, Santa Rosa, CA.
Gibson Canyon Tracer Study, Solano County (May 8, 2017).
Tracer Study - Modified Step-Dose
| 41. | Schott, J. Guy. & Kent, Aaron, State Water Resources Control Board
Division of Drinking Water, Santa Rosa, CA.
Gualala CSD Tracer Study, Sonoma County (May 15 & July 20, 2017).
Tracer Study - Slug-Dose
| 42. | Schott, J. Guy., State Water Resources Control Board
Division of Drinking Water, Santa Rosa, CA.
Gualala CSD Tracer Study, Sonoma County (August 9, 2017).
Tracer Study - Slug-Dose
Main Menu

## Data (hidden)
[14 empty] | Excludes | [5 empty] | Excludes
| T10/T | [11 empty] | All | M&B | Rectangle Tanks |  | Over and under Tanks |  | L:W | M&B, Circular Tanks
L/W | Bishop's Study | Santa Rosa | City of Fairfield | Marske & Boyle's Study | SPH | Carollo | City of San Diego | Kern CWA | HEI | REB | DJWWTP | L:W | t10/T | t10/T | L:W | t10/T | L:W | t10/T |  | t10/T | L/W | Bishop's Study
3 |  |  |  | 0.24 | [7 empty] | 3 | 0.24 |  | 3 |  | 3 |  | 3 |  | 3
4.4 | [11 empty] | 4.4 |  |  | 4.4 |  | 4.4 | 0.56 | 4.4
4.4 | [11 empty] | 4.4 |  |  | 4.4 |  | 4.4 | 0.62 | 4.4
6.9 | 0.27 | [10 empty] | 6.9 | 0.27 | 0.27 | 7.4 | 0.3 | 7.4 |  | 6.9 | 0.27 | 7.4 | 0.3
7.5 |  |  |  | 0.4 | [7 empty] | 7.5 | 0.4 |  | 7.5 |  | 7.5 |  | 7.5 |  | 7.5
8 | [11 empty] | 8 |  |  | 8 |  | 8 | 0.63 | 8
9.3 |  | 0.31 | [9 empty] | 9.3 | 0.31 | 0.31 | 9.3 | 0.31 | 9.3 |  | 9.3 |  | 9.3
10.35 | [11 empty] | 10.35 |  |  | 10.4 |  | 10.4 |  | 10.35
11 |  | 0.37 | [9 empty] | 11 | 0.37 | 0.37 | 11 |  | 11 |  | 11 | 0.37
11.5 | [7 empty] | 0.35 |  |  |  | 11.5 | 0.35 | 0.35 | 11.5 |  | 11.5 |  | 11.5 | 0.35
11.7 |  | 0.39 | [9 empty] | 11.7 | 0.39 | 0.39 | 11.7 |  | 11.7 |  | 11.7 | 0.39
12.5 |  |  |  | 0.51 | [7 empty] | 12.5 | 0.51 |  | 12.5 | 0.51 | 12.5 |  | 12.5 |  | 12.5
16.5 |  | 0.39 | [9 empty] | 16.5 | 0.39 | 0.39 | 16.5 | 0.39 | 16.5 |  | 16.5 |  | 16.5
16.6 | [8 empty] | 0.45 |  |  | 16.6 | 0.45 | 0.45 | 16.6 |  | 16.6 |  | 16.6 | 0.45
16.6 |  | 0.5 | [9 empty] | 16.6 | 0.5 | 0.5 | 16.6 |  | 16.6 |  | 16.6 | 0.5
16.7 | [11 empty] | 16.7 |  |  | 16.7 |  | 16.7 |  | 16.7 |  | 16.7 | 0.61
16.8 | [11 empty] | 16.8 |  |  | 16.8 |  | 16.8 | 0.75 | 16.8
16.8 | [11 empty] | 16.8 |  |  | 16.8 |  | 16.8 | 0.82 | 16.8
20 |  |  |  |  | 0.44 | [6 empty] | 20 | 0.44 | 0.44 | 20 |  | 20 |  | 20 | 0.44 | 20
21 | [11 empty] | 21 |  |  | 21 |  |  |  | 21
21 | [10 empty] | 0.59 | 21 | 0.59 | 0.59 | 21 | 0.59 |  |  | 21 |  | 21.7
21 | [10 empty] | 0.53 | 21 | 0.53 | 0.53 | 21 | 0.53 |  |  | 21 |  | 23.5
21 | [10 empty] | 0.66 | 21 | 0.66 | 0.66 | 21 | 0.66 |  |  | 21 |  | 24.4
21.7 |  |  |  | 0.55 | [7 empty] | 21.7 | 0.55 | 0.55 | 21.7 | 0.55 |  |  | 21.7 |  | 24.5
23.5 | [11 empty] | 23.5 |  |  | 23.5 |  |  |  | 23.5
24.4 |  |  |  | 0.61 | [7 empty] | 24.4 | 0.61 |  | 24.4 | 0.61 |  |  | 24.4
24.5 | [5 empty] | 0.59 | [5 empty] | 24.5 | 0.59 | 0.59 | 24.5 | 0.59 |  |  | 24.5
34 |  | 0.5 | [9 empty] | 34 | 0.5 | 0.5 | 34 |  |  |  | 34 | 0.5 | 37.7
37.6 | [7 empty] | 0.55 |  |  |  | 37.6 | 0.55 | 0.55 | 37.6 | 0.55 |  |  | 37.6 |  | 46 | 0.64
37.6 | [7 empty] | 0.64 |  |  |  | 37.6 | 0.64 | 0.64 | 37.6 | 0.64 |  |  | 37.6 |  | 56
37.7 | [6 empty] | 0.52 |  |  |  |  | 37.7 | 0.52 | 0.52 |  |  |  |  | 37.7 | 0.52 | 70
46 | [11 empty] | 46 |  |  | 46 |  |  |  | 46 |  | 70
56 |  |  | 0.73 | [8 empty] | 56 | 0.73 | 0.73 | 56 | 0.73 |  |  | 56 |  | 70
70 |  |  |  | 0.57 | [7 empty] | 70 | 0.57 |  | 70 | 0.57 |  |  | 70
70 |  |  |  | 0.63 | [7 empty] | 70 | 0.63 |  | 70 | 0.63 |  |  | 70 |  | 81
70 | [9 empty] | 0.73 |  | 70 | 0.73 | 0.73 | 70 | 0.73 |  |  | 70
76 |  | 0.7 | [9 empty] | 76 | 0.7 | 0.7 | 76 | 0.7 |  |  | 76
81 |  | 0.78 | [9 empty] | 81 | 0.78 | 0.78 | 81 |  |  |  | 81 | 0.78
L/W | Vel, ft/min | (vel*L:W)0.5 | BF | log(vel*L:W)
6.9 | 0.84 | 2.4075 | 0.27 | 0.76313
9 | 1.6 | 3.7947 | 0.31 | 1.1584
11 | 0.74 | 2.8531 | 0.37 | 0.91062
11.5 | 2.6 | 5.4681 | 0.35 | 1.4757
16.5 | 0.84 | 3.7229 | 0.39 | 1.1418
8 | 0.91 | 2.6981 | 0.42 | 0.86213
16.6 | 1.9 | 5.616 | 0.45 | 1.4989
8 | 1.87 | 3.8678 | 0.49 | 1.1749
16 | 1.36 | 4.6648 | 0.5 | 1.3377
34.1 | 1.19 | 6.3702 | 0.5 | 1.6083
37 | 8.08 | 17.2905 | 0.52 | 2.4756
4.4 | 10 | 6.6332 | 0.56 | 1.6435
8 | 2.1 | 4.0988 | 0.57 | 1.2253
21 | 3.58 | 8.6706 | 0.59 | 1.8761
21 | 5.13 | 10.3793 | 0.53 | 2.0323
21 | 4.65 | 9.8818 | 0.66 | 1.9897
25 | 5.2 | 11.4018 | 0.59 | 2.1139
4.4 | 12.8 | 7.5047 | 0.62 | 1.7507
8 | 12.8 | 10.1193 | 0.63 | 2.0103
76 | 6.3 | 21.8815 | 0.7 | 2.6802
24 | 2.8 | 8.1976 | 0.7 | 1.8274
70 | 1.79 | 11.1937 | 0.73 | 2.098
16.8 | 10 | 12.9615 | 0.75 | 2.2253
81 | 4.15 | 18.3344 | 0.78 | 2.5265
36 | 13.7 | 22.2081 | 0.8 | 2.693
16.8 | 12.8 | 14.6642 | 0.82 | 2.3325
76 | 0.264 | 4.4793 | 0.82 | 1.3024
192 | 0.264 | 7.1196 | 0.82 | 1.7049
114 | 0.264 | 5.486 | 0.84 | 1.4785
153 | 0.264 | 6.3555 | 0.85 | 1.6063
422 | 0.264 | 10.555 | 0.96 | 2.0469
12 | 0.125 | 1.2247 | 0.39 | 0.17609
8 | 0.91 | 2.6981 | 0.42 | 0.86213
8 | 1.87 | 3.8678 | 0.49 | 1.1749
8 | 2.1 | 4.0988 | 0.57 | 1.2253