## Read me
Please read the notes/instructions before you proceed!
Please find more instrucitons on individual worksheets.
How to name Excel spreadsheet
Please name this spreadsheet as
"XXXX nutrient 13267 study data_updated Month-/Day-Year"
(XXXX - Facility/Discharger name)
Agency Name, contact information; sampling dates
Only enter agency name and contact information in the worksheet "Inf Conc."; they will be automatically populated in other worksheets.
Only enter season/quarter/sampling dates in "Inf Conc.", "Eff Conc." worksheets; they will be automatically populated in load/QA/QC worksheets.
How to report non-detected (ND) results
For NDs, i.e., <MDL, report MDL in the cell, insert a comment
(Select the cell, right click the mouse, choose "insert comment", put "ND, report MDL" in the comment box)
How to report DNQ or J flagged results
Report the DNQ value in the cell, insert a comment
(Select the cell, right click the mouse, choose " insert comment", put "DNQ" in the comment box)
Do not put any text like "ND", "MDL", "DNQ" in front of the number.
How to report a missed result
If a required sampling result is missing (failed to sample, sampling error, lab error, etc.), add a note at the end of that worksheet.
Report this missed sample incident in the transmittal email/letter.
Do not put "NA" or any text in the cell for that parameter.
How to save as CSV (comma separated values) files:
In addition to submitting this MS Excel Worksheet file, please also submit CSV (comma deliminted) files of each worksheet (multiple files).
To generate CSV files from the Excel Worksheet file, open one worksheet at a time, go to "File" - "save as" - name the CSV file
such as "XXXX Inf conc", "XXXX eff conc", etc. where XXXX is the Facility/Discharger name.
choose "CSV" (comma delimited) in the "save as type" drop down menu, and click save.
You will need to save each worksheet as a separate CSV file.
How to copy data from another Excel Spreadsheet
If copying data from another worksheet, only paste the values to this worksheet; do not copy the format.
Glossary of Abbreviations
TDN | Total Dissolved Nitrogen
TKN | Total Kjedahl Nitrogen
SKN | Soluble Kjedahl Nitrogen
NH3 | Ammonia
NO3 | Nitrate
NO2 | Nitrite
TP | Total Phosphorous
TDP | Total Dissolved Phosphorous
DRP | Dissolved Reactive Phosphorous
TSS | Total Suspended Solids

## Requirement Summary
Sausalito - Marin City Sanitary District
Facility Category |  | Report Due Dates
Major (flow >=5 mgd or flow <5 mgd) or Minor |  | Reporting Period | Report Due Date
Year-round or Seasonal |  | July - September 2012 | 2012-10-30
Is this one of the largest five POTWs for effluent urea monitoring (Y/N)? |  | October - December 2012 | 2013-01-30
|  | January - March 2013 | 2013-04-30
|  | April - June 2013 | 7/30/2013, may combine with the interim report
|  | Interim Report | 2013-07-31
|  | July - September 2013 | 2013-10-30
|  | October - December 2013 | 2014-01-30
|  | January - March 2014 | 2014-04-30
|  | April - June 2014 | 7/30/2014, may combine with the final report
|  | Final Report | 2014-07-31
Find your facility's cateogory, then look below for applicable requirements.
Minimum Influent Sampling Requirements for All Facilities
Once during wet (discharge) season; once during dry (non-discharge) season
Major (Flow<5.0 mgd) | Year-round | Seasonal
Influent | Once during wet season, once during dry season. | Once during wet season, once during dry season.
Routine Effluent | Once per month | Once per month during discharge season, once during non-discharge season.
Effluent Peak flow monitoring | Two times each wet season | Not required
Study duraiton | Two years | Two years

## Inf Conc
Influent Concentrations (mg/l)
Sausalito - Marin City Sanitary District
Omar Arias-Montez, Laboratory Director, 415-331-4716, omar@smcsd.net
Season | Date | Flow (MGD) |  | TN (mg/L) | TKN (mg/L) | NO3** (mg/L) | NO2** (mg/L) | Total NH3 (mg/L) | TP (mg/L) | DRP (mg/L) | TSS (mg/L)
| (mm/dd/yyyy) | Ave Daily | Peak | TKN+NO3+NO2 | [5 empty] | Grab or composite
Dry 2012 | 2012-07-17 | 1.422 | 2.67 | 41.79 | 41 | 0.17 | 0.62 | 27 | 5.3 | 2.5 | 286
Dry 2012 | 2012-08-07 | 1.348 | 3.87 | 50.44 | 50 | 0.11 | 0.33 | 31 | 2.1 | 2.9 | 257
Dry 2012 | 2012-09-08 | 1.343 | 2.67 | 45.281 | 45 | 0.071 | 0.21 | 29 | 4.9 | 4.1 | 326
Dry 2012 | 2012-10-12 | 1.451 | 2.11 | 32.88 | 32 | 0.4 | 0.48 | 28 | 2.6 | 2.6
Wet 2012/13 | 2013-01-14 | 1.507 | 3.96 | 26.7 | 24 | 1.3 | 1.4 | 22 | 4.3 | 1.9 | 291
Dry 2013 | 2013-05-07 | 1.294 | 2.6 | 49.88 | 49 | 0.3 | 0.58 | 28 | 6.3 | 3.2 | 361
0
0
0
0
0
0
0
0
0
0
0
0
0
0
THINGS TO DO
Enter agency name, contact information.
Only enter numbers in the cells for concentrations; or leave blank if no data (do not enter "NA")
Delete red striked-through numbers under TN/TKN after all the data for that date are entered; leave the cell blank.
THINGS NOT TO DO
Do not report zero for non-detected values or DNQ(J) values;
Do not put text before the number to indicate it is ND or DNQ.
Do not report combined result for NO3+ NO2 under both parameters (see footnote ** below)
Seasons are defined as followed:
Dry 2012: July - October 2012
Wet 2012/13 - November 2012 - April 2013
Dry 2013: May - October 2013
Wet 2013/14 - November 2013 - April 2014
Dry 2014: May - June 2014. Influent sampling is optional during this period for those who have complete required influent sampling;
For those who missed a prior dry weather influent sampling, sampling is required to make up the missed sample during this period.
Cells are conditionally formatted as explained below:
1. when a date is entered, the row is highlighted in orange;
2. When a text is entered, the cell is shaded in blue; remove the text ("ND", "DNQ", etc.), report a number.
3. If TKN or both NO3/NO2 conc. is missing, the calculated TN result is shown in red strike-through number.
That means this TN result is not complete, deleted that TN, leave the cell blank.
Footnotes for Table
** Dischargers may analzye NO3+NO2 combined for influent.
Report the combined result under NO3, and add a comment in the NO3 or NO2 cell, indicating the result is for both parameters.
*** *Collect DRP sample as a grab or composite in accordance with your agency's Sample Analysis Plan
How to report non-detected (ND) /DNQ results
For NDs, i.e., <MDL, report MDL in the cell, insert a comment
For DNQ or J flagged value, report the estimated value, insert a comment
(Select the cell, right click the mouse, choose " insert comment", type "ND" or "DNQ" in the comment box)

## Inf Load
Influent Loads (Kg/d) [mg/l X MGD X 3.78 = Kg/d]
Sausalito - Marin City Sanitary District
Omar Arias-Montez, Laboratory Director, 415-331-4716, omar@smcsd.net
Season | Date | Flow (MGD) |  | TN (kg/d) | TKN (kg/d) | NO3 (kg/d) | NO2 (kg/d) | Total NH3 (kg/d) | TP (kg/d) | DRP (kg/d) | TSS (kg/d)
| (mm/dd/yyyy) | Ave Daily | Peak | [6 empty] | Use Max Flow if sample type is grab
Dry 2012 | 2012-07-17 | 1.422 | 2.67 | 224.6279 | 220.3816 | 0.91378 | 3.3326 | 145.1293 | 28.4883 | 25.2315 | 1537.2958
Dry 2012 | 2012-08-07 | 1.348 | 3.87 | 257.014 | 254.772 | 0.5605 | 1.6815 | 157.9586 | 10.7004 | 42.4229 | 1309.5281
Dry 2012 | 2012-09-08 | 1.343 | 2.67 | 229.8708 | 228.4443 | 0.36043 | 1.0661 | 147.2197 | 24.875 | 41.3797 | 1654.952
Dry 2012 | 2012-10-12 | 1.451 | 2.11 | 180.3396 | 175.513 | 2.1939 | 2.6327 | 153.5738 | 14.2604 | 20.7371
Wet 2012/13 | 2013-01-14 | 1.507 | 3.96 | 152.0955 | 136.715 | 7.4054 | 7.975 | 125.3221 | 24.4948 | 28.4407 | 1657.6699
Dry 2013 | 2013-05-07 | 1.294 | 2.6 | 243.979 | 239.6747 | 1.4674 | 2.837 | 136.957 | 30.8153 | 31.4496 | 1765.7665
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
THINGS TO DO
Correct bright yellow highlighted load calulations (0, #VALUE!") by correcting the "Conc" worksheet
Use correct flow for load calculation: for grab sample, use peak flow; for composit sample, use average flow.
Cells are conditionally formatted as explained below:
1. Cells are shaded purple if there is no load calculated for that parameter due to lack of concentration data. No need to do anything if that sampling is not required.
2. Cells are shaded bright yellow if the load is calculated as "0" due to concentration reported as "0", go to 'Conc" worksheet to correct the concentration reported.
3. Cells are shaded bright yellow if concentration is reporetd as a text (such as ND, <MDL, J value), go to "Conc" worksheet to correct the concentration reported.
How to choose correct flow for load calcultion.
Load calculation formulas provided use "avg daily flow" for all parameters, except for "DRP", where peak flow is used.
If DRP is collected as composite, replace "peak flow" with "avg daily flow" in the formula for load calculation.
If other parameters are grabs according to your sampling plan; replace "avg daily flow" with "peak flow" in load calculation for that parameter.

## Eff Conc.
Effluent Concentrations (mg/l)
Sausalito - Marin City Sanitary District
Omar Arias-Montez, Laboratory Director, 415-331-4716, omar@smcsd.net
Quarter of Year (Q1, Q2, Q3, Q4 YYYY) | Date | Peak Flow Event (Y/N) | Flow (MGD) |  | TN (mg/L) | TDN (mg/L) | TKN (mg/L) | SKN (mg/L) | NO3 (mg/L) | NO2 (mg/L) | Total NH3 (mg/L) | Urea* (mg/L) | TP (mg/L) | TDP (mg/L) | DRP** (mg/L) | pH (s.u.) |  | Temp (oC) |  | TSS (mg/L)
| (mm/dd/yyyy) |  | Ave Daily | Peak | TKN+NO3+NO2 | SKN+NO3+NO2 | [8 empty] | Grab or composite | Min | Max | Min | Max
Q3 2012 | 2012-07-17 | N | 1.32 | 2.39 | 32.4 | 31.4 | 13 | 12 | 18 | 1.4 | 11 |  | 4.2 | 4.1 | 4 | 6.89 | 6.89 | 20.6 | 20.6 | 15
Q3 2012 | 2012-08-07 | N | 1.22 | 3.33 | 30.4 | 29.4 | 12 | 11 | 17 | 1.4 | 10 |  | 6.1 | 6 | 5 | 6.92 | 6.92 | 21.3 | 21.3 | 11
Q3 2012 | 2012-09-05 | N | 1.22 | 2.25 | 14.8 | 13.8 | 12 | 11 | 1.2 | 1.6 | 11 |  | 5.4 | 5 | 4.7 | 6.97 | 6.97 | 21.3 | 21.3 | 20
Q4 2012 | 2012-10-12 | N | 1.4 | 2.39 | 32.7 | 30.7 | 18 | 16 | 13 | 1.7 | 15 |  | 5.3 | 4.7 | 4.7 | 6.68 | 6.68 | 21.1 | 21.12 | 6
Q4 2012 | 2012-11-09 | N | 1.63 | 4.07 | 29.28 | 28.38 | 9.4 | 8.5 | 19 | 0.88 | 8 |  | 4.5 | 4.2 | 4.1 | 6.98 | 6.98 | 19.8 | 19.8 | 20
Q4 2012 | 2012-12-03 | Y | 5.18 | 10.4 | 12.078 | 9.478 | 5.6 | 3 | 6.4 | 0.078 | 1.7 |  | 1.5 | 1.1 | 1.1 | 7.12 | 7.12 | 17.5 | 17.5 | 58
Q4 2012 | 2012-12-31 | N | 1.85 | 3.21 | 16.76 | 16.96 | 5.5 | 5.7 | 11 | 0.26 | 4.6 |  | 2.1 | 1.6 | 1.4 | 6.89 | 6.89 | 16.2 | 16.2 | 13
Q1 2013 | 2013-01-14 | N | 2.82 | 1.32 | 15.02 | 14.02 | 13 | 12 | 1.6 | 0.42 | 11 |  | 3.1 | 3 | 3.1 | 7.18 | 7.18 | 15.1 | 15.1 | 38
Q1 2013 | 2013-03-22 | N | 1.31 | 2.85 | 29.71 | 26.91 | 12 | 9.2 | 17 | 0.71 | 10 |  | 4.3 | 3.8 | 3.3 | 7.14 | 7.14 | 17.7 | 17.7 | 15
Q1 2013 | 2013-03-31 | N | 1.61 | 2.81 | 27.89 | 25.49 | 10 | 7.6 | 17 | 0.89 | 8.3 |  | 4.9 | 4.4 | 4 | 6.96 | 6.96 | 18.5 | 18.5 | 23
Q2 2013 | 2013-04-09 | N | 1.362 | 2.25 | 26.57 | 24.97 | 9.6 | 8 | 16 | 0.97 | 7.2 |  | 4 | 3.6 | 3.4 | 7.19 | 7.19 | 18.2 | 18.2 | 18
Q2 2013 | 2013-05-07 | N | 1.265 | 2.32 | 32.6 | 32.6 | 16 | 16 | 15 | 1.6 | 14 |  | 4.8 | 4.3 | 4.1 | 7.16 | 7.16 | 20.4 | 20.4 | 26
Q3 2013 | 2013-06-04 | N | 1.211 | 3.72 | 44.5 | 33.5 | 27 | 16 | 15 | 2.5 | 14 |  | 5.4 | 4.7 | 4.8 | 7.16 | 7.16 | 20.7 | 20.7 | 24
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
SMCSD Note: A sample was not taken in February 2013 due to an error in sample hold time. Two samples were run in March to make up for the missing sample.
THINGS TO DO
Only enter numbers in the cells for concentrations; or leave blank if no data (do not enter "NA")
Delete red striked-through numbers under TN/TKN after all the data for that date are entered; leave the cell blank.
THINGS NOT TO DO
Do not report zero for non-detected values or DNQ(J) values;
Do not put text before the number to indicate it is ND or DNQ.
Do not report combined result for NO3+ NO2 under both parameters (see footnote ** below)
Quarter of Year definition
Q3 2012 - July - September 2012
Q4 2012: October - December 2012
Q1 2013: January - March 2013
Q2 2013: April - June 2013
Q3 2013: July - September 2013
Q4 2013: October - December 2013
Q1 2014: January - March 2014
Q2 2014: April - June 2014
For seasonal dischargers, effluent sampling is not required in May/June 2014. However, if a prior dry weather sampling event is not conducted,
then the discharger shall make up the missed sampling event during May-June 2014; unless other arrangements have been made.
Cells are conditionally formatted as explained below:
1. when a date is entered, the row is highlighted in orange;
2. When a text is entered, the cell is shaded in blue; remove the text ("ND", "DNQ", etc.), report a number.
3. If TKN or both NO3/NO2 conc. is missing, the calculated TN result is shown in red strike-through number.
That means this TN result is not complete, deleted that TN, leave the cell blank.
Footnotes for Table
* Urea monitoring is only required for the five largest POTWs: CCCSD, EBDA, EBMUD, SF Southeast, SJSC
**Collect DRP sample as a grab or composite in accordance with your agency's Sample Analysis Plan
How to report non-detected (ND) /DNQ results
For NDs, i.e., <MDL, report MDL in the cell, insert a comment
For DNQ or J flagged value, report the estimated value, insert a comment
(Select the cell, right click the mouse, choose " insert comment", type "ND" or "DNQ" in the comment box)

## Eff Loads
Effluent Loads (Kg/d) [mg/l X MGD X 3.78 = Kg/d]
Sausalito - Marin City Sanitary District
Omar Arias-Montez, Laboratory Director, 415-331-4716, omar@smcsd.net
Quarter of Year | Date | Peak Flow Event (Y/N) | Flow (MGD) |  | TN (kg/d) | TDN (kg/d) | TKN (kg/d) | SKN (kg/d) | NO3 (kg/d) | NO2 (kg/d) | Total NH3 (kg/d) | Urea (kg/d) | TP (kg/d) | TDP (kg/d) | DRP (kg/d) | TSS (kg/d)
| (mm/dd/yyyy) |  | Ave Daily | Peak | [10 empty] | Use Max Flow if sample type is Grab
Q3 2012 | 2012-07-17 | N | 1.32 | 2.39 | 161.663 | 156.6734 | 64.8648 | 59.8752 | 89.8128 | 6.9854 | 54.8856 |  | 20.9563 | 20.4574 | 36.1368 | 74.844
Q3 2012 | 2012-08-07 | N | 1.22 | 3.33 | 140.1926 | 135.581 | 55.3392 | 50.7276 | 78.3972 | 6.4562 | 46.116 |  | 28.1308 | 27.6696 | 62.937 | 50.7276
Q3 2012 | 2012-09-05 | N | 1.22 | 2.25 | 68.2517 | 63.6401 | 55.3392 | 50.7276 | 5.5339 | 7.3786 | 50.7276 |  | 24.9026 | 23.058 | 39.9735 | 92.232
Q4 2012 | 2012-10-12 | N | 1.4 | 2.39 | 173.0484 | 162.4644 | 95.256 | 84.672 | 68.796 | 8.9964 | 79.38 |  | 28.0476 | 24.8724 | 42.4607 | 31.752
Q4 2012 | 2012-11-09 | N | 1.63 | 4.07 | 180.4058 | 174.8605 | 57.9172 | 52.3719 | 117.0666 | 5.422 | 49.2912 |  | 27.7263 | 25.8779 | 63.0769 | 123.228
Q4 2012 | 2012-12-03 | Y | 5.18 | 10.4 | 236.4921 | 185.583 | 109.6502 | 58.7412 | 125.3146 | 1.5273 | 33.2867 |  | 29.3706 | 21.5384 | 43.2432 | 1135.6632
Q4 2012 | 2012-12-31 | N | 1.85 | 3.21 | 117.2027 | 118.6013 | 38.4615 | 39.8601 | 76.923 | 1.8182 | 32.1678 |  | 14.6853 | 11.1888 | 16.9873 | 90.909
Q1 2013 | 2013-01-14 | N | 2.82 | 1.32 | 160.1072 | 149.4476 | 138.5748 | 127.9152 | 17.0554 | 4.477 | 117.2556 |  | 33.0448 | 31.9788 | 15.4678 | 405.0648
Q1 2013 | 2013-03-22 | N | 1.31 | 2.85 | 147.118 | 133.2529 | 59.4216 | 45.5566 | 84.1806 | 3.5158 | 49.518 |  | 21.2927 | 18.8168 | 35.5509 | 74.277
Q1 2013 | 2013-03-31 | N | 1.61 | 2.81 | 169.733 | 155.127 | 60.858 | 46.2521 | 103.4586 | 5.4164 | 50.5121 |  | 29.8204 | 26.7775 | 42.4872 | 139.9734
Q2 2013 | 2013-04-09 | N | 1.362 | 2.25 | 136.7919 | 128.5545 | 49.4243 | 41.1869 | 82.3738 | 4.9939 | 37.0682 |  | 20.5934 | 18.5341 | 28.917 | 92.6705
Q2 2013 | 2013-05-07 | N | 1.265 | 2.32 | 155.8834 | 155.8834 | 76.5072 | 76.5072 | 71.7255 | 7.6507 | 66.9438 |  | 22.9522 | 20.5613 | 35.9554 | 124.3242
Q3 2013 | 2013-06-04 | N | 1.211 | 3.72 | 203.7023 | 153.3489 | 123.5947 | 73.2413 | 68.6637 | 11.444 | 64.0861 |  | 24.7189 | 21.5146 | 67.4957 | 109.8619
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
THINGS TO DO
Correct bright yellow highlighted load calulations (0, #VALUE!") by correcting the "Conc" worksheet
Use correct flow for load calculation: for grab sample, use peak flow; for composit sample, use average flow.
Cells are conditionally formatted as explained below:
1. Cells are shaded purple if there is no load calculated for that parameter due to lack of concentration data. No need to do anything if that sampling is not required.
2. Cells are shaded bright yellow if the load is calculated as "0" due to concentration reported as "0", go to 'Conc" worksheet to correct the concentration reported.
3. Cells are shaded bright yellow if concentration is reporetd as a text (such as ND, <MDL, J value), go to "Conc" worksheet to correct the concentration reported.
How to choose correct flow for load calcultion.
Load calculation formulas provided use "avg daily flow" for all parameters, except for "DRP", where peak flow is used.
If DRP is collected as composite, replace "peak flow" with "avg daily flow" in the formula for load calculation.
If other parameters are grabs according to your sampling plan; replace "avg daily flow" with "peak flow" in load calculation for that parameter.

## Inf QAQC MLs
Influent MDL / ML (mg/l)
Sausalito - Marin City Sanitary District
Omar Arias-Montez, Laboratory Director, 415-331-4716, omar@smcsd.net
Season | Date | TKN |  | NO3 |  | NO2 |  | Total NH3 |  | TP |  | DRP |  | TSS |  | NO3+NO2
| (mm/dd/yyyy) | MDL | ML | MDL | ML | MDL | ML | MDL | ML | MDL | ML | MDL | ML | MDL | ML | MDL | ML
Dry 2012 | 2012-07-17 | 0.07 | 0.1 | 0.02 | 0.1 | 0.01 | 0.2 | 0.04 | 0.1 | 0.38 | 0.5 | 0.15 | 0.2 | 2 | 6
Dry 2012 | 2012-08-07 | 0.07 | 0.1 | 0.02 | 0.1 | 0.01 | 0.2 | 0.04 | 0.1 | 0.15 | 0.2 | 0.06 | 0.1 | 2 | 3
Dry 2012 | 2012-09-08 | 0.14 | 0.2 | 0.02 | 0.1 | 0.002 | 0.03 | 0.04 | 0.1 | 0.15 | 0.2 | 0.15 | 0.2 | 2 | 3
Dry 2012 | 2012-10-12 | 0.14 | 0.2 | 0.02 | 0.1 | 0.002 | 0.03 | 0.04 | 0.1 | 0.075 | 0.1 | 0.06 | 0.1 | 2 | 3
Wet 2012/13 | 2013-01-14 | 0.07 | 0.1 | 0.02 | 0.1 | 0.02 | 0.3 | 0.04 | 0.1 | 0.075 | 0.1 | 0.06 | 0.1 | 2 | 3
Dry 2013 | 2013-05-07 | 0.07 | 0.1 | 0.02 | 0.1 | 0.02 | 0.3 | 0.04 | 0.1 | 0.075 | 0.1 | 0.06 | 0.1 | 2 | 3
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
Do not enter "Season" or "Date" information on this worksheet. Make changes to the "Inf Conc." worksheet.
This sheet will be automatically updated with the new information.

## Eff QAQC MLs
Effluent MDL / ML (mg/l)
Sausalito - Marin City Sanitary District
Omar Arias-Montez, Laboratory Director, 415-331-4716, omar@smcsd.net
Quarter of Year | Date | TKN |  | SKN |  | NO3 |  | NO2 |  | Total NH3 |  | Urea |  | TP |  | TDP |  | DRP |  | TSS
| (mm/dd/yyyy) | MDL | ML | MDL | ML | MDL | ML | MDL | ML | MDL | ML | MDL | ML | MDL | ML | MDL | ML | MDL | ML | MDL | ML
Q3 2012 | 2012-07-17 | 0.07 | 0.1 | 0.07 | 0.1 | 0.1 | 0.2 | 0.01 | 0.2 | 0.04 | 0.1 |  |  | 0.38 | 0.5 | 0.38 | 0.5 | 0.15 | 0.2 | 2 | 3
Q3 2012 | 2012-08-07 | 0.07 | 0.1 | 0.07 | 0.1 | 0.1 | 0.2 | 0.05 | 0.8 | 0.04 | 0.1 |  |  | 0.07 | 0.1 | 0.07 | 0.1 | 0.15 | 0.2 | 2 | 3
Q3 2012 | 2012-09-05 | 0.07 | 0.1 | 0.07 | 0.1 | 0.02 | 0.1 | 0.01 | 0.2 | 0.04 | 0.1 |  |  | 0.035 | 0.05 | 0.035 | 0.05 | 0.15 | 0.2 | 2 | 3
Q4 2012 | 2012-10-12 | 0.07 | 0.1 | 0.07 | 0.1 | 0.1 | 0.2 | 0.02 | 0.3 | 0.04 | 0.1 |  |  | 0.035 | 0.05 | 0.035 | 0.05 | 0.06 | 0.1 | 1 | 3
Q4 2012 | 2012-11-09 | 0.07 | 0.1 | 0.07 | 0.1 | 0.5 | 1 | 0.004 | 0.06 | 0.04 | 0.1 |  |  | 0.035 | 0.05 | 0.035 | 0.05 | 0.06 | 0.1 | 2 | 3
Q4 2012 | 2012-12-03 | 0.07 | 0.1 | 0.07 | 0.1 | 0.1 | 0.2 | 0.002 | 0.3 | 0.04 | 0.1 |  |  | 0.007 | 0.01 | 0.007 | 0.01 | 0.06 | 0.1 | 2 | 3
Q4 2012 | 2012-12-31 | 0.07 | 0.1 | 0.07 | 0.1 | 0.1 | 0.2 | 0.002 | 0.3 | 0.04 | 0.1 |  |  | 0.007 | 0.01 | 0.007 | 0.01 | 0.06 | 0.1 | 2 | 3
Q1 2013 | 2013-01-14 | 0.07 | 0.1 | 0.07 | 0.1 | 0.02 | 0.1 | 0.002 | 0.03 | 0.04 | 0.1 |  |  | 0.035 | 0.05 | 0.035 | 0.05 | 0.06 | 0.1 | 2 | 3
Q1 2013 | 2013-03-22 | 0.07 | 0.1 | 0.07 | 0.1 | 0.1 | 0.2 | 0.02 | 0.3 | 0.04 | 0.1 |  |  | 0.035 | 0.05 | 0.035 | 0.05 | 0.06 | 0.1 | 2 | 3
Q1 2013 | 2013-03-31 | 0.07 | 0.1 | 0.07 | 0.1 | 0.1 | 0.2 | 0.02 | 0.3 | 0.04 | 0.1 |  |  | 0.035 | 0.05 | 0.035 | 0.05 | 0.06 | 0.1 | 2 | 3
Q2 2013 | 2013-04-09 | 0.07 | 0.1 | 0.07 | 0.1 | 0.1 | 0.2 | 0.02 | 0.3 | 0.04 | 0.1 |  |  | 0.015 | 0.1 | 0.015 | 0.1 | 0.06 | 0.1 | 2 | 3
Q2 2013 | 2013-05-07 | 0.07 | 0.1 | 0.07 | 0.1 | 0.1 | 0.2 | 0.02 | 0.3 | 0.04 | 0.1 |  |  | 0.035 | 0.05 | 0.035 | 0.05 | 0.06 | 0.1 | 2 | 3
Q3 2013 | 2013-06-04 | 0.35 | 0.5 | 0.14 | 0.2 | 0.48 | 1 | 0.02 | 0.3 | 0.04 | 0.1 |  |  | 0.075 | 0.1 | 0.075 | 0.1 | 0.15 | 0.2 | 2 | 3
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
Do not enter "Season" or "Date" information on this worksheet. Make changes to the "Eff Conc." worksheet.
This sheet will be automatically updated with the new information.