## Read me
Please read the notes/instructions before you proceed!
Please find more instrucitons on individual worksheets.
How to name Excel spreadsheet
Please name this spreadsheet as
"XXXX nutrient 13267 study data_updated Month-/Day-Year"
(XXXX - Facility/Discharger name)
Agency Name, contact information; sampling dates
Only enter agency name and contact information in the worksheet "Inf Conc."; they will be automatically populated in other worksheets.
Only enter season/quarter/sampling dates in "Inf Conc.", "Eff Conc." worksheets; they will be automatically populated in load/QA/QC worksheets.
How to report non-detected (ND) results
For NDs, i.e., <MDL, report MDL in the cell, insert a comment
(Select the cell, right click the mouse, choose "insert comment", put "ND, report MDL" in the comment box)
How to report DNQ or J flagged results
Report the DNQ value in the cell, insert a comment
(Select the cell, right click the mouse, choose " insert comment", put "DNQ" in the comment box)
Do not put any text like "ND", "MDL", "DNQ" in front of the number.
How to report a missed result
If a required sampling result is missing (failed to sample, sampling error, lab error, etc.), add a note at the end of that worksheet.
Report this missed sample incident in the transmittal email/letter.
Do not put "NA" or any text in the cell for that parameter.
How to save as CSV (comma separated values) files:
In addition to submitting this MS Excel Worksheet file, please also submit CSV (comma deliminted) files of each worksheet (multiple files).
To generate CSV files from the Excel Worksheet file, open one worksheet at a time, go to "File" - "save as" - name the CSV file
such as "XXXX Inf conc", "XXXX eff conc", etc. where XXXX is the Facility/Discharger name.
choose "CSV" (comma delimited) in the "save as type" drop down menu, and click save.
You will need to save each worksheet as a separate CSV file.
How to copy data from another Excel Spreadsheet
If copying data from another worksheet, only paste the values to this worksheet; do not copy the format.
Glossary of Abbreviations
TDN | Total Dissolved Nitrogen
TKN | Total Kjedahl Nitrogen
SKN | Soluble Kjedahl Nitrogen
NH3 | Ammonia
NO3 | Nitrate
NO2 | Nitrite
TP | Total Phosphorous
TDP | Total Dissolved Phosphorous
DRP | Dissolved Reactive Phosphorous
TSS | Total Suspended Solids

## Requirement Summary
Napa Sanitation District
Facility Category |  | Report Due Dates
Major (flow >=5 mgd or flow <5 mgd) or Minor |  | Reporting Period | Report Due Date
Year-round or Seasonal |  | July - September 2012 | 2012-10-30
Is this one of the largest five POTWs for effluent urea monitoring (Y/N)? |  | October - December 2012 | 2013-01-30
|  | January - March 2013 | 2013-04-30
|  | April - June 2013 | 7/30/2013, may combine with the interim report
|  | Interim Report | 2013-07-31
|  | July - September 2013 | 2013-10-30
|  | October - December 2013 | 2014-01-30
|  | January - March 2014 | 2014-04-30
|  | April - June 2014 | 7/30/2014, may combine with the final report
|  | Final Report | 2014-07-31
Find your facility's cateogory, then look below for applicable requirements.
Minimum Influent Sampling Requirements for All Facilities
Once during wet (discharge) season; once during dry (non-discharge) season
Minimum Effluent Moniotring Requirements
Minor (Flow<1.0 mgd) | Year-round | Seasonal
Influent | Once during wet season, once during dry season. | Once during wet season, once during dry season.
Routine Effluent | Once per month | Once per month during discharge season, once during non-discharge season.
Effluent Peak flow monitoring | Two times each wet season | Not required
Study duraiton | One Year | One year
Major (Flow<5.0 mgd) | Year-round | Seasonal
Influent | Once during wet season, once during dry season. | Once during wet season, once during dry season.
Routine Effluent | Once per month | Once per month during discharge season, once during non-discharge season.
Effluent Peak flow monitoring | Two times each wet season | Not required
Study duraiton | Two years | Two years
Major (Flow>=5.0 mgd) | Year-round | Seasonal
Influent | Once during wet season, once during dry season. | Once during wet season, once during dry season.
Routine Effluent | Two times per month | Two times per month during discharge season, once during non-discharge season.
Effluent Peak flow monitoring | Two times each wet season | Not required
Study duraiton | Two years | Two years
Five Largest POTWs - CCCSD, EBDA, EBMUD, SJSC, SF Southeast
Additional effluent urea monitoring | Once per month for one year

## Inf Conc
Influent Concentrations (mg/l)
Napa Sanitation District
James Keller, Plant Manager, 707-258-6020 x601, Jkeller@napasan.com
Season | Date | Flow (MGD) |  | TN (mg/L) | TKN (mg/L) | NO3** (mg/L) | NO2** (mg/L) | Total NH3 (mg/L) | TP (mg/L) | DRP (mg/L) | TSS (mg/L)
| (mm/dd/yyyy) | Ave Daily | Peak | TKN+NO3+NO2 | [5 empty] | Grab or composite
Q4 2012 | 2012-12-12 | 9.09 | 11.09 | 37.27 | 37.2 | 0.02 | 0.05 | 25.7 | 4.41 | 2.3 | 198
Q4 2012 | 2012-12-19 | 9.06 | 11.19 | 34.04 | 34 | 0.02 | 0.02 | 20.4 | 2.43 | 1.8 | 144
Q4 2013 | 2013-11-07 | 6.051 | 8.86 | 57.21 | 56.9 | 0.02 | 0.29 | 43.3 | 9.6 | 4.44 | 472
Q4 2013 | 2013-11-18 | 6.04 | 8.61 | 63.65 | 63.5 | 0.02 | 0.13 | 34.7 | 7.4 | 4.59 | 328
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
THINGS TO DO
Enter agency name, contact information.
Only enter numbers in the cells for concentrations; or leave blank if no data (do not enter "NA")
Delete red striked-through numbers under TN/TKN after all the data for that date are entered; leave the cell blank.
THINGS NOT TO DO
Do not report zero for non-detected values or DNQ(J) values;
Do not put text before the number to indicate it is ND or DNQ.
Do not report combined result for NO3+ NO2 under both parameters (see footnote ** below)
Seasons are defined as followed:
Dry 2012: July - October 2012
Wet 2012/13 - November 2012 - April 2013
Dry 2013: May - October 2013
Wet 2013/14 - November 2013 - April 2014
Dry 2014: May - June 2014. Influent sampling is optional during this period for those who have complete required influent sampling;
For those who missed a prior dry weather influent sampling, sampling is required to make up the missed sample during this period.
Cells are conditionally formatted as explained below:
1. when a date is entered, the row is highlighted in orange;
2. When a text is entered, the cell is shaded in blue; remove the text ("ND", "DNQ", etc.), report a number.
3. If TKN or both NO3/NO2 conc. is missing, the calculated TN result is shown in red strike-through number.
That means this TN result is not complete, deleted that TN, leave the cell blank.
Footnotes for Table
** Dischargers may analzye NO3+NO2 combined for influent.
Report the combined result under NO3, and add a comment in the NO3 or NO2 cell, indicating the result is for both parameters.
*** *Collect DRP sample as a grab or composite in accordance with your agency's Sample Analysis Plan
How to report non-detected (ND) /DNQ results
For NDs, i.e., <MDL, report MDL in the cell, insert a comment
For DNQ or J flagged value, report the estimated value, insert a comment
(Select the cell, right click the mouse, choose " insert comment", type "ND" or "DNQ" in the comment box)
Note on G7: Mark Koekemoer: DNQ
Note on G8: Mark Koekemoer: ND, report MDL
Note on G9: Koekemoer, Mark: ND, Report MDL
Note on G10: Koekemoer, Mark: ND, Report MDL
Note on H7: Mark Koekemoer: DNQ
Note on H8: Mark Koekemoer: DNQ

## Inf Load
Influent Loads (Kg/d) [mg/l X MGD X 3.78 = Kg/d]
Napa Sanitation District
James Keller, Plant Manager, 707-258-6020 x601, Jkeller@napasan.com
Season | Date | Flow (MGD) |  | TN (kg/d) | TKN (kg/d) | NO3 (kg/d) | NO2 (kg/d) | Total NH3 (kg/d) | TP (kg/d) | DRP (kg/d) | TSS (kg/d)
| (mm/dd/yyyy) | Ave Daily | Peak | [6 empty] | Use Max Flow if sample type is grab
Q4 2012 | 2012-12-12 | 9.09 | 11.09 | 1280.6047 | 1278.1994 | 0.6872 | 1.718 | 883.0571 | 151.5285 | 96.4165 | 6803.3196
Q4 2012 | 2012-12-19 | 9.06 | 11.19 | 1165.7611 | 1164.3912 | 0.68494 | 0.68494 | 698.6347 | 83.2197 | 76.1368 | 4931.5392
Q4 2013 | 2013-11-07 | 6.051 | 8.86 | 1308.5517 | 1301.4612 | 0.45746 | 6.6331 | 990.3914 | 219.5787 | 148.6992 | 10795.9522
Q4 2013 | 2013-11-18 | 6.04 | 8.61 | 1453.2059 | 1449.7812 | 0.45662 | 2.9681 | 792.2426 | 168.9509 | 149.3852 | 7488.6336
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
0 | 0 | 0 | 0
THINGS TO DO
Correct bright yellow highlighted load calulations (0, #VALUE!") by correcting the "Conc" worksheet
Use correct flow for load calculation: for grab sample, use peak flow; for composit sample, use average flow.
Cells are conditionally formatted as explained below:
1. Cells are shaded purple if there is no load calculated for that parameter due to lack of concentration data. No need to do anything if that sampling is not required.
2. Cells are shaded bright yellow if the load is calculated as "0" due to concentration reported as "0", go to 'Conc" worksheet to correct the concentration reported.
3. Cells are shaded bright yellow if concentration is reporetd as a text (such as ND, <MDL, J value), go to "Conc" worksheet to correct the concentration reported.
How to choose correct flow for load calcultion.
Load calculation formulas provided use "avg daily flow" for all parameters, except for "DRP", where peak flow is used.
If DRP is collected as composite, replace "peak flow" with "avg daily flow" in the formula for load calculation.
If other parameters are grabs according to your sampling plan; replace "avg daily flow" with "peak flow" in load calculation for that parameter.

## Eff Conc.
Effluent Concentrations (mg/l)
Napa Sanitation District
James Keller, Plant Manager, 707-258-6020 x601, Jkeller@napasan.com
Quarter of Year (Q1, Q2, Q3, Q4 YYYY) | Date | Peak Flow Event (Y/N) | Flow (MGD) |  | TN (mg/L) | TDN (mg/L) | TKN (mg/L) | SKN (mg/L) | NO3 (mg/L) | NO2 (mg/L) | Total NH3 (mg/L) | Urea* (mg/L) | TP (mg/L) | TDP (mg/L) | DRP** (mg/L) | pH (s.u.) |  | Temp (oC) |  | TSS (mg/L)
| (mm/dd/yyyy) |  | Ave Daily | Peak | TKN+NO3+NO2 | SKN+NO3+NO2 | [8 empty] | Grab or composite | Min | Max | Min | Max
Q4 2012 | 2012-11-08 | N | 14.2 | 16.7 | 9.79 | 9.26 | 2.07 | 1.54 | 7.48 | 0.24 | 0.005 |  | 1.3 | 3.4 | 1.14 | 6.9 | 7.2 |  |  | 5.2
Q4 2012 | 2012-12-12 | N | 16.6 | 18 | 11.09 | 11.02 | 5.6 | 5.53 | 5.22 | 0.27 | 3.25 |  | 1.43 | 1.34 | 1.07 | 6.8 | 7.1 |  |  | 4
Q4 2012 | 2012-12-19 | N | 16.6 | 18.7 | 12.16 | 11.92 | 5.9 | 5.66 | 6.09 | 0.17 | 3.29 |  | 1.26 | 1.15 | 0.97 | 7 | 7.2 |  |  | 4.8
Q1 2013 | 2013-01-17 | N | 15.56 | 17.98 | 11.45 | 10.58 | 7.69 | 6.82 | 3.42 | 0.34 | 4.94 |  | 1.05 | 0.63 | 1.488 | 7 | 7.3 |  |  | 11.4
Q1 2013 | 2013-01-22 | N | 15.57 | 17.91 | 10.35 | 9.48 | 6.4 | 5.53 | 3.6 | 0.35 | 3.51 |  | 0.89 | 0.49 | 1.494 | 7.1 | 7.6 |  |  | 11
Q1 2013 | 2013-01-24 | N | 12.9 | 15.07 | 12.52 | 11.43 | 8.31 | 7.22 | 3.72 | 0.49 | 5.19 |  | 1.09 | 0.58 | 2.304 | 7.2 | 7.5 |  |  | 13.8
Q1 2013 | 2013-02-07 | N | 6.51 | 8.12 | 11.48 | 10.61 | 2.1 | 1.23 | 9.36 | 0.02 | 0.005 |  | 1.29 | 0.8 | 0.289 | 6.9 | 7.2 |  |  | 15.2
Q1 2013 | 2013-02-13 | N | 5.99 | 7.89 | 13.02 | 12.4 | 2.23 | 1.61 | 10.77 | 0.02 | 0.005 |  | 0.94 | 0.52 | 0.164 | 6.8 | 7 |  |  | 10.6
Q1 2013 | 2013-02-20 | N | 5.48 | 7.95 | 11.93 | 11.82 | 1.44 | 1.33 | 10.47 | 0.02 | 0.005 |  | 0.55 | 0.46 | 0.159 | 6.8 | 7.1 |  |  | 4
Q1 2013 | 2013-03-06 | N | 6.55 | 8.31 | 14.93 | 14.23 | 3.12 | 2.42 | 11.79 | 0.02 | 0.76 |  | 1.24 | 0.91 | 0.402 | 7 | 7.2 |  |  | 7.6
Q1 2013 | 2013-03-27 | N | 11.64 | 14.92 | 12.33 | 12.23 | 4.72 | 4.62 | 7.59 | 0.02 | 2.92 |  | 1.07 | 1.04 | 0.801 | 6.8 | 7.2 |  |  | 4
Q4 2013 | 2013-11-07 | N | 7.18 | 10.78 | 14.63 | 14.86 | 2.19 | 2.42 | 12.42 | 0.02 | 0.16 |  | 0.53 | 0.31 | 0.043 | 6.8 | 7.1 |  |  | 9.4
Q4 2013 | 2013-11-18 | N | 11.1 | 17.47 | 9.62 | 9.61 | 2.07 | 2.06 | 7.53 | 0.02 | 0.14 |  | 0.39 | 0.28 | 0.11 | 7 | 7.4 |  |  | 6
Q4 2013 | 2013-12-05 | N | 7.77 | 15.39 | 12.33 | 11.89 | 2.05 | 1.61 | 10.26 | 0.02 | 0.19 |  | 0.38 | 0.15 | 0.244 | 6.9 | 7 |  |  | 7.6
Q4 2013 | 2013-12-16 | N | 10.6 | 13.3 | 10.67 | 9.87 | 2.14 | 1.34 | 8.5 | 0.03 | 0.18 |  | 0.32 | 0.18 | 0.25 | 6.9 | 7.1 |  |  | 4.2
Q1 2014 | 2014-01-08 | N | 6.59 | 8.63 | 17.52 | 17.1 | 2.35 | 1.93 | 14.79 | 0.38 | 0.81 |  | 0.85 | 0.68 | 0.303 | 6.8 | 6.9 |  |  | 4.6
Q1 2014 | 2014-01-22 | N | 7.69 | 10.04 | 13.6 | 13.12 | 2.21 | 1.73 | 11.37 | 0.02 | 0.58 |  | 0.84 | 0.49 | 0.576 | 6.8 | 8.1 |  |  | 7
Q1 2014 | 2014-02-06 | N | 9.66 | 11.34 | 13.73 | 13.39 | 2.13 | 1.79 | 11.58 | 0.02 | 0.23 |  | 0.57 | 0.25 | 0.072 | 6.9 | 7.5 |  |  | 10.4
Q1 2014 | 2014-02-18 | N | 16.99 | 18.1 | 8.69 | 7.82 | 2.22 | 1.35 | 6.45 | 0.02 | 0.09 |  | 0.8 | 0.58 | 0.411 | 7 | 7.3 |  |  | 14
Q1 2014 | 2014-03-05 | N | 17.55 | 18.73 | 8.01 | 7.97 | 2.2 | 2.16 | 5.79 | 0.02 | 0.1 |  | 0.92 | 0.69 | 0.086 | 6.9 | 7 |  |  | 9.4
Q1 2014 | 2014-03-18 | N | 12.79 | 14.62 | 15.15 | 14.87 | 7.45 | 7.17 | 7.68 | 0.02 | 3.78 |  | 1.82 | 1.56 | 0.852 | 7 | 7.3 |  |  | 9.4
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
[5 empty] | 0 | 0
THINGS TO DO
Only enter numbers in the cells for concentrations; or leave blank if no data (do not enter "NA")
Delete red striked-through numbers under TN/TKN after all the data for that date are entered; leave the cell blank.
THINGS NOT TO DO
Do not report zero for non-detected values or DNQ(J) values;
Do not put text before the number to indicate it is ND or DNQ.
Do not report combined result for NO3+ NO2 under both parameters (see footnote ** below)
Quarter of Year definition
Q3 2012 - July - September 2012
Q4 2012: October - December 2012
Q1 2013: January - March 2013
Q2 2013: April - June 2013
Q3 2013: July - September 2013
Q4 2013: October - December 2013
Q1 2014: January - March 2014
Q2 2014: April - June 2014
For seasonal dischargers, effluent sampling is not required in May/June 2014. However, if a prior dry weather sampling event is not conducted,
then the discharger shall make up the missed sampling event during May-June 2014; unless other arrangements have been made.
Cells are conditionally formatted as explained below:
1. when a date is entered, the row is highlighted in orange;
2. When a text is entered, the cell is shaded in blue; remove the text ("ND", "DNQ", etc.), report a number.
3. If TKN or both NO3/NO2 conc. is missing, the calculated TN result is shown in red strike-through number.
That means this TN result is not complete, deleted that TN, leave the cell blank.
Footnotes for Table
* Urea monitoring is only required for the five largest POTWs: CCCSD, EBDA, EBMUD, SF Southeast, SJSC
**Collect DRP sample as a grab or composite in accordance with your agency's Sample Analysis Plan
How to report non-detected (ND) /DNQ results
For NDs, i.e., <MDL, report MDL in the cell, insert a comment
For DNQ or J flagged value, report the estimated value, insert a comment
(Select the cell, right click the mouse, choose " insert comment", type "ND" or "DNQ" in the comment box)
Note on K13: Mark Koekemoer: ND, report MDL
Note on K14: Mark Koekemoer: ND, report MDL
Note on K15: Mark Koekemoer: DNQ
Note on K16: Mark Koekemoer: DNQ
Note on K17: Mark Koekemoer: ND, report MDL
Note on K18: Koekemoer, Mark: DNQ
Note on K19: Koekemoer, Mark: DNQ
Note on K20: Koekemoer, Mark: DNQ
Note on K21: Koekemoer, Mark: DNQ
Note on K23: Koekemoer, Mark: DNQ
Note on K24: Mark Koekemoer: ND, report MDL
Note on K25: Koekemoer, Mark: DNQ
Note on K26: Mark Koekemoer: ND, report MDL
Note on K27: Koekemoer, Mark: DNQ
Note on L7: Mark Koekemoer: ND, report MDL
Note on L13: Mark Koekemoer: ND, report MDL
Note on L14: Mark Koekemoer: ND, report MDL
Note on L15: Mark Koekemoer: ND, report MDL
Note on P21: Koekemoer, Mark: ND, Report MDL

## Eff Loads
Effluent Loads (Kg/d) [mg/l X MGD X 3.78 = Kg/d]
Napa Sanitation District
James Keller, Plant Manager, 707-258-6020 x601, Jkeller@napasan.com
Quarter of Year | Date | Peak Flow Event (Y/N) | Flow (MGD) |  | TN (kg/d) | TDN (kg/d) | TKN (kg/d) | SKN (kg/d) | NO3 (kg/d) | NO2 (kg/d) | Total NH3 (kg/d) | Urea (kg/d) | TP (kg/d) | TDP (kg/d) | DRP (kg/d) | TSS (kg/d)
| (mm/dd/yyyy) |  | Ave Daily | Peak | [10 empty] | Use Max Flow if sample type is Grab
Q4 2012 | 2012-11-08 | N | 14.2 | 16.7 | 525.488 | 497.0398 | 111.1093 | 82.661 | 401.4965 | 12.8822 | 0.26838 |  | 69.7788 | 182.4984 | 71.9636 | 279.1152
Q4 2012 | 2012-12-12 | N | 16.6 | 18 | 695.8753 | 691.483 | 351.3888 | 346.9964 | 327.5446 | 16.942 | 203.931 |  | 89.7296 | 84.0823 | 72.8028 | 250.992
Q4 2012 | 2012-12-19 | N | 16.6 | 18.7 | 763.0157 | 747.9562 | 370.2132 | 355.1537 | 382.1353 | 10.6672 | 206.4409 |  | 79.0625 | 72.1602 | 68.5654 | 301.1904
Q1 2013 | 2013-01-17 | N | 15.56 | 17.98 | 673.4524 | 622.2817 | 452.3012 | 401.1306 | 201.1535 | 19.9977 | 290.555 |  | 61.7576 | 37.0546 | 101.131 | 670.5115
Q1 2013 | 2013-01-22 | N | 15.57 | 17.91 | 609.1451 | 557.9416 | 376.6694 | 325.4659 | 211.8766 | 20.5991 | 206.5796 |  | 52.3806 | 28.8388 | 101.1435 | 647.4006
Q1 2013 | 2013-01-24 | N | 12.9 | 15.07 | 610.5002 | 557.3497 | 405.2122 | 352.0616 | 181.3946 | 23.8934 | 253.0748 |  | 53.1506 | 28.282 | 131.2464 | 672.9156
Q1 2013 | 2013-02-07 | N | 6.51 | 8.12 | 282.4975 | 261.0888 | 51.6764 | 30.2676 | 230.329 | 0.49216 | 0.12304 |  | 31.7441 | 19.6862 | 8.8705 | 374.0386
Q1 2013 | 2013-02-13 | N | 5.99 | 7.89 | 294.8014 | 280.7633 | 50.4921 | 36.4539 | 243.8565 | 0.45284 | 0.11321 |  | 21.2837 | 11.7739 | 4.8912 | 240.0073
Q1 2013 | 2013-02-20 | N | 5.48 | 7.95 | 247.1228 | 244.8442 | 29.8287 | 27.5502 | 216.8798 | 0.41429 | 0.10357 |  | 11.3929 | 9.5286 | 4.7781 | 82.8576
Q1 2013 | 2013-03-06 | N | 6.55 | 8.31 | 369.6519 | 352.3206 | 77.2481 | 59.9168 | 291.9086 | 0.49518 | 18.8168 |  | 30.7012 | 22.5307 | 12.6275 | 188.1684
Q1 2013 | 2013-03-27 | N | 11.64 | 14.92 | 542.5101 | 538.1102 | 207.6762 | 203.2763 | 333.9539 | 0.87998 | 128.4777 |  | 47.0791 | 45.7592 | 45.1745 | 175.9968
Q4 2013 | 2013-11-07 | N | 7.18 | 10.78 | 397.0641 | 403.3063 | 59.4375 | 65.6798 | 337.0838 | 0.54281 | 4.3425 |  | 14.3844 | 8.4135 | 1.7522 | 255.1198
Q4 2013 | 2013-11-18 | N | 11.1 | 17.47 | 403.636 | 403.2164 | 86.8531 | 86.4335 | 315.9437 | 0.83916 | 5.8741 |  | 16.3636 | 11.7482 | 7.264 | 251.748
Q4 2013 | 2013-12-05 | N | 7.77 | 15.39 | 362.1395 | 349.2164 | 60.2097 | 47.2867 | 301.3424 | 0.58741 | 5.5804 |  | 11.1608 | 4.4056 | 14.1945 | 223.2166
Q4 2013 | 2013-12-16 | N | 10.6 | 13.3 | 427.5256 | 395.4712 | 85.7455 | 53.6911 | 340.578 | 1.202 | 7.2122 |  | 12.8218 | 7.2122 | 12.5685 | 168.2856
Q1 2014 | 2014-01-08 | N | 6.59 | 8.63 | 436.4267 | 425.9644 | 58.539 | 48.0767 | 368.4219 | 9.4659 | 20.1773 |  | 21.1737 | 16.9389 | 9.8843 | 114.5869
Q1 2014 | 2014-01-22 | N | 7.69 | 10.04 | 395.3275 | 381.3748 | 64.2407 | 50.288 | 330.5054 | 0.58136 | 16.8596 |  | 24.4173 | 14.2434 | 21.8599 | 203.4774
Q1 2014 | 2014-02-06 | N | 9.66 | 11.34 | 501.3482 | 488.9332 | 77.7765 | 65.3615 | 422.8414 | 0.7303 | 8.3984 |  | 20.8134 | 9.1287 | 3.0863 | 379.7539
Q1 2014 | 2014-02-18 | N | 16.99 | 18.1 | 558.0909 | 502.2176 | 142.5733 | 86.7 | 414.2332 | 1.2844 | 5.78 |  | 51.3778 | 37.2489 | 28.1198 | 899.1108
Q1 2014 | 2014-03-05 | N | 17.55 | 18.73 | 531.3754 | 528.7218 | 145.9458 | 143.2922 | 384.1028 | 1.3268 | 6.6339 |  | 61.0319 | 45.7739 | 6.0887 | 623.5866
Q1 2014 | 2014-03-18 | N | 12.79 | 14.62 | 732.4449 | 718.908 | 360.1792 | 346.6423 | 371.2988 | 0.96692 | 182.7486 |  | 87.9901 | 75.4201 | 47.0846 | 454.4543
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0
THINGS TO DO
Correct bright yellow highlighted load calulations (0, #VALUE!") by correcting the "Conc" worksheet
Use correct flow for load calculation: for grab sample, use peak flow; for composit sample, use average flow.
Cells are conditionally formatted as explained below:
1. Cells are shaded purple if there is no load calculated for that parameter due to lack of concentration data. No need to do anything if that sampling is not required.
2. Cells are shaded bright yellow if the load is calculated as "0" due to concentration reported as "0", go to 'Conc" worksheet to correct the concentration reported.
3. Cells are shaded bright yellow if concentration is reporetd as a text (such as ND, <MDL, J value), go to "Conc" worksheet to correct the concentration reported.
How to choose correct flow for load calcultion.
Load calculation formulas provided use "avg daily flow" for all parameters, except for "DRP", where peak flow is used.
If DRP is collected as composite, replace "peak flow" with "avg daily flow" in the formula for load calculation.
If other parameters are grabs according to your sampling plan; replace "avg daily flow" with "peak flow" in load calculation for that parameter.

## Inf QAQC MLs
Influent MDL / ML (mg/l)
Napa Sanitation District
James Keller, Plant Manager, 707-258-6020 x601, Jkeller@napasan.com
Season | Date | TKN |  | NO3 |  | NO2 |  | Total NH3 |  | TP |  | DRP |  | TSS |  | NO3+NO2
| (mm/dd/yyyy) | MDL | ML | MDL | ML | MDL | ML | MDL | ML | MDL | ML | MDL | ML | MDL | ML | MDL | ML
Q4 2012 | 2012-12-12 | 0.3 | 3 | 0.024 | 0.24 | 0.02 | 0.18 | 0.03 | 0.3 | 0.05 | 0.5 | 0.024 | 0.12 | 0.4 | 2
Q4 2012 | 2012-12-19 | 0.6 | 6 | 0.024 | 0.24 | 0.02 | 0.18 | 0.05 | 0.5 | 0.05 | 0.5 | 0.024 | 0.12 | 0.4 | 2
Q4 2013 | 2013-11-07 | 0.1 | 10 | 0.018 | 0.15 | 0.002 | 0.15 | 0.003 | 0.5 | 0.05 | 5 | 0.011 | 0.15 | 0.3 | 2
Q4 2013 | 2013-11-18 | 0.1 | 10 | 0.018 | 0.15 | 0.002 | 0.15 | 0.005 | 0.5 | 0.05 | 5 | 0.011 | 0.15 | 0.3 | 2
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
Do not enter "Season" or "Date" information on this worksheet. Make changes to the "Inf Conc." worksheet.
This sheet will be automatically updated with the new information.

## Eff QAQC MLs
Effluent MDL / ML (mg/l)
Napa Sanitation District
James Keller, Plant Manager, 707-258-6020 x601, Jkeller@napasan.com
Quarter of Year | Date | TKN |  | SKN |  | NO3 |  | NO2 |  | Total NH3 |  | Urea |  | TP |  | TDP |  | DRP |  | TSS
| (mm/dd/yyyy) | MDL | ML | MDL | ML | MDL | ML | MDL | ML | MDL | ML | MDL | ML | MDL | ML | MDL | ML | MDL | ML | MDL | ML
Q4 2012 | 2012-11-08 | 0.1 | 1 | 0.1 | 1 | 0.16 | 1.6 | 0.12 | 1.2 | 0.005 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.5 | 0.16 | 0.8 | 0.4 | 2
Q4 2012 | 2012-12-12 | 0.1 | 1 | 0.1 | 1 | 0.024 | 0.24 | 0.02 | 0.18 | 0.005 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.5 | 0.024 | 0.12 | 0.4 | 2
Q4 2012 | 2012-12-19 | 0.1 | 1 | 0.1 | 1 | 0.024 | 0.24 | 0.02 | 0.18 | 0.005 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.5 | 0.024 | 0.12 | 0.4 | 2
Q1 2013 | 2013-01-17 | 0.1 | 1 | 0.1 | 1 | 0.024 | 0.24 | 0.02 | 0.18 | 0.005 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.5 | 0.024 | 0.12 | 0.4 | 2
Q1 2013 | 2013-01-22 | 0.1 | 1 | 0.1 | 1 | 0.024 | 0.24 | 0.02 | 0.18 | 0.005 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.5 | 0.024 | 0.12 | 0.4 | 2
Q1 2013 | 2013-01-24 | 0.1 | 1 | 0.1 | 1 | 0.024 | 0.24 | 0.02 | 0.18 | 0.005 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.5 | 0.024 | 0.12 | 0.4 | 2
Q1 2013 | 2013-02-07 | 0.1 | 1 | 0.1 | 1 | 0.024 | 0.24 | 0.02 | 0.18 | 0.005 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.5 | 0.024 | 0.12 | 0.4 | 2
Q1 2013 | 2013-02-13 | 0.1 | 1 | 0.1 | 1 | 0.024 | 0.24 | 0.02 | 0.18 | 0.005 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.5 | 0.024 | 0.12 | 0.4 | 2
Q1 2013 | 2013-02-20 | 0.1 | 1 | 0.1 | 1 | 0.024 | 0.24 | 0.02 | 0.18 | 0.005 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.5 | 0.024 | 0.12 | 0.4 | 2
Q1 2013 | 2013-03-06 | 0.1 | 1 | 0.1 | 1 | 0.024 | 0.24 | 0.02 | 0.18 | 0.005 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.5 | 0.024 | 0.12 | 0.4 | 2
Q1 2013 | 2013-03-27 | 0.1 | 1 | 0.1 | 1 | 0.024 | 0.24 | 0.02 | 0.18 | 0.005 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.5 | 0.024 | 0.12 | 0.4 | 2
Q4 2013 | 2013-11-07 | 0.1 | 1 | 0.1 | 1 | 0.0018 | 0.15 | 0.002 | 0.15 | 0.003 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.5 | 0.011 | 0.15 | 0.3 | 2
Q4 2013 | 2013-11-18 | 0.1 | 1 | 0.1 | 1 | 0.0018 | 0.15 | 0.002 | 0.15 | 0.005 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.5 | 0.011 | 0.15 | 0.3 | 2
Q4 2013 | 2013-12-05 | 0.1 | 1 | 0.1 | 1 | 0.055 | 0.15 | 0.007 | 0.15 | 0.003 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.5 | 0.034 | 0.15 | 0.3 | 2
Q4 2013 | 2013-12-16 | 0.1 | 1 | 0.1 | 1 | 0.092 | 0.25 | 0.01 | 0.25 | 0.003 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.5 | 0.056 | 0.25 | 0.3 | 2
Q1 2014 | 2014-01-08 | 0.1 | 1 | 0.1 | 1 | 0.055 | 0.15 | 0.007 | 0.15 | 0.003 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.5 | 0.034 | 0.15 | 0.3 | 2
Q1 2014 | 2014-01-22 | 0.1 | 1 | 0.1 | 1 | 0.055 | 0.15 | 0.007 | 0.15 | 0.003 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.05 | 0.034 | 0.15 | 0.3 | 2
Q1 2014 | 2014-02-06 | 0.1 | 1 | 0.1 | 1 | 0.055 | 0.15 | 0.007 | 0.15 | 0.003 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.5 | 0.034 | 0.15 | 0.3 | 2
Q1 2014 | 2014-02-18 | 0.1 | 1 | 0.1 | 1 | 0.055 | 0.15 | 0.007 | 0.15 | 0.003 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.05 | 0.034 | 0.15 | 0.3 | 2
Q1 2014 | 2014-03-05 | 0.1 | 1 | 0.1 | 1 | 0.055 | 0.15 | 0.007 | 0.15 | 0.003 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.05 | 0.034 | 0.15 | 0.3 | 2
Q1 2014 | 2014-03-18 | 0.1 | 1 | 0.1 | 1 | 0.073 | 0.2 | 0.009 | 0.2 | 0.003 | 0.05 |  |  | 0.05 | 0.5 | 0.05 | 0.05 | 0.045 | 0.2 | 0.3 | 2
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
0 | 0
Do not enter "Season" or "Date" information on this worksheet. Make changes to the "Eff Conc." worksheet.
This sheet will be automatically updated with the new information.