## SEWER
DATEREP | TIMEREP | REPBY | PHONE | AGENCY | STARTDATE | STARTTIME | ENDDATE | ENDTIME | VOLUME | UNITS | STREET | CITY | COUNTY | STRUCTURE | CAUSE | SURFACE | PRIMH2O | SECH2O | DESTI | HSANOTI | POSTED | DAYSPOST | REMARKS
870106 | 1450 | FRED WOOD | 6192216626 | SAN DIEGO, CITY OF | 870106 | UNKNWN | 870106 | UNKNWN | 10 | GAL | NOT REPORTED | NOT REPORTED | SD | NOT REPORTED | UNKNOWN AT THIS TIME | Y | PACIFIC OCEAN | NONE | NONE | Y
860715 | 1500 | RAY MILLER | 7144494555 | SOUTH COAST COUNTY WATER DISTR | 860715 | 1330 | 860715 | 1330 | 100 | GAL | CROWN VALLEY ROAD | LAGUNA NIGUEL |  | PIPELINE | CRUSHED 8" PIPELINE | Y | PACIFIC OCEAN |  |  | Y | Y |  | DISCHARGE MAY BE ONGOING. SLOW LEAKING PIPE. DISTRICT TAKING CORRECTIVE ACTION.
870107 | 1420 | WALTER O'LEARY | 2367030 | SAN DIEGO, CITY OF | 870106 | 0943AM | 870106 | 1143AM | 240 | GAL | 5226 LA PAZ DRIVE | SAN DIEGO | SD | MANHOLE (FRONT OF 5209) | GREASE STOPPAGE IN 6" CONCRETE PIPE | N | NONE |  |  | Y
870107 | 1420 | WALTER O'LEARY | 2367030 | SAN DIEGO, CITY OF | 870106 | 1030AM | 870106 | 1230PM | 720 | GAL | 4041 ESTRELLA DRIVE | SAN DIEGO | SD | COMMODE | GREASE STOPPAGE IN 6" CONCRETE PIPE. | N | NONE |  |  | Y |  |  | COMMODE OVERFLOWED INTO FLOOR DRAIN TO STORM DRAIN AND INTO CANYON.
870107 | 0830AM | JIM McCURDY | 5789772 | SAN DIEGO, CITY OF | 870106 | 1630PM | 870106 | 2130PM | 10 | GAL | 3810 WYNONA | SAN DIEGO | SD | MANHOLE AT ABOVE ADDRESS | ROCKS/ROOTS BLOCKAGE | N | NONE |  |  | N | N
870107 | 1000AM | FRED WOOD | 2216626 | SAN DIEGO, CITY OF | 870107 | 0135AM | 870107 | 0136AM | 10 | GAL | POINT LOMA VORTEX | SAN DIEGO | SD | VORTEX | "BURP" DUE TO GASES IN THE VORTEX BACKING UP WHEN CHANGING FROM 3 TO 2 PUMPS. | Y | PACIFIC OCEAN |  |  | Y | N |  | SAND BAGS KEPT THE MAJORITY OF THE SPILL ON LAND- SOME SEEPAGE THROUGH BAGS REACHED SHORE.
870112 | LETTER | BEN DUNCAN | 6197478702 | SAN DIEGO, CITY OF | 870101 | 0800AM | 870101 | 0930AM | 50 | GAL | HIKING TRAIL ADJ. PICNIC AREA | SAN DIEGO | SD | MANHOLE | STOPPAGE DUE TO TRASH AND DEBRIS. | N | NONE
861009 | LETTER | JAMES FUNGE | 6192216600 | SAN DIEGO, CITY OF | 860926 | 1225PM | 860926 | 1325PM | 250 | GAL | POINT LOMA WASTEWATER T.P. | SAN DIEGO | SD | VORTEX | RAIN AS WELL AS PLANT SHUT DOWN ON 9/25/86 FOR REPAIR OF OUTFALL PIPE. |  | PACIFIC OCEAN
861009 | LETTER | JAMES FUNGE | 6192216626 | SAN DIEGO, CITY OF | 860925 | 0830AM | 860925 | 0900AM | 500 | GAL | POINT LOMA WASTEWATER T.P. | SAN DIEGO | SD | VORTEX | DISCHARGE OF AIR AND EFFLUENT FROM VORTEX STRUCTURE. | Y | PACIFIC OCEAN | [5 empty] | NOTE:**THERE WAS A SECOND OVERFLOW THE SAME DAY STARTED AT 1315PM,ENDED AT 1415PM.********
870112 | 0815 | JOHN McPHEARSON | 6192367341 | SAN DIEGO, CITY OF | 870111 | 0700AM | 870111 | 0930AM | 150 | GAL | SOUTH COAST BLVD. | SAN DIEGO | SD | NOT REPORTED | GREASE | Y | PACIFIC OCEAN |  |  | Y | Y
870112 | 0810AM | JOHN McPHEARSON | 6192367341 | SAN DIEGO, CITY OF | 870111 | 1300PM | 870111 | 1800PM | 6000 | GAL | LOOKOUT DRIVE | SAN DIEGO | SD | 8" SEWER MAIN | VANDALISM | Y | PACIFIC OCEAN |  |  | Y
870109 | 1510PM | DEL HENNINGER | 6192365534 | SAN DIEGO, CITY OF | 870109 | 1000AM | 870109 | 1053AM | 265 | GAL | 989 SUNSET CLIFFS BLVD. | SAN DIEGO | SD | PUMP STATION 35 | HG SWITCH FAILURE. | Y | PACIFIC OCEAN |  |  | Y | Y
870109 | 1620PM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870108 | 1005AM | 870108 | 1140AM | 30000 | GAL | COUNTRY CLUB AND ROMERO DRIVE | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT OBSTRUCTION. | Y | STORM DRAIN TO 210 SOUTH COAST | BLVD. |  | Y | Y
870109 | 0845AM | JIM McCURLY | 6195789772 | SAN DIEGO, CITY OF | 870108 | 1630PM | 870108 | 2130PM | 180 | GAL | 5115 27th STREET (ALLEY) | SAN DIEGO | SD | 6"VC MAIN | GREASE AND ROCK BLOCKAGE. | N | NONE
870109 | 0845AM | JIM McCURLY | 6195789772 | SAN DIEGO, CITY OF | 870108 | 1700PM | 870108 | 1930PM | 450 | GAL | 5141 CANTERBURY DRIVE | SAN DIEGO |  | 6" CONCRETE PIPE | PALM ROOTS BLOCKAGE. | N | NONE
870108 | 0800AM | GEORGE L LONG SR | 6195655359 | SPRING VALLEY SANITATION DIST. | 870108 | 0800AM | 870108 | 0830AM | 6000 | GAL | RAMONA AVE AT SAN CARLOS ST | SPRING VALLEY | SD | RAMONA AVE PUMPING STATION | BROKEN 4" ABS FORCE MAIN. | Y | CHANNEL TO SWEETWATER RESERVOI | R. |  | Y | N |  | HEALTH AGENCY DETERMINED THAT IT DID REACH THE LAKE SINCE THE DITCH WAS FLOWING.
870108 | 0830 | GEORGE LONG | 6195655359 | SPRING VALLEY SANITATION DIST. | 870108 | 0830 | 870108 | UNKNWN | 10 | GAL | SAN MARCOS AND RAMONA AVE. | SPRING VALLEY | SD | FORCE MAIN. | FORCE MAIN BREAK. | ? | NONE |  |  | Y |  |  | UNKNOWN AT PRESENT IF LEAK WILL REACH SURF. WATER. MR. LONG WILL CALL IF IT DOES.
870109 | LETTER | ROBERT McCAMPBELL | 6192216600 | SAN DIEGO, CITY OF | 870106 | UNKNWN | 870106 | UNKNWN | 10 | GAL | POINT LOMA WWTP. | SAN DIEGO | SD | VORTEX | DISCHARGE OF AIR AND EFFLUENT FROM VORTEX STRUCTURE. | Y | PACIFIC OCEAN
870112 | LETTER | ROBERT McCAMPBELL | 6192216600 | SAN DIEGO, CITY OF | 870101 | 0115AM | 870101 | UNKNWN | 10 | GAL | POINT LOMA WWTP. | SAN DIEGO | SD | VORTEX | AIR AND EFFLUENT BEING DISCHARGED UP THROUGH THE VORTEX STRUCTURE. |  | PACIFIC OCEAN
870112 | 1433PM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870112 | 1030AM | 870112 | 1130AM | 600 | GAL | 100 BLOCK OF ROOSEVELT STREET | SAN DIEGO | SD | MANHOLE | 6" CONCRETE MAIN CLOGGED WITH ROOTS AND GREASE. | Y | MISSION BAY |  |  | Y | Y |  | ONLY 200 GALLONS REACHED THE BAY. SDGE WORKERS DAMMED THE FLOW WITH DIRT PILES.
870112 | 1350PM | DEL HERNANDEZ | 6192365534 | SAN DIEGO, CITY OF | 870112 | 0700AM | 870112 | 0800AM | 9000 | GAL | 3255 LA JOLLA VILLAGE DRIVE | SAN DIEGO | SD | SUMP 30 ALPHA | FAILURE OF PUMP ALTINATOR AND TELEMETERING SYSTEM. | Y | MISSION BAY VIA ROSE CREEK | MISSION BAY | MISSION BAY | Y | Y
860630 | 0850AM | ALLEGRA,CNTY HEALTH | 6192366840 | SAN DIEGO, CITY OF | 860627 | UNKNWN | 860627 | UNKNWN | 10 | GAL | SANTA BARBARA PLACE (COVE) | SAN DIEGO | SD | PUMP STATION 14 | NOT REPORTED | Y | MISSION BAY |  |  | Y | Y |  | CO. HEALTH DEPT. POSTED BEACH AT SANTA BARBARA COVE DUE TO HIGH COLIFORM COUNTS.
870102 | 0830AM | ALICE BENSON | 6192216626 | SAN DIEGO, CITY OF | 870102 | 0030AM | 870102 | 0035AM | 10 | GAL | POINT LOMA WWTP. | SAN DIEGO | SD | VORTEX STRUCTURE | UNKNOWN | Y | PACIFIC OCEAN |  |  | Y | N
861114 | 1430PM | ALLEGRA | 6192364717 | SAN DIEGO, CITY OF | 861114 | 0909AM | 861114 | 1143AM | 10 | GPM | 1800 FORTUNA AVE | SAN DIEGO | SD | MANHOLE | OBSTRUCTION | Y | MISSION BAY |  |  | Y | Y |  | 200 YARDS NORTH OF CROWN POINT AND 50 YARDS SOUTH OF CROWN POINT.
861208 | 0920AM | ALLEGRA | 6192364717 | SAN DIEGO, CITY OF | 861207 | 1010AM | 861207 | 1210PM | 6000 | GAL | 2600 BLUFFSIDE AVE | SAN DIEGO | SD | MANHOLE | DEBRIS BLOCKAGE | Y | MISSION BAY |  |  | Y | Y |  | CAMPLAND BEACH AREA POSTED COUNTY HEALTH SAMPLING 12/8 AND 12/9
861205 | 1430PM | ALLEGRA,CNTY HEALTH | 6192366840 | SAN DIEGO, CITY OF | 861204 | 0830AM | 861204 | 0950AM | 300 | GAL | 998 W. MISSION BAY DRIVE | SAN DIEGO | SD | NOT REPORTED | SEWER MAIN STOPPAGE. | Y | MISSION BAY |  |  | Y | Y
861211 | 1430PM | ALLEGRA,CNTY HEALTH | 6192366840 | SAN DIEGO, CITY OF | 861211 | 0730AM | 861211 | UNKNWN | 75 | GAL | 3055 ERIE ST.(NR INFO CTR.) | SAN DIEGO | SD | NOT REPORTED | STOPPAGE | Y | MISSION BAY |  |  | Y | Y
861211 | 0820AM | FRANK POTTER | 6192362802 | SAN DIEGO, CITY OF | 861210 | 0930 | 861210 | UNKNWN | 50 | GPM | TARA PL. AND LIMERICK | SAN DIEGO | SD | NOT REPORTED | NOT REPORTED | Y | MISSION BAY | NONE | NONE | Y | Y |  | 200 YARDS ON EACH SIDE OF MOUTH POSTED AS A PRECAUTIONARY MEASURE.
861211 | 0944 | WALTER O'LEARY | 6192367030 | SAN DIEGO, CITY OF | 861210 | 1540PM | 861210 | UNKNWN | 69000 | GAL | 5096 TRIANA (TECOLOTE CANYON) | SAN DIEGO | SD | MANHOLE 220FT FROM LIMERICK | UNKNOWN | Y | MISSION BAY |  |  |  | Y
861229 | 1545PM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 861229 | 1100AM | 861229 | 1215PM | 180 | GAL | EDGECLIFF DR. & RIVIERA | SAN DIEGO | SD | NOT REPORTED | ROOTS | Y | MISSION BAY |  | BEACH AREA | Y | Y |  | HEALTH DEPT. POSTED BEACH 100 YDS EITHER SIDE OF THE STORM DRAIN OUTLET AS PRECAUTION.
860317 | 0935AM | JOHN MELBOURN | 6192362802 | SAN DIEGO, CITY OF | 860315 | 1600PM | 860315 | 1700PM | 1200 | GAL | NOYES AND OR PACIFIC BCH. DR. | SAN DIEGO | SD | MANHOLE | OBSTRUCTION | Y | MISSION BAY |  |  | Y | Y
870102 | 0832AM | ALICE BENSON | 6192216626 | SAN DIEGO, CITY OF | 870101 | 0115AM | 870101 | 0120AM | 10 | GAL | POINT LOMA WWTP. | SAN DIEGO | SD | VORTEX STRUCTURE | UNKNOWN | Y | PACIFIC OCEAN |  |  | Y | N
870102 | 0930AM | DUNCAN | 6197478702 | SAN DIEGO, CITY OF | 870101 | 0800AM | 870101 | 0810AM | 50 | GAL | S.D. WILD ANIMAL PARK | SAN DIEGO | SD | MANHOLE | DEBRIS | Y | NONE |  | MANMADE CREEK IN PARK | N | Y |  | SPILL WAS DILUTED WITH FIRE HOSE AND WASHED INTO CREEK. NO SOLIDS EVIDENT.
870102 | 1000AM | WALTER O'LEARY | 6192367030 | SAN DIEGO, CITY OF | 870101 | 0815AM | 870101 | 1015AM | 34 | GAL | 870 LORING ST. | SAN DIEGO | SD | MANHOLE | HEAVY GREASE | N | NONE |  |  | Y | N
870102 | 1000AM | WALTER O'LEARY | 6192367030 | SAN DIEGO, CITY OF | 870101 | 1115AM | 870101 | 1315PM | 75 | GAL | 3720 POLK AVE | SAN DIEGO | SD | MANHOLE | HEAVY GREASE | N | NONE |  |  | Y | N
870102 | 1000AM | WALTER O'LEARY | 6192367030 | SAN DIEGO, CITY OF | 870101 | 1900PM | 870101 | 2200PM | 180 | GAL | 14350 LA TRUCHA | SAN DIEGO | SD | MANHOLE | ROCKS, GREASE, RAGS | N | NONE |  |  | Y | N
870102 | 1000AM | WALTER O'LEARY | 6192367030 | SAN DIEGO, CITY OF | 870101 | 2015PM | 870101 | 2115PM | 10 | GAL | 3927 TAMARCA DRIVE | SAN DIEGO | SD | MANHOLE | HEAVY GREASE | N | NONE |  |  | Y | N
870102 | 1000AM | WALTER O'LEARY | 6192367030 | SAN DIEGO, CITY OF | 870101 | 1116AM | 870101 | 1246PM | 18 | GAL | 4196 SYCAMORE DR | SAN DIEGO | SD | MANHOLE | ROOTS | N | NONE |  |  | Y | N
870102 | 1550PM | WALTER O'LEARY | 6192367030 | SAN DIEGO, CITY OF | 870102 | 1025AM | 870102 | 1225PM | 120 | GAL | 4416 PARK BLVD (IN ALLEY) | SAN DIEGO | SD | MANHOLE | GREASE BLOCKAGE | N | NONE |  | STORM DRAIN (MEADE & PARK BL.) | N | N |  | DEODORIZED AND DECONTAMINATED AREA.NO SURFACE WATER REACHED.
870112 | 1630PM | DAVE SEYMOUR | 7145222330 | SANTA MARGARITA WATER DISTRICT | 870110 | 0920AM | 870110 | 1030AM | 5500 | GAL | CORDOVA RD | MISSION VIEJO |  | MANHOLE | OBSTRUCTION OF MAIN LINE | Y | PACIFIC OCEAN |  |  | Y | N
861030 | 1215PM | JOHN MELBOURN | 6192364718 | SAN DIEGO, CITY OF | 861030 | 0715AM | 861030 | 1130AM | 24000 | GAL | 2475 GRAND AVE | SAN DIEGO | SD | NOT REPORTED | NOT REPORTED | Y | MISSION BAY | NONE | NONE | Y | Y |  | CO. HEALTH HAS POSTED SECTION OF MISSION BAY FROM THE MOUTH OF ROSE CREEK TO WILDLIFE SANC
861114 | 1545PM | NEIL TUCKER | 6192366710 | SAN DIEGO, CITY OF | 861114 | 0100AM | 861114 | 1200PM | 1200 | GAL | LAMONT AND CROWN PT. DRIVE | SAN DIEGO | SD | NOT REPORTED | DEBRIS BLOCKAGE | Y | MISSION BAY |  |  | Y | Y
861208 | 0930AM | WALTER O'LEARY | 6192367030 | SAN DIEGO, CITY OF | 861207 | 1010AM | 861207 | 1210PM | 6000 | GAL | 2600 BLOCK OF BLUFFSIDE | SAN DIEGO | SD | MANHOLE | DEBRIS IN SEWER LINE | Y | MISSION BAY VIA ROSE CREEK |  |  | Y | Y |  | MACHINE RODDED TO CLEAN
870114 | 0830AM | FRED WOOD | 6192216626 | SAN DIEGO, CITY OF | 870114 | 0210AM | 870114 | 0212AM | 10 | GAL | POINT LOMA WWTP. | SAN DIEGO | SD | VORTEX STRUCTURE | BURP-TRAPPED GAS IN EFFLUENT SYSTEM. | Y | PACIFIC OCEAN |  |  | Y | N
870109 | 1053AM | D E HERNANDEZ | 6192365534 | SAN DIEGO, CITY OF | 870109 | 1000AM | 870109 | 1053AM | 265 | GAL | 989 SUNSET CLIFFS BLVD. | SAN DIEGO | SD | PUMP STATION 35 | MALFUNCTION OF MERCURY SWITCH | Y | PACIFIC OCEAN |  |  | Y | Y
870109 |  | WALTER O'LEARY | 6192367030 | SAN DIEGO, CITY OF | 870109 | 0845AM | 870109 | 1115AM | 750 | GAL | 3100 BLOCK OF JUNIPER ST. | SAN DIEGO | SD | MANHOLE | RAGS AND GREASE | N | NONE |  | CANYON IN DIRT | N |  |  | NO SIGNS NEEDED
870109 |  | WALTER O'LEARY | 6192367030 | SAN DIEGO, CITY OF | 870109 | 1415PM | 870109 | 1715PM | 900 | GAL | 2904 MARTIN LUTHER KING WAY | SAN DIEGO | SD | CLEAN OUT | MUD FROM BROKEN LATERAL | N | NONE |  | STORM DRAIN TO CANYON |  |  |  | NO SIGNS NEEDED
870109 | 1053AM | D E HERNANDEZ | 6192365534 | SAN DIEGO, CITY OF | 870109 | 1000AM | 870109 | 1053AM | 265 | GAL | 989 SUNSET CLIFFS BLVD. | SAN DIEGO | SD | PUMP STATION 35 | MALFUNCTION OF MERCURY SWITCH | Y | PACIFIC OCEAN |  |  | Y | Y
870109 | 1620PM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870109 | 1005AM | 870109 | 1140AM | 30000 | GAL | COUNTRY CLUB AND ROMERO DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT OBSTRUCTION | Y | PACIFIC OCEAN |  |  | Y | Y
870112 | 0800AM | J McPHERSON | 6192365600 | SAN DIEGO, CITY OF | 870111 | 0700AM | 870111 | 0930AM | 150 | GAL | SOUTH COAST BLVD. | SAN DIEGO | SD | SEWER LINE | GREASE | Y | PACIFIC OCEAN |  |  | Y | Y
870112 | 0800AM | J McPHERSON | 6192365600 | SAN DIEGO, CITY OF | 870111 | 1300PM | 870111 | 1800PM | 6000 | GAL | LOOKOUT DRIVE | SAN DIEGO | SD | 8" SEWER MAIN | VANDALISM. ROUNDPOINT SHOVEL IN MANHOLE | Y | PACIFIC OCEAN |  |  | Y | Y
870112 | 1430PM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870112 | 1030AM | 870112 | 1115AM | 200 | GAL | 1700 ROOSEVELT | SAN DIEGO | SD | 6" CL MAIN-MANHOLE | ROOTS AND GREASE | Y | MISSION BAY | PACIFIC OCEAN |  | Y | Y | 02
870112 |  | WALTER O'LEARY | 6192367030 | SAN DIEGO, CITY OF | 870112 | 0900AM | 870112 | 1030AM | 900 | GAL | 3760 WARD ROAD | SAN DIEGO | SD | MANHOLE | GREASE | N | NONE |  | EO3BST AND WARD |  |  |  | NO SIGNS NEEDED
870112 | 1540PM | JIM McCURLY | 6195789772 | SAN DIEGO, CITY OF | 870112 | 1300PM | 870112 | 1530PM | 300 | GAL | 4738 BOUNDARY ST | SAN DIEGO | SD | SEWER LINE | GREASE | Y | SAN DIEGO RIVER | PACIFIC OCEAN |  | Y | N |  | NOT POSTED BECAUSE CO. HEALTH SAID NOT NEEDED.
870108 | 0845AM | JIM McCURLY | 6195789772 | SAN DIEGO, CITY OF | 870108 | 1830PM | 870108 | 2130PM | 180 | GAL | 515 NORTH 27TH ST | SAN DIEGO | SD | SEWER LINE | GREASE BLOCKAGE AND ROCKS | N | NONE |  | SURFACE INTO STORM DRAIN | Y | Y
870108 | 0845AM | JIM McCURLY | 6195789772 | SAN DIEGO, CITY OF | 870108 | 1700PM | 870108 | 1930PM | 450 | GAL | 5141 CANTERBURY DRIVE | SAN DIEGO | SD | SEWER LINE | ROOTS | N | NONE |  | STORM DRAIN | Y | N
870105 | 1400PM | ALLEGRA, CNTY HEALTH | 6192362802 | SAN DIEGO, CITY OF | 870105 | 1116AM | 870105 | 1250PM | 6000 | GAL | EAST MISSION BAY DRIVE | SAN DIEGO | SD | PUMP STATION 41 | 42" MAIN BLOCK | Y | DE ANZA COVE |  |  | Y | Y
870116 | 1400PM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870116 | 0815AM | 870116 | 0915AM | 1200 | GAL | CASTLE HILL DR & VICKY DR | SAN DIEGO | SD | MONHOLE | GREASE IN 8" VC MAIN | Y | PACIFIC OCEAN |  |  | Y | Y |  | 4 SIGNS POSTED 50FT APART.
860416 | 1000AM | MERRILY SEVERANCE | 6192713321 | MIRAMAR NAVAL AIR STATION | 860415 | 1330PM | 860416 | 1430PM | 50000 | GAL | TIGER AVE - ON BASE. | SAN DIEGO | SD | MANHOLE | SEWERLINE BLOCKAGE | Y | MISSION BAY VIA ROSE CREEK |  |  | Y | Y |  | MISSION BAY POSTED.
870119 | 1400PM | DAVE | 7145822230 | SANTA MARGARITA WATER DISTRICT | 870118 | 1330PM | 870118 | 1800PM | 7000 | GAL | GOLETA AND OSO PARKWAY | MISSION VIEJO | OC | CORDOVA GRAVITY SEWER | UNKNOWN OBSTRUCTION | Y | PACIFIC OCEAN |  |  | N | N |  | COUNTY HEALTH WILL BE NOTIFIED ON 1/20/87 BY DAVE.
870122 | 0810AM | JOHN McPHERSON | 6192367341 | SAN DIEGO, CITY OF | 870122 | 0015AM | 870122 | 0200AM | 525 | GAL | 4465 MISSION BLVD. | SAN DIEGO | SD | 8" SEWER MAIN | GREASE IN 8" SEWER MAIN | Y | PACIFIC OCEAN |  |  | Y | Y |  | OVERFLOW RATE WAS 5 GPM.
870114 | 1440PM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870113 | 1415PM | 870114 | 1000AM | 12600 | GAL | ARRIBA ST & PALMILLA DR CANYON | SAN DIEGO | SD | MANHOLE | DEBRIS IN MANHOLE.CHANNEL IN MANHOLE NOT CUT OUT. | Y | ROSE CREEK | NONE | INTERCEPTOR-DAMON AV | Y | N
870120 |  | W J O'LEARY | 6192367030 | SAN DIEGO, CITY OF | 870114 | 0927AM | 870114 | 1027AM | 1200 | GAL | 3300 BLOCK OF REDWOOD ST. | SAN DIEGO | SD | MANHOLE IN ALLEY WEST OF 33ST. | ROOTS 344' SECTION OF 6" EPMN NORTH OF MANHOLE, REDWOOD ST. | N | NONE | NONE | STM DRAIN AT FELTON & NUTMEG | N | N
870120 |  | W J O'LEARY | 6192367030 | SAN DIEGO, CITY OF | 870113 | 1405PM | 870113 | 1705PM | 4500 | GAL | 4041 T ST. | SAN DIEGO | SD | MANHOLE | GREASE AND ROCKS 8"VC AT 340' CLEARED MAIN RODDING | N | NONE | NONE |  | N | N
870122 |  | R L WILLIAMS | 6192367030 | SAN DIEGO, CITY OF | 870120 | 0845AM | 870120 | 1030AM | 600 | GAL | 3713 37TH ST | SAN DIEGO | SD | MANHOLE | ROOTS IN 6" VC MAIN NORTH OF LANDIS,EAST OF 37TH IN CANYON. | N | NONE | NONE | NORTH INTO CANYON INTO GROUND | N | N
870122 |  | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870115 | 0740AM | 870115 | 0810AM | 600 | GAL | 4927 QUINCY ST | SAN DIEGO | SD | 8" VC MAIN | ROOT OBSTRUCTION | N | NONE | NONE | CANYON | Y | N
870120 | 1635PM | GARY K ORR | 6194397164 | OCEANSIDE, CITY OF | 870120 | 1400PM | 870120 | 1700PM | 900 | GAL | 3100 BLOCK OF OCEANSIDE BLVD. | OCEANSIDE | SD | SEWER MAIN | CONTRACTORS BACKHOE OPENED CRACK IN 18" GRAVITY SEWER MAIN.FLOW SPREAD THROUGH STORM DRAIN INTO UPPER LOMA ALTA CREEK | Y | LOMA ALTA CREEK | LA SALINA SLUGH |  | Y | N |  | STORM DRAIN SAND BAGGED. AREA TOO REMOTE FOR PUBLIC CONTACT.NO SOLIDS REACHED RECEIVING H2
870116 | 0800AM | LLOY THOMPSON | 7144973311 | LAGUNA BEACH, CITY OF | 870116 | 0800AM | 870116 | 0900AM | 100 | GAL | 688 SOUTH COAST HWY. | LAGUNA BEACH | OR | MANHOLE #29 | SEWER LINE PLUGGED WITH GREASE AND ROOTS | Y | PACIFIC OCEAN | NONE |  | Y | N |  | FLUSHED STORM DRAIN WITH 1000 GAL WATER AND 5 LBS OF CHLORINE.
870121 |  | R.L. WILLIAMS | 6192367030 | SAN DIEGO, CITY OF | 870116 | 0830AM | 870116 | 1000AM | 3600 | GAL | ALBATROSS & WASHINGTON ST. | SAN DIEGO | SD | MANHOLE IN ALLEY NORTH OF WASH | GREASE AND RAGS FLOWED TO STORM DRAIN AT WASHINGTON AND BRANT. | N | NONE | NONE | STORM DRN. WASHINGTON & BRANT | N | N |  | CLEANED AND SPRAYED .
870114 | 0830AM | FRED WOOD | 6192216626 | SAN DIEGO, CITY OF | 870114 | 0210AM | 870114 | 0212AM | 10 | GAL | 1902 GATCHELL RD. | SAN DIEGO | SD | VORTEX | AIR AND EFFLUENT DISCHARGED UP THROUGH VORTEX STRUCTURE. | Y | PACIFIC OCEAN | NONE |  | Y | N
870121 | 0815AM | FRED WOOD | 6192216626 | SAN DIEGO, CITY OF | 870121 | 0340AM | 870121 | 0343AM | 10 | GAL | POINT LOMA WWTP VORTEX | SAN DIEGO | SD | VORTEX | BURP- AIR AND EFFLUENT | Y | PACIFIC OCEAN | NONE |  | Y | N
870120 | 1500PM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870120 | 0810AM | 870120 | 0840AM | 450 | GAL | FOOTHILL & LAURING ST. | SAN DIEGO | SD | MANHOLE | ROCKS BLOCKING 8" MAIN | Y | PACIFIC OCEAN | NONE |  | Y | Y
870123 | 0835AM | GARY ORR | 6194397164 | OCEANSIDE, CITY OF | 870122 | 1730PM | 870122 | 2200PM | 900 | GAL | INT. I-5 SAN LUIS REY RIVER | OCEANSIDE | SD | NORTH BRIDGE WASTE PUMP STA. | 1 LINE OF A 3 PHASE LINE BLEW,CAUSING POWER FAILURE-NOBACKUP POWER.VOLUME OF STATION IS 200 GALLONS PER HOUR. | Y | SAN LUIS REY RIVER | PACIFIC OCEAN |  | Y | N |  | SUGGEST LETTER TO OCEANSIDE REQUESTING INFO ON THE LACK OF BACKUP SYSTEM.
870123 | UNKNWN | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870117 | 1145AM | 870117 | 1345PM | 120 | GAL | 4920 DEFIANCE WAY | SAN DIEGO | SD | 8" VC MAIN | ROOT OBSTRUCTION | N | NONE | NONE | NONE | N | N | N
870118 | UNKNWN | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870118 | 1345PM | 870118 | 1445PM | 600 | GAL | GENESEE & PARK MESA WAY | SAN DIEGO | SD | 8" VC MAIN | GREASE OBSTRUCTION | N | NONE | NONE | NONE | N | N
870123 | UNKNWN | R L WILLIAMS | 6192367030 | SAN DIEGO, CITY OF | 870121 | 1330PM | 0 | UNKNWN | 10 | GAL | 4954 CRESITA DRIVE | SAN DIEGO | SD | MANHOLE | ROOTS | N | NONE | NONE | MANHOLE REAR OF 4954 CRESITA | N |  |  | WATER IS DOWN BUT NOT CLEAR.TRYING TO LOCATE MANHOLE TO COMPLETE RODDING MAIN.
870123 | UNKNWN | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870118 | 1500PM | 870118 | 1800PM | 180 | GAL | 3535 MADISON AVENUE | SAN DIEGO | SD | 6" VC MAIN | GREASE OBSTRUCTION | N | NONE | NONE | NONE | N | N
870123 | UNKNWN | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870116 | 0540PM | 870116 | 0640PM | 1400 | GAL | 1400 COMMERCIAL ST | SAN DIEGO | SD | 6" VC MAIN | GREASE OBSTRUCTION | N | NONE | NONE | NONE | N | N
870123 | UNKNWN | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870119 | 0945AM | 870119 | 1115AM | 900 | GAL | 5402 REDLANDS PLACE | SAN DIEGO | SD | 8" VC MAIN | ROOT OBSTRUCTION | N | NONE | NONE | NONE | N | N
870123 | UNKNWN | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870117 | 1040AM | 870117 | 1140AM | 60 | GAL | 1100 BLOCK OF 40TH ST. | SAN DIEGO | SD | 6" VC MAIN | GREASE OBSTRUCTION | N | NONE | NONE | NONE | N | N
870126 | 0940AM | JEANNIE DUNHAM | 6194521556 | SAN DIEGO, CITY OF | 0 | UNKNWN | 0 | UNKNWN | 10 | GAL | PORTOLA & WASHINGTON PLACE | SAN DIEGO | SD | SUSPECTED: SEWER MAIN | UNKNOWN-THE WATER IS PERCOLATING OUT OF THE PAVEMENT. IT IS MURKY AND HAS BAD ODOR. | Y | STRM DRN TO ?? UNKNWN NOW | NONE | NONE | N | N |  | WG CALLED CITY UTIL. -THEY ARE INVESTIGATING-WAIT FOR REPORT FROM CITY.
870127 | 0830AM | ALICE BENSON | 6192216626 | SAN DIEGO, CITY OF | 870126 | 2200PM | 870126 | 2205PM | 10 | GAL | 1902 GATCHELL ROAD | SAN DIEGO | SD | VORTEX | TRAPPED AIR AND EFFLUENT ("BURP") | Y | PACIFIC OCEAN | NONE | NONE | Y | N |  | EFFLUENT SEEPED THROUGH LOW SPOT IN SAND BAGS.
870127 | 0830AM | ALICE BENSON | 6192216626 | SAN DIEGO, CITY OF | 870127 | 0130AM | 870127 | 0132AM | 10 | GAL | 1902 GATCHELL ROAD | SAN DIEGO | SD | VORTEX | TRAPPED AIR AND EFFLUENT ("BURP") | Y | PACIFIC OCEAN | NONE | NONE | Y | N |  | EFFLUENT SEEPED THROUGH LOW SPOT IN SAND BAGS.
870105 | LETTER | LIBERATO D.TORTORICI | 6194387444 | BUENA SANITATION DISTRICT | 861219 | 1400PM | 861219 | 1445PM | 1500 | GAL | NO. 1 SANITARY WAY | VISTA | SD | SECONDARY SEDIMENTATION TANK | SKIMMER PAN IN SED. TANK WAS LEFT IN LOWERED POSITION. WELL FILLED,PUMPS WERE OFF,EFFLUENT PASSED SURFACE VALVE. | N | NONE | NONE | DOWN HILL BEHIND PLANT. |  |  |  | THIS SPILL WAS ORIGINALLY REPORTED TO WQCB BY PHONE ON 12/19/86.
870121 | 1502PM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870121 | 1040AM | 870121 | 1140AM | 6 | GAL | 4428 PARK BLVD. | SAN DIEGO | SD | SEWER LINE | GREASE | N | NONE | NONE | NONE | N | N |  | AREA WAS CLEANED UP BY CREW.
870127 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870122 | 2030PM | 870122 | 2200PM | 900 | GAL | 47TH AND POLK ST. | SAN DIEGO | SD | 6" VC MAIN | GREASE BLOCKAGE | N | NONE | NONE | NONE | N | N
870121 | 1900PM | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 870121 | 1900PM | 870121 | 2015PM | 1000 | GAL | EAST LINCOLN/1100 BLOCK | ESCONDIDO | SD | MANHOLE PG21 MH7 | GREASE BLOCKAGE IN SEWER MAIN | N | NONE | NONE | NONE | Y
870126 | 0830AM | M ARNOLD | 6192364717 | SAN DIEGO, CITY OF | 870125 | 1530PM | 870125 | 1730PM | 360 | GAL | 4211 CENTRAL AVE | SAN DIEGO | SD | 6" VC SEWER | GREASE BLOCKAGE | N | NONE | NONE | STORM DRAIN | Y | N |  | "ZEP" DISINFECTANT WAS APPLIED.
870126 | 0830AM | M ARNOLD | 6192364717 | SAN DIEGO, CITY OF | 870125 | 1100AM | 870125 | 1500PM | 240 | GAL | 3634 17TH AVENUE IN CANYON | SAN DIEGO | SD | 8" VC SEWER MAIN | TREE ROOT BLOCKAGE | N | NONE | NONE | SOAKED INTO DIRT IN CANYON | Y | N
870121 | 0830AM | FRED WOOD | 6192216626 | SAN DIEGO, CITY OF | 870121 | 0340AM | 870121 | 0343AM | 10 | GAL | 1902 GATCHELL ROAD | SAN DIEGO | SD | EFFLUENT VORTEX | GAS BACKING UP IN EFFLUENT DISCHARGE PIPE | Y | PACIFIC OCEAN | NONE | NONE | Y | N |  | SEWAGE SEEPED THROUGH CONTAINMENT AREA AT BOTTOM OF DISCHARGE VORTEX.
870129 | 0845AM | ALICE BENSON | 6192216626 | SAN DIEGO, CITY OF | 870129 | 0010AM | 870129 | 0012AM | 10 | GAL | 1902 GATCHELL ROAD | SAN DIEGO | SD | VORTEX | TRAPPED AIR AND EFFLUENT CAUSED "BURP". | Y | PACIFIC OCEAN | NONE | NONE | Y | N |  | EFFLUENT SEEPED THROUGH LOW SPOT IN SANDBAG PILE.
870129 | 1415PM | DALE HOFFLAND | 6195655343 | SPRING VALLEY SANITATION DIST. | 870129 | 0620AM | 870129 | 0735AM | 5000 | GAL | INT. OF JAMACHA & SPRING VALLE | SPRING VALLEY | SD | MANHOLE (3 MH'S E. OF INT.) | ROCK OBSTRUCTING THE INSIDE OF SEWER MAIN. | Y | CREEK TO SWEETWATER RESERVOIR | NONE | NONE | Y | N |  | CREW CHLORINATED FEW HUNDRED YDS. DOWNSTREAM OF MH AND RODDED SEWER LINE.
870128 | 0854AM | ALICE BENSON | 6192216626 | SAN DIEGO, CITY OF | 870128 | 0235AM | 870128 | 0237AM | 10 | GAL | POINT LOMA WWTP | SAN DIEGO | SD | VORTEX | VORTEX "BURP" - AIR & EFFLUENT TRAPPED. | Y | PACIFIC OCEAN | NONE | NONE | Y | N
861201 | 0925AM | ALLEGRA & N. TUCKER | 6192364717 | SAN DIEGO, CITY OF | 861126 | 2300PM | 861127 | 1300PM | 42000 | GAL | 2634 GRAND AVE & BOND ST. | SAN DIEGO | SD | MANHOLE | OBSTRUCTED SEWER | Y | MISSION BAY VIA ROSE CREEK | NONE | NONE | Y | Y |  | CAMPLAND BEACH POSTED AND SAMPLED BY CO. HEALTH ON 11/28, 12/1, 12/2.
870129 | LETTER | WALTER O'LEARY | 6192367030 | SAN DIEGO, CITY OF | 870123 | 1245PM | 870123 | 1400PM | 456 | GAL | 3777 44TH ST | SAN DIEGO | SD | CLEAN OUT VALVE | GREASE | N | NONE | NONE | NONE | N | N
870129 | LETTER | WALTER O'LEARY | 6102367030 | SAN DIEGO, CITY OF | 870126 | 1415PM | 870126 | 1515PM | 300 | GAL | 4567 DWIGHT ST. | SAN DIEGO | SD | MANHOLE | GREASE | N | NONE | NONE | NONE | N | N
870129 | LETTER | WALTER O'LEARY | 6192367030 | SAN DIEGO, CITY OF | 870123 | 0600AM | 870123 | 0900AM | 500 | GAL | DATE ST & DELEVAN ST | SAN DIEGO | SD | ABANDONED PIPE | BACKUP INTO PORTION OF ABANDONED MAIN AND MANHOLE | N | NONE | NONE | NONE | N | N |  | POURED 2 YDS. OF CONCRETE IN MANHOLE AND MAIN.
870129 | LETTER | WALTER O'LEARY | 6192367030 | SAN DIEGO, CITY OF | 870127 | 1230PM | 870127 | 1430PM | 0 | ??? | 2000 EAST STREET | SAN DIEGO | SD | MANHOLE | ROCKS | N | NONE | NONE | NONE | N
870105 | 1500PM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870105 | 1130AM | 870105 | 1230PM | 6000 | GAL | MISSION BAY DRIVE & ROSEWOOD | SAN DIEGO | SD | MANHOLES (3) | SURCHARGE-60" LINE COULD NOT HANDLE FLOW CAUSING SURCHARGE IN A 30 & 42" UPSTREAM LINE. | Y | MISSION BAY | NONE | NONE | Y | Y |  | ENTERED COVE APPROX. 150' EAST OF P.S. 41. 4 SIGNS WERE POSTED @ 200FT.
870127 | 0800AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870127 | 1700PM | 870127 | 1900PM | 60 | GAL | 7917 IVANHOE AVENUE | SAN DIEGO | SD | SEWER LINE | GREASE | N | NONE | NONE | NONE | Y | N
870202 | LETTER | EMINGO | 6192367084 | SAN DIEGO, CITY OF | 870124 | 1400PM | 870124 | 1500PM | 120 | GAL | 4010 THORN | SAN DIEGO | SD | MANHOLE | SEWER MAIN STOP | N | NONE | NONE | NONE | N | N
870202 | LETTER | EMINGO | 6192367084 | SAN DIEGO, CITY OF | 870124 | 0300PM | 870124 | 1400PM | 300 | GAL | 4942 CLAIRMONT DRIVE | SAN DIEGO | SD | MANHOLE | GREASE IN SEWER MAIN | N | NONE
870202 | LETTER | EMINGO | 6192367084 | SAN DIEGO, CITY OF | 870123 | 1500PM | 870123 | 2200PM | 2100 | GAL | 1805 INTERNATIONAL ROAD | SAN DIEGO | SD | MANHOLE | ROCKS IN MAIN. | N | NONE | NONE | NONE | N | N
870202 | LETTER | WALTER O'LEARY | 6192367030 | SAN DIEGO, CITY OF | 870128 | 0810AM | 870128 | 0910AM | 300 | GAL | 5337 MEADE AVENUE | SAN DIEGO | SD | MANHOLE | ROOTS & GREASE. | N | NONE | NONE | NONE | N | N
870202 | LETTER | WALTER O'LEARY | 6192367030 | SAN DIEGO, CITY OF | 870128 | 0825AM | 870128 | 1025AM | 480 | GAL | 6394 ELMHURST STREET | SAN DIEGO | SD | MANHOLE | ROCKS | N | NONE | NONE | NONE | N | N
870129 | 0830AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870128 | 1430PM | 870128 | 1500PM | 15 | GAL | 2040 HARBOR ISLAND DRIVE | SAN DIEGO | SD | MANHOLE IN PARKING LOT | 8" VC SEWER MAIN STOPPED BY GREASE. | N | NONE | NONE | PARKING LOT. | Y |  |  | APPLIED DISINFECTANT TO WATER SOAKED AREA IN LOT.
870202 | LETTER | WALTER O'LEARY | 6192367030 | SAN DIEGO, CITY OF | 870129 | 1000AM | 870129 | 1100AM | 300 | GAL | 3900 BLOCK OF ADAMS AVENUE | SAN DIEGO | SD | MANHOLE | ROOTS & GREASE | N | NONE | NONE | NONE | N | N
870202 | LETTER | WALTER O'LEARY | 6192367030 | SAN DIEGO, CITY OF | 870129 | 1312PM | 870129 | 1412PM | 120 | GAL | 5447 MAISEL WAY | SAN DIEGO | SD | MANHOLE | BIG ROCK IN MANHOLE. | N | NONE | NONE | NONE | N | N |  | ROCK REMOVED FROM MANHOLE. STOPPAGE RELIEVED.
870202 | LETTER | UNKNOWN | 6194397164 | OCEANSIDE, CITY OF | 870127 | 1320PM | 870127 | 1340PM | 200 | GAL | 3679 CAMEO DRIVE | OCEANSIDE | SD | CAMEO ST. PUMP STATION | MOTOR SAVER SWITCH ON PUMP MOTOR ACTIVATED, CAUSING POWER FAILURE TO PUMP. | N | NONE | NONE | STORM DRAINAGE DITCH | N |  |  | DRAINAGE DITCH IS UNLINED. EFFLUENT PERCOLATED INTO SOIL. NO RESIDUE.
870127 | 1000AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870123 | 2300PM | 870123 | 2330PM | 5 | GAL | 3476 MONROE STREET | SAN DIEGO | SD | SEWER LINE. | GREASE | N | NONE | NONE | STAYED IN ALLEY | Y
870127 | 1000AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870125 | 1200AM | 870125 | 1400PM | 2400 | GAL | 2171 ALTA VIEW DRIVE | SAN DIEGO | SD | SEWER LINE | GREASE | N | NONE | NONE | STORM DRAIN | Y
870128 | 0800AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870127 | 1505PM | 870127 | 2030PM | 600 | GAL | 3634 7TH AVE / IN CANYON | SAN DIEGO | SD | 7-33 MANHOLE IN CANYON | 6" VC SEWER STOPPED BY ROOTS AND GREASE. | N | NONE | NONE | CANYON DRAIN SOAKED IN GROUND. | Y | N |  | APPLIED DEOTORANT AND DISINFECTANT TO SATURATED AREA.
870203 | 1145AM | JIM SMITH | 7146432006 | MOULTON NIGUEL WATER DISTRICT | 870203 | 1130AM | 870205 | 1900PM | 75000 | GAL | LOS ALISOS & JERONIMO | MISSION VIEJO | OR | 10" FORCE MAIN | BREAK IN A 1964 FORCE MAIN MADE OF TACITE MATERIAL. | NO | NONE | NONE | PARK BASEBALL FIELD | Y | Y | ? | NEW MAIN WILL BE IN BY JUL OR AUG..APPLIED HTH DISINFECTANT AT OVERFLOW POINT.
870129 | 1205PM | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF/S.D. CITY | 870129 | 1145AM | 870129 | 1215PM | 6000 | GAL | 1750 W CITRACADO PKWY | ESCONDIDO | SD | RANCHO BERNARD PUMP STATION | CITY OF SAN DIEGO TESTING PUMPING CAPACITY AT RANCHO BERNARD PUMP STATION. | N | NONE | NONE | STORM DRAIN SYSTEM | N |  |  | AREA TREATED WITH DISINFECTANT AND WASHED DOWN.CITY OF S.D. PERSONNELDID NOT COOPERATE.
870203 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870129 | 1230PM | 870129 | 1430PM | 600 | GAL | 6787 HILLSIDE DRIVE | SAN DIEGO | SD | 6" VC MAIN | ROOT OBSTRUCTION | N | NONE | NONE | YARD | N
870127 | 1000AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870123 | 2000PM | 870123 | 2100PM | 10 | GAL | 4243 INGRAHAM ST. | SAN DIEGO | SD | SEWER LINE | GREASE & ROOTS | N | NONE | NONE | CHURCH PARKING LOT | Y
870202 | 0810AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870130 | 1530PM | 870130 | 1630PM | 60 | GAL | 4494 CALLE DE VIDA | SAN DIEGO | SD | SEWER LINE | GREASE AND ROOTS | N | NONE | NONE | STORM DRAIN | Y
870205 | 1030AM | GEORGE LONG | 6195655359 | SAN DIEGO, COUNTY OF | 870204 | 1400PM | 0 | UNKNWN | 1000 | GAL | PINE VALLEY WASTEWATER T.P. | PINE VALLEY | SD | PERCOLATION POND | GOPHER HOLE IN PERCOLATION BED BERM | N | NONE | NONE | SOIL ADJACENT TO PERC. POND | ?
870206 | LETTER | DELVIN BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870203 | 1715PM | 870203 | 1945PM | 2250 | GAL | 4076 MYRTLE AVENUE | SAN DIEGO | SD | CLEANOUT | GREASE | N | NONE | NONE | NONE | N
870203 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870203 | 1100AM | 870203 | 1200PM | 900 | GAL | 8821 VIA ANDAR | SAN DIEGO | SD | MANHOLE-8" VC MAIN | ROOT OBSTRUCTION | N | NONE | NONE | NONE | ? | ? | ?
870206 | LETTER | AYAP BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870204 | 1820PM | 870204 | 2220PM | 480 | GAL | 3180 UNIVERSITY AVE | SAN DIEGO | SD | MANHOLE | GREASE & SLUDGE | N | NONE | NONE | NONE | ? | ? | ?
870202 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870202 | 1115AM | 870202 | 1145AM | 300 | GAL | 7600 LA JOLLA BLVD. | SAN DIEGO | SD | MANHOILE-8" VC MAIN | GREASE OBSTRUCTION | N | NONE | NONE | NONE | ? | ? | ?
870205 | LETTER | W. O'LEARY & DELVIN | 6192367030 | SAN DIEGO, CITY OF | 870202 | 0750AM | 870202 | 0930AM | 10 | GAL | 3412 PETRA PLACE | SAN DIEGO | SD | MANHOLE | UNKNOWN | N | NONE | NONE | NONE | N | N |  | MANHOLE NOT OVERFLOWING WHEN CREW ARRIVED.
870205 | LETTER | O'LEARY & DELVIN | 6192367030 | SAN DIEGO, CITY OF | 870202 | 2100PM | 870203 | 0300AM | 10 | GAL | 2672 ISLAND AVENUE | SAN DIEGO | SD | MANHOLE | UNKNOWN | N | NONE | NONE | NONE | N | N |  | MANHOLE NOT OVERFLOWING WHEN CREW ARRIVED.
870202 | 0805AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870130 | 1230AM | 870131 | 0430AM | 4800 | GAL | 3100 BLOCK OF MARTIN AVENUE | SAN DIEGO | SD | SEWER MANHOLE | 8" VC MAIN STOPPED BY ROCKS, ROOTS, SLUDGE AND OTHER DEBRIS. | N | NONE | NONE | STORM DRAIN IN AREA | N | ? |  | OVERFLOW ACCUMULATED IN STORM DRAIN AREA TREAATED WITH DISINFECTANT.
870205 | LETTER | O'LEARY & FAYAP | 6192367030 | SAN DIEGO, CITY OF | 870131 | 1325PM | 870131 | 1815PM | 900 | GAL | 1139 ALBERTIN PLACE | SAN DIEGO | SD | MANHOLE | UNKNOWN | N | NONE | NONE | NONE | N | N
870205 | LETTER | O'LEARY & FAYAP | 6192367030 | SAN DIEGO, CITY OF | 870131 | 1325PM | 870131 | 2115PM | 720 | GAL | 200 EAST PARK AVENUE | SAN DIEGO | SD | MANHOLE | HEAVY GREASE | N | NONE | NONE | NONE | N | N
870205 | LETTER | O'LEARY & GRATE | 6192367030 | SAN DIEGO, CITY OF | 870131 | 0113AM | 870131 | UNKNWN | 10 | GAL | 1381 PALM AVENUE SB. | SAN DIEGO | SD | CLEAN OUT | UNKNOWN | N | NONE | NONE | NONE | N | N |  | AREA AROUND CLEANOUT WET, VOLUME UNKNOWN.
870205 | LETTER | O'LEARY & GRATE | 6192367030 | SAN DIEGO, CITY OF | 870201 | 1119AM | 870201 | 1519PM | 720 | GAL | 3526 ORANGE AVENUE | SAN DIEGO | SD | MANHOLE | GREASE | N | NONE | NONE | NONE | N | N
870205 | LETTER | BEADLE & GRATE | 6192367030 | SAN DIEGO, CITY OF | 870201 | 1000AM | 870201 | 1200 N | 120 | GAL | 4893 VOLTAIRE ST | SAN DIEGO | SD | HOUSE LINE | GREASE | N | NONE | NONE | NONE | N | N
870205 | LETTER | O'LEARY & FAYAP | 6192367030 | SAN DIEGO, CITY OF | 870131 | 0955AM | 870131 | 1315PM | 900 | GAL | 5254 TIPTON STREET | SAN DIEGO | SD | MANHOLE | UNKNOWN | N | NONE | NONE | NONE | N | N
870204 | 0930AM | GEORGE LONG | 6195655359 | SAN DIEGO, COUNTY OF | 870203 | 0700AM | 870203 | 0715AM | 500 | GAL | JAPUTAL VALLEY RD & I-8 EAST | DESCANSO CA | SD | SLUDGE DRYING BED J800 FT3 | START-STOP SWITCH ON EFFLUENT PUMPS FAILED TO START PUMPS.EMERGENCY ALARM FAILED ALSO DUE TO LOOSE CONNECTION AT SWITCH. | N | NONE | NONE | DRY CREEK BED | Y | N |  | SPILL WAS RESULT OF MECHANICAL & ELECTRICAL MALFUNCTION OF EQUIPMENT.SPILL=>2.PPM RESI CL2
870203 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870202 | 1100AM | 870202 | 1600PM | 15000 | GAL | 9494 CARROL CANYON ROAD | SAN DIEGO | SD | MANHOLE-12" VC MAIN | ROOT OBSTRUCTION | N | NONE | NONE | NONE | N | ?
870205 | LETTER | O'LEARY & F. AYAP | 6192367030 | SAN DIEGO, CITY OF | 870131 | 0240AM | 870131 | 0840AM | 6000 | GAL | 32ND ST. & GREELY AVENUE. | SAN DIEGO | SD | MANHOLE | BRICKS AND ROCKS | N | NONE | NONE | NONE | N | N
870206 | LETTER | BEADLE & DENLIN | 6192367030 | SAN DIEGO, CITY OF | 870203 | 1250PM | 870203 | 1550PM | 900 | GAL | 3747 32ND STREET | SAN DIEGO | SD | MANHOLE | GREASE | N | NONE | NONE | NONE | N | N
870205 | LETTER | O'LEARY & F. AYAP | 6192367030 | SAN DIEGO, CITY OF | 870201 | 1515PM | 870201 | 2315PM | 14400 | GAL | 9494 CARROL CANYON ROAD | SAN DIEGO | SD | MANHOLE | UNKNOWN | N | NONE | NONE | NONE | N | N
870206 | LETTER | BEADLE & AYAP | 6192367030 | SAN DIEGO, CITY OF | 870204 | 2250PM | 870205 | 0150AM | 360 | GAL | 3235 40TH STREET | SAN DIEGO | SD | MANHOLE | GREASE | N | NONE | NONE |  | N | ?
870211 | 0915AM | STEVE MAURER/BEJAR,C | 6194662405 | LA MESA, CITY OF | 870209 | 1100AM | 870211 | 1700PM | 9000 | GAL | 8810 CENTER DR/CANYON/92041 | LA MESA | SD | GRAVITY MAIN/MANHOLE | VANDALS FILLED MANHOLE WITH ROCKS AND CLOGGED LINE. | N | NONE | NONE | STORM DRAIN TO ALVARADO CANYON | Y | N |  | THE SEWAGE PERCOLATED INTO THE SOIL. THE ROCKS WERE REMOVED FROM THE MANHOLE.
870213 | 0900AM | GARY ORR | 6194397164 | OCEANSIDE, CITY OF | 870212 | 1645PM | 870212 | 1730PM | 9000 | GAL | OCEAN BLVD. PUMP STATION | OCEANSIDE | SD | PUMP STATION | SDGE POWER FAILURE. | Y | LOMA ALTA CREEK | NONE | NONE | N | N |  | PUBLIC HAS NO ACCESS TO AREA AFFECTED-PUMP STATION SHOULD HAVE BACKUP POWER.
870213 | 0955AM | RICK SMITH | 6192918208 | SAN DIEGO, CITY OF | 870112 | 830AM | 870212 | 0945AM | 200000 | GAL | BROWN FIELD WWTP | SAN DIEGO | SD | SECONDARY HOLDING POND | UNAUTHORIZED CONTRACTOR RIPPED OUT BERMS, DRAINING ALL THE PONDS. | ?? | UNKNOWN AT THIS TIME/TJ RIVER? | NONE | NONE | Y | N
870204 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870204 | 0930AM | 870204 | 1030AM | 30 | GAL | 2625 ULRIC ST. | SAN DIEGO | SD | 8" VC MAIN/MANHOLE | GREASE | N | NONE | NONE | NONE | ? | ?
870209 | LETTER | BEADLE/AYAP | 6192367030 | SAN DIEGO, CITY OF | 870205 | 1610PM | 870205 | 1910PM | 900 | GAL | AERO & J.J. MONTGOMERY DRIVE | SAN DIEGO | SD | MANHOLE | HEAVY GREASE | N | NONE | NONE | NONE | N | N
870129 | 0620AM | RON BASILE | 6195655343 | SAN DIEGO, COUNTY OF | 870129 | 0620AM | 870129 | 0735AM | 5000 | GAL | JAMACHA BL E. OF SWEETWATER | SPRING VALLEY | SD | SEWER MANHOLE/10" MAIN LINE | LARGE ROCK BLOCKAGE | Y | SWEETWATER LAKE | NONE | NONE | Y | N |  | MOST OF THE VOLUME DID NOT REACH THE LAKE./LOCATION WAS EAST OF SWEETWATER SPRING BLVD.
870209 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870206 | 1415PM | 870206 | 1515PM | 60 | GAL | 3210 MISSION BLVD | SAN DIEGO | SD | MANHOLE-6" VC MAIN | GREASE | N | NONE | NONE | NONE | ? | ? | ?
870217 | LETTER | BEADLE/THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870206 | 0800AM | 870206 | 0900AM | 300 | GAL | 4569 DWIGHT ST | SAN DIEGO | SD | MANHOLE | GREASE | N | NONE | NONE | NONE | N | N | NA
870217 | LETTER | BEADLE/DENLIN | 6192367030 | SAN DIEGO, CITY OF | 870209 | 1410PM | 870209 | 1510PM | 600 | GAL | 3841 39TH ST | SAN DIEGO | SD | CLEAN OUT | GREASE & DEBRIS | N | NONE | NONE | NONE | N | N | NA
870210 | 0815AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870209 | 1100AM | 870209 | 1430PM | 720 | GAL | CANYON WO 163/SO ROBINSON | SAN DIEGO | SD | 8" VC SEWER IN CANYON | ROOTS AND RAGS | N | NONE | NONE | CANYON & STORM DRAIN | Y | N | NA
870209 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870206 | 0900AM | 870206 | 0920AM | 100 | GAL | LAJOLLA COLONY DR&PORTE LA PAZ | SAN DIEGO | SD | MANHOLE -8" VC MAIN | GREASE | N | NONE | NONE | NONE | ? | ? | NA
870209 | 0915AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870208 | 1245PM | 870208 | 1445PM | 600 | GAL | LA MANCHA DR & PROMONTORY ST. | SAN DIEGO | SD | 6" CEMENT PIPE | ROOTS & GREASE | N | NONE | NONE | CURB LINE-LA MANCHA & PROMON. | N | N
870209 | LETTER | DONN BRIFFIN | 6192367334 | SAN DIEGO, CITY OF | 870208 | 1000AM | 870208 | 1230PM | 600 | GAL | LA MANCHA & BAYONNE | SAN DIEGO | SD | MANHOLE 6"-VC MAIN | ROOTS & GREASE | N | NONE | NONE | INGRAHAM & LA MANCHA GUTTER | N | ? | NA
870208 | LETTER | DONN GRIFFIN | 6192367334 | SAN DIEGO, CITY OF | 870208 | 1200 M | 870209 | 0400AM | 100 | GAL | BET. ROSEMONT & PALOMAR | SAN DIEGO | SD | MANHOLE-6"CP MAIN | ROOTS | N | NONE | NONE | 545 ROSEMONT BACKYARD | N | ? | NA
870217 | 1400PM | PAUL DUVEL | 6197530155 | LEUCADIA COUNTY WATER DISTRICT | 870217 | 0830AM | 870217 | 1000AM | 6000 | GAL | LA COSTA PUMPING STATION | CARLSBAD | SD | PUMPING STATION | 6" PLUMBERS TOOL BLOCKED PUMP LINE. | N | NONE | NONE | PENSIQUITAS LAGOON | Y | N | NA | NONE
870213 | 1135AM | JOHN MELBOURNE | 6192362802 | SAN DIEGO, CITY OF | 870213 | 1000AM | 870213 | 1735PM | 45000 | GAL | 4800 FAIRMOUNT | SAN DIEGO | SD | MANHOLE | PIPE BREAK | Y | S.D. RIVER TO OCEAN | NONE | NONE | Y | Y | ??
870217 | 1600PM | DEL HERNANDEZ | 6192365534 | SAN DIEGO, CITY OF | 870215 | 1500PM | 870215 | 1600 | 300 | GAL | 5790 AVENIDA DE NUSTO | RANCHO BERNARDO | SD | PUMP STATION 73 | PLUGGED BUBBLER TUBE IN CONTROL SYSTEM. | Y | POND ON GOLF COURSE | NONE | NONE | N | Y | 06 | POSTED 10 SIGNS.
870217 | 1640PM | DICK ARNOLD | 6194485420 | EL CAJON, CITY OF | 870215 | 1030AM | 870215 | 1330PM | 750 | GAL | 600 BLOCK OF LA SOMBRE | EL CAJON | SD | MANHOLE | ROOT BLOCKAGE | Y | SAN DIEGO RIVER | NONE | NONE | Y | N | NA | NONE
870218 | 1000AM | ALICE BENSON | 6192216626 | SAN DIEGO, CITY OF | 870218 | 0300AM | 870218 | 0301AM | 10 | GAL | POINT LOMA WWTP | SAN DIEGO | SD | VORTEX | BURP IN VORTEX STRUCTURE | Y | PACIFIC OCEAN | NONE | NONE | Y | N | NA | NONE
870210 | 1000AM | STEVEN MAURER | 6194662405 | LA MESA, CITY OF | 870209 | 1100AM | 870210 | 1700PM | 9000 | GAL | 8810 CENTER DRIVE | LA MESA | SD | 8" VC PIPE | ROCK BLOCKAGE | Y | SAN DIEGO RIVER | NONE | SAN DIEGO RIVER | N | N | 00 | NOT POSTED SINCE IT IS A REMOTE AREA.
870219 | 0830AM | DICK ARNOLD | 6194485420 | EL CAJON, CITY OF | 870218 | 0900AM | 870218 | 1015AM | 2300 | GAL | CORNER BATHURST & HEMPDEN CT. | EL CAJON | SD | SEWER MANHOLE | ROOT BLOCKAGE | Y | SAN DIEGO RIVER (POSSIBLY) | NONE | NONE | N | N | NA
870209 | 1530PM | JAMES E. SMITH | 7146432006 | MOULTON NIGUEL WATER DISTRICT | 870208 | 1530PM | 870210 | 0100AM | 30000 | GAL | LOS ALISOS BL & JERONIMO RD | MISSION VIEJO | OR | FORCE MAIN | BREAK IN 10" FORCE MAIN THAT CONVEYS SEWAGE FROM NORTH ALISOS LIFT STA. TO OBRERO IN JERONIMO ROAD. | N | NONE | NONE | GRASS FIELD IN PARK | Y | ? | ?? | NONE
870201 | 0930AM | PETER HUHN | 6197281180 | FALLBROOK SANITARY DISTRICT | 870201 | 0830AM | 870201 | 1000AM | 50 | GAL | 1320 GERALD WAY | FALLBROOK | SD | LATERAL | PLUGGED LATERAL | N | NONE | NONE | SURFACE CONTAINMENT | N | N | NA | NONE
870212 | 1017AM | NANCY ? | 6197288319 | FALLBROOK SANITARY DISTRICT | 870212 | 1015AM | 870212 | 1030AM | 15 | GAL | 1210 SOUTH VINE STREET | FALLBROOK | SD | LATERAL C.O. | ROOTS IN LATERAL | N | NONE | NONE | SURFACE CONTAINMENT | N | N | NA | NONE
870220 | LETTER | BEADLE / THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870212 | 0700AM | 870212 | 1200PM | 500 | GAL | 4775 SEMINOLE DR. | SAN DIEGO | SD | CLEANOUT | LATERAL PROBLEM ON PRIVATE PROPERTY | NO | NONE | NONE | NONE | N | N | NA | CITIZEN WAS NOTIFIED THAT IT WAS A PROPERTY PROBLEM THAT NEEDS A PLUMBER.
870217 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870217 | 0930AM | 870217 | 1230PM | 5400 | GAL | 4955 ACUNA ST | SAN DIEGO | SD | MANHOLE-10" VC MAIN | POSSIBLY ROOT BLOCKAGE. | NO | NONE | NONE | NONE | ? | ? | ?? | NONE
870217 | 1615PM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870217 | 1200 N | 870217 | 1300PM | 60 | GAL | 14248 LA TRUCHA ST | SAN DIEGO | SD | SEWER LINE | ROCKS, SAND AND GRAVEL BLOCKAGE | NO | NONE | NONE | STORM DRAIN | Y | N | NA | NONE
870217 | 1615PM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870214 | 1700PM | 870214 | 1830PM | 180 | GAL | FOREST GLEN RD W OF PICADOR | SAN DIEGO | SD | SEWER LINE | GREASE BLOCKAGE | NO | NONE | NONE | STORM DRAIN | Y | N | NA | NONE
870217 | 0830AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870214 | 1230PM | 870214 | 1530PM | 7 | GAL | 4794 WINONA AVE | SAN DIEGO | SD | SEWER LINE | ROOT AND GREASE BLOCKAGE | NO | NONE | NONE | GROUND DIRT IN ALLEY | Y | N | NA | NONE
870217 | 0830AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870214 | 1700PM | 870214 | 1830PM | 90 | GAL | FOREST GLEN & MAJESTIC | SAN DIEGO | SD | SEWER LINE | GREASE BLOCKAGE | NO | NONE | NONE | DRAINAGE CHANNEL | Y | N | NA | NONE
870220 | LETTER | BEADLE/THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870217 | 1003AM | 870217 | 1303PM | 360 | GAL | 4717 UNIVERSITY AV ALLEY EAST | SAN DIEGO | SD | MANHOLE | GREASE BLOCKAGE | NO | NONE | NONE | NONE | N | N | NA | NONE
870213 | 1209PM | BEADLE STA 38 | 6192367030 | SAN DIEGO, CITY OF | 870213 | 1000AM | 870213 | 1730PM | 22500 | GAL | FAIRMOUNT & ALDINE DR | SAN DIEGO | SD | BROKEN SEWER MAIN | 15" VC SEWER MAIN BREAK | Y | SAN DIEGO RIV./MISSION BAY | NONE | NONE | Y | Y | ?? | NONE
870218 | 1555PM | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 870218 | 1400PM | 870218 | 1630PM | 1000 | GAL | 1100 BLOCK N GAMBLE ST. | ESCONDIDO | SD | MANHOLE ATLAS PG41 MH31 | GREASE STOPPAGE IN MAIN SEWER LINE | NO | NONE | NONE | NONE | N | N | NA | AREA TREATED WITH HTH THEN WASHED DOWN-WATER TO STORM DRAIN.
870217 | 1000AM | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 870217 | 1000AM | 870217 | 1100AM | 200 | GAL | 500FT N OF 1399 HAMILTON LN | ESCONDIDOP | SD | FORCE MAIN AIR RELIEF VALVE | SUB CONTRACTOR PULLED 1" COPPER PIPE OUT OF FORCE MAIN CONNECTED TO AIR RELIEF. | NO | NONE | NONE | NONE | N | N | NA | SPILL TREATED WITH HTH BY STANDARD PACIFIC. SPILL ABSORBED BY GROUND.
870223 | 1500PM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870223 | 0900AM | 870223 | 1000AM | 300 | GAL | VICKY DR & CASTLE HILLS | SAN DIEGO | SD | MANHOLE | CONCRETE IN SEWER LINE AND MANHOLE CAUSED BLOCKAGE. | Y | PACIFIC OCEAN | NONE | NONE | Y | Y | ?? | NONE
870218 | 0950AM | ALICE BENSON | 6192216626 | SAN DIEGO, CITY OF | 870218 | 0300AM | 870218 | 0301AM | 10 | GAL | 1902 GATCHEL/POINT LOMA WWTP | SAN DIEGO | SD | VORTEX STRUCTURE | TRAPPED AIR AND EFFLUENT CAUSED "BURP" AND SEEPAGE FROM VORTEX. | Y | PACIFIC OCEAN | NONE | NONE | Y | N | NA | NONE
870224 | 0900AM | BRUCE BONAR | 7148580946 | SANTA ANA MTNS. CO WATER DIST. | 870223 | 1530PM | 870223 | 2100PM | 10000 | GAL | EL TORO RD & LIVE OAK CANYONRD | TRABUCO CANYON | OR | SEWER LINE, MANHOLE | CONSTRUCTION WORKERS KNOCKED OFF MANHOLE COVER & DUMPED DIRT INTO LINE. CURRENTLY BEING CLEARED OUT. | NO | NONE | NONE | WATER STAYED IN GRADING AREA. | Y | N | NA | NONE
870225 | 1300PM | GARY ORR | 6194397164 | OCEANSIDE, CITY OF | 870225 | 1045AM | 870225 | 1200 N | 15000 | GAL | 1664 OCEANSIDE BLVD. PUMP STA. | OCEANSIDE | SD | OCEANSIDE BLVD. PUMP STATION | EQUIPMENT BREAKDOWN AT PUMP STATION. | Y | LOMA ALTA CREEK/LA SALINA SLOU | LA SALINA SLOUGH | LA SALINA SLOUGH | Y | Y | 01 | BOTH SIDES OF SLOUGH WERE POSTED.
870220 | 0805AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870219 | 0930AM | 870219 | 1230AM | 600 | GAL | INDIANA ST & MYRTLE AVE | SAN DIEGO | SD | MANHOLE IN INTERSECTION | 6" CP SEWER MAIN STOPPED BY TREE ROOTS. | NO | NONE | NONE | TO CANYON | N | N | NA | APPLIED DISINFECTANT TO FLOODED AREA IN CANYON, DRAIN AND CANYON AREA.
870225 | LETTER | BEADLE/DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870218 | 1055AM | 870218 | 1155AM | 600 | GAL | 3758 GILLETT ST. | SAN DIEGO | SD | LEAKING JOINT | GREASE AND SLUDGE | NO | NONE | NONE | NONE | N | N | NA | NONE
870224 | LETTER | VAUGHN BRADLEY | 7145822330 | SANTA MARGARITA WATER DISTRICT | 870216 | 1030AM | 870216 | 1330PM | 800 | GAL | ANTONIO & ALAS DE PAZ | RANCHO SANTA MAR | OR | ????? | CLOGGED WITH CONSTRUCTION DEBRIS | NO | NONE | NONE | DIRT | N | N | NA | NONE
870221 | 1100AM | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 870221 | 1055AM | 870221 | 1245PM | 500 | GAL | 1300 BLOCK OF BORDEN DR. | ESCONDIDO | SD | MANHOLE ATLAS PG106 MH13 | GRIT STOPPAGE IN MAIN LINE SEWER | N | NONE | NONE | STORM DRAIN | N | N | NA | FLUSHED W/CLEAN WATER & HTH TO DISINFECT AREA USED APPROX 1600 GAL WATER.
870226 | LETTER | BEADLE/DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870221 | 1400PM | 870221 | 1600PM | 5 | GAL | 1340 THERMAL AVE | SAN DIEGO | SD | MANHOLE | GREASE | N | NONE | NONE | NONE | N | N | NA | NONE
870219 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870219 | 1200 N | 870219 | 1500PM | 5 | GAL | 6545 CAINITO DEL TREATRO | SAN DIEGO | SD | MANHOLE 8"VC MAIN | ROOT OBSTRUCTION | NO | NONE | NONE | NONE | N | N | NA | NONE
870220 | 1000AM | NANCY | 6197288319 | FALLBROOK SANITARY DISTRICT | 870220 | 0800AM | 870220 | 1000AM | 50 | GAL | 234 E. VIEW ST. | FALLBROOK | SD | CLEAN OUT | ROOTS IN MAIN LINE | NO | NONE | NONE | SURFACE CONTAINMENT | N | N | NA | NONE
870220 | 1300PM | NANCY | 6197288319 | FALLBROOK SANITARY DISTRICT | 870220 | 1330PM | 870220 | 1400PM | 20 | GAL | HAWTHORNE ST. | FALLBROOK | SD | CLEANOUT | OBSTRUCTION IN MAIN | NO | NONE | NONE | SURFACE CONTAINMENT | N | N | NA | NONE
870302 | 1056AM | ALLEGRA,COUNTY HEALT | 6192364717 | SAN DIEGO, CITY OF | 870302 | 0815AM | 870302 | 0930AM | 1100 | GAL | FOOT OF GRAND AV & OCEAN BLVD. | SAN DIEGO | SD | ??????? | BLOCAGE | NO | NONE | NONE | CONTAINED ON SAND AT BEACH | Y | Y | 02 | POSTED 150FT ON BOTH SIDES OF BEACH.
870223 | 1635PM | M. ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870223 | 0800AM | 870223 | 1100AM | 450 | GAL | 28TH ST AND WEBSTER AVE | SAN DIEGO | SD | MANHOLE | 8" VC SEWER STOPPED BY ROOTS,GREASE AND RAGS | NO | NONE | NONE | STORM DRAIN(28TH & WEBSTER) | Y | N | NA | DISINFECTANT AND DEOTORIZER APPLIED TO AREA.
870227 | LETTER | BEADLE / HARRIS | 6192367030 | SAN DIEGO, CITY OF | 870224 | 1248PM | 870224 | 1348PM | 6 | GAL | 4613 CONTOUR BLVD. | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE | NONE | NONE | N | N | NA | NONE
870220 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870220 | 2300PM | 870221 | 1100AM | 1680 | GAL | LAUREL ST & SAN MARCOS | SAN DIEGO | SD | MANHOLE / 6" CP MAIN | COLLAPSED 6" CP MAIN | NO | NONE | NONE | NONE | ? | ? | ?? | NONE
870225 | 0740AM | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 870225 | 0740AM | 870225 | 1445PM | 1000 | GAL | 3680 SUNSET DRIVE | ESCONDIDO | SD | 8" LATERAL ATLAS PG373 MH5 | CONTRACTOR BROKE 8" PLASTIC LATERAL AND DID NOT CAP IT. CITY CREW PUMPING OUT PUMP STA WET WELL WITH PLUGGED INLET LINE | NO | NONE | NONE | DIKED-PUMPED OUT BY COMMERCIAL | N | N | NA | SPILL CONTAINED AT CONST. SITE.REMOVED BY ATLAS PUMPING SERVICE.AREA TREATED 6-8 LB. HTH.
870223 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870223 | 0800AM | 870223 | ?????? | 600 | GAL | 6514 MUIRLANDS DR. | SAN DIEGO | SD | MANHOLE-8" VC MAIN | GREASE OBSTRUCTION. | NO | NONE | NONE | NONE | ? | ? | ?? | NONE
870224 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870224 | 0945AM | 870224 | 1045AM | 30 | GAL | 3750 JOHN J MONTGOMERY DR. | SAN DIEGO | SD | MANHOLE-6" LATERAL | GREASE OBSTRUCTION | NO | NONE | NONE | NONE | ? | ? | ?? | NONE.
870227 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870227 | 1900PM | 870227 | 2100PM | 1800 | GAL | 3580 MAJESTIC ST. | SAN DIEGO | SD | MANHOLE-8" PVC MAIN | GREASE OBSTRUCTION | NO | NONE | NONE | NONE | ? | ? | ?? | NONE
870225 | 1545PM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870225 | 1030AM | 870225 | 1130AM | 180 | GAL | 2484 HOTEL CIRCLE PLACE | SAN DIEGO | SD | MANHOLE | 8" VC SEWER STOPPED BY GREASE,SLUDGE,DEBRIS | NO | NONE | NONE | CURBLINE DRAIN TO OPEN SPACE. | Y | N | NA | AREA DISINFECTED AND DEOTORIZED.
870303 | 1035AM | ALLEGRA,CO. HEALTH | 6192364717 | ESCONDIDO, CITY OF | 870303 | 0950AM | 870303 | 1245PM | 500 | GAL | W SIDE HWY 15/N SIDE BRIDGE | ESCONDIDO | SD | MANHOLE | UNKNOWN AT THIS TIME. JOGGER OBSERVED MANHOLE OVERFLOWING AT FAST RATE. | NO | NONE | NONE | NONE | Y | N |  | NOT A HUMAN CONTACT AREA.ABSORBED INTO GROUND. AREA TREATED WITH HTH.
870403 | 1155AM | ALLEGRA,CO. HEALTH | 6192364717 | LA VALENCIA HOTEL | 870304 | 1150AM | 870304 | 1545PM | 50 | GPM | 1132 PROSPECT ST | SAN DIEGO | SD | PIPE??? | PLUGGED RESTAURANT LINE. | Y | PACIFIC OCEAN | NONE | NONE | Y | Y | 03 | LIFE GUARD CALLED CO. HEALTH.RAW SEWAGE FLOWING FROM RESTAURANT TO STREET TO COVE/OCEAN.
870305 | 1155AM | ALLEGRA,CO. HEALTH | 6192364717 | SAN DIEGO, CITY OF | 870305 | 0945AM | 0 | ?????? | 60 | MG | 10749 ROSELLE ST/PUMP STA 64 | SAN DIEGO | SD | FORCEMAIN BREAK/PRESSURE SURGE | POWER INTERRUPTION CAUSED SURGE.INFLUENT SHUT DOWN.SEWAGE FLOWING TO CREEK TO OCEAN.REPAIR COULD TAKE 2 DAYS. | Y | PACIFIC OCEAN | NONE | NONE | Y | Y | ?? | VOLUME COULD BE AFFECTED BY FORCASTED RAIN.USUAL VOL PUMPED DAILY IS 20MGD NORMAL CONDITIO
870205 | LETTER | TERRY E HANLEY | 6192367030 | SAN DIEGO, CITY OF | 870227 | 1400PM | 870227 | 1800PM | 240 | GAL | 2900 BLK CHAMOUNE ST | SAN DIEGO | SD | UNKNOWN | ??????? | NO | NONE | NONE | NONE | Y | Y | 02 | NONE
870302 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870302 | 0830AM | 870302 | 0940AM | 1050 | GAL | GRAND AVE & OCEAN BLVD. | SAN DIEGO | SD | CLEAN OUT | GREASE | NO | NONE | NONE | NONE | ? | ? | ?? | NONE
870227 | 0845AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870226 | 1400PM | 870226 | 1500PM | 600 | GAL | 8920 MIRAMAR RD. | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE | NONE | NONE | Y | N
870305 | LETTER | TERRY HANLEY | 6192367030 | SAN DIEGO, CITY OF | 870302 | 1005AM | 870302 | 1300PM | 1200 | GAL | 2549 46 ST | SAN DIEGO | SD | ?????? | UNKNOWN | NO | NONE | NONE | NONE | ? | ? | ??
870305 | LETTER | TERRY HANLEY | 6192367030 | SAN DIEGO, CITY OF | 870228 | 0900AM | 870228 | 1200NO | 3600 | GAL | 5719 JAMES DRIVE | SAN DIEGO | SD | ?? | ROOTS | NO | NONE | NONE | NONE | ? | ? | ??
870305 | LETTER | TERRY HANLEY | 6192367030 | SAN DIEGO, CITY OF | 870227 | 1830PM | 870228 | 0130AM | 2100 | GAL | 1640 NEWTON AVE | SAN DIEGO | SD | ?? | UNKNOWN | NO | NONE | NONE | NONE | ? | N
870305 | LETTER | TERRY HANLEY | 6192377030 | SAN DIEGO, CITY OF | 870228 | 1700PM | 870228 | 1900PM | 1200 | GAL | 822 GRAND AVE | SAN DIEGO | SD | ?? | GREASE | NO | NONE | NONE | NONE | ? | N
870303 | 0815AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870302 | 1200N | 879392 | 1300PM | 60 | GAL | 2008 PACIFIC HWY | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE | NONE | NONE | Y | N
870302 | 1230PM | BRIAN ANDERSON | 7146765485 | EASTERN MUNICIPAL WATER DIST. | 870228 | ?????? | 870301 | 1600PM | 5.96 | MG | HWY 79 5MI. E OF HWY 215 | HEMET | RI | PAUBA PONDS | BLENDED WATER LEFT POND THROUGH ABANDONED IRRIGATION LINE | NO | NONE | NONE | OPEN FIELD NW OF PONDS | ? | ?
870309 | 0930AM | GEORGE LONG | 6195655359 | SAN DIEGO, COUNTY OF | 870309 | 0730AM | 870309 | 0800AM | 100 | GAL | MANCHESTER & I-5 | ENCINITAS | SD | OLIVENHIEM PUMP STATION. | RUPTURED 10" FORCE MAIN/LOSS OCCURRED WHEN ATLAS PUMPING TRANSFERRED TO VAC. TRUCK.SEWAGE CONTAINED IN PUMP STA...****** | NO | NONE | NONE | NONE | Y | N |  | D.O. 'S TAKEN UPSTREAM=6.4,AT SPILL=5.41 AND DOWMSTREAM=15.5MG/L PROBABLY VERY INACUURATE.
870310 | LETTER | TERRY E HANLEY | 6192367030 | SAN DIEGO, CITY OF | 870301 | 0930AM | 870301 | 1130AM | 120 | GAL | 300 BLK BROOKS AVE | SAN DIEGO | SD | UNKNOWN | GREASE | NO | NONE | NONE | NONE | N | N | 00
870310 | LETTER | TERRY E HANLEY | 6192367030 | SAN DIEGO, CITY OF | 870228 | 2100PM | 870228 | 2300PM | 600 | GAL | PETER PAN & SYCHAR | SAN DIEGO | SD | ?????? | ROOTS | NO | NONE | NONE | NONE | Y | N | 00
870310 | LETTER | TERRY E HANLEY | 6192367030 | SAN DIEGO, CITY OF | 870303 | 0900AM | 870303 | 1000AM | 60 | GAL | 5675 ALBEMARLE ST. | SAN DIEGO | SD | ?????? | ROOTS AND GREASE | NO | NONE | NONE | SEEPED INTO GROUND | ? | ? | ??
870303 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870303 | 0800AM | 870303 | 1400PM | 6120 | GAL | 7555 EADS AVE | SAN DIEGO | SD | 8" VC MAIN BROKEN BY CONTRCTR. | BROKEN MAIN.SPILL CONFINED TO CONSTRCTN SITE.CONTRCTR PUMPED SPILL TO NEXT MANHOLE. | NO | NONE | NONE | NONE | ? | ? | ??
870310 | LETTER | TERRY E HANLEY | 6192367030 | SAN DIEGO, CITY OF | 870304 | 1800 | 870300 | ?????? | 1200 | GAL | 4646 NOGAL ST. | SAN DIEGO | SD | ??????? | ROCKS IN MAIN | NO | NONE | NONE | YARD***OPEN FIELD** | N | ? | ??
870310 | LETTER | TERRY E HANLEY | 6192367030 | SAN DIEGO, CITY OF | 870303 | 1530PM | 870304 | 1130AM | 6000 | GAL | 2900 CHAMOUNE ST | SAN DIEGO | SD | ??????? | ROCKS AND DEBRIS IN MANHOLE.MAIN AND PARTIAL FLOW M/H HAS BEEN CLEARED.3/4/87******** | NO | NONE | NONE | CANYON AREA*** | ? | ? | ??
870303 | 1000AM | NANCY | 6197288319 | FALLBROOK SANITARY DISTRICT | 870303 | 1000AM | 870303 | 1030AM | 20 | GAL | 715 SUTTON HILL PLACE | FALLBROOK | SD | CLEANOUT OVERFLOWING | ROOTS IN LATERAL | NO | NONE | NONE | SURFACE CONTAINMENT. | N | N | NA
870310 | LETTER | TERRY E HANLEY | 6192367030 | SAN DIEGO, CITY OF | 870305 | 1645PM | 870305 | 1845PM | 75 | GAL | 5345 COLLIER AVE | SAN DIEGO | SD | ?????? | ROOTS IN MAIN | NO | NONE | NONE | NONE | ? | ? | ??
870310 | LETTER | TERRY E HANLEY | 6192367030 | SAN DIEGO, CITY OF | 870304 | 1150AM | 870304 | 1400PM | 1200 | GAL | 3802 49TH ST | SAN DIEGO | SD | ??????? | HOLE IN PIPE ABOVE GROUND | NO | NONE | NONE | NONE | ? | Y | ??
870305 | 0800AM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870304 | 1200PM | 870304 | 1530PM | 630 | GAL | 1132 PROSPECT ST | SAN DIEGO | SD | MANHOLE-8" VC MAIN | GREASE OBSTRUCTION | Y | PACIFIC OCEAN | NONE | NONE | Y | Y | 03
870305 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870305 | 1100AM | 870305 | 1200AM | 180 | GAL | 2755 SNEAD AVE | SAN DIEGO | SD | 4" LATERAL | GREASE OBSTRUCTION | NO | NONE | NONE | NONE | ? | ? | ??
870310 | LETTER | TERRY E HANLEY | 6192367030 | SAN DIEGO, CITY OF | 870304 | 1145AM | 870304 | 1345PM | 1200 | GAL | 6150 CAMINITO SACATE | SAN DIEGO | SD | ?????? | ROOTS IN MAIN | NO | NONE | NONE | NAVAJO & CAMINITO ESTRELLA | ? | ? | ??
870310 | LETTER | TERRY E HANLEY | 6192367030 | SAN DIEGO, CITY OF | 870305 | 0700AM | 870305 | ?????? | 100 | GAL | 6425 MEDIO ST | SAN DIEGO | SD | ?????? | ROOTS | NO | NONE | NONE | HENSON ST IN DRAINAGE | ? | ? | ??
870312 | 0820AM | MR. KLENN | 6192365534 | SAN DIEGO, CITY OF | 870311 | 0945AM | 870311 | 1015AM | 3000 | GAL | 9888 LA JOLLA FARMS RD. | SAN DIEGO | SD | PUMP STATION 45 | BROKEN FORCE MAIN | NO | NONE | NONE | CANYON ADJACENT TO STA. 45 | Y | Y | ?? | BEACH POSTED AS PRECAUTIONARY MEASURE. 6 SIGNS POSTED.
870311 | 0905AM | ALLEGRE DIAZ | 6192362222 | SAN DIEGO, CITY OF | 870311 | 0752AM | 870311 | 0845AM | 3000 | GAL | PACIFIC BEACH DR. & NOYES | SAN DIEGO | SD | SEWER LINE | GREASE BLOCKAGE | Y | MISSION BAY | NONE | NONE | Y | Y | ?? | CAMPLAND AREA/WILDLIFE REFUGE AREA POSTED.
870312 | 1410PM | SD COUNTY HEALTH DEP | 6192362222 | EL CAJON, CITY OF | 870305 | ?????? | 870312 | 1430PM | 168000 | GAL | ANITA & VALLEY LAKE DR. | EL CAJON | SD | GRAVITY MAIN / MANHOLE | ASSUMED TO BE BLOCKAGE. ALSO, THE START DATE IS ASSUMED BASED ON CALCULATION. | Y | FANITA CREEK | SAN DIEGO RIVER | NONE | Y | ? | ?? | EL CAJON CONTACT:DICK ARNOLD @ 441-1758//BLOCKAGE AREA BYPASSED ON 87/03/12.
870309 | 0920AM | GEORGE L LONG SR. | 6195655359 | SAN DIEGO, COUNTY OF | 870309 | 0730AM | 870309 | 0800AM | 100 | GAL | MANCHESTER AV & I-15 E OF FRWY | CARDIFF | SD | STORM DRAIN | SEWAGE SPILLED ON GROUND FROM PUMPING & LOADING COMM. TANKERS W/SEWAGE. | Y | SAN ELIJO LAGOON EAST BASIN | PACIFIC OCEAN | NONE | Y | Y | ??
870307 | 1015AM | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 870307 | 1015AM | 870307 | 1115AM | 3000 | GAL | 100 BLK EAST MISSION | ESCONDIDO | SD | MH ATLAS PG 20 MH 50&51 | GREASE COMBINED WITH SHOP TOWELS | NO | NONE | NONE | STORM DRAIN | N | N | NA | AREA DISINFECTED AND WASHED WITH CLEAN WATER.
870309 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870309 | 2110PM | 870309 | 2310PM | 1800 | GAL | 5650 HARDY ST | SAN DIEGO | SD | CLEAN OUT 6" | RAGS//PUMP STATION | NO | NONE | NONE | NONE | ? | ? | ?? | NONE
870313 | LETTER | BEADLE//GRATE | 6192367030 | SAN DIEGO, CITY OF | 870311 | 1045AM | 870311 | 1230PM | 1200 | GAL | 402 63RD ST | SAN DIEGO | SD | MANHOLE | UNKNOWN | NO | NONE | NONE | NONE | N | N | NA | THIS IS A PRIVATE LATERAL AND MAIN.
870313 | LETTER | BEADLE//THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870309 | 1430PM | 870309 | 1730PM | 180 | GAL | 2655 MONTCLAIR ST. | SAN DIEGO | SD | MANHOLE | GREASE AND SLUDGE | NO | NONE | NONE | NONE | N | N | NA | NONE
870313 | LETTER | BEADLE//THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870309 | 0810AM | 870309 | 0900AM | 60 | GAL | 3035 32ND ST | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE | NONE | NONE | N | N | NA | NONE
870313 | LETTER | BEADLE//THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870309 | 1115AM | 870309 | 1315PM | 1200 | GAL | 40TH ST & THORN ST | SAN DIEGO | SD | MANHOLE | OBSTRUCTION// TYPE UNKNOWN | NO | NONE | NONE | NONE | N | N | NA | NONE
870317 | 0945AM | ALLEN CRUTCHER | 6199428346 | ESCONDIDO, CITY OF | 870317 | 0810AM | 0 | ?????? | 0 | ??? | 1/4 MI W OF I-5 ON MANCHESTER | CARDIFF/ESCONDID | SD | TREATMENT PLANT LINE | CITY OF ESCONDIDO IS WORKING ON A LINE ALONG MANCHESTER AND CARDIFF.BREAK IN LINE?? | Y | SAN ELIJO LAGOON | NONE | NONE | Y | ? | ?? | MR CRUTCHER OBSERVED ROAD FLOODED W/ODOR & GREY WATER WHILE DRIVING MANCHESTER 3/17/87 AM.
870316 | 1430PM | ALLEGRE, CO HEALTH | 6192364717 | RITCHIE COTTON,MGR | 870314 | PM | 870314 | ?????? | 4 | GPM | 6986 LA JOLLA BLVD. | SAN DIEGO | SD | SLUGGERS & DON JUAN RESTAURANT | UNKNOWN. RESTAURANTS WERE CLOSED DOWN/CONSIDERED HEALTH HAZARD BY DEPT OF HEALTH | Y? | PACIFIC OCEAN WINDANDSEA BEACH | NONE | NONE | Y | Y | 02 | POSTED SIGNS REMOVED ON 3/16/87.
870316 | 1430PM | ALLEGRE, CO HEALTH | 6192364717 | SAN DIEGO, CITY OF | 870315 | PM | 870315 | ?????? | 5 | GPM | 134 HAWTHORNE ST. | SAN DIEGO | SD | MANHOLE AT 2100 1ST AVE. | CLEANOUT ON PRIVATE PROPERTY. | Y | SAN DIEGO BAY | NONE | NONE | Y | Y | ?? | AFFECTED AREA IS A NON HUMAN CONTACT AREA. POSTED FOR EXTRA PRECAUTION.
870312 | 0300PM | RICHARD ARNOLD | 6194411658 | EL CAJON, CITY OF | 870310 | ?????? | 870312 | 0230PM | 28000 | GAL | 400FT S 2861 VALLEY LAKE DR. | EL CAJON | SD | SEWER MANHOLE | UNKNOWN PERSONS DUMPED ROCK AND DEBRIS IN THE MANHOLE | Y | FANITA CHANNEL | NONE | NONE | Y | N | NA | NONE
870320 | 1425PM | DALE HAUFLAND | 6195655343 | SAN DIEGO, COUNTY OF | 870320 | 0730AM | 870320 | ?????? | 200 | GAL | EDGEMORE HOSPITAL | SANTEE | SD | MANHOLE | STOPPAGE AT HASPITAL CAUSED RAW SEWAGE TO OVERFLOW.SOAKED INTO SAND/ CHLORINATED & CLEARED.NO SURFACE WATER REACHED. | NO | NONE | NONE | SOAKED INTO SAND | Y | ? | ?? | CO HEALTH CLASSIFIED SPILL AS NON HAZARDOUS UNDER PROP 65
870320 | LETTER | BEADLE DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870316 | 2100PM | 870316 | 2300PM | 1200 | GAL | 47TH & POLK AVE | SAN DIEGO | SD | MANHOLE | RAGS AND GREASE | NO | NONE | NONE | NONE | N | N | NA | NONE
870320 | LETTER | BEADLE/DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870317 | 2300PM | 870318 | 0100AM | 3000 | GAL | 1606 DEL SUR | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE | NONE | NONE | N | N | NA | NONE
870320 | LETTER | BEADLE/SENIOR | 6192367030 | SAN DIEGO, CITY OF | 870317 | 0715AM | 870317 | 1015AM | 5400 | GAL | N OF HWY 94 W. OF HWY 15 | SAN DIEGO | SD | ABANDONED SEWER MAIN | 24" MAIN BACKING UP INTO 8" ABANDONED MAIN | NO | NONE | NONE | NONE | N | N | NA | NONE
870318 | LETTER | BEADLE/DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870314 | 1100AM | 870314 | 1400PM | 3600 | GAL | MAJESTIC & FOREST GLENN | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE | NONE | NONE | N | N | NA | NONE
870318 | LETTER | BEADLE/DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870315 | 2000PM | 870315 | 2200PM | 2400 | GAL | 3927 1ST AVE | SAN DIEGO | SD | CLEANOUT | ROCKS & GREASE | NO | NONE | NONE | NONE | N | N | AN | ONE
870318 | LETTER | BEADLE/DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870314 | 0830AM | 870314 | 1030AM | 120 | GAL | 2820 IVY ST | SAN DIEGO | SD | CLEANOUT | ROOTS | NO | NONE | NONE | NONE | N | N | AN | ONE
870318 | LETTER | BEADLE/DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870314 | 1500PM | 870314 | 1600PM | 300 | GAL | 1381 PALM AVE ( SOUTH BAY ) | SAN DIEGO | SD | CLEANOUT | GREASE & RAGS | NO | NONE | NONE | NONE | N | N | NA | NONE
870318 | LETTER | BEADLE/DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870314 | 1445PM | 870314 | 2045PM | 1080 | GAL | 4490 ALAMO WAY | SAN DIEGO | SD | MANHOLE | CONTRACTORS CONNECTION | NO | NONE | NONE | NONE | N | N | NA | NONE
870318 | LETTER | BEADLE/DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870313 | 2130PM | 870313 | 2330PM | 1200 | GAL | 7526 ROCK CANYON DR | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE | NONE | NONE | N | N | NA | NONE
870318 | LETTER | BEADLE/DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870313 | 2130PM | 870313 | 2330PM | 60 | GAL | 4340 KANSAS ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE | NONE | NONE | N | N | NA | NONE
870318 | LETTER | BEADLE/DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870315 | 1330PM | 870316 | 1330PM | 4320 | GAL | 1754 N ARBOR | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE | NONE | NONE | N | N | NA | NONE
870318 | LETTER | BEADLE/DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870312 | 1130AM | 870312 | 1230PM | 60 | GAL | 5075 CAMPANILE DR | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE | NONE | NONE | N | N | NA | NONE
870318 | LETTER | BEADLE/DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870312 | 0930AM | 870312 | 1030AM | 300 | GAL | 4644 VISTA ST | SAN DIEGO | SD | CLEANOUT | GREASE & ROOTS | NO | NONE | NONE | NONE | N | N | NA | NONE
870318 | LETTER | BEADLE DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870313 | 1930PM | 870313 | 2030PM | 300 | GAL | 333 24TH ST | SAN DIEGO | SD | MANHOLE & CLEANOUT | ROOTS & GREASE | NO | NONE | NONE | NONE | N | N | NA | NONE
870318 | LETTER | BEADLE/DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870315 | 1600PM | 870315 | 1800PM | 1200 | GAL | 604 TIBBETTS | SAN DIEGO | SD | CLEANOUT | ROOTS & GREASE | NO | NONE | NONE | NONE | N | N | NA | NONE
870320 | 0937AM | GEORGE LONG | 6195655359 | SAN DIEGO, COUNTY OF | 870320 | ?????? | 870320 | 0800AM | 75000 | GAL | JAPUTAL VALLEY ROAD & I-8 EAST | DESCANSO | SD | FOUR INCH PVC PIPE | BROKEN FOUR INCH HEADER PIPE FOR RECLAIMED IRRIGATIO SYSTEM FOR CAMP GRASSY AREA & SHRUBBERY. | Y | SWEETWATER RIVER | LOVELAND RESERVIOR |  | Y | N | NA | THE SPILL WATER WAS WATER USED FOR RECLAMATION.WATER WAS CHLORINATED.
870311 | 0830AM | NANCY | 6197288319 | FALLBROOK SANITARY DISTRICT. | 870311 | 0800AM | 870311 | 0900AM | 100 | GAL | 1320 GERALD WAY | SAN DIEGO | SD | LATERAL` | LIFT STATION PUMPS TRIP OUT | NO | NONE | NONE | WITHIN PROPERTY BOUNDARIES. | N | N | NA | NONE
870318 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870318 | 1100AM | 870318 | 1200 N | 600 | GAL | 7850 VISTA HILLS | SAN DIEGO | SD | MANHOLE-8"VC MAIN | GREASE | NO | NONE | NONE | CANYON | Y | N | NA | NONE
870325 | 0900AM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870325 | 0630AM | 870325 | 0800AM | 2200 | GAL | ACADEMY AND LAW STREETS | SAN DIEGO P.B. | SD | MANHOLE @ OLLAY & PAC BCH DR. | ROOT BLOCKAGE///THE DISCHARGE WAS TO THE WILDLFE PRESERVE IN NORTH MISSION BAY. | Y | MISSION BAY | NONE | NONE | Y | Y | ??
870323 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870323 | 1100AM | 870323 | 1200 N | 60 | GAL | 8200 POTTERY CANYON RD | SAN DIEGO | SD | MANHOLE-8"VC MAIN | ROOT OBSTRUCTION | NO | NONE | NONE | CANYON | Y | N | NA | NONE
870325 | LETTER | BEADLE // GRATE | 6192367030 | SAN DIEGO, CITY OF | 870320 | 1900PM | 870321 | 0100AM | 1800 | GAL | 3633 MILLIKIN | SAN DIEGO | SD | MANHOLE | GREASE & ROCKS | NO | NONE | NONE | NONE | N | N | NA | NONE
870326 | LETTER | BEADLE // DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870319 | 1040AM | 870319 | 1340PM | 9000 | GAL | 33RD ST AND BROADWAY | SAN DIEGO | SD | MANHOLE | UNKNOWN | NO | NONE | NONE | NONE | N | N | NA | NONE
870326 | LETTER | BEADLE // DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870319 | 1730PM | 870319 | 1830PM | 120 | GAL | 1079 WEST MORENA BLVD. | SAN DIEGO | SD | MANHOLE | GREASE & DEBRIS | NO | NONE | NONE | NONE | N | N | NA | NONE
870326 | LETTER | BEADLE // DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870319 | 2000PM | 870319 | 2400PM | 7200 | GAL | 4646 NOGAL | SAN DIEGO | SD | MANHOLE | ROCKS & DEBRIS | NO | NONE | NONE | NONE | N | N | NA | NONE
870326 | 0830AM | MIKE GARNER,SUPT. | 7149257676 | EASTERN MUNICIPAL WATER DIST. | 870325 | 1630PM | 870325 | 1830PM | 15000 | GAL | MARGARITA ROAD | RANCHO CALIFORNI | RI | LA SERENA PUMP STATION | SHORT IN LEAD PUMP CAUSED POWER LOSS & PUMP SHUT DOWN.SPILL CONTAINED.TREATED WITH SODIUM HYPOCHLORITE. | Y | FLOOD CONTROL CHANNEL (DRY) | NONE | NONE | N | N | NA | ELECTRICAL BACKUP TO BE INSTALLED TODAY.
870330 | 0900AM | DON GRIFFEN | 6192367334 | SAN DIEGO, CITY OF | 870328 | 1915PM | 870328 | 2145PM | 4000 | GAL | PAC BCH DR & MISSION BL CATAMR | SAN DIEGO | SD | PUMP STATION 17 | POWER OUTAGE AT PUMP STA 17 | Y | SAIL BAY | OCEAN | NONE | Y | Y | ?? | POSTED 150 YDS ON EACH SIDE.
870326 | 1550PM | ANN ERICKSON | 7144994555 | ORANGE, COUNTY OF | 870326 | ?????? | 0 | ?????? | 0 | ??? | 31092 COAST HWY.NR. WESLEY DR. | SOUTH LAGUNA | OR | 6" LATERAL CLAY PIPE | BROKEN 6" LATERAL CLAY PIPE | Y | ALISO CREEK | PACIFIC OCEAN | NONE | Y | Y | ?? | COUNTY TAKING SAMPLES. POSTED FOR AT LEAST 48 HOURS.
870325 | 1000AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF UTIL. SYS. | 870325 | 1000AM | 870325 | 1100AM | 120 | GAL | 3000 MADISON AVE | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE | NONE | STORM DRAIN | Y | N | NA | NONE
870330 | LETTER | BEADLE/GRATE | 6192367030 | SAN DIEGO, CITY OF | 870326 | 1800PM | 870326 | 2100PM | 900 | GAL | 2806 GREGORY ST. | SAN DIEGO | SD | MANHOLE | GREASE & DEBRIS | NO | NONE | NONE | NONE | N | N | NA | NONE
870330 | LETTER | BEADLE/GRATE | 6192367030 | SAN DIEGO, CITY OF | 870323 | 1430PM | 870323 | 1830PM | 4800 | GAL | 5553 UNIVERSITY AVE | SAN DIEGO | SD | MANHOLE | HEAVY ROOTS | NO | NONE | NONE | NONE | N | N | NA | NONE
870330 | LETTER | BEADLE / GRATE | 6192367030 | SAN DIEGO, CITY OF | 870323 | 1730PM | 870323 | 2100PM | 2400 | GAL | 7850 VISTA HILL | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE | NONE | NONE | N | N | NA | NONE
870325 | 1700PM | JIM SELBY | 6199257676 | EASTERN MUNICIPAL WATER DIST. | 870325 | 1630PM | 870325 | 1830PM | 12000 | GAL | 2800 LA SERENA WAY | RANCHO CALIFORNI | RV | LA SERENA LIFT STATION | SHORT IN PUMP MOTOR DROPPED POWER TO LIFT STATION. | NO | NONE | NONE | DRY FLOOD CONTROL CHANNEL | Y | Y | 05 | WILL BE POSTED UNTIL DRY.
870330 | 1000AM | JOHN CASEY | 6192367843 | SAN DIEGO, CITY OF | 870329 | ?????? | 870300 | ?????? | 0 | ??? | 32ND & JUNIPER BEHIND 3100 JUN | SAN DIEGO | SD | MANHOLE | UNKNOWN.CASEY THINKS THE SEWER LINE CAPACITY IS INADEQUATEFOR THE PRESENT FLOW-SEEMS TO HAPPEN EVERY 6 WEEKS. | ?? | WABASH CANYON |  |  | Y | ? | ?? | APPEARS TO NOT HAVE BEEN REPORTED BY THE CITY, WE SHOULD CHECK TO SEE IF CITY IS REPORTING
870401 | 0830AM | DEL HERNANDEZ | 6192365534 | SAN DIEGO, CITY OF | 870331 | 1830PM | 870331 | 1930PM | 300 | GAL | 5402 HARDY WAY | SAN DIEGO | SD | MANHOLE/ PUMP STATION 31 | OBSTRUCTION IN THE PUMPS AT PUMP STATION 31 LOCATED AT 5699 HARDY WAY. | NO | NONE | NONE | SOAKED INTO GROUND IN CANYON | Y | N | NA | NONE
870401 | 0845AM | DON GRIFFIN | 6192367334 | SAN DIEGO, CITY OF | 870331 | 2130PM | 870331 | 1330PM | 1200 | GAL | 7596 EADS AVE | SAN DIEGO | SD | LATERAL CLEANOUT. | GREASE IN MAIN. SEWAGE ENTERED OCEAN BEHIND 202 COAST BLVD. | Y | PACIFIC OCEAN | NONE | NONE | Y | Y | ?? | POSTED BETWEEN 202 AND 210 COAST BLVD. 3 SIGNS. 100 YARDS.
870401 | 1130AM | GARY ORR | 6194397164 | OCEANSIDE, CITY OF | 870401 | 0915AM | 870401 | 1040AM | 5000 | GAL | 1664 OCEANSIDE BLVD. | OCEANSIDE | SD | OCEANSIDE BLVD PUMP STATION | CONTRACTOR FAILED TO CLEAN OUT WET PIT AND DEBRIS BECAME WEDGED INTO PUMPS. | Y | LOMA ALTA CREEK TO PACIFIC OCE | PACIFIC OCEAN | NONE | Y | Y | ?? | NONE......................................................................................
870325 | 1145AM | DALLAS BROWN/R POLLE | 6194630294 | SAN DIEGO COUNTY | 870323 | 0800AM | 870325 | 1235 | 0 | ??? | EASEMENT BACK OF 8309 BROADWAY | LEMON GROVE | SD | 8" SEWER MAIN | PAPER TOWELS & OTHER DEBRIS | Y | BROOKSIDE DRAINAGE CHANNEL | SWEETWATER RIVER BELOW DAM | NONE | ? | ? | ?? | WATER REACHED STORM DRAIN, MAY EVENTUALLY REACH SAN DIEGO BAY.
870402 | 1450PM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 0 | ?????? | 870402 | 0810AM | 10500 | GAL | 4881 ACADEMY ST | SAN DIEGO | SD | MANHOLE | BROKEN SEWER ROD,CITY VACUUMED 10500GAL W/VACUUM TRUCK TO DISCHARGE TO THE NEXT DOWNHILL MANHOLE.CAUSE UNKNOWN. | NO | NONE | NONE | NONE | Y | N | NA | NONE
870403 | LETTER | BEADLE / GRATE | 6192367030 | SAN DIEGO, CITY OF | 870331 | 0640AM | 870331 | 0840AM | 2400 | GAL | 424 VALENCIA PARKWAY | SAN DIEGO | SD | MANHOLE | GREASE & DEBRIS | NO | NONE | NONE | NONE | N | N | NA | NONE
870330 | 1315PM | M. ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870329 | 1130AM | 870329 | 1330PM | 120 | GAL | SPARKS AVE & SPARKS PLACE | SAN DIEGO | SD | MANHOLE | 8" SEWER STOPPED BY ROOTS & GREASE | NO | NONE | NONE | STORM DRAIN AREA | N | N | NA | NONE
870403 | LETTER | BEADLE / DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870331 | 0700AM | 870331 | 1300PM | 180 | GAL | ALLEY BET. IVY/JUNIPER ON 33RD | SAN DIEGO | SD | MANHOLE | BROKEN MANHOLE BOTTOM | NO | NONE | NONE | NONE | N | N | NA | NONE
870327 | 0945AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF UTIL. SYS. | 870327 | 1130AM | 870327 | 1230PM | 120 | GAL | ALLEY UTAH & KANSAS SO. EL CAJ | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE | NONE | MANHOLE BACK INTO SEWER MAIN. | Y | N | NA | NONE
870323 | 0800AM | D.E. HERNANDEZ | 6192365534 | SAN DIEGO, CITY OF | 870322 | 0700AM | 870322 | 0730AM | 300 | GAL | 14034 BARRYMORE ST. | SAN DIEGO | SD | POND ON HAMPE RANCH | ELECTRICAL PROBLEM AT STATION WITH HIGH TEMPERATURE SWITCHES. | Y | POND ON PRIVATE RANCH. | NONE | NONE | Y | Y | 10 | PEOPLE ON RANCH DO NOT LIKE CITY TO GO ON PROPERTY.
870401 | 1110 | GARY K. ORR | 6194397164 | OCEANSIDE, CITY OF | 870401 | 0915AM | 870401 | 1030AM | 5000 | GAL | 1664 OCEANSIDE BLVD. | OCEANSIDE | SD | OCEANSIDE BLVD PUMP STATION | CONTRACTOR FAILED TO REMOVE DEBRIS FROM WET PIT.PUMPS FOULED AND MAINS PLUGGED. | Y | LOMA ALTA CREEK | LA SALINA SLOUGH |  | Y | Y | 02 | SLOUGH & BEACH POSTED BEFORE FLOW ARRIVED.CONTRACTOR NOW HAS EXTRA PUMPS ON SITE FOR EMER.
870409 | 1315PM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870408 | 1345PM | 870408 | 1403PM | 1500 | GAL | 4700 CONRAD AVE | SAN DIEGO | SD | ???????? | GREASE BLOCKAGE IN 8" MAIN. | NO | NONE | NONE | CONTAINED ON GROUND. | Y | N | NA | NONE
870410 | 1530PM | DALE HOFFLAND | 6195655243 | SAN DIEGO, COUNTY OF | 870410 | 1352PM | 870410 | 1420PM | 200 | GAL | WHISPERING PALMS GOLF COURSE | RANCHO SANTA FE | SD | PUMP STATION ON GOLF COURSE | STOPPAGE | NO | NONE | NONE | SURFACE DISPOSAL | N | N | NA | WILL CHLORINATE IF GOLF COURSE ALLOWS. NO WRITTEN REPORT NECESSARY.
870409 | 1315PM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870409 | 0800AM | 870409 | 0930AM | 6750 | GAL | CANYON .5MI FROM BALBOA TERRAC | SAN DIEGO | SD | ???????? | VANDALISM OF BRICK MANHOLE IN CANYON. | NO | NONE | NONE | CONTAINED ON GROUND. | Y | N | NA | AREA WILL BE VACUUMED BY CITY TO REMOVE EXCESS SEWAGE.
870413 | 0900AM | JOHN McPHERSON | 6192367341 | SAN DIEGO, CITY OF | 870412 | 1715PM | 870412 | 1815PM | 600 | GAL | 1441 QUIVIRA ROAD. | SAN DIEGO | SD | 8"VC SEWER MAIN | GREASE BLOCKAGE | Y | SAN DIEGO BAY-ISLANDIA MARINA? | NONE | NONE | Y | Y | ?? | NONE
870408 | 1420PM | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 870408 | 0300AM | 870408 | 0900AM | 200000 | GAL | 2045 SO. ESCONDIDO BLVD. | ESCONDIDO | SD | LIFT STATION NO.3 | VANDALISM-DISCONNECTED TELEPHONE ALARM LINE,BROKEN BUBBLER LINE TO WET WELL WHICH CONTROLS OPERATION OF PUMPS. | Y | KIT CARSON PARK PONDS (LAKES) | LAKE HODGES | LAKE HODGES | Y | Y | ?? | AREA FLUSHED WITH CLEAN WATER CONTAINING HTH TO DISINFECT.
870415 | 1100AM | DAVE CAREY,CO HEALTH | 6192364717 | SAN DIEGO, CITY OF | 870414 | 1130AM | 870414 | 2130PM | 3000 | GAL | 18000 BLK POLVERA WAY | SAN DIEGO | SD | MANHOLE E SIDE LAKE HODGES | ROCK OBSTRUCTION IN MH CAUSED 5 GPM TO FLOW INTO LAKE HODGES. | Y | LAKE HODGES | NONE | NONE | Y | Y | ?? | STATE HEALTH DEPT. IS BANNING USE FOR DRINKING H20 UNTIL SAMPLING FOR SAFETY IS COMPLETE.
870414 | 1435PM | ALLEGRE,CO. HEALTH | 6192364717 | SAN DIEGO, CITY OF | 870414 | 1100AM | 870414 | 1330PM | 7500 | GAL | 2400 BLK FLEETWOOD | SAN DIEGO | SD | MANHOLE | ROOT STOPPAGE-MH OVERFLOWED INTO CANYON TO STORM DRAIN TO SAN DIEGO RIVER.AREA POSTED AND CO. HEALTH IS SAMPLING. | Y | SAN DIEGO RIVER | NONE | NONE | Y | Y | ?? | CO. HEALTH TAKING SAMPLES.
870416 | LETTER | BEADLE/DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870413 | 1045AM | 870413 | 1145AM | 60 | GAL | 5200 BLK ADAMS AVE | SAN DIEGO | SD | MANHOLE | ROOTS & GREASE | NO | NONE | NONE | NONE | N | N | NA | NONE
870410 | 0845AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870409 | 0900AM | 870409 | 1200PM | 5 | GAL | BEHIND 8450 MIRA MESA BLVD. | SAN DIEGO | SD | SEWER LINE | ROCKS | NO | NONE | NONE | NONE | Y | N | NA | NONE
0 |  |  |  | SAN DIEGO, CITY OF | 870124 | 0011AM | 870124 | 1500PM | 4800 | GAL | 49TH & TROJAN AVE | SAN DIEGO | SD | MANHOLE | BROKEN SEWER MAIN | N | NONE | NONE |  |  |  |  | NONE
870420 | 1500PM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870420 | 0900AM | 0 | ?????? | 15 | GPM | 4879 RONSON CT. | SAN DIEGO | SD | SEWER LINE | HEAVY GREASE | Y | ROSE CREEK TO INTERCEPTOR |  | INTERCEPTOR TO SEWER LINE | Y | N | NA | CREWS CLEANING UP & UNPLUGGING SEWER LINE.
870420 | LETTER | BEADLE / SENIOR | 6192367030 | SAN DIEGO, CITY OF | 870413 | 1545PM | 870414 | 1145PM | 60000 | GAL | 4500 BLK COLLWOOD BLVD. | SAN DIEGO | SD | MANHOLE | ROOT BLOCKAGE | NO | NONE | NONE | NONE | N | N | NA | NONE
870421 | 0900AM | MARK STROMAN | 6192366092 | SAN DIEGO, CITY OF | 870414 | ?????? | 870414 | ?????? | 600 | GAL | CORONADO AVE & HAWAII AVE. | SAN DIEGO | SD | MANHOLE | CONTRACTOR KNOCKED OFF MANHOLE COVER & PUSHED ROCKS & DEBRIS INTO MANHOLE -CLOGGING LINE. | NO | NONE | NONE | HILLSIDE NEAR MANHOLE | Y | N | NA | NONE
870423 | LETTER | JAY SENIOR | 6192367030 | SAN DIEGO, CITY OF | 870418 | 1000AM | 870418 | 1500PM | 2400 | GAL | 2550 VIA BARLETTA | SAN DIEGO | SD | MANHOLE | ROOTS IN MAIN | NO | NONE | NONE | NONE | N | N | NA | NONE
870423 | LETTER | JAY SENIOR | 6192367030 | SAN DIEGO, CITY OF | 870417 | 1530PM | 870417 | 1730PM | 120 | GAL | 4504 MARTIN LUTHER KING WAY | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE | NONE | I-805 & MARTIN LUTHER KING WAY | N | N | NA | NONE
870428 | ?????? | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870428 | 1130AM | 870428 | 1200 N | 50 | GAL | 5122 MIDDLETON ROAD | SAN DIEGO | SD | MANHOLE | GREASE | Y | ROSE CREEK/MISSION BAY | MISSION BAY | MISSION BAY | Y | N | NA | NONE
870424 | 0930AM | DICK ARNOLD | 6194411658 | UNKNOWN PRIVATE PARTY | 870423 | 0730AM | 870423 | 1530PM | 320 | GAL | 297 & 299 ORLANDO | EL CAJON | SD | LATERAL ON PRIVATE PROPERTY | OBSTRUCTION | Y | HORSE CREEK/SAN DIEGO RIVER | SAN DIEGO RIVER | SAN DIEGO RIVER | Y | N | NA | CITY OF EL CAJON NOT RESPONSIBLE FOR THIS SPILL.
870425 | 1700PM | MIKE HOGEN | 6194383941 | ENCINA WPCF | 870425 | 0400AM | 870425 | 0410AM | 5000 | GAL | ENCINA SEWAGE TRMNT PLANT | CARLSBAD?????? | SD | DIGESTER #3 | DIGESTED SLUDGE IN LINE BURST HOLE IN DIGESTER. SEWAGE WAS PUMPED BACK TO PLANT. | Y | ENCINA CREEK | NONE | PUMPED BACK TO PLANT | Y | N | NA | EARTH DAM CONTROLLED FLOW. SAMPLING CREEK & OCEAN.
870424 | 1000AM | RON INN | 714??????? | SANTA ANA MTNS CO WATER DIST. | 870423 | 1030AM | 870423 | 1040AM | 13000 | GAL | LIFT STATION #2/ROBINSON RANCH | TRABUCO CANYON | OR | LIFT STATION #2 | DIESEL MOTOR FAILED | Y | LAKE ON ROBINSON RANCH |  |  | N | Y | ?? | LAKE IS ON PRIVATE PROPERTY AND IS FENCED.
870427 | 0845AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF UTIL SYSTEM | 870424 | 0930AM | 870424 | 1030AM | 300 | GAL | BARRYMORE & GAINSBOROUGH AVE | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE | NONE | STORM DRAIN | Y | N | NA | NONE
870425 | LETTER | FRANK PADUA | 6102367340 | SAN DIEGO, CITY OF | 870425 | 1150AM | 870425 | 1320PM | 450 | GAL | 14465 PENASQUITOS DR | SAN DIEGO | SD | MANHOLE-8"VC MAIN | ROOT OBSTRUCTION IN MANHOLE ON GOLF COURSE | NO | NONE | NONE | GOLF COURSE | Y | N | NA | NONE
870425 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870425 | 0840AM | 870425 | 0940AM | 480 | GAL | 2342 MONCLAIR ST | SAN DIEGO | SD | MANHOLE - 8"VC MAIN | ROOT OBSTRUCTION | NO | NONE | NONE | CANYON | Y | N | NA | NONE
870429 | LETTER | JAY SENIOR/WANTIEZ | 6192367030 | SAN DIEGO, CITY OF | 870423 | 0830AM | 870423 | 1030PM | 4500 | GAL | 3617 MYRTLE AVE | SAN DIEGO | SD | MANHOLE | SLUDGE IN MAIN | NO | NONE | NONE | NONE | N | N | NA | NONE
870425 | 0950AM | RESIDENT NEAR BY | ?????????? | CAPISTRANO BEACH SANITARY | 870425 | 0950AM | 870425 | 1030AM | 150 | GAL | PACIFIC COAST HWY. | CAPISTRANO BEACH | OR | SEWAGE PUMP #2 | PUMP FAILURE | NO | NONE | NONE | DRAINAGE DITCH | Y | N | NA | CHLORINE SPREAD AROUND MANHOLE COVER & AREA OF SPILL. AREA CLEANED UP.
870501 | 1020AM | DALE HOFFLAND | 6195655343 | SAN DIEGO, COUNTY OF | 870430 | 1100AM | 870430 | 1430PM | 1225 | GAL | 7656 LEMON ST | LEMON GROVE | SD | GRAVITY MAIN | VANDALS BROKE MAIN | Y | UNKNOWN CREEK TO SAN DIEGO BAY | SAN DIEGO BAY |  | Y | ? | ?? | DISCHARGE 75% CONTAINED. CHLORINATED.
870504 | 0930AM | DICK ARNOLD |  | EL CAJON, CITY OF | 870502 | 1600PM | 870502 | 2200PM | 10000 | GAL | BROADWAY WEST OF GRAVES | EL CAJON | SD | MANHOLE | GREASE | Y | FORRESTER CREEK CHANNEL | SAN DIEGO RIVER |  | Y | ? | ?? | NONE
870504 | 1045AM | DALE HOFFLAND |  | SAN DIEGO, COUNTY OF /PUB. WKS | 870503 | 1000AM | 870503 | 1830PM | 20000 | GAL | 3149 HIGHLAND AVE |  | SD | MANHOLE | ROOTS | Y | CREEK & SWEETWATER LAKE |  |  | Y | ? | ?? | COUNTY CHLORINATED THE AREA
870504 | 1000AM | ALLEGRA DIAZ |  | SAN DIEGO, CITY OF | 870504 | 0830AM | 870504 | 1000AM | 450 | GAL | 5930 CAMINO DE LA COSTA | SAN DIEGO | SD | MANHOLE | UNKNOWN | Y | PACIFIC OCEAN |  |  | Y | Y | 03 | NONE
870506 | 1130AM | DALE HOFFLAND |  | SAN DIEGO, COUNTY OF | 870506 | ?????? | 870506 | 0647AM | 1000 | GAL | DESCANSO DETENTION FACILITY |  | SD | VIEJAS TREATMENT PLANT | T-SHIRT CLOGGED INFLUENT CHANNEL | NO | DRY CREEK BED |  |  | Y | N | NA | NONE
870504 | LETTER | BEADLE / DEVLIN | 6192367030 | SAN DIEGO,CITY OF | 870428 | 0700AM | 870428 | 0800AM | 120 | GAL | MADISON & ALTADENA IN ALLEY | SAN DIEGO | SD | MANHOLE | GREASE & DEBRIS | NO | NONE | NONE | NONE | Y | N | NA | NONE
870504 | LETTER | BEADLE /DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870428 | 1100AM | 870428 | 1400PM | 1800 | GAL | 2624 46 ST IN CANYON | SAN DIEGO | SD | MANHOLE | ROCKS & DEBRIS | NO | NONE | NONE | NONE | Y | N | NA | NONE
870421 | 1030AM | HARRIS #812 | 6192366092 | SAN DIEGO, CITY OF | 870421 | 1030AM | 870421 | 1130AM | 300 | GAL | 4236 VENUS ST | SAN DIEGO | SD | ????? | GREASE | NO | NONE | NONE | CANYON | Y | N | NA | NONE
870428 | 1130AM | HARRIS #812 | 6192366092 | SAN DIEGO, CITY OF | 870428 | 1130AM | 870428 | 1330PM | 240 | GAL | 2806 GREGORY ST | SAN DIEGO | SD | ?????? | ROCKS & ROOTS | NO | NONE | NONE | CANYON | Y | N | NA | NONE
870428 | 0900AM | SHIPLEY #818 | 6192366092 | SAN DIEGO, CITY OF | 870428 | 0900AM | 870428 | 1400PM | 2400 | GAL | W. WASHINGTON & HWY 163 | SAN DIEGO | SD | ?????? | ROOTS & ROCKS | NO | NONE | NONE | CANYON EAST OF HWY 163 | Y | N | NA | NONE
870429 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870429 | 1700PM | 870429 | 1835PM | 375 | GAL | 1110 "C" STREET | SAN DIEGO | SD | MANHOLE | UNKNOWN | NO | NONE | NONE | UNKNOWN | Y | N | NA | NONE
870504 | LETTER | BEADLE / GRATE | 6192367030 | SAN DIEGO, CITY OF | 870429 | 1030AM | 870429 | 1230PM | 1200 | GAL | BLERIOT & LINDBERGH ST. | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE | NONE | NONE | N | N | NA | NONE
870427 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870427 | 1950PM | 870427 | 2150PM | 1200 | GAL | 2386 ADIRONDACK ROW | SAN DIEGO | SD | PRIVATE CLEANOUT | GREASE | NO | NONE | NONE | CANYON | Y | N | NA | NONE
870428 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870428 | 0800AM | 870428 | 1200 N | 9600 | GAL | 4604 HURON AVE./CANYON | SAN DIEGO | SD | 8" VC MAIN | DEBRIS | NO | NONE | NONE | INTERCEPTOR INGULF & MERENA BL | Y | N | NA | NONE
870506 | LETTER | BEADLE / GRATE | 6192367030 | SAN DIEGO, CITY OF | 870502 | 1145AM | 870502 | 1445PM | 1800 | GAL | 6424 POTOMAC | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE | NONE | NONE | N | N | NA | NONE
870506 | LETTER | BEADLE / AYAP | 6192367030 | SAN DIEGO, CITY OF | 870501 | 0900AM | 870501 | 1000AM | 240 | GAL | 6900 BLACK LAKE SHORE DRIVE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE | NONE | NONE | N | N | NA | NONE
870429 | 1313PM | VAUGHN T BRADLEY | 7145822330 | SANTA MARGARITA WATER DISTRICT | 870428 | 2300PM | 870429 | 0903AM | 12000 | GAL | 43 ALLYSSUM | SANTA MARGARITA | OR | MANHOLE | LINE OBSTRUCTION | NO | NONE | NONE | STORM DRAIN | Y | N | NA | NONE
870507 | 1515PM | JOHN MELBOURNE | 6192362802 | SAN DIEGO, CITY OF | 87050 | ?????? | 87050 | ?????? | 180 | GAL | NEAR LAKE HODGES | ESCONDIDO | SD | LEAKY MAIN GASKET | LEAKY GASKET | N | NONE | NONE | THOMAS BROS. PAGE 27 D3 | Y | N | NA | CITY OF SAN DIEGO CONTACT: CHUCK FERRIS.
870504 | 1530PM | HARRIS #812 | 6192366092 | SAN DIEGO, CITY OF | 870405 | 1530PM | 870405 | 1645PM | 6 | GAL | 932 COURT ST. | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE | NONE | NONE | N | N | NA | NONE
870505 | 1330PM | HARRIS #812 | 6192366092 | SAN DIEGO, CITY OF | 870504 | 1330PM | 870504 | 1330PM | 6 | GAL | 1805 UPAS ST | SAN DIEGO | SD | CLEANOUT | ROOTS | NO | NONE | NONE | NONE | N | N | NA | NONE
870504 | 1420PM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870504 | ?????? | 870504 | ?????? | 0 | ??? | 6035 FOLSOM DRIVE | SAN DIEGO | SD | MANHOLE | ROOTS | Y | PACIFIC OCEAN | NONE | NONE | Y | Y | ?? | NONE
870504 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870504 | 0730AM | 870504 | 1045AM | 2250 | GAL | BIRMINGTON DR & MEADOWLARK DR | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE | NONE | TECOLOTE CANYON | Y | N | NA | NONE
870504 | LETTER | BEADLE//GRATE | 6192367030 | SAN DIEGO, CITY OF | 870504 | 1800PM | 870504 | 2100PM | 900 | GAL | 515 27TH ST. | SAN DIEGO | SD | MANHOLE | DEBRIS //ROCK | NO | NONE | NONE | NONE | N | N | NA | NONE
870511 | LETTER | BEADLE//DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870506 | 0700AM | 870506 | 0900AM | 120 | GAL | 5089 COLLEGE AVE. | SAN DIEGO | SD | CLEANOUT | FOOD & GREASE | NO | NONE | NONE | NONE | N | N | NA | NONE
870505 | 1200 | HARRIS #812 | 6192366092 | SAN DIEGO, CITY OF | 870505 | 1200 N | 870505 | 1415PM | 150 | GAL | 3020 WEBSTER | SAN DIEGO | SD | ??????? | ROOTS | NO | NONE | NONE | INTO GROUND NEAR HOUSE. | Y | N | NA | NONE
870505 | 1530PM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF /UTIL SYS | 870505 | 0830AM | 870505 | 1000AM | 630 | GAL | 8600 VIA COLONIA | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE | NONE | STORM DRAIN | Y | N | NA | NONE
870504 | 0945AM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF/UTIL SYS. | 870503 | 1030AM | 870503 | 1230PM | 600 | GAL | 3528 MARLBOROUGH ST | SAN DIEGO | SD | SEWER LINE | LARGE ROCKS | NO | NONE | NONE | STORM DRAIN | Y | N | NA | NONE
870504 | 0945AM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF/UTIL SYS. | 870503 | 1630PM | 870503 | 1830PM | 600 | GAL | 4555 KANSAS ST | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE | NONE | STORM DRAIN | Y | N | NA | NONE
870504 | 0945AM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF/UTIL SYS | 870502 | 1200 N | 870502 | 1500PM | 2 | GAL | 1900 SHELTER ISLAND DR. | SAN DIEGO | SD | SEWER LINE | ROOTS/DEBRIS | NO | NONE | NONE | PARKING LOT | Y | N | NA | NONE
870513 | 1420PM | DAVE SEYMOUR | 7145822330 | SANTA MARGARITA WATER DIST. | 870513 | 0830AM | 870513 | 1400PM | 35000 | GAL | CROWN VALLEY PKWY & JARDINE ST | MISSION VIEJO | OR | FORCE MAIN | CONTRACTOR BROKE MAIN. | Y | OSO CREEK | PACIFIC OCEAN | NONE | Y | N | NA | NONE
870513 | 1100AM | MIKE GARNER | 7149257676 | EASTERN MUNICIPAL WATER DIST. | 870512 | 1400PM | 870512 | 1415PM | 5000 | GAL | MAIN & PUJOL STS. | RANCHO CALIF. | RV | FORCE MAIN | CABLE TV CO. BROKE MAIN WHILE TRENCHING. | Y | TEMECULA CREEK | SANTA MARGARITA RIVER BASIN | NONE | Y | Y | 01 | AREA CHLORINATED. FORCE MAIN REPAIRED.
870511 | 1030AM | BURT SEALY | 6194411658 | SAN DIEGO, CITY OF | 870510 | 1000AM | 870510 | 1300PM | 13062 | GAL | KEY LARGO PL W/O MOLLISON | SAN DIEGO | SD | MANHOLE | GREASE | Y | FORRESTER CREEK | SAN DIEGO RIVER |  | Y | N | NA | NONE
870508 | 1045AM | OCTAVIO CASTRO | 6194820683 | CHULA VISTA, CITY OF | 870508 | 0800AM | 870508 | 1400PM | 1200 | GAL | BEHIND 536 HAMPSHIRE LANE | CHULA VISTA | SD | CHULA VISTA WOODS PUMP STATION | BREAK IN MAIN DISCHARGE LINE OUTSIDE PUMP STATION. | NO | NONE | NONE | DESILTING BASIN BY PUMP STATIO | N | N | NA | LEAKAGE CONTAINED IN DESILTING BASIN & PUMPED BACK INTO SEWER SYSTEM.
870515 | 0830AM | DICK ARNOLD | 6194411658 | EL CAJON, CITY OF | 870514 | 0830AM | 870514 | 0900AM | 1200 | GAL | FLETCHER PKWY AT NAVAJO | EL CAJON | SD | MANHOLE | GREASE | Y | SWALPIRO CHANNEL |  |  | Y | N | NA | NONE
870511 | 1150AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870510 | 0800AM | 870510 | 1700PM | 5400 | GAL | 2270 VANCOUVER AVE | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE | NONE | CANYON | Y | N | NA | NONE
870511 | 1150AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870509 | 1100AM | 870509 | 1500PM | 1500 | GAL | 5017 WARING RD TO CANYON WEST | SAN DIEGO | SD | MANHOLE | ROOTS & GREASE | NO | NONE | NONE | CANYON WEST OF ADDRESS | Y | N | NA | NONE
870509 | 1948PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DIST. | 870509 | 1720PM | 870509 | 2045PM | 20 | GAL | SOUTH STAGE COACH LINE | FALLBROOK | SD | C.O. OVERFLOWING | OBSTRUCTION IN LATERAL | NO | NONE | NONE | NONE | N | N | NA | NONE
870507 | 0800AM | HARRIS | 6192366092 | SAN DIEGO, CITY OF | 870507 | 0800AM | 870507 | 1200 N | 15 | GAL | 950 HOTEL CIRCLE NORTH | SAN DIEGO | SD |  | GREASE | NO | NONE | NONE | NONE | Y | N | NA | NONE
870507 | 1100AM | CHARLES E. FERRIS | 6195789760 | SAN DIEGO, CITY OF | 870507 | 0700AM | 870507 | 1100AM | 240 | GAL | 12511 LAKE DRIVE | SAN DIEGO | SD | 20" DI PIPE | LEAK IN RUBBER GASKET | NO | NONE | NONE | GROUND | Y | N | NA | SEWER PIPE SHUT DOWN. AREA OF CANYON DIKED TO PREVENT POSSIBILITY OF REACHING LAKE.
870512 | 1030AM | M. ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870511 | 1430PM | 870511 | 1630PM | 12 | GAL | 1805 UPAS ST. | SAN DIEGO | SD | CLEANOUT | RAGS AND DEBRIS | N | NONE | NONE | AROUND CLEANOUT AREA | Y | N |  | AREA DEOTORIZED.
870512 | 1030AM | M.ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870511 | 1730PM | 870511 | 1900PM | 60 | GAL | 1070 TOURMALINE ST. | SAN DIEGO | SD | CLEANOUT | ROOT & GREASE BLOCKAGE | N | NONE | NONE | SOAKED INTO GROUND | Y | N |  | AREA DEOTORIZED AND HOSED DOWN.
870512 | 1000AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870511 | 1900PM | 870511 | 2100PM | 900 | GAL | 2000 ELM ST ///SOUTH BAY | SAN DIEGO | SD | MANHOLE | ROOT AND ROCKS//VANDALISM. | N | NONE | NONE | CREEK BED | Y | Y | 02 | AREA DEOTORIZED AND 3 SIGNS POSTED.
870510 | 0800AM | T. CLIPPER JR. | 6192365534 | SAN DIEGO, CITY OF | 870510 | 0800AM | 870510 | 0900AM | 1500 | GAL | 14034 BARRYMORE ST. | SAN DIEGO | SD | MANHOLE | POWER OUTAGE DUE TO BLOWN FUSE ON POLE. | Y | POND ON FARM(PRIVATE PROPERTY) |  |  | Y | N
870519 | 0918AM | GEORGE LONG | 6196942133 | SAN DIEGO, COUNTY OF | 870518 | 1730PM | 870519 | 2000PM | 4000 | GAL | 143 CEDROS & LOMA SANTA FE | SOLANA BEACH | SD | MAIN TRUNK COLLECTION LINE | GREASE & ROOT BLOCKAGE | Y | OCEAN AT SOLANA BCH COVE. |  |  | Y | Y | 02
870510 | 1300PM | VAUGHN TOM BRADLEY | 7145822330 | SANTA MARGARITA WTR DIST. | 870510 | 1300PM | 870510 | 1600PM | 750 | GAL | #161 DAFFODILE | RANCHO SANTA MAR | OR | SEWER LINE | GRAVEL & ROCK | NO | NONE | NONE | NONE | Y | N | NA | AREA WASHED AND CHLORINATED.
870516 | 0930AM | MANAGER | 4969247 | CAPISTRANO BCH SANITARY DIST. | 870516 | 0930AM | 870516 | 1330PM | 300 | GAL | CALLE LOMA CALLE ALMANZA | CAPISTRANO BCH | OR | SEWER LINE | GREASE | NO | NONE | NONE | NONE | N | N | NA | NONE
870519 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870509 | 0900AM | 870512 | 2200PM | 5100 | GAL | 2200 BLK OF VANCOUVER ST. | SAN DIEGO | SD | MANHOLE | ROOTS & ROCK | NO | NONE | NONE | NONE | N | N | NA | NONE
870519 | LETTER | BEADLE//GRATE | 6192367030 | SAN DIEGO, CITY OF | 870513 | 0815AM | 870513 | 1015AM | 1200 | GAL | 5740 DIVISION ST. | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE | NONE | NONE | N | N | NA | NONE
870519 | LETTER | BEADLE // AYAP | 6192367030 | SAN DIEGO, CITY OF | 870512 | 1115AM | 870512 | 1415PM | 540 | GAL | BROOKS ST & FOURTH AVE | SAN DIEGO | SD | MANHOLE | HEAVY GREASE | NO | NONE | NONE | NONE | N | N | NA | NONE
870512 | 1530PM | STATION 38 STAFF | 6192365640 | SAN DIEGO, CITY OF | 870512 | 1530PM | 870512 | 1630PM | 198 | GAL | 1714 PALM AVE | PALM CITY | SD | DISCHARGE HOSE TO MANHOLE | BROKEN DISCHARGE HOSE | NO | NONE | NONE | FIELD BEHIND TRAILER COURT | Y | N | NA | AREA TREATED WITH ZEP FOR DISINFECTION.
870513 | 0840AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870512 | 1800PM | 870513 | 0100AM | 90 | GAL | 1110 "C" STREET | SAN DIEGO | SD | MANHOLE & CLEANOUT | ROOTS AND RAGS | NO | NONE | NONE | NONE | Y | N | NA
870520 | 1200 N | TONY LAURICIA | 6197440460 | SAN MARCOS COUNTY WATER DIST. | 870520 | 0400AM | 870520 | 0405AM | 100 | GAL | 2310 RANCHO SANTA FE RD | CARLSBAD | SD | CHLORINE CONTACT TANK | WATER LEVEL HIGH IN TANK DUE TO EFFLUENT PUMP SHORTING OUT. | ?? | SAN MARCOS CREEK |  |  | Y | N | NA | NONE
870521 | 1125AM | SIMON EVANS | 6192367340 | SAN DIEGO, CITY OF | 870521 | 0754AM | 870521 | 0910AM | 1900 | GAL | 2500 BLK INGRAHAM ST/DANA LNDG | SAN DIEGO | SD | MANHOLE | HEAVY GREASE IN 12" MAIN | Y | MISSION BAY |  |  | Y | Y | 03 | 5 SIGNS POSTED, CO. HEALTH IS SAMPLING.
870519 | LETTER | BEADLE // GRATE | 6192367030 | SAN DIEGO, CITY OF | 870516 | 1615PM | 870517 | 0115AM | 2700 | GAL | 56TH ST & MEADE | SAN DIEGO | SD | MANHOLE | COLLAPSED MAIN | NO | NONE | NONE | NONE | N | N | NA | NONE
870519 | LETTER | BEADLE // DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870515 | 1930PM | 870515 | 2130PM | 1200 | GAL | 1706 PENTUCKETT | SAN DIEGO | SD | MANHOLE | ROCKS// DEBRIS | NO | NONE |  |  | N | N | NA | NONE
870519 | LETTER | BEADLE // GRATE | 6192367030 | SAN DIEGO, CITY OF | 870516 | 1340PM | 870516 | 1540PM | 2400 | GAL | 500 BLK OF HOTEL CIRCLE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA | NONE
870515 | 1930PM | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 870515 | 1900PM | 870515 | 2000PM | 500 | GAL | 1010 EAST WASHINGTON | ESCONDIDO | SD | MH-PAGE 72 MH 4 | GREASE | NO | NONE |  |  | N | N | NA | AREA TREATED WITH HTH AND WASHED WITH FRESH WATER.
870519 | LETTER | BEADLE//WANTIES | 6192367030 | SAN DIEGO, CITY OF | 870514 | 0800AM | 870514 | 1000AM | 360 | GAL | 1110 "C" STREET | SAN DIEGO | SD | CLEANOUT | UNKNOWN | NO | NONE |  |  | N | N | NA | NONE
870518 | 0825AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870515 | 0700AM | 870515 | 1000AM | 30 | GAL | 11TH AND "C" STREET | SAN DIEGO | SD | CLEANOUT IN PARKING LOT | STOPPAGE BY UNKNOWN OBJECT | NO | NONE |  |  | Y | N | NA | WASHED AND DEOTORIZED FLOODED AREA IN STREET AND LOT.
870519 | 0845AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870518 | 1000AM | 870518 | 1300PM | 90 | GAL | 1908 ORA VISTA RD. | SAN DIEGO | SD | MANHOLE | GREASE & RAGS | NO | NONE |  |  | Y | N | NA | DEOTORANT APPLIED TO AREA.
870519 | 0845AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870518 | 1300PM | 870518 | 1700PM | 150 | GAL | E/O WASHINGTON & INDIA STS. | SAN DIEGO | SD | MANHOLE IN CANYON | ROOTS, DIRT & ROCKS | NO | NONE |  |  | N | N | NA | DEOTORANT APPLIED TO OVERFLOW AREA.
870526 | 0900 | MS. ANN HEINKEL | 6192840763 | SAN DIEGO, CITY OF | 870508 | ?????? | 870511 | ?????? | 1000000 | GAL | 4900 BLK ORANGE AVE | SAN DIEGO | SD | BROKEN MAIN | BROKEN SEWER MAIN.SEWAGE ROUTED TO ANOTHER SEWER NEAR 5085 UNIVERSITY. | NO | NONE |  |  | Y | Y | 15 | THERE WAS A PRESS RELEASE ON THIS SPILL BUT IT IS NOT A PROP 65 INCIDENT.
870526 | 1415PM | ALLEGRE DIAZ |  | SAN DIEGO, CITY OF | 870525 | 1045AM | 870525 | 1245PM | 1200 | GAL | 1100 BLK ANCHORAGE | SAN DIEGO | SD | MANHOLE | GREASE // DEBRIS | Y | SAN DIEGO BAY |  |  | Y | Y | 02 | COUNTY HEALTH IS SAMPLING.
870526 | 1330PM | JOAN GEISELHART | 6197530155 | LEUCADIA COUNTY WATER DIST. | 870526 | 1115AM | 0 | ?????? | 10 | EGD | S MARCOS CRK NR LA COSTA HOTEL | LEUCADIA?? | SD | LEAKING FORCE MAIN UNDER CREEK | UNKNOWN AT THIS TIME.MAIN IS BEING DUG UP TO DETERMINE CAUSE. | Y | SAN MARCOS CREEK |  |  | Y | ? | ?? | NONE
870526 | LETTER | BEADLE//GRATE | 6192367030 | SAN DIEGO, CITY OF | 870520 | 1600PM | 870520 | 1800PM | 600 | GAL | 4041 UNIVERSITY AVE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA | NONE
870526 | LETTER | BEADLE//DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870520 | 0900AM | 870520 | 1000AM | 3100 | GAL | 920 SOUTH 33RD ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA | NONE
870521 | 0940AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870520 | 1520PM | 870520 | 1720PM | 120 | GAL | 15TH AND BROADWAY | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA | STREET CLEANED WITH DISINFECTANT.
870521 | 0940AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870520 | 0900AM | 870520 | 1000AM | 60 | GAL | 4753 LOTUS ST | SAN DIEGO | SD | MANHOLE | GREASE & ROOTS | NO | NONE |  |  | Y | N | NA | STREET AREA WASHED AND DEOTORIZED.
870520 | LETTER | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870519 | 2130PM | 870519 | 2330PM | 600 | GAL | 2744 GREGORY ST | SAN DIEGO | SD | SEWER LINE | UNKNOWN | NO | NONE |  |  | Y | N | NA | NONE
870520 | LETTER | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870519 | 1900PM | 870519 | 2000PM | 300 | GAL | 1620 CATALINA BLVD. | SAN DIEGO | SD | SEWER LINE | ROOTS | NO | NONE |  |  | Y | N | NA | NONE
870518 | LETTER | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870518 | 1630PM | 870518 | 1800PM | 450 | GAL | KETTNER BL. & PALM ST. | SAN DIEGO | SD | SEWER LINE | GREASE | Y | SAN DIEGO BAY |  |  | Y | N | NA | NONE
870518 | 2000PM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870518 | 1900PM | 870518 | 2000PM | 300 | GAL | ROSECRANS & JAMES | SAN DIEGO | SD | SEWER LINE | GREASE | Y | SAN DIEGO BAY |  |  | Y | N | NA | NONE
870519 | LETTER | GEORGE LONG | 6196942133 | SAN DIEGO, COUNTY OF | 870518 | 1730PM | 870518 | 2000PM | 4500 | GAL | CEDROS AVE NR LOMA SANTA FE DR | SOLANA BEACH | SD | MANHOLE | ROOTS & GREASE | Y | OCEAN AT STATE PARK |  |  | Y | Y | ??
870525 | LETTER | BEADLE// DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870525 | 1045AM | 870525 | 1245PM | 1200 | GAL | ADDISON & SHAFTER | SAN DIEGO | SD | MANHOLE | ROOTS //DEBRIS | Y | YATCH HARBOR |  |  | Y | Y | ??
870601 | 0820AM | DON GRIFFIN | 6192367334 | SAN DIEGO, CITY OF | 870531 | 2145PM | 870601 | 1245PM | 45000 | GAL | BEHIND 11000 BERNARDO TRAIL CT | SAN DIEGO | SD | 3 MANHOLES | ROOTS SUSPECTED | Y | LAKE HODGES |  |  | Y | Y | ??
870529 | 1530PM | DICK ARNOLD | 6194411658 | EL CAJON, CITY OF | 870528 | 1700PM | 870528 | 1900PM | 700 | GAL | 1008 VICTOR ST. | EL CAJON | SD | MANHOLE | GREASE | Y | BROADWAY CHANNEL | FORESTER CREEK | SAN DIEGO RIVER | Y | N
870529 | LETTER | BEADLE//DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870525 | 1030AM | 870525 | 1530PM | 300 | GAL | 3173 GOLDFINCH | SAN DIEGO | SD | CLEANOUT | ROOTS & GREASE | NO | NONE |  |  | N | N | NA
870529 | LETTER | BEADLE//DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870525 | 1500PM | 870525 | 2000PM | 300 | GAL | 751 GEORGIA | SAN DIEGO | SD | CLEANOUT | OVERLOADED SEWER MAIN | NO | NONE |  |  | N | N | NA
870526 | 0845AM | M ARNOLD | 6102366092 | SAN DIEGO, CITY OF | 870522 | 1030AM | 870522 | 1130AM | 90 | GAL | 1702 NATIONAL AVE | SAN DIEGO | SD | CLEANOUT | GREASE / DEBRIS | NO | NONE |  |  | Y | N | NA | STREET AND YARD AREAS WASHED DOWN AND DEOTORIZED.
870521 | 1530PM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870521 | 0830AM | 870521 | 0930AM | 120 | GAL | 7970 PORT ROYALE DRIVE | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N | NA
870601 | LETTER | BEADLE//DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870527 | 2200PM | 870528 | 0200AM | 1200 | GAL | 924 44TH ST | SAN DIEGO | SD | CLEANOUT | ROOTS & GREASE | NO | NONE |  |  | N | N | NA
870601 | LETTER | BEADLE / DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870527 | 1900PM | 870527 | 2100PM | 1200 | GAL | OMEGA & SYLVY | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
870523 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870523 | 0900AM | 870523 | 1200 N | 2700 | GAL | HALLER & BOUNDRY | SAN DIEGO | SD | MANHOLE | ROCK OBSTRUCTION | NO | NONE |  |  | Y | ? | ??
870527 | 0810AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870526 | 0700AM | 870526 | 1000AM | 1500 | GAL | 600 BUSH ST | SAN DIEGO | SD | MANHOLE IN CANYON | ROOTS & GREASE | NO | NONE |  |  | Y | N | NA | DEOTORANT APPLIED TO SPILL AREA.
870603 | 1000AM | ALLGRE DIAZ |  | SAN DIEGO, CITY OF | 870602 | 1609PM | 870602 | 1907PM | 2670 | GAL | 2418 FLEETWOOD ST | SAN DIEGO | SD | MANHOLE | UNKNOWN AT THIS TIME | Y | SAN DIEGO BAY |  |  | Y | Y | ?? | POSTED 4 SIGNS ON AVENIDA DEL RIO AND 100 YDS EA SIDE DOWNSTREAM ALONG CHANNEL.SAMPLING
870529 | 1530PM | RICHARD ARNOLD | 6194411658 | EL CAJON, CITY OF | 870528 | 1700PM | 870528 | 1900PM | 700 | GAL | 1008 VICTOR ST | EL CAJON | SD | MANHOLE | GREASE | Y | BROADWAY CHANNEL |  |  | Y | ? | ?? | NONE
870603 | 0800AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870602 | 1900PM | 870602 | 2000PM | 600 | GAL | 2418 FLEETWOOD | SAN DIEGO | SD | MANHOLE | GREASE, ROCKS | Y | SAN DIEGO RIVER |  |  | Y | Y | 05 | ENTERED S.D. RIVER AT CAM DE LA REINA AND HWY 163 VIA STORM DRAIN.
870601 | 0840AM | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 870601 | 0830AM | 870601 | 0850AM | 5000 | GAL | 2698 SO. ESCONDIDO BL PS N02 | ESCONDIDO | SD |  | CONTRACTOR BROKE FORCE MAIN WHILE EXCAVATING. | NO | NONE |  | LAND AREA ADJACENT TO P.S. NO2 | N | N | NA | AREA DISINFECTED AND CLEANED BY CITY CREWS.
870603 | LETTER | ANTHONY LAURICIA | 6197440460 | SAN MARCOS COUNTY WATER DIST. | 870530 | 1015AM | 870530 | 1200 N | 600 | GAL | CRIBBAGE LN & SAN MARCOS BLVD. | SAN MARCOS | SD | SEWER LINE | GREASE | NO | NONE |  | DRAINAGE DITCH | N | N | NA | DITCH AREA CHLORINATED W/ HTH.
870605 | LETTER | BEADLE//GRATE | 6192367030 | SAN DIEGO, CITY OF | 870530 | 1200PM | 870530 | 1400PM | 1200 | GAL | 2412 FLEETWOOD IN CANYON | SAN DIEGO | SD | MANHOLE | GREASE//DEBRIS | NO | NONE |  |  | N | N | NA | NONE
870605 | LETTER | BEADLE//GRATE | 6192367030 | SAN DIEGO, CITY OF | 870530 | 1010AM | 870530 | 1210PM | 1200 | GAL | 8163 WESTMORE RD. | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA | NONE
870605 | LETTER | BEADLE//DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870603 | 0900AM | 870603 | 1200 N | 900 | GAL | 5314 SAN BERNARDO WAY | SAN DIEGO | SD | CLEANOUT | ROOTS | NO | NONE |  |  | N | N | NA | NONE
870605 | LETTER | BEADLE//GRATE | 6192367030 | SAN DIEGO, CITY OF | 870530 | 1400PM | 870530 | 1600PM | 600 | GAL | 69TH BET IMPERIAL & JAMACHA | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA | NONE
870605 | LETTER | BEADLE//THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870528 | 0700AM | 870528 | 0900AM | 240 | GAL | 4794 WINONA | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA | NONE
870601 | 1025AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870531 | 1519PM | 870531 | 1620PM | 6 | GAL | S/O ROBINSON W/O HWY 163 CNYN | SAN DIEGO | SD | MANHOLE | TREE ROOTS | NO | NONE |  |  | N | N | NA | CANYON AREA DEOTORIZED.
870608 | 1145AM | PATTY VANIK | 6192216608 | SAN DIEGO, CITY OF | 870604 | ?????? | 0 | ?????? | 0 | ??? | PT. LOMA WWTP | SAN DIEGO | SD | OUTFALL MIXING BOX | SUSPECT SMALL LEAK IN MIXING BOX VALVE GASKET | Y | PACIFIC OCEAN |  |  | Y | ? | ?? | CITY IS MONITORING COLIFORM COUNTS ON DAILY BASIS.
870605 | 0925AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870604 | 1100AM | 870604 | 1200PM | 120 | GAL | SAN DIEGO ZOO | SAN DIEGO | SD | MANHOLE | 6" SEWER MAIN STOPPED BY ROCKS & ASPHALT | NO | NONE |  |  | Y | N
870605 | 1015AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870603 | 1916PM | 870604 | 1116AM | 14400 | GAL | 7506 AEGEAN CT. | SAN DIEGO | SD | SEWER LINE | ROCKS & DEBRIS | NO | NONE |  |  | Y | N
870604 | 1800PM | BEADLE//GRATE | 6192367030 | SAN DIEGO, CITY OF | 870604 | 1000AM | 870604 | 1700PM | 2100 | GAL | 3422 ADDISON | SAN DIEGO | SD | MANHOLE | GREASE & DEBRIS | Y | YACHT HARBOR |  |  | Y | N
870605 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870604 | 0840AM | 870604 | 0940AM | 120 | GAL | 1025 SIGSBEE ST | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | Y
870615 | 0924AM | LES JONES | 6195227380 | CORONADO, CITY OF | 870614 | 0806AM | 870614 | 0900AM | 300 | GAL | ADMIRALITY CROSS AT THE POINT | CORONADO | SD | POINT PUMPING STATION MANHOLE | DEBRIS BLOCKAGE | Y | SAN DIEGO BAY |  |  | Y | N | NA | NO SOLIDS, ONLY LIQUID.
870611 | LETTER | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870610 | 2000PM | 870611 | 0030AM | 750 | GAL | 6589 BLUEFIELD PLACE | SAN DIEGO | SD | MANHOLE | TREE ROOTS | NO | NONE |  |  | Y | N | NA
870611 | LETTER | M ARNOLD | 6192366092 | SAN DIEGO, VITY OF | 870610 | 1010AM | 870610 | 1350PM | 210 | GAL | 15TH ST & BROADWAY | SAN DIEGO | SD | MANHOLE | RAGS,PAPER,GREASE | NO | NONE |  |  | Y | N | NA
870611 | 0910AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870610 | 2000PM | 870610 | 2200PM | 120 | GAL | 4828 ART ST | SAN DIEGO | SD | LATERAL | ROCKS | NO | NONE |  |  | N | N | NA
870608 | LETTER | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870606 | 1130AM | 870606 | 1230PM | 30 | GAL | 900 BLK SUNSET CLIFFS BLVD. | SAN DIEGO | SD | MANHOLE | GREASE & RAGS | Y | PACIFIC OCEAN AT ADDRESS |  |  | Y | Y | ??
870615 | LETTER | BEADLE//GRATE | 6192367030 | SAN DIEGO, CITY OF | 870607 | 1830PM | 870608 | ?????? | 50 | GPM | CANYON S/O BOUNDARY & HALLER | SAN DIEGO | SD | 18" PIPE | HIGH FLOW AND LEAK IN MAIN | NO | NONE |  |  | N | N | NA | 50 GAL PER MINUTE FLOW DURING PEAK FLOW.
870608 | LETTER | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870606 | 1600PM | 870606 | 1800PM | 12 | GAL | 3147 COLLURA ST | SAN DIEGO | SD | LATERAL | BROKEN LATERAL IN STREET | NO | NONE |  |  | N | N | NA | OVERFLOW NOT DUE TO CITY SEWER SYS. DEFECT.
870608 | LETTER | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870606 | 1245PM | 870606 | 1345PM | 12 | GAL | 753 GEORGIA ST | IMPERIAL BEACH | SD | CLEANOUT AT ADDRESS | 15"MAIN OVERLOADED. | NO | NONE |  | PARKING AREA REAR OF ADDRESS | N | N | NA
870608 | LETTER | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870606 | 1400PM | 870606 | 1500PM | 6 | GAL | 1529 GOLDEN GATE DR | SAN DIEGO | SD | MANHOLE | DIRT & LEAVES | NO | NONE |  |  | N | N | NA | AREA DEOTORIZED.
870618 | 1345PM | DENNIS POLLACK | 6197530155 | LEUCADIA COUNTY WATER DIST. | 870618 | 0900AM | 870619 | 1800PM | 24000 | GAL | SAN MARCOS CREEK E/O LAGOON. | CARLSBAD | SD | SEWER FORCE MAIN | LEAK IN OLD PIPE. | Y | BATIQUITAOS LAGOON |  |  | Y | Y | ?? | LAGOON CLOSED OFF FROM OCEAN DUE TO HIGH TIDES.LINE STILL UNDER REPAIR FROM LAST LEAK.
870618 | LETTER | BEADLE // AYAP | 6192367030 | SAN DIEGO, CITY OF | 870611 | 0745AM | 870611 | 1045AM | 540 | GAL | 6589 BLUEFIELD PLACE | SAN DIEGO | SD | MANHOLE | UNKNOWN | NO | NONE |  |  | N | N | NA | NONE
870615 | 0825AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870613 | 1130AM | 870613 | 1330PM | 240 | GAL | 68TH & UNIVERSITY | SAN DIEGO | SD | MANHOLE | GREASE BLOCKAGE | NO | NONE |  |  | Y | N | NA | DISINFECTANT APPLIED TO AREA.
870614 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870614 | 1030AM | 870614 | 1530PM | 1800 | GAL | 3675 VAN DYKE ST | SAN DIEGO | SD | CLEANOUT | GREASE OBSTRUCTION | NO | NONE |  |  | Y | N | NA | NONE
870618 | LETTER | BEADLE//GRATE | 6192367030 | SAN DIEGO, CITY OF | 870615 | 1007AM | 870615 | 1107AM | 60 | GAL | CUMBERLAND & MORNINGSIDE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA | NONE
870622 | 1430PM | GARY ORR | 6194397164 | OCEANSIDE, CITY OF | 870622 | 0800AM | 870622 | 2100PM | 51750 | GAL | 510 JONES ROAD | OCEANSIDE | SD | ROYMAR SEWAGE PUMP STATION. | PUMP STATION NOT CLEARING SEWAGE FAST ENOUGH,CONSTRUCTION DEBRIS JAMMED IMPELLORS. | Y | SAN LUIS REY RIVER TO OCEAN | PACIFIC OCEAN |  | Y | Y | 04 | THERE WAS A MEDIA RELEASE ON THIS.
870622 | 1530PM | ALLEGRE DIAZ | 6192364717 | SAN DIEGO, CITY OF | 870622 | 1330PM | 870622 | ?????? | 300 | GAL | 1700 PACIFIC HWY AT ELM ST. | SAN DIEGO | SD | MANHOLE | GREASE | Y | SAN DIEGO BAY |  |  | Y | Y |  | 3 SIGNS POSTED.
870622 | LETTER | BEADLE // DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870617 | 0700AM | 870617 | 0900AM | 1200 | GAL | 3412 PETRA PLACE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA | NONE
870612 | 1500PM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870612 | 1000AM | 870612 | 1100AM | 300 | GAL | 3400 MONROE AVE | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N
870612 | 1500PM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870612 | 1000AM | 870612 | 1100AM | 10 | GAL | 3472 MADISON AVE | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N
870623 | 1050AM | DALE HOFFLAND | 6196942132 | SAN DIEGO, COUNTY OF | 870623 | 0830AM | 870623 | 0900AM | 23000 | GAL | W OF I-5 NR. MANCHESTER AVE | CARDIFF | SD | 3 INCH BLOW OFF PIPE | AIR RELEASE VALVE STRUCTURE COLLAPSED SEVERING 3" PVC LINE DIRECTLY TIED TO 14" OLIVENHAIN FORCE MAIN. | Y | SAN ELIJO LAGOON |  |  | Y | N | NA | NO FLOW TO OCEAN DUE TO HIGH TIDES. MOUTH BLOCKED BY SAND.
870623 | 0930AM | JIM SMITH | 7146432006 | MOULTON NIGUEL MWD | 0 | ?????? | 870622 | 1430PM | 75000 | GPD | CHOLLINAS CAPISTRANO FLD CHANN | ????? | OR | MANHOLE | UNKNOWN BLOCKAGE POSSIBLY DUE TO GRADING OR VANDALISM. ASPHALT IN MANHOLE. | Y | OSO CREEK TO SAN JUAN CREEK |  |  | N | N | NA | NONE
870625 | LETTER | JOAN GEISELHART | 6197530155 | LEUCADIA COUNTY WATER DIST. | 870617 | 0300AM | 870617 | ?????? | 1800 | GAL | LA COSTA AV 1500FT W EL CAMINO | CARLSBAD | SD | SEWER LINE BLOWOFF | DRUNK DRIVER STRUCK SEWER LINE BLOWOFF WITH VEHICLE. | N | NONE |  |  | ? | ? | ?? | IT IS VERY DOUBFUL THAT SEWAGE REACHED BATIQUITOS LAGOON.
870619 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870618 | 1500PM | 870618 | 1900PM | 2400 | GAL | 4497 REVILLO DR | SAN DIEGO | SD | MANHOLE | ROOTS AND ROCKS | NO | NONE |  |  | Y | N | NA | NONE.
870624 | LETTER | BEADLE//THOMPSON | 6192367030 | SAN DIEGO,CITY OF | 870621 | 1100AM | 870621 | 1600PM | 1500 | GAL | BERNARDO CENTER DR & ESCALA | SAN DIEGO | SD | MANHOLE | HEAVY GREASE | NO | NONE |  |  | N | N | NA | NONE
870624 | LETTER | BEADLE // THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870620 | 1000AM | 870620 | 1200 N | 600 | GAL | 6780 FRIARS ROAD | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA | PLACED 2 SIGNS NORTH OF AND SOUTH OF FRIARS ROAD.
870624 | LETTER | BEADLE//THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870620 | 1600PM | 870620 | 2100PM | 300 | GAL | 2821 CLAY AVE | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | N | N | NA | NONE
870624 | LETTER | BEADLE//THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870620 | 1930PM | 870620 | 2230PM | 180 | GAL | 2045 HAWTHORN | SAN DIEGO | SD | CLEANOUT | RAGS AND PAPER. | NO | NONE |  |  | N | N | NA | NONE.
870624 | LETTER | BEADLE // THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870621 | 1100AM | 870621 | 1300PM | 120 | GAL | 3800 BLK KENDALL IN EAST ALLEY | SAN DIEGO | SD | MANHOLE | WOOD IN CHANNEL OF MANHOLE. | NO | NONE |  |  | N | N | NA | NONE.
870624 | LETTER | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870621 | 1630PM | 870621 | 1930PM | 180 | GAL | KENYON CT. | SAN DIEGO | SD | SEWER LINE | ROOTS. | NO | NONE |  |  | Y | N | NA | NONE.
870623 | 0830AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870622 | 0755AM | 870622 | 0855AM | 300 | GAL | CORONADO AVE & CATALINA AVE | SAN DIEGO | SD | MANHOLE | ROOTS & GREASE | NO | NONE |  |  | N | N | NA
870623 | 0810AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870622 | 1830PM | 870622 | 2030PM | 120 | GAL | GOLD GULCH IN BALBOA PARK | SAN DIEGO | SD | SEWER LINE | ROOTS | NO | NONE |  |  | Y | N | NA
870625 | 1420PM | DALE HOFFLAND | 6196942132 | SAN DIEGO, COUNTY OF | 870625 | 0930AM | 870625 | 1100AM | 5000 | GAL | 3600 SO. GRANADA & FONDA RD. | CASA DE ORO | SD | MANHOLE | ROCKS & DEBRIS | Y | NEARBY CREEK FLOWING WEST |  |  | Y | Y | ?? | NONE
870629 | 1015AM | DAVE SEYMOUR |  | SANTA MARGARITA WATER DIST. | 870627 | 1000AM | 870627 | 1230PM | 3000 | GAL | INTRSEC OF ANAYA & ONTUR STS. | MISSION VIEJO | OR | MANHOLE | GREASE | Y | OSO CREEK |  |  | Y | N | NA | BARRIER STPPED FLOW
870624 | 0800AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870623 | 1215PM | 870623 | 1315PM | 6 | GAL | 2301 PAN AM PLAZA | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N | NA
870629 | LETTER | BEADLE//THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870625 | 2200PM | 870625 | 2400PM | 120 | GAL | GESNER ST & GESNER PLACE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA | NONE
870629 | LETTER | BEADLE//THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870624 | 0700AM | 870624 | 1100AM | 240 | GAL | 4715 CASTANA | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA | NONE
870629 | LETTER | BEADLE//GRATE | 6192367030 | SAN DIEGO, CITY OF | 870624 | 0910AM | 870624 | 1010AM | 120 | GAL | 1800 THOR ST | SAN DIEGO | SD | MANHOLE | DEBRIS | NO | NONE |  |  | N | N | NA | NONE
870629 | LETTER | BEADLE//WANTIEZ | 6192367030 | SAN DIEGO, CITY OF | 870623 | 1200 N | 870623 | 1330PM | 90 | GAL | 15TH ST & BROADWAY | SAN DIEGO | SD | MANHOLE | SLUDGE & PAPER | NO | NONE |  |  | N | N | NA | NONE
870622 | 0740AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870621 | 1300PM | 870621 | 1600PM | 30 | GAL | 3102 FIRST AVE | SAN DIEGO | SD | SEWER LINE | ROOTS | NO | NONE |  |  | Y | N | NA | NONE
870701 | 0900AM | ALLEGRE DIAZ | 6192362802 | CARLSBAD, CITY OF | 870630 | 0930AM | 870630 | 1015AM | 600 | GAL | BATIQUITOS LAGOON N. SHORE | CARLSBAD | SD | 2 MANHOLES | PUMP FAILURE AT LA COSTA LIFT STA. SPILL AT SO. END OF BATIQUITOS DR.//CALLED IN BY CARLSBAD UTIL. MAINT. DEPT. | Y | BATIQUITOS LAGOON |  |  | Y | N | NA | DID NOT REACH OCEAN.
870623 | 1315PM | STATION 38 | 6192365640 | SAN DIEGO, CITY OF | 870623 | 1315PM | 870623 | 1500PM | 816 | GAL | 9888 LA JOLLA FARMS RD. | SAN DIEGO | SD | STATION 45 | BLOCKAGE IN STA. 45 CAUSED BY UNIT 651 RODDING MAIN. | NO | NONE |  |  | Y | N | NA | NONE
870701 | LETTER | BEADLE // THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870626 | 0900AM | 870626 | 1000AM | 1200 | GAL | 4965 MONROE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA | NONE
870626 | 1030AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870625 | 0900AM | 870625 | 1100AM | 240 | GAL | 4190 INGALLS AVE | SAN DIEGO | SD | MANHOLE | GREASE & ROOTS | NO | NONE |  |  | Y | N | NA | NONE
870629 | 1000AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870627 | 1830PM | 870628 | 0200AM | 270 | GAL | 3102 1ST AVE | SAN DIEGO | SD | MANHOLE | ROCKS/ROOTS | NO | NONE |  |  | Y | N | NA | NONE
870626 | 1030AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870625 | 1100AM | 870625 | 1500PM | 60 | GAL | 4388 ARCADIA DR | SAN DIEGO | SD | MANHOLE | ROOTS//SLUDGE | NO | NONE |  |  | Y | N | NA | NONE
870626 | 1030AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870625 | 0930AM | 870625 | 1030AM | 120 | GAL | FASHION VALLEY & HOTEL CIRCLE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
870702 | 1350PM | MIKE GARNER | 7149257676 | EASTERN MUNICIPAL WATER DIST. | 870701 | 1943PM | 870702 | 0200AM | 25000 | GAL | 12899 FRONT ST AT TEMECULA | RANCHO CALIF. | RI | 60" MANHOLE-LIFT STATION | SUSPECT LARGE VALVE LEFT OPEN. | Y | TEMECULA CREEK | SANTA MARG. RIVER ?? |  | Y | N | NA | POOLED SEWEAGE PUMPED BACK INTO SEWER. AREA BARRICADED.
870706 | 0945AM | PAT HOY | 6192365241 | SAN DIEGO, CITY OF | 870705 | ?????? | 870705 | ?????? | 35000 | GAL | CORNER DELEVAN & ASH STREETS | SAN DIEGO | SD | ??????? | ROCK BLOCKAGE | NO | NONE |  | ABSORBED INTO SOIL | Y | N | NA | NONE
870708 | 0925AM | MR. HOWARD | 6196943643 | SAN DIEGO, COUNTY OF | 870707 | 1415PM | 870707 | 1435PM | 2000 | GAL | OLD HWY 80 & CHIMNEY ROCK LN |  | SD | MANHOLE | DEBRIS BLOCKAGE | NO | NONE |  |  | Y | N |  | THE SPILL AREA WAS CHLORINATED.
870713 | 0830AM | LLOYD THOMPSON | 7144973311 | LAGUNA BEACH, CITY OF | 870710 | 1800PM | 870711 | 0400AM | 5000 | GAL | BET. CLEO & LEGION STS. | LAGUNA BEACH | OR | VENT PIPE AT CLEO PUMP STA #9 | POWER FAILURE DUE TO TELEPHONE POLE FIRE. | Y | PACIFIC OCEAN |  |  | Y | Y | 04 | NONE
870708 | 1100AM | DOUG CLARK | 6194622222 | OTAY MUNICIPAL WATER DISTRICT | 870707 | 1045AM | 870707 | 1115AM | 20 | GPM | 10595 JAMACHA BLVD. |  | SD | AIRVAC #4 | CRACK IN PVC BUSHING | NO | NONE |  |  | N | N | NA | DISCH WAS AT EFFL FORCE MAIN 2000FT SO. OF TREATMENT PLANT.
870710 | LETTER | BEADLE// BURTON | 6192367030 | SAN DIEGO, CITY OF | 870707 | 1137AM | 870707 | 1337PM | 120 | GAL | CAREFREE DR. & PLAZA BLVD. | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N
870708 | 0830AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870707 | 1200 N | 870707 | 1330PM | 900 | GAL | 60 BEYER WAY | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
870707 | 0830AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870707 | 0940AM | 870707 | 1040AM | 300 | GAL | 4201 VENUS ST | SAN DIEGO | SD | CLEANOUT | GREASE & DEBRIS | NO | NONE |  |  | Y | N
870708 | LETTER | BEADLE//THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870703 | 1230PM | 870703 | ?????? | 300 | GAL | 753 GEORGIA ST | SAN DIEGO | SD | CLEANOUT | MAIN OVERLOADED. | NO | NONE |  |  | N | N
980708 | LETTER | BEADLE//THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870705 | 1630PM | 870705 | 1830PM | 1200 | GAL | 2170 BLUEHAVEN DR. | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N
870708 | LETTER | BEADLE//THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870705 | 1440PM | 870705 | 1640PM | 120 | GAL | 3636 DUPONT ST | SAN DIEGO | SD | VLEANOUT | ROOTS | NO | NONE |  |  | N | N
870708 | LETTER | BEADLE//BURTON | 6192367030 | SAN DIEGO, CITY OF | 870702 | 1030AM | 870702 | 1330PM | 180 | GAL | 4101 T STREET | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N
870708 | LETTER | BEADLE//THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870703 | 0800AM | 870703 | 1000AM | 120 | GAL | 4460 CENTRAL | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | N | N
870708 | LETTER | BEADLE//THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870703 | 1045AM | 870703 | 1345PM | 1800 | GAL | 607 BEYER WAY | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N
870708 | LETTER | BEADLE//THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870704 | 1645PM | 870704 | 1845PM | 600 | GAL | KATE SESSION WAY & SOLEDAD RD. | SAN DIEGO | SD | MANHOLE | HEAVY ROOTS | NO | NONE |  |  | N | N
870608 | LETTER | BEADLE//THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870705 | 1300PM | 870705 | 1500PM | 120 | GAL | HAYDEN WAY & LINWOOD | SAN DIEGO | SD | MANHOLE | ROOTS | NO |  |  |  | N | N
870709 | 0830AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870708 | 2000PM | 870709 | 0100AM | 25 | GAL | 636 SAN YSIDRO BLVD. | SAN DIEGO | SD | SEWER LINE | ROCKS & GREASE | NO | NONE |  |  | Y | N
870706 | 0900AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870704 | 1500PM | 870704 | 1700PM | 30 | GAL | 631 CRESCENT | SAN DIEGO | SD | SEWER LINE | ROOTS | NO | NONE |  |  | Y | N
870706 | 0900AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870704 | 2400PM | 870705 | 0100AM | 20 | GAL | 4495 32ND ST. | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N
870706 | 0900AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870704 | 1300PM | 870704 | 1430PM | 540 | GAL | 4626 BANCROFT ST | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N
870706 | 0900AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870704 | 2000PM | 870705 | 1100AM | 1800 | GAL | 3876 ALAMEDA DR | SAN DIEGO | SD | SEWER LINE | ROOTS | NO | NONE |  |  | Y | N
870706 | 0900AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870705 | 1700PM | 870705 | 2100PM | 36000 | GAL | DELEVAN & DEAD END OF ASH | SAN DIEGOP | SD | SEWER LINE | ROCKS | NO | NONE |  |  | Y | N
870706 | 0900AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870704 | 2200PM | 870704 | 2300PM | 300 | GAL | 2668 F STREET | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N
870714 | 0810AM | FRANK PADUA | 6192367430 | SAN DIEGO, CITY OF | 870713 | 2200PM | 870714 | 0300AM | 60000 | GAL | 3000 WINONA AVE | SAN DIEGO | SD | MANHOLE | STOPPAGE DUE TO VANDALS DUMPING ROCKS INTO MANHOLE | Y | CHOLLAS CREEK/SAN DIEGO BAY |  |  | Y | Y | ?? | CONTACT:DEL HERNANDEZ 236-5534 AT CITY OF SAN DIEGO.
870715 | 0820AM | BRUCE BONER | 7148580946 | SANTA ANA MTNS CO. WTR DIST. | 870714 | 1430PM | 870714 | 2200PM | 2000 | GAL | LOS ALISOS BL & SANTA MARG.PKY | MISSION VIEJO | OR | SEWER FORCE MAIN | HEAVY CONSTRUCTION EQUIPMENT CRAKED PIPE DURING STORM DRAIN INSTALLATION. | Y | UNKNOWN STORM DRAIN DESTNATN |  |  | Y | N | NA | NONE
870714 | 0915AM | DALE HOFFLAND | 6196942132 | ALPINE S.D.,CO. OF SAN DIEGO | 870711 | 1600PM | 870711 | 1900PM | 4000 | GAL | 2400 ALPINE BLVD. | ALPINE | SD | LATERAL AT TRAILER PARK | ROOTS | NO | NONE |  |  | Y | N | NA | SPILL CONTAINED & AREA CHLORINATED.
870715 | LETTER | BOB WADE | 6197891330 | RAMONA MUNICIPAL WATER DIST. | 870711 | 1930PM | 870712 | 0800AM | 55000 | GAL | 260 SAWDAY STREET. | RAMONA | SD | PUMP STATION SEWER MAIN | PUMP CONTROLLED COMPRESSOR FAILED TO CONTROL PUMPS.SEWAGE OVERFLOWED OUT OF 3 MANHOLES | NO | NONE |  |  | Y | N | NA | AREAS BEING PUMPED DRY, DIRT ROAD WILL BE COVERED & REPAIRED.
870714 | 0900AM | ANN ERICKSON | 7144994555 | SOUTH COAST CO. WATER DIST. | 870714 | 0900AM | 870714 | 1100AM | 36000 | GAL | 31755 COAST HWY & CIRCLE DR. | SOUTH LAGUNA | OR | 10" SEWER PIPE IN TUNNEL | HOLE WORN IN PIPE. | NO | NONE |  |  | Y | Y | ?? | FLOW 98% CONTAINED. PIPIE REPAIR ON 7/15/87. MOST FLOW IN TUNNEL SOME OUT ON SAND.
870715 | LETTER | BEADLE//DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870712 | 1230PM | 870712 | 1430PM | 6000 | GAL | 40TH & UNIVERSITY | SAN DIEGO | SD | MANHOLE | ROCKS | NO | NONE |  |  | N | N |  | NONE
870715 | LETTER | BEADLE//DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870713 | 0030AM | 870713 | 0330AM | 900 | GAL | 2800 PALM AVE | SAN DIEGO | SD | ?????? | ROOTS | NO | NONE |  |  | N | N | NA | NONE
870712 | 2030PM | BEADLE//DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 870712 | 2030PM | 870712 | 2330PM | 1800 | GAL | MISSION CNTR & CAM DE LA RENA | SAN DIEGO | SD | MANHOLE | HEAVY GREASE | Y | S.D. RIVER /OCEAN |  |  | Y | Y | ?? | THIS IS A PRIVATE SEWER MAIN.
870707 | 1430PM | PAUL RODRIGUEZ | 6194628504 | LAKESIDE S.D.,CO. OF SAN DIEGO | 870707 | 1415PM | 870707 | 1435PM | 2000 | GAL | 14526 OLDE HWY 80 | LAKESIDE | SD | TEN INCH SEWER PIPE | DEBRIS IN OVERFLOW LINE CAUSING OVERFLOW. | NO | NONE |  | SIDE OF OLDE HWY 80 | Y | N | NA | OVERFLOW LINE WILL BE INSPECTED & CLEANED ON MORE FREQUENT SCHEDULE.
870720 | LETTER | BEADLE//BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870715 | 1300PM | 870715 | 1500PM | 240 | GAL | 32ND ST. & UNIVERSITY AVE | SAN DIEGO | SD | MANHOLE | ROOTS & PAPER | NO | NONE |  |  | N | N | NA | NONE
870716 | 1130AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870715 | 1455PM | 870715 | 1755PM | 180 | GAL | TORRANCE & PRINGLE | SAN DIEGO | SD | MANHOLE IN CANYON | ROOT BLOCKAGE | NO | NONE |  | IN CANYON | Y | N | NA | DISINFECTANT APPLIED.
870716 | 1130AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870715 | 0940AM | 870715 | 1040AM | 300 | GAL | N. 163 SO. OF ROBINSON | SAN DIEGO | SD | MANHOLE | ROOT BLOCKAGE | NO | NONE |  | CANYON TO STORM DRAIN | Y | N | NA | DISINFECTANT APPLIED.
870713 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870713 | 1410PM | 870713 | 1440PM | 90 | GAL | 2598 EADS AVE | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | Y | N | NA | NONE
870715 | 0840AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870714 | 1000AM | 870714 | 1100AM | 300 | GAL | 2484 HOTEL CIRCLE PL | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  | DIRT AREA | Y | N | NA | DISINFECTANT APPLIED.
870715 | 0840AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870714 | 0805AM | 870714 | 0915AM | 120 | GAL | 2900 JARVIS ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA | DISINFECTANT APPLIED.
870717 | 1530PM | ALLGRE DIAZ |  | SAN DIEGO, CITY OF | 870709 | 0730AM | 870709 | 1630PM | 2700 | GAL | 3936 JUPITER ST. | SAN DIEGO | SD | MANHOLE | UNKNOWN | Y | OCEAN AT DOG BEACH |  |  | Y | Y | 08 | 5 SIGNS POSTED ALONG BEACH. CITY DID NOT CALL IN THIS SPILL.
870717 | 1530PM | ALLEGRE DIAZ |  | SAN DIEGO, CITY OF | 870714 | 2030PM | 870714 | 2130PM | 120 | GAL | 3050 RUE DE ORLEANS- | SAN DIEGO | SD | MANHOLE | UNKNOWN | Y | OCEAN AT DOG BEACH |  |  | Y | Y | 03 | POSTED AT BEACH & CHANNEL. CITY DID NOT CALL IN THIS SPILL.
870709 | 1700PM | R. CHERWINK | 6192365534 | SAN DIEGO, CITY OF | 870709 | 1201PM | 870709 | 1630PM | 1350 | GAL | VENUS ST. & CAMULOS ST. | SAN DIEGO | SD | MANHOLE//CLEANOUT | BLOCKAGE IN LINE TO WENCO PUMP. | Y | SAN DIEGO RIVER | YOGI BEACH OF OCEAN |  | Y | Y | 06 | NONE
870707 | 1900PM | R. CHERWINK | 6192365534 | SAN DIEGO, CITY OF | 870709 | 1730PM | 870709 | 1900PM | 18000 | GAL | I-5 & LA JOLLA BLVD. | SAN DIEGO | SD | MANHOLE | MAIN BREAKER TRIPPED. | Y | ROSE CREEK TO STATION Q |  |  | Y | N | NA | NO POSTING REQUIRED.
870716 | 1430PM | LYODD THOMPSON | 7144973311 | LAGUNA BEACH, CITY OF | 870716 | 1000AM | 870716 | 1145AM | 300 | GAL | ANITA ST & GAVIOTA AT BEACH | LAGUNA BEACH | OR | ANITA ST PUMP STATION #8 | POWER FAILURE AT STA 8 DUE TO CORROSION OF PWER LINE// BREAK IN POWER LINE. | Y | PACIFIC OCEAN |  |  | Y | Y | 02 | COUNTY HEALTH IS SAMPLING.
870731 | 1535PM | CALTRANS DISPATCH | 6192376845 | SAN DIEGO, CITY OF | 870731 | 1430PM | 0 | ?????? | 0 | ??? | 4630 BOUNDARY ST | SAN DIEGO | SD | ????? | BREAK IN LINE DUE TO UNKNOWN CAUSE | NO | NONE |  |  | N | ? |  | WILL NOTIFY CO. HEALTH.
870730 | LETTER | V.T. BRADLEY | 7145822330 | SANTA MARGARITA WATER DIST. | 870725 | 1130AM | 870725 | 1145AM | 2000 | GAL | S. CROWN VALLEY E. OF MARGRITE | MISSION VIEJO | OR | ????? | SDGE POWER FAILURE. | NO | NONE |  |  | Y | N
870727 | 0915AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870726 | 1310PM | 870726 | 1400PM | 30 | GAL | 753 GEORGIA ST | SAN DIEGO | SD | CLEANOUT | OVERLOAD ON 15" MAIN | NO | NONE |  |  | Y | N |  | AREA CLEANED & DEOTORIZED.
870727 | 0915AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870726 | 0940AM | 870726 | 1040AM | 240 | GAL | 3504 MARLBOROUGH | SAN DIEGO | SD | CLEANOUT | 8" SEWER MAIN STOPPED BY ROCKS | NO | NONE |  |  | Y | N |  | DEOTORANT APPLIED TO AREA
870727 | 0915AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870725 | 1000AM | 870725 | 1100AM | 6 | GAL | 807 LA JOLLA RANCHO RD. | SAN DIEGO | SD | CLEANOUT | 8" MAIN STOPPED BY ROCKS | NO | NONE |  |  | Y | N |  | AREA DISINFECTED
870730 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870727 | 1900PM | 870727 | 2200PM | 900 | GAL | 4451 LOGAAY | SAN DIEGO | SD | MANHOLE | GREASE BLOCKAGE | NO | NONE |  |  | Y | N | NA
870728 | 0800AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870727 | 0910AM | 870727 | 1010AM | 12 | GAL | 1200 BLK W. LEWIS ST | SAN DIEGO | SD | MANHOLE | ROOT BLOCKAGE | NO | NONE |  |  | Y
870728 | 0800AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870727 | 0740AM | 870727 | 0910AM | 150 | GAL | CATALINA & NARRAGANSETT | SAN DIEGO | SD | MANHOLE | ROOT & GREASE BLOCKAGE | NO | NONE |  |  | Y |  |  | DEOTORANT APPLIED TO AREA.
870727 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870727 | 0915AM | 870727 | 1000AM | 300 | GAL | 1500 LA MANCHA | SAN DIEGO | SD | MANHOLE | ROOT BLOCKAGE | NO | NONE |  |  | Y | N
870723 | 0900AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870722 | 0915AM | 870722 | 1015AM | 60 | GAL | 4456 KANSAS | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N | NA
870729 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870725 | 2300PM | 870726 | 0100AM | 240 | GAL | 708 OLIVEWOOD TERRACE | SAN DIEGO | SD | MANHOLE | ROOT BLOCKAGE | NO | NONE |  |  | N | N | NA
870727 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870723 | 0900AM | 870723 | 1100AM | 120 | GAL | CANYON E/O 3600 BLK 35TH ST. | SAN DIEGO | SD | MANHOLE | ROOT BLOCKAGE | NO |  |  |  | N | N | NA
870727 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870722 | 2230PM | 870723 | 0030AM | 2400 | GAL | 3535 BLENA VISTA | SAN DIEGO | SD | MANHOLE & CLEANOUT | ROOTS & GREASE | NO | NONE |  |  | N | N | NA
870714 | LETTER | TOM BRADLEY | 7145822330 | SANTA MARGARITA WATER DIST | 870714 | 1300PM | 870714 | 1330PM | 1000 | GAL | SANTA MARGARITA PKWY | RANCHO SANTA MAR | OR | MANHOLE | DESIGN OMISSION IN FORCE MAIN | NO | NONE |  |  | Y | N | NA
870724 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870721 | 2130PM | 870722 | 0030AM | 7200 | GAL | 4437 41ST STREET | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
870724 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870721 | 0700AM | 870721 | 1030AM | 4200 | GAL | 5800 BLK RADIO DR | SAN DIEGO | SD | MANHOLE | ROCKS & DEBRIS | NO | NONE |  |  | N | N | NA
870724 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870721 | 1930PM | 870721 | 2030PM | 120 | GAL | 6249 SCIMATAR | SAN DIEGO | SD | MANHOLE | ROOTS & GREASE | NO | NONE |  |  | N | N | NA
870720 | 1000AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870717 | 1430PM | 870718 | 0130AM | 300 | GAL | REAR HOUSE AT HOSPITALITY | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA | AREA DISINFECTED
870723 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870719 | 1800PM | 870720 | 1300PM | 11400 | GAL | 5800 RADIO DR | SAN DIEGO | SD | MANHOLE | ROCKS & DEBRIS | NO | NONE |  |  | N | N | NA
870723 | LETTER | BEADLE | 6102367030 | SAN DIEGO, CITY OF | 870717 | 1900PM | 870717 | 2100PM | 2400 | GAL | 3700 BLK WARD RD | SAN DIEGO | SD | MANHOLE | ROOTS & RAGS | NO | NONE |  |  | N | N | NA
870723 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870719 | 1700PM | 870720 | 0800AM | 7800 | GAL | 7864 WHELAN DR | SAN DIEGO | SF | MANHOLE | ROCKS | NO | NONE |  |  | N | N | NA
870723 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870719 | 1115AM | 870719 | 1315PM | 2400 | GAL | 10800 SUNSET RIDGE DR | SAN DIEGO | SD | MANHOLE | RAGS & DEBRIS | NO | NONE |  |  | N | N | NA
870723 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870718 | 1230PM | 870718 | 1430PM | 1200 | GAL | 219 HENSLY | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
870723 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870717 | 2030PM | 870718 | 2030PM | 7200 | GAL | 3420 MENLO AVE | SAN DIEGO | SD | MANHOLE | ROCKS & DEBRIS | NO | NONE |  |  | N | N | NA
870715 | 0815AM | BRUCE BONER | 7148580946 | SANTA ANA MTNS CO WATER DIST. | 870714 | 1430PM | 870714 | 2200PM | 2000 | GAL | LOS ALISOS SANTA MARG PKWY | MISSION VIEJO | OR | SEWER FORCE MAIN | CONSTRUCTION WORK BROKE MAIN | Y | STORM DRAIN TO UNKNOWN H2O |  |  | Y | Y | 01
870729 | 0805AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870728 | 1400PM | 870728 | 1600PM | 960 | GAL | 18490 BERNARDO TRAILS CT | SAN DIEGO | SD | ???? | SLUDGE & BOTTLE BLOCKAGE | Y | CREEK TO LAKE HODGES |  |  | Y | Y | ??
870731 | 1630PM | FRANK PADUA | 6192367341 | SAN DIEGO, CITY OF | 870731 | 0230AM | 870731 | 0535AM | 15000 | GAL | 600 BLK TOURMALINE | SAN DIEGO | SD | MANHOLE | ROOT BLOCKAGE | Y | OCEAN |  |  | Y | Y | ??
870728 | 1122AM | RICK SMITH | 6192216600 | SAN DIEGO, CITY OF | 870727 | 0120AM | 870727 | 0240AM | 0 | ??? | I-5 & SAN DIEGO RIVER CHANNEL | SAN DIEGO | SD | COVER CLAPPERS IN CHANNEL | CONTRACTOR ERROR PUMP STA 2 POWER SHUT DOWN | Y | SAN DIEGO RIVER TO OCEAN |  |  | Y | Y | ?? | CITY SAMPLING UPSTREAM & DOWNSTREAM
870724 | 1145AM | DEL HERNANDEZ | 6192365534 | SAN DIEGO, CITY OF | 870724 | 0850AM | 870724 | 0920AM | 150 | GAL | 18695 POMERADO ROAD | SAN DIEGO | SD | PUMP STA 76 | PUMPS AIRBOUND | Y | LAKE HODGES |  |  | Y | Y | ??
870730 | 0920AM | DALE HOFFLAND | 6196942132 | SPRING VALLEY S.D.,CO OF S.D. | 870729 | 1915PM | 870729 | 1925PM | 2000 | GAL | 3345 HELIX ST | SPRING VALLEY | SD | MANHOLE | CONTRACTOR PUSHED ROCKS INTO MANHOLE | Y | CASA DE ORO CREEK |  |  | Y | Y | ?? | DISCHARGE CHLORINATED.
870727 | 1458PM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870726 | ?????? | 870727 | 1000AM | 0 | ??? | 938 SAN JUAN PLACE | SAN DIEGO | SD | CLEANOUT | CLEANOUT CLOGGED | Y | MISSION BAY// OCEAN |  |  | Y | Y | ?? | 3 SIGNS POSTED.
870727 | 1455PM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870727 | 0845AM | 870727 | 1000AM | 0 | ??? | 838 SAN JUAN PL. | SAN DIEGO | SD | PROPERTY CLEANOUT | PLUGGED LATERAL | Y | BAY |  |  | Y | Y | ??
870804 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870730 | 1020AM | 870730 | 1220PM | 600 | GAL | 2140 ALTA VIEW DR | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
870731 | 0850AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870730 | 1000AM | 870730 | 1020AM | 144 | GAL | 3725 ROBINSON PL. | SAN DIEGO | SD | MANHOLE | ROOT BLOCKAGE | NO | NONE |  |  | Y | N | NA | DEOTORIZER APPLIED.
870729 | 1830PM | GARY HIGGINS | 6196980538 | SPRING VALLEY S.D., CO OF S.D. | 870729 | 1830PM | 870729 | 2130PM | 2000 | GAL | 3345 HELIX ST | SPRING VALLEY | SD | 12" PIPE | ROCKS IN MANHOLE | Y | DRAINAGE TRENCH |  |  | Y | Y | 03
870730 | 1010AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870729 | 1210PM | 870729 | 1240PM | 3 | GAL | 2920 PERRY ST | SAN DIEGO | SD | CRACK IN STREET | COLLAPSED MAIN | NO | NONE |  |  | Y | N
870730 | 1010AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870729 | 1114AM | 870729 | 1144AM | 30 | GAL | 4663 SANTA CRUZ AVE | SAN DIEGO | SD | CLEANOUT | ROOT BLOCKAGE | NO | NONE |  |  | N | N
870803 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870729 | 1400PM | 870729 | 1630PM | 300 | GAL | 60TH N/O UNIVERSITY IN CANYON | SAN DIEGO | SD | MANHOLE | UNKNOWN | NO | NONE |  |  | N | N | NA
870803 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870729 | 0930AM | 870729 | 1130AM | 600 | GAL | 4818 UNIVERSITY AVE | SAN DIEGO | SD | CLEANOUT SUMP | ROOTS & DEBRIS | NO | NONE |  |  | N | N | NA
870731 | 1635PM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870731 | 1030AM | 870731 | 1535PM | 15000 | GAL | CASS ST & VAN NUYS ST | SAN DIEGO | SD | MANHOLE | ROOT BLOCKAGE | Y | OCEAN |  |  | Y | Y | ??
870804 | 1045AM | PAT HOY | 6192362222 | SAN DIEGO, CITY OF | 870803 | 1300PM | 870803 | 1800PM | 3000 | GAL | KELLOG & SAN GOROGONIO | SAN DIEGO | SD | CRACK IN MAIN | ROOTS IN MAIN | Y | SAN DIEGO BAY |  |  | Y | Y | ?? | SAMPLING BY HAZ MAT.
870806 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870803 | 0900AM | 870803 | 1100AM | 120 | GAL | 3694 UNIVERSITY AVE | SAN DIEGO | SD | CLEANOUT | GREASE & SLUDGE | NO | NONE |  |  | N | N | NA
870727 | 1445PM | MIKE HOGAN | 6194383941 | ENCINA WATER POLLUTION C.F. | 870726 | 1000AM | 870726 | 1030AM | 100 | GAL | 6200 AVENIDA ENCINAS | CARLSBAD | SD | DIGESTOR | OPERATOR ERROR-VALVE LEFT OPEN//DIGESTED SLUDGE SPILLED. | Y | ENCINAS CREEK//OCEAN |  |  | N | N | NA | FLUSHED WITH CLEAN WATER.
870807 | 1406PM | PETER HUHN | 6197281180 | FALLBROOK SAN DIST. | 870807 | 1000AM | 870807 | 1230PM | 150000 | GAL | CAMP PENDELTON NR RODEO GRNDS | OCEANSIDE | SD | OCEAN OUTFALL LINE | RELIEF VALVE ON LINE BROKE | Y | PILGRAM CRK TO SAN LUIS REY RI |  |  | N | N | NA | 80% FLOW REACHED CREEK
870810 | 1000AM | GENE ERNSTER | 6196942132 | CARDIFF S.D.,CO OF SAN DIEGO | 870725 | ?????? | 870731 | ?????? | 720000 | GAL | SAN ELIJO OUTFALL | CARDIFF | SD | OUTFALL SHOREWARD OF DIFFUSER | PLUG IN LINE. BOLT SHEARED OFF T SECTION /DUE TO CRROSION/PLUG UNSEATED. | Y | OCEAN |  |  | Y | Y | 02 | 80% SECO. EFFLUENT, 20% ADV. PRIMARY, COLIF. ANALYSIS NEG..
870806 | 1000AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870805 | 1120AM | 870805 | 1320PM | 12 | GAL | 1724 W HARBOR DR | SAN DIEGO | SD | MANHOLE | ROOT BLOCKAGE | NO | NONE |  |  | Y | N |  | AREA DISINFECTED.
870810 | 1330PM | PETER HUHN | 6197281180 | FALLBROOK SANITARY DISTRICT | 870710 | 0900AM | 870810 | 1130AM | 100000 | GAL | FOUSAT RD-1 MI N/O MISSION AVE | OCEANSIDE | SD | OUTFALL LINE TO HALE AVE WWTP | AIR & VAC RELEASE VALVE DID NOT SEAT AS USUAL | NO | NONE |  | DORMANT FARM LAND | Y | N | NA
870810 | 1330PM | PETER HUHN | 6197281180 | FALLBROOK SANITARY DISTRICT | 870810 | 1000AM | 870810 | 1015AM | 1000 | GAL | LORETTA ST 1/2 MI E/O I-5. | OCEANSIDE | SD | OUTFALLLINE TO HALE AVE WWTP | AIR & VAC. VALVE DID NOT SEAT AS USUAL. | NO | NONE |  |  | Y | N | NA
870810 | 0830AM | JAY SENIOR | 6192367030 | SAN DIEGO, CITY OF | 870809 | 1610PM | 870809 | 1710PM | 0 | ??? | 2200 BLK SHELTER ISLAND DR | SAN DIEGO | SD | SEWER MAIN | GREASE | Y | SAN DIEGO BAY |  |  | Y | Y | ??
870803 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870803 | 0930AM | 870803 | 1030AM | 1500 | GAL | 6300 FRIARS ROAD | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
870804 | 0915AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870803 | 0630PM | 870803 | 0830PM | 240 | GAL | 4341 BETA ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA | DEOTORANT APPLIED.
870804 | LETTER | L. TORTORICI | 6194387444 | BEUNA SANITATION DIST. | 870728 | ?????? | 870728 | ?????? | 2500 | GAL | SYCAMORE AVE & ROAD TO AIRPORT | ?????? | SD | OCEAN OUTFALL PIPE | AIR RELEASE VALVE FLOAT MECHANISM FAILED. | NO | NONE |  |  | Y | ? | ?? | SECO EFFLUENT SPILLED
870812 | 0810AM | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 870811 | 1600PM | 870811 | 1730PM | 45000 | GAL | PUMP STA 3 FORCE MAIN | ESCONDIDO | SD | STA 3 FORCE MAIN | FORCE MAIN COUPLING BROKE | Y | KIT CARSON PONDS |  |  | Y | Y | ?? | POSTING ALONG KIT CARSON CREEK.MAIN REPAIRED BY 2330PM.
870810 | 1530PM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870807 | 1500PM | 870807 | 1530PM | 300 | GAL | 6500 BLK NEPTUNE PLACE | SAN DIEGO | SD | MANHOLE | GREASE | Y | OCEAN |  |  | Y | Y | ?? | NONE
870810 | 0935AM | GENE ERNSTER | 6196942111 | SPRING VALLEY S.D.,CO OF S.D. | 870808 | 1030AM | 870808 | 1145AM | 500 | GAL | FAIRWAY DR. BET PAR & NIBLICK | SPRING VALLEY | SD | MANHOLE | GREASE | Y | CREEK TO SWEETWATER RIVER |  |  | Y | N | NA | CREEK CHLORINATED.
870811 | 1000AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870810 | 1400PM | 870810 | 1500PM | 300 | GAL | 3641 8TH AVE | SAN DIEGO | SD | MANHOLE | ROOT & DEBRIS BLOCKAGE | NO | NONE |  |  | Y | N | NA | DEOTORANT APPLIED TO CANYON SPILL AREA.
870807 | 0900AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870806 | 1030AM | 870806 | 1230PM | 24 | GAL | 3138 1ST AVE | SAN DIEGO | SD | CLEANOUT | ROOT & GREASE BLOCKAGE | NO | NONE |  |  | Y | N | NA | DEOTORANT APPLIED TO CANYON AREA.
870811 | 1000AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870810 | 0830AM | 870810 | 0900AM | 150 | GAL | 1600 ROSECRANS | SAN DIEGO | SD | MANHOLE | HEAVY GREASE | NO | NONE |  |  | Y | N | NA | AREA DISINFECTED.
870810 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870810 | 1000AM | 870810 | 1330PM | 2100 | GAL | 2010 VIA LADETA | SAN DIEGO | SD | MANHOLE | ROOT BLOCKAGE | NO | NONE |  |  | Y | N | NA | NONE
870811 | 1530PM | LARRY CARLSON | 6197254512 | U.S. MARINES-PLANT 13 | 870811 | 0715AM | 870811 | 0800AM | 15000 | GAL | BLDG NO. 21537 | SAN DIEGO | SD | LIFT STATION NEAR BLDG 21537 | BUBBLER SWITCH MALFUNCTION. OVERFLOW FROM WET WELL. | Y | DEL MAR BOAT BASIN |  |  | Y | Y | ?? | REMOVED SOLIDS,WASHED,LIMED AREA. COMPUTERIZED ALARM TO BE INSTALLED.
870810 | 0855AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870807 | 1130AM | 870807 | 1230PM | 6 | GAL | 515 27TH ST. | SAN DIEGO | SD | MANHOLE | ROCKS BLOCKING LINE | NO | NONE |  |  | Y | N | NA | AREA DISINFECTED.
870812 | 0845AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870811 | 1130AM | 870811 | 1230PM | 300 | GAL | 2030 JULIAN AVE | SAN DIEGO | SD | JOINT IN SEWER PIPE | GREASE & ROCK BLOCKAGE | NO | NONE |  |  | Y | N | NA | AREA DEOTORIZED.
870817 | 0825AM | TOM BRADLEY | 7145822330 | SANTA MARGARITA WATER DIST. | 870815 | 1200 N | 870816 | 1000AM | 200000 | GAL | PLANO LIFT STATION | RANCHO SANTA MAR | OR | LIFT STATION | CONTROL VOLTAGE CIRCUT KICKED OUT | NO | CREEK BED WITH STANDING WATER |  |  | Y | N | NA | NONE
870814 | 1215PM | DALE HOFFLAND | 6195655771 | LEMON GROVE SAN. DISTRICT | 870814 | 0800AM | 870814 | 0900AM | 1500 | GAL | 1995 ENSENADA ST | LEMON GROVE | SD | ?????? | CONTRACTOR BROKE MANHOLE | Y | CREEK NEAR ADDRESS |  |  | Y | N | NA | AREA CHLORINATED.
870813 | 1500PM | BRANCO | 6195789772 | SAN DIEGO, CITY OF | 870814 | 1500PM | 870814 | 1600PM | 30 | GAL | 4165 MONROE AVE | SAN DIEGO | SD | MANHOLE IN ALLEY ON MONROE | GREASE | NO | NONE |  |  | Y | N | NA
870814 | 0830AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870813 | 1300PM | 870813 | 2200PM | 54 | GAL | 3733 ELLIOT ST | SAN DIEGO | SD | CLEANOUT | ROOTS | NO | NONE |  |  | Y | N | NA | AREA DEOTORIZED.
870814 | 0840AM | SENIOR WANTIEZ | 6192367030 | SAN DIEGO, CITY OF | 870813 | 0930AM | 870813 | 1130AM | 60 | GAL | CEDAR ST & FELTON ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
870813 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870813 | 1030PM | 870813 | 1130PM | 600 | GAL | 6646 KELLY ST | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | Y | N | NA
870810 | 0828AM | R CHERWINK | 6192365534 | SAN DIEGO, CITY OF | 870810 | 0745AM | 870810 | 0815AM | 150 | GAL | CAPRICORN WAY | MIRA MESA | SD | MANHOLE | POWER OUTAGE BY SDGE | NO | NONE |  |  | Y | N
870810 | 0900AM | SENIOR | 6192367030 | SAN DIEGO, CITY OF | 870809 | 1152AM | 870809 | 1315PM | 2120 | GAL | 2818 COLLIER AVE | SAN DIEGO | SD | MANHOLE | GREASE & ROOTS | NO | NONOE |  |  | Y | N
870810 | 0903AM | R CHERWINK | 6192365534 | SAN DIEGO, CITY OF | 870810 | 0850AM | 870810 | 0903AM | 650 | GAL | 15500 PAYMOGO ST | PENASQUITOS | SD | STATION 62 OVERFLOW PIPE. | ELECTRICAL PROBLEM, CALL PUMP FAILED, #1 PUMP LEFT IN OFF POSITION. | NO | NONE |  |  | Y | N
870814 | 1340PM | SENIOR AND GRATE | 6192367030 | SAN DIEGO, CITY OF | 870814 | 1340PM | 870814 | 1530PM | 2400 | GAL | 4023 & 4027 BOSTON AVE (40TH) | SAN DIEGO | SD | MANHOLE | GREASE,RAGS, DEBRIS | NO | NONE |  |  | Y | N |  | AREA DEOTORIZED.
870819 | 0850AM | LARRY CARLSON | 6197254512 | CAMP PENDELTON, USMC | 870818 | 0920AM | 870818 | 1845PM | 215000 | GAL | PLANT NO. 10 | CAMP PENDELTON | SD | ?????? | BROKEN CLAY PIPE. | Y | SAN ONOFRE CREEK |  |  | Y | Y | ?? | SPILL AREA TO BE QUARANTINED BY CAMP PENDELTON STAFF.
870817 | 1005AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870814 | 0930AM | 870814 | 1030AM | 18 | GAL | 3722 FLORIDA ST. | SAN DIEGO | SD | CLEANOUT | ROOTS AND ROCKS | NO | NONE |  |  | Y | N | NA | APPLIED DEOTORANT.
870817 | 1005AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870816 | 2120PM | 870816 | 2220PM | 300 | GAL | 33RD & MADISON | SAN DIEGO | SD | MANHOLE | GREASE & DEBRIS | NO | NONE |  |  | Y | N | NA | DEOTORANT APPLIED
870819 | LETTER | FRANK PADUA | 6192347340 | SAN DIEGO, CITY OF | 870819 | 0630AM | 870819 | ?????? | 60 | GAL | 4340 LA JOLLA VILLAGE DR. | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  | CANYON | Y | N | NA
870821 | 1115AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870820 | 1230PM | 870820 | 1730PM | 600 | GAL | 4472 HORTENS CANYON REAR | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N | NA | DEOTORANT APPLIED
870824 | 0815AM | SENIOR/THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870823 | 0930AM | 870823 | 1130AM | 120 | GAL | 6755 DRAPER ST | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N | NA
870824 | 0815AM | SENIOR/WANTIEZ | 6192367030 | SAN DIEGO, CITY OF | 870921 | 0900AM | 870921 | 1200 N | 540 | GAL | 2744 GREGORY SY IN CANYON | SAN DIEGO | SD | MANHOLE | ROOTS AND ROCKS | NO | NONE |  |  | Y | N | NA
870824 | 0800AM | SENIOR/THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870822 | 1300PM | 870822 | 1500PM | 60 | GAL | PACIFIC BCH DR & INGRAHAM | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA | DOETORANT APPLIED
870821 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870821 | 1201PM | 870821 | 1300PM | 450 | GAL | 226 PLAYA DEL NORTE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE | SOAKED INTO SAND AT BEACH |  | Y | Y | ??
870827 | 0815AM | DON GRIFFEN | 6192367334 | SAN DIEGO, CITY OF | 870821 | 1830PM | 870821 | 2000PM | 180 | GAL | BALBOA CT. & BAYSIDE WALK | SAN DIEGO | SD | MANHOLE | GREASE | Y | MISSION BAY |  |  | Y | Y | 06
870825 | 0400 | CINDY OSWALD | 6196966014 | U.S. NAVY, PUBLIC WORKS | 870824 | 0400AM | 0 | ?????? | 25 | GPM | 3178 TEA PARTY LANE | SAN DIEGO | SD | MANHOLE | LINE OBSTRUCTION | Y | TRIBUTARY TO SAN DIEGO RIVER |  |  | Y | Y | ?? | PONDED IN MURPHY CANYON
870822 | 1400PM | BRANCO | 6195789772 | SAN DIEGO, CITY OF | 870822 | 1400PM | 870822 | 1430PM | 10 | GAL | 6555 CAMINO DEL TEATRO | SAN DIEGO | SD | ???????? | ROOTS | NO | NONE |  |  | Y | N
870825 | 0825AM | SENIOR/THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870824 | 0700AM | 870824 | 0900AM | 1200 | GAL | 431 WINONA | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | Y | N
870824 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870824 | 0700AM | 870824 | 1030AM | 420 | GAL | CANYON-SOUTH OF COBB PLACE | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  | CANYON | Y | Y | 02
870822 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870822 | 0700AM | 870822 | 2000PM | 39000 | GAL | 5270 LENOX DR | SAN DIEGO | SD | MANHOLE | ROCKS | NO | NONE |  |  | Y | ? | ??
870825 | 0830AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870824 | 0900AM | 870824 | 1100AM | 60 | GAL | 738 ROSECRANS ST | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N |  | DEOTORANT APPLIED
870825 | 0830AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870824 | 1045AM | 870824 | 1145AM | 60 | GAL | 28TH AND VALLEY PLACE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA | DEOTORANT APPLIED. FLOW TO STORM DRN NE CORNER 28TH & VALLEY
870826 | 1830PM | BRANCO | 6195789772 | SAN DIEGO, CITY OF | 870826 | 1830PM | 870826 | 1930PM | 60 | GAL | 4978 ORANGE AVE | SAN DIEGO | SD | ???????? | GREASE AND ROOTS | NO | NONE |  | PUDDLED IN STREEET | Y | N | NA | ZEPPED AREA.
870827 | 0830AM | SENIOR/AYAP | 6192367030 | SAN DIEGO, CITY OF | 870826 | 0700AM | 870826 | 1130AM | 4800 | GAL | JACKSON DR & MISSION GORGE RD. | SAN DIEGO | SD | MANHOLE | VANDALISM | NO | NONE |  |  | Y | N
870831 | LETTER | ?????? | ?????????? | SANTA MARGARITA WATER DISTRICT | 870824 | 1130AM | 870824 | 1245AM | 1500 | GAL | SANTA POLA & MELINDA | MISSION VIEJO | OR | MANHOLE | PLUMBERS TEST PLUG CAUGHT IN LINE. | NO | NONE |  |  | Y | N
870901 | 0845AM | DEL HERNANDEZ | 6192365534 | SAN DIEGO, CITY OF | 870831 | 1200 N | 870831 | 1500PM | 3600 | GAL | 5387 CALUMET | SAN DIEGO | SD | FORCE MAIN/PUMP STA. 42. | DEBRIS BLOCKAGE. | Y | OCEAN |  |  | Y | Y | ??
870831 | 1030AM | JAY SENIOR | 6192367030 | SAN DIEGO, CITY OF | 870829 | 1850PM | 870829 | 2150PM | 9000 | GAL | 4236 VENUS | SAN DIEGO | SD | STORM DRAIN | GREASE | Y | SAN DIEGO RIVER TO DOG BEACH |  |  | Y | Y | ??
870828 | 0800AM | TOENNESSON | 6195789772 | SAN DIEGO, CITY OF | 870827 | 2230PM | 870827 | 2430PM | 360 | GAL | INTSEC. CHAMBERS & COLUMBIA | SAN DIEGO | SD | ?????? | ROOTS | NO | NONE |  |  | Y | ? | ?? | AREA ZEPPED
870828 | 0800AM | TOENNESSON | 6195789772 | SAN DIEGO, CITY OF | 870827 | 1900PM | 870827 | 2030PM | 1350 | GAL | 54TH & LAUREL | SAN DIEGO | SD | ?????? | GREASE,ROOTS,RAGS | NO | NONE |  |  | Y | ? | ?? | AREA ZEPPED
870828 | 0800AM | TOENNESSON | 6195789772 | SAN DIEGO, CITY OF | 870827 | 1530PM | 870827 | 1700PM | 900 | GAL | 408 408 CAMINO DEL RIO SOUTH. | SAN DIEGO | SD | ?????? | GREASE,ROOTS. | NO | NONE |  |  | Y | N | NA | STREET ZEPPED.
870828 | 0830AM | SENIOR/THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870828 | 1430PM | 870828 | 1530PM | 60 | GAL | 4174 50TH ST. | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
870831 | 0900AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870828 | 1115AM | 870828 | 1515PM | 120 | GAL | 304 SO. 33RD ST. | SAN DIEGO | SD | CLEANOUT REAR 349 BANCROFT ST. | ROOTS, GREASE | NO | NONE |  | BACKYARD | Y | N | NA | YARD DEOTORIZED
870904 | 1140AM | TOM ZUGSAY | 6197254535 | U.S. MARINE CORP. | 870903 | 1130AM | 870903 | 1145AM | 300 | GAL | 33 AREA PLANT 8(MARGARITA) | CAMP PENDELTON | SD | ???????? | LINE FROM DIGESTER BROKEN DURING CONSTRUCTION. | NO | NONE |  |  | N | N |  | CLEANED UP. SLUDGE DISPOSED IN BEDS.
870902 | 0815AM | SENIOR/GRATE | 6192367030 | SAN DIEGO, CITY OF | 870902 | 1430PM | 870902 | 1630PM | 360 | GAL | 2721 HIGHLAND AVE | SAN DIEGO | SD | MANHOLE | VANDALS | NO | NONE |  | CANYON | Y | N
870903 | 1500PM | GEORGE HOWARD | 6196943643 | CARDIFF S.D., CO OF SAN DIEGO | 870903 | 1200 N | 870903 | 1500PM | 400 | GAL | NEAR SAN ELIJO PLANT | CARDIFF | SD | MAIN MANHOLE | CONTRACTOR BROKE LINE. | NO | NONE |  |  | Y | N | NA | AREA CHLORINATED.
870906 | 1130AM | GARY ORR | 6194397164 | OCEANSIDE, CITY OF | 870908 | 0530AM | 870908 | 0900AM | 350 | GAL | BEHIND 4222 LA TIERA | CARLSBAD | SD | MANHOLE | BLOCKAGE BY WOOD & CONSTRUCTION DEBRIS. | Y | LAKE CALAVERAS |  |  | N | Y | ?? | LAKE IS NON RECREATIONAL.
870901 | 0815AM | SENIOR/GRATE | 6192367030 | SAN DIEGO, CITY OF | 870831 | 1655PM | 870831 | 1855PM | 1200 | GAL | 10759 CARIUTO | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N |  | STORM DRAIN DEOTORIZED.
870830 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870830 | 1230PM | 870830 | 1400PM | 900 | GAL | DUCOS PL & RUEDA DR | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  | CANYON | Y | N
870901 | 0900AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870831 | 0700AM | 870831 | 1300PM | 360 | GAL | 3876 ALAMEDA PL. | SAN DIEGO | SD | MANHOLE IN CANYON | ROOTS | NO | NONE |  |  | N | N | NA | CANYON DEOTORIZED.
870909 | 0930AM | TOM ZUGSAY | 6197254535 | U.S. MARINE CORP | 870909 | 0730AM | 870909 | 0830AM | 250 | GAL | MANHOLE ADJ. BLDG 21571 | CAMP PENDELTON | SD | BUBBLER SYSTEM | BUBBLER SYSTEM FAILED. | Y | DEL MAR BOAT BASIN |  |  | Y | N | NA
870901 | LETTER | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 870829 | 0930AM | 870829 | 1000AM | 1000 | GAL | 200 BLK SO. SPRUCE | ESCONDIDO | SD | MANHOLE 39 SEWER ATLAS P4 | GREASE | NO | NONE |  | STORM DRAIN | N | N | NA | STREET FLUSHED AND DISINFECTED.
870902 | LETTER | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870902 | 1035AM | 870902 | 1140AM | 325 | GAL | 10001 GENTER ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  | ???? | Y | N | NA
870904 | 1531PM | SENIOR/GRATE | 6192367030 | SAN DIEGO, CITY OF | 870903 | 1700PM | 870903 | 2000PM | 180 | GAL | 6242 ESTELLE ST. | SAN DIEGO | SD | MANHOLE | ROCKS AND DEBRIS | Y | OCEAN??? |  |  | Y | N | NA
870909 | 1115AM | TOM BRADLEY | 7145822330 | SANTA MARGARITA WATER DIST. | 870909 | 0930AM | 870909 | 1030AM | 12000 | GAL | PLANO LIFT STA.-RANCHO MISSION | R M VIEJO | OR | PLANO LIFT STATION | PUMP FAILURE | NO | NONE |  | DRY CREEK BED | Y | N | NA | NO HUMAN CONTACT AREA.
870910 | 0900AM | DEL HERNANDEZ | 6192365534 | SAN DIEGO, CITY OF | 870909 | ?????? | 870909 | ?????? | 0 | ??? | 15790 AVENIDA DE NUSTO | SAN DIEGO | SD | PUMP STA 73 | ELECTRICAL PROBLEM IN STA 73 CAUSED PUMP ALARM NOT TO GO OFF. | Y | POND ON GOLF COURSE |  |  | Y | Y | 03 | 4 SIGNS POSTED.
870903 | 0810AM | FRANK PADUA | 6192367340 | SAN DIEGO, CITY OF | 870903 | 1935PM | 870903 | 1955PM | 400 | GAL | 5382 CALUMET AVE | SAN DIEGO | SD | PUMP STA 42 | STA 42 SHUT DOWN FOR CLEANING RESULTED IN SPILL. | Y | OCEAN |  |  | Y | Y | 03
870909 | 1600PM | PAT HOY | 6192362222 | SAN DIEGO, CITY OF | 870908 | 1450PM | 870908 | 2100PM | 7200 | GAL | 5074 MERCURY ST | SAN DIEGO | SD | MANHOLE NR STA 61 | MANHOLE BLOCKAGE. FLOW TO DAMON ST. INTERCEPTOR. | Y | ROSE CREEK/MISSION BAY ? |  |  | Y | Y | ?? | INTERCEPTOR MAY NOT HAVE CAUGHT ALL THE FLOW.
870910 | 0900AM | DEL HERNANDEZ | 6192365534 | SAN DIEGO, CITY OF | 870909 | 2000PM | 870909 | 2100PM | 1800 | GAL | 5074 MERCURY ST. | SAN DIEGO | SD | STA 61 | BUBBLER SYSTEM LEAK (COMPREESOR) PUMPS FAILED TO GO ON. | NO | NONE |  |  | Y | Y | ?? | POSTING UP FROM 9/78/87 SPILL.
870907 | 0630AM | BEADLE GRATE | 6192367030 | SAN DIEGO, CITY OF | 870907 | 0630AM | 870907 | 0830AM | 120 | GAL | INFO CTR I-5 & MISSION BAY | SAN DIEGO | SD | RV DUMP SUMP | DEBRIS IN CLEANOUT | Y | MISSION BAY |  |  | Y | Y | NA
91087 | LETTER | BEADLE GRATE | 6192367030 | SAN DIEGO, CITY OF | 870907 | 1000AM | 870907 | 1200 N | 2400 | GAL | 11021 TURRET | SAN DIEGO | SD | MANHOLE | DEBRIS | NO | NONE
870910 | LETTER | BEADLE GRATE | 6192367030 | SAN DIEGO, CITY OF | 870907 | 1030AM | 870907 | 1330PM | 4500 | GAL | 3210 DWIGHT | SAN DIEGO | SD | MANHOLE | DEBRIS | NO
870910 | LETTER | BEADLE GRATE | 6192367030 | SAN DIEGO, CITY OF | 870906 | 0930AM | 870906 | 1430AM | 1500 | GAL | 6085 TARRAGONA | SAN DIEGO | SD | MANHOLE | COLLAPSED MAIN | NO
870908 | 0930AM | M W GARNER | 7149257676 | EASTERN MUNICIPAL WATER DIST. | 870906 | 1000AM | 870906 | 1200 N | 30000 | GAL | DIAZ RD, SO END OF AIRSTRIP | RANCHO CALIF. | RI | SECONDARY EFFLUENT FORCE MAIN | BROKEN FORCE MAIN | Y | FLOOD CNTRL DITCH |  |  | Y | Y | 02 | POOLED EFFLUENT WAS CHLORINATED.
81087 | 1330PM | PETER HUHN | 6197281180 | FALLBROOK SANITARY DISTRICT | 870810 | 0900AM | 870810 | 1130AM | 100000 | GAL | 1 MI N/O HWY 76 ON N FOUSSATT | OCEANSIDE | SD | OUTFALL LINE | AIR VAC VALVE GASKET FAILED. | NO |  |  |  | Y | N |  | FARMING FIELD HAD NO CROPS IN IT AT THE TIME.
870810 | 1330PM | PETER HUHN | 6197281180 | FALLBROOK SANITARY DISTRICT | 870810 | 1000AM | 870810 | 1030AM | 1000 | GAL | LORETTA ST 1 MI N/O I-5 | OCEANSIDE | SD | OUTFALL LINE | AIR VAC VALVE RUBBER GASKET FAILED. | NO |  |  | FIELD NEXT TO VALVE | Y | N
870909 | 1120AM | VAUGHN T. BRADLEY | 7145822330 | SANTA MARGARITA WATER DISTRICT | 870909 | 0930AM | 870909 | 1030AM | 12000 | GAL | RANCHO MISSION VIEJO O'NEILL | ????? | OR | PLANO LIFT STATION | BOTH PUMPS FAILED TO START | Y | DRY CREEK BED |  |  | Y | N | NA | NO HUMAN CONTACT//REMOTE LOCATION.
870909 | LETTER | V.T. BRADLEY | 7145822330 | SANTA MARGARITA WATER DISTRICT | 870909 | 0740AM | 870909 | 0750AM | 2000 | GAL | 21115 SANTA MARGARITA PKWY | ????? | OR | TRABUCO LIFT STATION | PUMPS FAILED TO START | NO | NONE |  |  | Y | N
870910 | LETTER | DENNIS ERDMAN | 7144969247 | CAPISTRANO BEACH SAN. DIST. | 870909 | ????AM | 870909 | ????PM | 25000 | GAL | CAMINO CAPISTRANO | CAPISTRANO BEACH | OR | SEWER LINE | VANDALISM | NO | NONE |  |  | Y | N
870915 | LETTER | BEADLE THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 870909 | 1200 M | 870910 | 1100AM | 1380 | GAL | 2705 TERESITA | SAN DIEGO | SD | MANHOLE | BROKEN MAIN | NO | NONE
870915 | LETTER | BEADLE GRATE | 6192367030 | SAN DIEGO, CITY OF | 870909 | 0930AM | 870909 | 1130AM | 480 | GAL | 999 SO. 43RD ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE
870915 | LETTER | BEADLE GRATE | 6192367030 | SAN DIEGO, CITY OF | 870910 | 0900AM | 870910 | 1100AM | 600 | GAL | 6300 BLK IMPERIAL AVE | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE
870915 | LETTER | BEADLE WANTIEZ | 6192367030 | SAN DIEGO, CITY OF | 870909 | 0800AM | 870909 | 1000AM | 240 | GAL | 40TH & EL CAJON ALLEY E/O | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE
870909 | 0800AM | TOENNESSEN | 6195789772 | SAN DIEGO, CITY OF | 870908 | 1450PM | 870908 | 2100PM | 9000 | GAL | MERCURY ST & MERCURY CT. | SAN DIEGO | SD | ??????? | PUMP STA DOWN;NO STOP ON MAIN. | Y | SAN CLEMENTE CREEK/ROSE CREEK |  |  | Y | N
870914 | LETTER | BEADLE GRATE | 6192367030 | SAN DIEGO, CITY OF | 870908 | 1530PM | 870908 | 1730PM | 120 | GAL | 6252 SCIMITAR DR. | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE
870914 | LETTER | BEADLE GRATE | 6192367030 | SAN DIEGO, CITY OF | 870908 | 1410PM | 870908 | 1610PM | 600 | GAL | 5030 MANOMAT DR. | SAN DIEGO | SD | MANHOLE | DEBRIS/VANDALS | NO | NONE
870914 | 1500PM | SENIOR | 6192367030 | SAN DIEGO, CITY OF | 870913 | 1400PM | 870913 | 1700PM | 360 | GAL | BRIGHTON & SPRAY ST. | SAN DIEGO | SD | MANHOLE | COLLAPSED LATERAL | NO | NONE |  |  |  | N | NA
870917 | LETTER | DONN GRIFFEN | 6192367340 | SAN DIEGO, CITY OF | 870911 | 0840AM | 870911 | 0940AM | 18 | GAL | 1035 GARNET AVE IN ALLEY | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | Y
870914 | 1100AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870912 | 2230PM | 870912 | 2400PM | 4500 | GAL | 4100 GEORGIA ST. | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N |  | AREA DISINFECTED.
870914 | 1100AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870912 | 1330PM | 870912 | 1530PM | 36 | GAL | HAWK AND BUSH ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N |  | AREA DISINFECTED
870914 | 1100AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870912 | 1615PM | 870912 | 2045PM | 18 | GAL | 2823 BONDITCH PL | SAN DIEGO | SD | CLEANOUT | OBSTRUCTION | NO | NONE |  |  | Y | N
870914 | 1100AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870912 | 1015AM | 870912 | 1315PM | 30000 | GAL | LORING AND OCEAN BLVD. | SAN DIEGO | SD | MANHOLE | GREASE DEBRIS | Y | OCEAN |  |  | T | T | 05 | AREA DEOTORIZED.
870914 | 1100AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870911 | 1230PM | 870911 | 1400PM | 45 | GAL | 2418 J ST. | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | Y | N |  | AREA DEOTORIZED
870910 | 1515PM | TOENNESSEN | 6195789772 | SAN DIEGO, CITY OF | 870910 | 1130AM | 870910 | 1300PM | 180 | GAL | 3328 MADISON AVE | SAN DIEGO | SD | ??????? | GREASE | NO | NONE |  |  | Y |  |  | AREA TREATED WITH ZEPP.
870917 | 1400PM | PAUL WILSON | 6197288319 | FALLBROOK | 870917 | 1345PM | 870917 | 2300PM | 0 | ??? | FALLBROOK OCEAN OUTFALL LINE | FALLBROOK | SD | OCEAN OUTFALL | CONTRACTOR RUPTURED OUTFALL LINE | Y | OCEAN///FALLBROOK CREEK |  |  | Y | Y | ?? | FLOW DIVERTED TO FALLBROOK CREEK FROM 1700-2300PM. OUTFALL ON LINE BY 2300PM.
870918 | LETTER | DON GRIFFEN | 6192367340 | SAN DIEGO, CITY OF | 870918 | 0930AM | 870918 | 1030AM | 3 | GAL | 6450 ELECTRIC AVE | SAN DIEGO | SD | MANHOLE 6" CEMENT MAIN | ROOT BLOCKAGE | NO | NONE |  | GUTTER SW CORNER ELECTRIC/PALO | Y | ? | ?? | NONE
870921 | LETTER | DONN GRIFFEN | 6192367340 | SAN DIEGO, CITY OF | 870919 | 1100AM | 870919 | 1200PM | 3000 | GAL | 3235 40TH ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | ? | ?? | NONE
870921 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 870918 | 0600AM | 870918 | 0700AM | 120 | GAL | 1835 DAVID ST. | SAN DIEGO | SD | CLEANOUT | ROOTS | NO | NONE |  |  | Y
870922 | 0840AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870921 | 1300PM | 870921 | 1630PM | 210 | GAL | 2757 A ST. | SAN DIEGO | SD | CLEANOUT | ROOTS / DEBRIS | NO | NONE |  |  | Y | N |  | DEOTORANT APPLIED TO FLOOD AREA.
870922 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 870921 | 1945PM | 870921 | 2145PM | 240 | GAL | 3730 LANDIS ST | SAN DIEGO | SD | MANHOLE | ROOTS & GREASE | NO | NONE |  |  | Y | N | NA | CONTAINED IN CANYON
870917 | 1015AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870916 | 1900PM | 870916 | 2330PM | 2700 | GAL | THORN BET. CENTRAL & 40TH ST. | SAN DIEGO | SD | MANHOLE | ROCKS | NO | NONE |  |  | Y | N | NA | APPLIED DISINFECTANT
870917 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 870916 | 0800AM | 870916 | 1020AM | 2800 | GAL | 1486 WILBUR AVE | SAN DIEGO | SD | MANHOLE | SLUDGE & GREASE STOPPAGE. | NO | NONE |  |  | Y | N | NA
870922 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 870919 | 0800AM | 870919 | 2300PM | 7200 | GAL | 2596 46TH ST IN REAR CANYON | SAN DIEGO | SD | MANHOLE | ROCKS & DEBRIS | NO | NONE |  |  | Y | N | NA
870918 | 0800AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870917 | 1400PM | 870917 | 1430PM | 0 | ??? | WESCHESTER & DUNHOLME ST. | SAN DIEGO | SD | SEWER LINE | UNKNOWN | NO | NONE |  |  | Y | N | NA
870918 | 0800AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870917 | 0915AM | 870917 | 1045AM | 180 | GAL | 3528 MADISON AVE | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N
870923 | LETTER | ????? | ????? | SANTA MARGARITA WATER DISTRICT | 870918 | 1330PM | 870918 | 1415PM | 750 | GAL | PINECREST & SANTA MARG. PKWY. | MISSION VIEJO | OR | MANHOLE | ROCKS & DEBRIS | NO | NONE |  |  | Y | N
870923 | LETTER | ????? | ????? | SANTA MARGARITA WATER DISTRICT | 870920 | 1415PM | 870920 | 1425PM | 500 | GAL | RANCHO MISSION VIEJO (O'NEILL) | RANCHO SANTA MAR | OR | PLANO LIFT STATION | PUMPS FAILED TO START. | NO | NONE |  |  | Y | N
870921 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 870918 | 0700AM | 870918 | 0900AM | 4800 | GAL | 3900 CALGARY AVE | SAN DIEGO | SD | MANHOLE | ROOTS & SLUDGE | NO | NONE |  |  | Y | N | NA
870924 | 1130AM | JOHN SCHOLLER | 6197551556 | DEL MAR, CITY OF | 870923 | 1100AM | 870923 | 1130AM | 25 | GAL | 9TH & CAMINO DEL MAR | DEL MAR | SD | MANHOLE | DEBRIS & ROOTS | Y | OCEAN |  |  | Y | Y | 01 | POSTED 100 YDS EACH SIDE OF ENTRY POINT
870923 | 0815AM | M ARNOLD | 6192366092 | SANB DIEGO, CITY OF | 870922 | 1000AM | 870922 | 1030AM | 3 | GAL | 515 27TH ST. | SNA DIEGO | SD | MANHOLE | ROCKS & SLUDGE | NO | NONE |  |  | Y | N
870923 | 1530PM | SENIOR | 6192367030 | SAN DIEGO, CITY OF | 870923 | 0700AM | 870923 | 1530PM | 1440 | GAL | 3055 40TH ST | SAN DIEGO | SD | MANHOLE | ROCKS & ROOTS | NO | NONE |  |  | Y | N | NA | ZEP APPLIED
870925 | 1000AM | BRANCO | 6195789772 | SAN DIEGO, CITY OF | 870924 | 1000AM | 870924 | 1100AM | 300 | GAL | 5200 BLK QUEMADO CT | SAN DIEGO | SD | SEWER LINE | ROOTS | NO | NONE |  |  | Y | N |  | AREA ZEPPED
870930 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 870925 | 1400PM | 870925 | 1430PM | 750 | GAL | FOOTHILL & VICKIE | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y
870928 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 870925 | 1300PM | 870925 | 1400PM | 1500 | GAL | WESTKNOLL DR & VICKIE DR | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N
870930 | LETTER | SENIOR | 6192367030 | SAN DIEGO, CITY OF | 870927 | 1015AM | 870927 | 1515PM | 3000 | GAL | 2618 46TH ST | SAN DIEGO | SD | MANHOLE | ROCKS | NO | NONE |  |  | Y | N
870928 | 0815AM | SENIOR | 6192367030 | SAN DIEGO, CITY OF | 870925 | 2200PM | 870925 | 2400PM | 120 | GAL | 1040 WEST UPAS ST | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N
870925 | 0815AM | SENIOR | 6192367030 | SAN DIEGO, CITY OF | 870925 | 1915PM | 870925 | 2100PM | 120 | GAL | 2302 AVENIDA DE LA PLAYA | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | Y | N
870928 | 0800AM | TOENNESSEN | 6195789772 | SAN DIEGO, CITY OF | 870926 | 1300PM | 870926 | 1430PM | 180 | GAL | 2618 46TH ST | SAN DIEGO | SD | SEWER LINE | ROCKS IN MAIN | NO | NONE |  |  | Y |  |  | AREA ZEPPED
870928 | 0800AM | TOENNESSEN | 6195789772 | SAN DIEGO, CITY OF | 870927 | 1730PM | 870927 | 1830PM | 30 | GAL | 3202 MISSION BLVD. | SAN DIEGO | SD | SEWER LINE | RAGS & GREASE | NO | NONE |  |  | Y |  |  | AREA ZEPPED
870928 | 0800AM | TOENNESSEN | 6195789772 | SAN DIEGO, CITY OF | 870926 | 0930AM | 870926 | 1130AM | 600 | GAL | GENOA & MILLPEAK RD | SAN DIEGO | SD | SEWER LINE | GREASE/ROOTS/SLUDGE | NO | NONE |  |  | Y |  |  | AREA ZEPPED
870929 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 870928 | 0830AM | 870928 | 0915AM | 225 | GAL | DORCAS & SAVANNAH PLACE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y
870929 | 0815AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 870928 | 1530PM | 870928 | 1630PM | 12 | GAL | 15TH & BROADWAY | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA | AREA DEOTORIZED.
871001 | 0900AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870930 | 1230PM | 870930 | 1330PM | 120 | GAL | RECHO RD IN CANYON | SAN DIEGO | SD | SEWER LINE | ROCKS & DEBRIS | NO | NONE |  |  | Y | N |  | AREA ZEPPED
870930 | 0830AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 870929 | 1000AM | 870929 | 1100AM | 600 | GAL | MESA COLLEGE DR N/O 805 EXIT | SAN DIEGO | SD | SEWER LINE | ROCKS/DEBRIS/VANDALS | NO | NONE |  |  | Y | N |  | AREA ZEPPED
871006 | 0900AM | DALE HOFFLAND | 6196942132 | LEMON GROVE SAN DIST | 871008 | ?????? | 871008 | ?????? | 200 | GAL | NEAR DRIVE IN THEATRE | LEMON GROVE | SD | SEWER LINE | CONTRACTOR BROKE LINE WHILE WORKING. | NO | NONE |  |  | Y |  |  | CONTAINED & CHLORINATED
871006 | LETTER | ??? | ??? | SANTA MARGARITA WATER DISTRICT | 871004 | 0630AM | 871004 | 0700AM | 1000 | GAL | 21115SANTA MARGARITA PKWY |  | OR | TRABUCO LIFT STATION | CRACKED BUBBLER LINE | NO | NONE |  |  | Y
871001 | 1955PM | 852A | 6192365534 | SANDIEGO, CITY OF | 871001 | 1955PM | 871001 | 2130PM | 4500 | GAL | 15790 AVENIDA VENUSTO | SAN DIEGO | SD | WET WELL AT STATION 73 | BAD RELAY ON CONTROL PANEL;PUMPS WOULD NOT OPERATE. | Y | GOLF COURSE POND |  |  | Y | Y | ??
871001 | LETTER | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 870930 | 1145AM | 870930 | 1345PM | 1500 | GAL | 1750 W. EL NORTE PKWY. | ESCONDIDO | SD | PUMP STATION 4 | CONTRACTOR WORKING BROKE FORCE MAIN | NO | NONE |  |  | N | N |  | CLEANED UP & DISINFECTED.
871005 | 1010AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871002 | 1015AM | 871002 | 1145AM | 45 | GAL | 3173 GOLDFINCH ST | SAN DIEGO | SD | CLEANOUT | ROOTS & GREASE | NO | NONE |  |  | Y | N
871005 | 1010AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871004 | 1030AM | 871004 | 1830PM | 7200 | GAL | 2800 INGRAHAM ST | SAN DIEGO | SD | MANHOLE | SLUDGE BLOCKAGE | Y | MISSION BAY |  |  | Y | Y | ?? | 20 SIGNS POSTED
871007 | 1030AM | PAUL WILSON | 6197281180 | FALLBROOK SANITARY DIST. | 871006 | 2100PM | 871007 | 0700AM | 78240 | GAL | FALLBROOK WWTP | FALLBROOK | SD | DIGESTER | W.A.S. VALVE LEFT OPEN-DIGESTER OVERFLOWED. | Y | FALLBROOK CREEK |  |  | Y | ? | ??
871006 | 0900AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871005 | 0900AM | 871005 | 1000AM | 30 | GAL | 4657 IOWA ST | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y
871007 | 1545PM | SENIOR | 6192367030 | SAN DIEGO, CITY OF | 871007 | 0845AM | 871007 | 0945AM | 60 | GAL | 3104 MEADE AVE | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | Y
871007 | 0800AM | SENIOR | 6192367030 | SAN DIEGO, CITY OF | 871006 | 1420PM | 871006 | 1620PM | 240 | GAL | 5420 55TH ST | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y
871008 | 1115AM | TOM BRADLEY | 7145822330 | SANTA MARGARITA WATER DISTRICT | 871008 | 0725AM | 871008 | 0750AM | 9500 | GAL | PLANO LIFT STATION | RANCHO MISSION V | OR | PLANO LIFT STATION | PUMPS FAILED TO ACTIVATE | NO | NONE |  |  | Y | N | NA
871008 | 1800PM | ANDY ANDERSON | 6195227380 | CORONADO, CITY OF | 871008 | 1827PM | 871008 | ?????? | 500 | GAL | GREENTURTLE PUMP STATION | CORONADO | SD | MANHOLE | PUMP STA. LIQUID LEVEL CONTROLLER FAILED. | Y | SAN DIEGO BAY |  |  | Y | N
871013 | 1120AM | PAT HOY | 6192362222 | SAN DIEGO, CITY OF | 871011 | 2000PM | 871011 | 2030PM | 325 | GAL | 850 COAST BLVD. | SAN DIEGO | SD | PUMP STATION 26 | POWER OUTAGE AT PUMP STATION | Y | OCEAN |  |  | Y | Y | 01
871013 | 1120AM | PAT HOY | 6192362222 | SAN DIEGO, CITY OF | 871011 | 0900AM | 871011 | 1300PM | 6000 | GAL | 8604 LA JOLLA SHORES DR. | SAN DIEGO | SD | MANHOLE FRONT OF SCRIPPS IGPP | ROOTS | Y | OCEAN |  |  | Y | Y | 02
871013 | 1220PM | GARY ORR | 6194397393 | OCEANSIDE, CITY OF | 871012 | 1600PM | 871012 | 2000PM | 10000 | GAL | INTSEC. MESA & GARRISON STS. | OCEANSIDE | SD | MANHOLE | INFILTRATION DURING RAIN STORM | Y | LOMA ALTA CREEK TO OCEAN |  |  | Y | ? | ??
871004 | 0900AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871013 | 0930AM | 871013 | 1000AM | 3 | GAL | 15TH & BROADWAY | SAN DIEGO | SD | MANHOLE | GREASE & DEBRIS | NO | NONE |  |  | Y | N |  | AREA DEOTORIZED
871014 | 0900AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871013 | 1400PM | 871013 | 1600PM | 1200 | GAL | 1360 SAN YSIDRO BLVD | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
871008 | 1540PM | THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 871008 | 0800AM | 871008 | 0900AM | 60 | GAL | 3726 ACACIA ST | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | Y
871008 | 0850AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871008 | 1830PM | 871008 | 2230PM | 600 | GAL | 47TH & POLK | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
871012 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871008 | 1330PM | 871008 | 1530PM | 120 | GAL | 5771 LA JOLLA BLVD. | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y
871007 | 1530PM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871006 | 1530PM | 871006 | 2030PM | 300 | GAL | 15TH & BROADWAY | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
871016 | LETTER | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 871011 | 1100AM | 871011 | 1215PM | 1000 | GAL | 400 BLK EAST MISSION | ESCONDIDO | SD | MANHOLE ATLAS PG.20 MH 50 | GREASE | NO | NONE |  |  | N | N |  | STREET & STORM DRAIN TREATED WITH DISINFECTANT AND WASHED DOWN.
871021 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871018 | 0900AM | 871018 | 1100AM | 1200 | GAL | 2818 JARVIS ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE
871021 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871018 | 1230PM | 871018 | 1430PM | 1200 | GAL | DANUBE & POLARIS | SNA DIEGO | SD | MANHOLE | ROCKS | NO | NONE
871021 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871017 | 1100AM | 871017 | 1600PM | 4500 | GAL | 6105 BEAUMONT AVE | SAN DIEGO | SD | MANHOLE | ROOTS & ROCKS | Y | PACIFIC OCEAN |  |  | Y | Y | ?? | 2 SIGNS POSTED.
871017 | 1100AM | CHARLES GOODMAN | 6192367340 | SAN DIEGO, CITY OF | 871017 | 1100AM | 871017 | 1330PM | 3750 | GAL | 1428 MINDEN DR | SAN DIEGO | SD | MANHOLE | ROOTS & GREASE | NO | NONE |  |  | Y | N | NA
871016 | 1600PM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871016 | 1430PM | 871016 | 1500PM | 3900 | GAL | 6750 VISTA DEL MAR | SAN DIEGO | SD | MANHOLE | GREASE | Y | PACIFIC OCEAN |  |  | Y | Y | ??
871016 | 1600PM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871016 | 1330PM | 871016 | 2230PM | 16200 | GAL | 1102 MUIRLANDS ST. | SAN DIEGO | SD | MANHOLE | ROOTS | N | NONE |  |  | Y | N | NA
871015 | 0900AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871014 | 1830PM | 871014 | 2100PM | 150 | GAL | 3605 GILLETTE ST. | SAN DIEGO | SD | SEWER LINE | UNKNOWN | NO | NONE |  |  | Y | N | NA | AREA ZEPPED.
871019 | 1030AM | LYODD THOMPSON | 7144973311 | LAGUNA BEACH, CITY OF | 871018 | 0800AM | 871018 | 1400PM | 15000 | GAL | PEARL ST & OCEAN WAY | LAGUNA BEACH | OR | PUMP STATION 5 (PEARL ST STA) | PUMP STATION POWER FAILURE | Y | PACIFIC OCEAN |  |  | Y | Y | 04 | ORANGE COUNTY HEALTH SAMPLING TODAY
871019 | LETTER | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 871014 | 1000AM | 871014 | 1130AM | 2000 | GAL | 728 WEST 7TH ST | ESCONDIDO | SD | MANHOLE 19 ATLAS PG 3 | GREASE & ROOT BLOCKAGE | NO | NONE |  |  | N | N | NA | AREA TREATED WITH DISINFECTANT
871019 | LETTER | D GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871013 | 0845AM | 871013 | 1045AM | 240 | GAL | 2625 ULRIC ST | SAN DIEGO | SD | MANHOLE | ROOTS & GREASE | NO | NONE |  |  | Y
871012 | LETTER | D GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871012 | 0830AM | 871012 | 1030AM | 360 | GAL | 6100 LA PINTURA DR | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y
871014 | LETTER | D GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871012 | 1230PM | 870112 | 1330PM | 60 | GAL | 806 VANITIE CT | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | Y | N | NA
871012 | 0900AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871010 | 1300PM | 871010 | 1400PM | 180 | GAL | OVEIDO & STARGAZE | SAN DIEGO | SD | SEWER LINE | CINDER BLOCKS | NO | NONE |  |  | Y |  |  | AREA ZEPPED.
871012 | 0900AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871010 | 1000AM | 871010 | 1130AM | 22 | GAL | FASHION VALLEY RD & HOTEL CIRL | SAN DIEGO | SD | SEWER MAIN | GREASE | NO | NONE |  |  | Y | N | NA | AREA ZEPPED.
871012 | 0900AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871010 | 1600PM | 871010 | 1700PM | 20 | GAL | 4190 INGELLS | SAN DIEGO | SD | SEWER MAIN | ROOTS | NO | NONE |  |  | Y | N | NA | AREA ZEPPED.
871022 | 1030AM | PAT HOY | 6192362222 | LEUCADIA COUNTY WATER DISTRICT | 871021 | 0800AM | 871021 | 0900AM | 75000 | GAL | HWY 101 N/O LA COSTA AVENUE | ?????? | SD | BATAQUITOS PUMP STATION | ELECTRICAL FIRE IN PUMP STATION CONTROL PANEL BURNT OUT THE MOTOR. | Y | BATAQUITOS LAGOON |  |  | Y | Y | 14 | SAND BAR KEPT SPILL IN LAGOON.
871020 | 0845AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871019 | 0930AM | 871019 | 1100AM | 18 | GAL | 4060 TERALTA PL | SAN DIEGO | SD | CLEANOUT | ROOTS | NO | NONE |  |  | Y | N | NA
871019 | 0900AM | GOODMAN | 6192367340 | SAN DIEGO, CITY OF | 871019 | 2100PM | 871019 | 2200PM | 1200 | GAL | LA JOLLA MESA BL & TURQOUISE | SAN DIEGO | SD | MANHOLE | ROOTS | Y | OCEAN |  |  | Y | Y | ??
871023 | LETTER | GOODMAN | 6192367340 | SAN DIEGO, CITY OF | 871020 | 0830AM | 871020 | 0930AM | 1200 | GAL | 7163 FAIRWAY RD | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N | NA
871026 | 0930AM | MR. LOWENTHAL-PRC | ?????????? | SAN DIEGO, CITY OF | 871024 | ????PM | 871000 | ?????? | 0 | ??? | 202 COAST BLVD | SAN DIEGO | SD | LATERAL | UNKNOWN AT THIS TIME | Y | PACIFIC OCEAN |  |  | Y | ? | ?? | HAZ MAT TO CALL CITY. WJG FILED COMPLAINT FORM.
871026 | 0930AM | PAT HOY | 6192362222 | SAN DIEGO, CITY OF | 871024 | 0930AM | 871024 | 1145AM | 450 | GAL | BAYSIDE LANE & ISLAND PORT | SAN DIEGO | SD | MANHOLE | GREASE | Y | MISSION BAY |  |  | Y | Y | 02 | 3 SIGNS POSTED. HAZ MAT SAMPLING TODAY. PRESS RELEASE ALREADY.
871026 | 1650PM | JAON GEISELHART | 6197530155 | LEUCADIA COUNTY WATER DISTRICT | 871025 | 0930AM | 871025 | 0950AM | 200 | GAL | 2017 HWY 101 | CARLSBAD | SD | BATAQUITOS PUMP STATION | ELECTRICAL CIRCUT MALFUNCTION RELATED TO 10/21/87 SPILL. | Y | BATAQUITOS LAGOON |  |  | Y | Y | 14
871029 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871026 | 1400PM | 871026 | 1800PM | 2400 | GAL | 52ND ST BET HANNIMAN & DE BURN | SAN DIEGO | SD | MANHOLE | UNKNOWN | NO | NONE |  |  | N
871027 | 0950AM | JOHN CROWDER | 6192366092 | SAN DIEGO, CITY OF | 871026 | 1000AM | 871026 | 1100AM | 300 | GAL | 29TH & PALM | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N
871029 | LETTER | CHARLES GOODMAN | 6192367340 | SAN DIEGO,CITY OF | 871023 | 1030AM | 871023 | 1130AM | 120 | GAL | BUENA VISTA ST | SAN DIEGO | SD | CLEANOUT | ROOTS | NO | NONE |  |  | Y | N
871027 | 0800AM | GARY ORR | 6194397164 | OCEANSIDE, CITY OF | 871024 | 1030AM | 871024 | 1400PM | 8000 | GAL | 3625 AMIGO COURT | OCEANSIDE | SD | MANHOLE | VANDALS JAMMED DOWNSTREAM MANHOLE WITH ROCKS, STICKS & DEBRIS. | NO | NONE |  |  | N | N
871028 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871024 | 0950AM | 871024 | 1500PM | 1500 | GAL | 4311 WINONA | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | N | N
871028 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871024 | 0950AM | 871024 | 1330PM | 450 | GAL | 3206 MISSION BLVD. | SAN DIEGO | SD | MANHOLE | GREASE | Y | VENTURA COVE TO OCEAN |  |  | Y | Y | ?? | 3 SIGNS POSTED AT ISLAND CT. & BAYSIDE LN..
871028 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871024 | 1815PM | 871025 | 0700AM | 19500 | GAL | 3002 ARMSTRONG ST | SAN DIEGO | SD | MANHOLE | ROCKS & DEBRIS | NO | NONE |  |  | Y | N | NA
871028 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871023 | 0600AM | 871023 | 0800AM | 1200 | GAL | 2035 SO.42ND ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
871028 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871024 | 1620PM | 871024 | 1820PM | 600 | GAL | 4348 COPELAND | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
871026 | 1045AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871025 | 1130AM | 871025 | 1330PM | 600 | GAL | 6435 CRYSTALLAIRE DR | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N | NA
871026 | 1045AM | M ARNOLD | 6192366092 | SAN DIEGO | 871025 | 1600PM | 871025 | 1800PM | 1800 | GAL | 2138 HANIMAN ST | SAN DIEGO | SD | CLEANOUT | ROOTS | NO | NONE |  |  | Y | N
871022 | 0900AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871021 | 1500PM | 871021 | 1800PM | 360 | GAL | 4480 CAMINITO FUENTE | SAN DIEGO | SD | SEWER LINE | ROOTS, SLUDGE, ROCKS | NO | NONE |  |  | Y | N | NA
871026 | LETTER | CHARLES GOODMAN | 6192367340 | SAN DIEGO, CITY OF | 871021 | 0900AM | 871021 | 1000AM | 600 | GAL | 1441 QUIVERA RD | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N
871026 | LETTER | CHARLES GOODMAN | 6192367340 | SAN DIEGO, CITY OF | 871021 | 1730PM | 871021 | 2030PM | 900 | GAL | 5065 EL CAJON BLVD | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
871102 | LETTER | CHARLES GOODMAN | 6192367340 | SAN DIEGO, CITY OF | 871027 | 1730PM | 871027 | 1731PM | 10 | GAL | 5600 BLK LA JOLLA BLVD. | SAN DIEGO | SD | MANHOLE | GREASE IN PIPE | NO | NONE |  |  | Y | N | NA | NONE
871028 | 0900AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871028 | 2330PM | 871028 | 0130AM | 120 | GAL | 28TH & WEBSTER | SAN DIEGO | SD | MANHOLE | ROOT & DEBRIS BLOCKAGE | NO | NONE |  |  | Y | N | NA
871028 | 1520PM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871028 | 0730AM | 871028 | 0930AM | 15 | GAL | 10760 ESMERALDAS DRIVE | SAN DIEGO | SD | SEWER LINE | ROOTS | NO | NONE |  |  | Y | N | NA | FLOWED INTO ALLEY. ALLEY ZEPPED.
871101 | 0945AM | STATION 38 | 6192365640 | SAN DIEGO, CITY OF | 871031 | 0942AM | 871101 | 1730PM | 168000 | GAL | ELWOOD & GENEVA AVE | SAN DIEGO | SD | MANHOLE | ROCKS & DEBRIS | Y | CHOLLAS CREEK/SAN DIEGO BAY |  |  | Y | Y | 02
871109 | LETTER | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 871103 | 1100AM | 871103 | 1145AM | 750 | GAL | CENTER CITY PKWY NR FELICITA | ESCONDIDO | SD | FORCE MAIN ATLAS P6S3 | 8 INCH AC FORCE MAIN BROKE DUE TO PRESSUE OF EUCLYPTUS TREE ROOTS. | NO | NONE |  |  | N | N | NA | ATLAS PUMPING REMOVED MATERIALFROM CATCH BASIN. STORM DRAIN DISINFECTED.
871109 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871103 | 0700AM | 871103 | 0830AM | 450 | GAL | 1100 BLK DELEVAN DR | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
871109 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871103 | 0815AM | 871103 | 1015AM | 120 | GAL | 69TH & IMPERIAL | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA | NONE
871104 | 1325PM | BURT SELE | 6194411658 | EL CAJON, CITY OF | 871104 | 0700AM | 871104 | 0730AM | 1100 | GAL | 1662 E MAIN ST | SAN DIEGO | SD | MANHOLE | GREASE | Y | FORRESTER CREEK/CHANNEL |  |  | Y | N | NA | NONE
871105 | 1530PM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871105 | 1130AM | 871105 | 1135AM | 10 | GAL | ROSEWOOD & MISSION BAY DRIVE | SAN DIEGO | SD | MANHOLE | LINE BREAK DUE TO RAINS | Y | DE ANZA COVE |  |  | Y | Y | 02
871109 | 0800AM | PAT HOY | 6192362222 | SAN DIEGO, CITY OF | 871108 | 0930AM | 871108 | 1124AM | 12000 | GAL | 3751 WINONA AVE | SAN DIEGO | SD | MANHOLE | ROCKS IN MANHOLE | Y | SAN DIEGO BAY |  |  | Y | Y | ??
871109 | 1010AM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871108 | 1715PM | 8711 | ?????? | 90000 | GAL | S. OF HWY 94 KELTON & EUCLID | SAN DIEGO | SD | MANHOLE | HOLE IN PIPE DUE TO ROCKS | Y | CHOLLAS CREEK/SAN DIEGO BAY |  |  | Y | Y | ??
871109 | 1010AM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871107 | 0915AM | 871107 | 1245PM | 7300 | GAL | 4340 WINONA AVE | SAN DIEGO | SD | ?????? | HEAD STOPPAGE BLEW JOINT | NO | NONE |  |  | Y |  |  | GRIFFIN SAID PIPE FAILS OFTEN & SHOULD BE REPLACED
871109 | 1540PM | TOM BRADLEY | 7145822330 | SANTA MARGARITA WATER DISTRICT | 871108 | 0001AM | 871108 | 0015AM | 5000 | GAL | PUERTA DE LUZ LIFT STATION | MISSION VIEJO | OR | LIFT STATION | STATION EXPERIENCED POWER FAILURE. | NO | NONE |  |  | Y | N | NA | STORM DRAIN ENTERED IS FAR FROM SURF WATER & IT WAS CHLORINATED & WASHED DOWN.
871110 | 0915AM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871110 | 0730AM | 871110 | 0830AM | 300 | GAL | 6611 VISTA DEL MAR | SAN DIEGO | SD | CLEANOUT | GREASE | Y | OCEAN AT COALMAR & NEPTUNE |  |  | Y | Y | ??
871110 | 0845AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871109 | 0930AM | 871105 | 1030AM | 120 | GAL | 1858 NEWTON AVE | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | Y | N |  | AREA WASHED DOWN & DEOTORIZED.
871109 | LETTER | GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871107 | 1415PM | 871107 | 1545PM | 450 | GAL | ALLEY BEHIND 4354 40TH STREET | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y
871109 | LETTER | GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871109 | 0900AM | 871109 | 1000AM | 60 | GAL | 742 SANTA RITA PLACE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  | PUMP STATION 17 | Y
871110 | 0845AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871109 | 1230PM | 871109 | 1400PM | 45 | GAL | 4284 IBIS ST | SAN DIEGO | SD | SEWER MAIN JOINT | ROOTS & ROCKS | NO | NONE |  |  | Y |  |  | AREA WASHED DOWN & DEOTORIZED.
871106 | 0900AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871105 | 2030PM | 871105 | 2200PM | 27 | GAL | 1920 FRONT ST | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | Y |  |  | AREA WASHED DOWN & DEOTORIZED.
871110 | 1200 N | JOAN GEISELHART | 6197530155 | LEUCADIA COUNTY WATER DISTRICT | 871110 | 0730AM | 871110 | 0930AM | 12000 | GAL | ADJACENT SAN MARCOS CREEK | CARLSBAD | SD | FORCE MAIN | UNKNOWN AT THIS TIME. BREAK WAS E/O EL CAMINO REAL & N/O LA COSTA AVE | Y | SAN MARCOS CREEK-BATAQUITOS LG |  |  | Y | Y | ??
871112 | 0830AM | PAT HOY,CO. HAZ MAT. | 6192362222 | SAN DIEGO, CITY OF | 871111 | 0445AM | 871111 | 0545AM | 54000 | GAL | 3200 KETTNER BLVD. | SAN DIEGO | SD | MANHOLE | WATER MAIN RUPTURE AT INDIA ST. INFILTRATED AND OVERLOADED SEWER LINE CAUSING BREAK. | Y | SAN DIEGO BAY**** |  |  | Y | Y | ?? | POSTED NEAR C.G. STATION & GENERAL DYNAMICS.
871117 | LETTER | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 871112 | 0740AM | 871112 | 0815AM | 0 | ??? | 1100 BLK EAST LINCOLN ST. | ESCONDIDO | SD | MANHOLE 7 ATLAS PAGE 21 | GREASE | NO | NONE |  |  | N | N |  | AREA DISINFECTED AND WASHED DOWN.
871117 | LETTER | BEADLE//THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 871110 | 0945AM | 871110 | 1245PM | 900 | GAL | 3105 C ST | SAN DIEGO | SD | MANHOLE | ROOTS & DEBRIS | NO | NONE |  |  | N | N | NA
871110 | LETTER | D. GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871109 | 1830PM | 871109 | 1930PM | 1500 | GAL | 4548 32ND ST | SAN DIEGO | SD | CLEANOUT & MANHOLE | GREASE & DEBRIS | NO | NONE |  |  | Y
871112 | LETTER | D. GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871111 | 0945AM | 871111 | 1130AM | 525 | GAL | PETER PAN & SYCHAR | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
871113 | 0925AM | LETTER | M. ARNOLD | SAN DIEGO, CITY OF | 871112 | 1910PM | 871112 | 2210PM | 6300 | GAL | 7800 VISTA HILL | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N | NA | AREA DEOTORIZED
871117 | 1100AM | GARY ORR | 6194397393 | OCEANSIDE, CITY OF | 871117 | 0710AM | 871117 | 0845AM | 1000 | GAL | LANCELOT & FRONTIER | OCEANSIDE | SD | MANHOLE | MISSION AVE PUMP STATION POWER OUTAGE. | Y | SAN LUIS REY RIVER? 7 MI. AWAY |  |  | Y | N | NA
871117 | 0830AM | PAT HOY | 6192362222 | SAN DIEGO, CITY OF | 871114 | 0906AM | 871114 | 1100AM | 6000 | GAL | TALBOT & UPSHER STS. | SAN DIEGO | SD | MANHOLE | GREASE & DEBRIS | Y | SAN DIEGO BAY |  |  | Y | Y | ?? | POSTED 200YDS BOTH SIDES OF BAY ENTRY POINT. HAZ MAT IS SAMPLING TODAY.
871118 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871113 | 0900AM | 871113 | 1000AM | 15 | GAL | 4837 CASTLE AVE | SAN DIEGO | SD | MANHOLE | GREASE & SLUDGE | NO | NONE |  |  | N | N | NA
871118 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871114 | 1530PM | 871114 | 1730PM | 120 | GAL | 6755 DRAPER ST | SAN DIEGO | SD | MANHOLE | ROOTS | N |  |  |  | N | N | NA
871112 | LETTER | D. GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871111 | 1800PM | 871111 | 1900PM | 600 | GAL | 1775 FROUDE ST | SAN DIEGO | SD | CLEANOUT | ROOTS IN MAIN | N | NONE |  |  | Y
871102 | 1350PM | M. ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871031 | 0900AM | 871031 | 1030AM | 450 | GAL | 4049 36TH ST. | SAN DIEGO | SD | MANHOLE | GREASE | N | NONE |  |  | Y | N
871102 | 1350PM | M. ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871101 | 1100AM | 871101 | 1300PM | 3600 | GAL | 4320 MISSION BLVD. | SAN DIEGO | SD | MANHOLE | GREASE | N | NONE |  |  | Y | N
871102 | 1350PM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871030 | 0930AM | 871030 | 1100AM | 450 | GAL | 4310 RANDOLPH ST. | SAN DIEGO | SD | MANHOLE | ROOTS | N | NONE |  |  | Y
871105 | 0825AM | M. ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871104 | 0920AM | 871104 | 1020AM | 6 | GAL | 4476 HORTENSIA ST | SAN DIEGO | SD | MANHOLE | ROOTS | N | NONE |  |  | Y | N
871118 | LETTER | CHARLES GOODMAN | 6192367340 | SAN DIEGO, CITY OF | 871030 | 1530PM | 871030 | 1630PM | 600 | GAL | BROSHAN ST. | SAN DIEGO | SD | MANHOLE | GREASE | N | NONE |  |  | Y | N
871118 | LETTER | CHARLES GOODMAN | 6192367340 | SAN DIEGO, CITY OF | 871102 | 1130AM | 871102 | 1230PM | 60 | GAL | 7760 & 7764 NIGHTINGALE WAY | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | Y
871117 | 1100AM | GARY ORR | 6194397164 | OCEANSIDE, CITY OF | 871117 | 0710AM | 871117 | 0845AM | 1000 | GAL | 154 TROPICANA DRIVE | OCEANSIDE | SD | MANHOLE | ELECTRICAL POWER PANEL FAILURE AT MISSION AVE PUMP STATION.INTERMITTENT FAILURE OF RELAY. | N | NONE |  |  | Y | N
871119 | LETTER | BEADLE//THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 871116 | 0800AM | 871116 | 0900AM | 3000 | GAL | 5045 CAMPANILE DRIVE | SAN DIEGO | SD | MANHOLE | GREASE | N | NONE |  |  | N | N | NA
871110 | 0900AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871109 | 1100AM | 871109 | 1300PM | 2400 | GAL | DEAD END OF CAMINO SANTA FE | SAN DIEGO | SD | SEWER LINE | CONTRACTORS PLUGGED LINE WITH DEBRIS. | N | NONE |  |  | Y | N
871110 | 1430PM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871110 | 1230PM | 871110 | 1430PM | 600 | GAL | 18490 BERNARDO TRAILS CT | SAN DIEGO | SD | SEWER LINE | HEAVY SLUDGE | Y | LAKE HODGES |  |  | Y | Y | 06
871112 | 1430PM | NANCY HECTOR | 6197288319 | FALLBROOK SANITARY DISTRICT | 871112 | 1430PM | 871112 | 1515PM | 15 | GAL | 1005 MAIN ST. | FALLBROOK | SD | CLEANOUT | ROOTS IN LATERAL | N | NONE |  |  | N | N | NA
871124 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871119 | 0930AM | 871119 | 1030AM | 300 | GAL | 4717 UNIVERSITY AVE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
871116 | 0900AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871113 | 1700PM | 871113 | 1900PM | 60 | GAL | 2821 CLAY AVE | SAN DIEGO | SD | SEWER LINE | GREASE | N | NONE |  |  | Y | N
871120 | 0900AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871119 | 1530PM | 871119 | 1730PM | 120 | GAL | 4432 NEW HAMPSHIRE ST | SAN DIEGO | SD | SEWER LINE | ROOTS & SLUDGE | N | NONE |  |  | Y | N
871116 | 0900AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871115 | 1330PM | 871115 | 1500PM | 180 | GAL | PUPPET THEATRE ON PRESIDENTS | SAN DIEGO | SD | SEWER LINE | GREASE & ROCK | N | NONE |  |  | Y | N
871117 | 0900AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871116 | 1630PM | 871116 | 1800PM | 90 | GAL | 940 SOUTH 33RD ST | SAN DIEGO | SD | SEWER LINE | GREASE & RAGS | N | NONE |  |  | Y | N
871118 | 1000AM | M. ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871117 | 1100AM | 871117 | 1300PM | 2400 | GAL | 1768 SUNSET BLVD | SAN DIEGO | SD | SEWER MAIN | BROKEN 8" MAIN | N | NONE |  |  | Y | N
871118 | 0900AM | JIM McCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871117 | 1600PM | 871117 | 2100PM | 6000 | GAL | 4770 VOLTAIRE ST | SAN DIEGO | SD | SEWER LINE | GREASE & PLUMBERS SNAKE | Y | OCEAN AT DOG BEACH |  |  | Y | Y | 04
871124 | 1400PM | PAT HOY | 6192362222 | SAN DIEGO, CITY OF | 871123 | 2230PM | 871123 | ?????? | 4500 | GAL | 9030 LA JOLLA SHORES DRIVE | SAN DIEGO | SD | MANHOLE | ROOTS | Y | OCEAN AT SCRIPPS PIER |  |  | Y | Y | ?? | POSTED 200YDS EACH WAY
871124 | 1400PM | PAT HOY | 6192362222 | SAN DIEGO, CITY OF | 871123 | ?????? | 0 | ?????? | 750 | GAL | 298 COAST BLVD. | SAN DIEGO | SD | PUMP STATION 24 | ????????PUMP STATION 24 FAILURE???? | Y | OCEAN |  |  | Y | Y | 02
871124 | 1500PM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871124 | 0900AM | 871124 | 1000AM | 300 | GAL | 9000 LA JOLLA SHORES LANE | SAN DIEGO | SD | MANHOLE | ROOTS | Y | OCEAN |  |  | Y | Y | ?? | POSTED BEHIND SCRIPPS / LA JOLLA SHORES DR.// CO. HEALTH IS SAMPLING.
871124 | 0930AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871123 | 2130PM | 871123 | 2230PM | 1500 | GAL | 9030 LA JOLLA SHORES LN | SAN DIEGO | SD | MANHOLE | ROOTS | Y | OCEAN |  |  | Y | Y | ??
871124 | 0930AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871123 | 0840AM | 871123 | 1010AM | 45 | GAL | 1805 LYNDON RD | SAN DIEGO | SD | LEAKING PIPE | ROCKS IN BROKEN PIPE | N0 | NONE |  |  | Y | N |  | SOAKED INTO GROUND IN CANYON. DEOTORANT APPLIED.
871123 | ?????? | DON GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871121 | 1030AM | 871122 | 1230AM | 600 | GAL | BACON & BRIGHTON ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
871130 | 0930AM | STEVE SANCHEZ | 6194969247 | CAPISTRANO BEACH SAN. DIST. | 871129 | 1030AM | 871129 | 1530PM | 900 | GAL | EL MOLINO & CALLE MONTEREY | CAPISTRANO BEACH | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N | NA | BLOCKAGE CLEARED BY EMPIRE CLEANING & AREA CHLORINATED.
871127 | 1600PM | LUIS HERNANDEZ | 6192367340 | SAN DIEGO, CITY OF | 871127 | 1200 N | 871127 | 1500PM | 1800 | GAL | 7342 COUNTRY CLUB DRIVE | SAN DIEGO | SD | MANHOLE | ROCKS & SLUDGE | Y | OCEAN |  |  | Y | Y | 01 | 2 SIGNS POSTED AT PROSPECT & COAST BLVD.
871127 | ?????? | LUIS HERNANDEZ | 6192367340 | SAN DIEGO | 871125 | ????AM | 871127 | 1000AM | 6000 | GAL | MISSION CTR RD & MARIE RIDGE | SAN DIEGO | SD | SEWER MAIN | MAIN BREAK | Y | SAN DIEGO RIVER TO OCEAN |  |  | Y | Y | ?? | DOG BEACH CLOSED FOR SAMPLING.
871117 | 0945AM | JOAN GEISELHART | 6197530115 | LEUCADIA COUNTY WATER DISTRICT | 871116 | 1600PM | 871116 | 1605PM | 300 | GAL | MAIN AT SAN MARCOS CREEK | LEUCADIA | SD | FORCE MAIN | CONTRACTOR REPLACING OLD MAIN HOOKED UP ABANDONED LINE IN ERROR,LINE WAS NOT SHOWN ON PLANS. | Y | SAN MARCOS CREEK |  |  | Y | ? | ??
871113 | ?????? | BEADLE THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 871119 | 1515PM | 871119 | 1615PM | 60 | GAL | 3859BREMS | SAN DIEGO | SD | MANHOLE | ROOTS & GREASE | NO | NONE |  |  | N | N | NA
871126 | 0830AM | LUIS HERNANDEZ | 6192367340 | SAN DIEGO, CITY OF | 871126 | 0830AM | 871126 | 1100AM | 7500 | GAL | 400 SYCHARD RD | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N
871126 | 1100AM | LUIS HERNANDEZ | 6192367340 | SAN DIEGO, CITY OF | 871126 | 1100AM | 871126 | 1400PM | 3600 | GAL | 5958 MADRA AVE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N
871124 | 1500PM | DON GRIFFIN | 6192367340 | SAN DIEGO ,CITY OF | 871124 | 0900AM | 871124 | 1000AM | 300 | GAL | 9000 LA JOLLA SHORES LANE | SAN DIEGO | SD | MANHOLE | ROOTS | Y | OCEAN |  |  | Y | Y | ??
871127 | 0800AM | SENIOR THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 871125 | 1030AM | 871125 | 1130AM | 300 | GAL | 6150 CAMINITO SACATE | SAN DIEGO | SD | MANHOLE | ROOTS & ROCKS | NO | NONE |  |  | Y | N | NA
871127 | 1530PM | SENIOR BURTON | 6192367030 | SAN DIEGO, CITY OF | 871127 | 0700AM | 871127 | 0800AM | 300 | GAL | CANYON BEHIND 1300 ALISLA DR | SAN DIEGO | SD | MANHOLE | ROCKS | NO | NONE |  |  | Y | Y | 03
871201 | ?????? | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 871123 | 1400PM | 871123 | 1445PM | 200 | GAL | 1100 BLK EAST VALLEY PKWY. | ESCONDIDO | SD | MANHOLE SEWER ATLAS PG. 23 | GREASE | NO | NONE |  |  | N | N | NA | STREET WASHED DOWN & DISINFECTED.
871130 | 0900AM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871128 | 2100PM | 871128 | 2300PM | 240 | GAL | 7981 LANDON PLACE | SAN DIEGO | SD | SEWER MAIN | GREASE | NO | NONE |  |  | Y | N | NA | AREA ZEPPED.
871130 | 0900AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871125 | 1330PM | 871125 | 1500PM | 270 | GAL | UNIVERSITY & WASHINGTON | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N | NA
871130 | 0900AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871126 | 1330PM | 871126 | 1500PM | 450 | GAL | 7555 LINDA VISTA RD | SAN DIEGO | SD | MANHOLE | ROOTS & DEBRIS | NO | NONE |  |  | Y | N | NA
871130 | 0900AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871127 | 0830AM | 871127 | 1030AM | 600 | GAL | ANDREWS & PUTERBAUGH | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N
871201 | 0830AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871130 | 1020AM | 871130 | 1150AM | 9 | GAL | GRAPE ST & PACIFIC HWY. | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
871130 | ?????? | CHARLES GOODMAN | 6192367340 | SAN DIEGO, CITY OF | 871130 | 0839AM | 871130 | 0900AM | 30 | GAL | 1775 OLIVER AVE | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | ? | ? | ??
871203 | ?????? | BEADLE THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 871130 | 2300PM | 871201 | 0100AM | 600 | GAL | 4065 EL CAJON BLVD. | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
871203 | ?????? | BEADLE BURTON | 6192367030 | SAN DIEGO, CITY OF | 871130 | 1100AM | 871130 | 1200 N | 60 | GAL | ALLEGHANY & CALLE TORTUOSA | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
871202 | 1530PM | DICK ARNOLD | 6194411658 | EL CAJON, CITY OF | 871202 | 0715AM | 871202 | 1015AM | 1500 | GAL | 720 EL CAJON BLVD. | EL CAJON | SD | MANHOLE | ROOTS, ROCKS, WOOD | Y | FORRESTER CREEK |  |  | Y | N | NA
871202 | 0800AM | DICK ARNOLD | 6194411658 | EL CAJON, CITY OF | 871201 | 0815AM | 871201 | 0900AM | 3150 | GAL | EL CAJON BLVD AT HILL STREET | EL CAJON | SD | MANHOLE | ROCKS & ROOTS | Y | FORRESTER CREEK |  |  | Y | N | NA
871202 | 0900AM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871201 | 2030PM | 871201 | 2230PM | 120 | GAL | 1252 23RD ST | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N | NA | AREA ZEPPED.
871127 | 1430PM | JOSE HERNANDEZ | 6192367340 | SAN DIEGO, CITY OF | 0 | ?????? | 871127 | 1000AM | 5760 | GAL | MISSION CENTER ROAD | SAN DIEGO | SD | MAIN | BROKEN SEWER MAIN | Y | SAN DIEGO RIVER TO OCEAN |  |  | Y | Y | ??
871127 | 1600PM | LUIS HERNANDEZ | 6192367340 | SAN DIEGO, CITY OF | 871127 | 1000AM | 871127 | 1300PM | 1800 | GAL | 7342 COUNTRY CLUB DRIVE | SAN DIEGO | SD | MANHOLE | ROOTS & ROCKS | Y | OCEAN |  |  | Y | Y | ??
871207 | ?????? | BEADLE BURTON | 6192367030 | SAN DIEGO, CITY OF | 871201 | 0815AM | 871201 | 0915AM | 60 | GAL | 6930 ALSACIA ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
871207 | ?????? | BEADLE WANTIEZ | 6192367030 | SAN DIEGO, CITY OF | 871201 | 0900AM | 871201 | 1030AM | 45 | GAL | ALLEY W/O FAIRMOUNT & POLK | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
871207 | ?????? | DON GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871205 | 1000AM | 871206 | 1200 N | 105000 | GAL | ZOO DRIVE | SAN DIEGO | SD | MANHOLE | HAY FROM HIPPO POND IN SAN DIEGO ZOO CLOGGED SEWER MAIN. | NO | NONE |  |  | Y | ? | ??
871204 | 1520PM | DICK ARNOLD | 6194411658 | EL CAJON, CITY OF | 871204 | 0640AM | 871204 | 0755AM | 2000 | GAL | MAIN ST 300FT E/O BROADWAY | EL CAJON | SD | MANHOLE | GREASE | Y | BROADWAY CHANNEL |  |  | Y | N | NA
871207 | 1012AM | DON GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871205 | 1200 N | 871205 | 1400PM | 12000 | GAL | 3900 TWIGGS ST | SAN DIEGO | SD | CLEANOUT | GREASE & ROOTS | Y | SAN DIEGO RIVER TO OCEAN |  |  | Y | N | NA | OCEAN BEACH IS ALREADY POSTED.
871205 | 1145PM | ED MCCAMPBELL | 6192216600 | SAN DIEGO, CITY OF | 871205 | 2115PM | 871205 | 2215PM | 2000000 | GAL | NORTH INTERCEPTOR/S.D. RIVER | SAN DIEGO | SD | METRO PUMP STATION #2 | POWER OUTAGE AT STATION 2 FOR 20 MINUTES. | Y | SAN DIEGO RIVER TO OCEAN |  |  | Y | Y | ??
871207 | 1530PM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871205 | 1300PM | 871207 | 1300PM | 1440000 | GAL | 1400 BLK MURRAY CANYON RD. | SAN DIEGO | SD | MANHOLE | HEAVY RAIN & BLOCKAGE IN 30" SEWER MAIN. | Y | SAN DIEGO RIVER TO OCEAN |  |  | Y | Y | ?? | COUNTY HEALTH WILL SAMPLE. DOG BEACH ALREADY POSTED.
871207 | 0915AM | PAT HOY |  | SAN DIEGO, CITY OF | 871205 | 1200 N | 0 | ?????? | 18000 | GAL | EAST MISSION BAY DRIVE | SAN DIEGO | SD | ?????? | ?????? | Y | DE ANZA COVE/MISSION BAY |  |  | Y | Y | ?? | SAMPLING IN PROGRESS.
871209 | ?????? | BEADLE DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 871206 | 1530PM | 871206 | 2030PM | 600 | GAL | 11940 BERNARDO PLAZA | SAN DIEGO | SD | CLEANOUT | GREASE | ?? | ????? |  |  | ? | ? | ??
871209 | ?????? | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871205 | 1400PM | 871205 | 1800PM | 120 | GAL | 4655 OHIO ST | SAN DIEGO | SD | MANHOLE | GREASE | ?? | ???? |  |  | ? | ? | ??
871207 | 1130AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871205 | 0001AM | 871206 | 1600PM | 1200 | GAL | 4320 FALCON ST (NR. BARR ST.) | SAN DIEGO | SD | MANHOLE | BROKEN SEWER MAIN. | NO | NONE |  |  | Y | N | NA
871207 | 1130AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871204 | 0830AM | 871204 | 1000AM | 9 | GAL | 4320 FALCO ST | SAN DIEGO | SD | MANHOLE | ROCKS | NO | NONE |  |  | N | N
871204 | 0900AM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871203 | 2000PM | 871203 | 2100PM | 300 | GAL | 10937 VIA SAN BLAS | SAN DIEGO | SD | SEWER MAIN | GREASE | NO | NONE |  |  | Y | N | NA | AREA ZEPPED
871203 | 0900AM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871202 | 1830PM | 871202 | 2030PM | 6000 | GAL | MUNDA & SAIPAN DRIVE | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N | NA | AREA ZEPPED
871203 | 0900AM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871202 | 0800AM | 871202 | 0900AM | 30 | GAL | 11102 CAMINITO ALVAREZ | SAN DIEGO | SD | SEWER LINE | ROCKS & DIRT | NO | NONE |  |  | Y | N | NA | AREA ZEPPED
871204 | 0900AM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871203 | 1500PM | 871203 | 1700PM | 60 | GAL | 2850 EL CAJON BLVD. | SNA DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N | NA | AREA ZEPPED.
871205 | 1700PM | TOMMY BOWMAN | 6197281180 | FALLBROOK SANITARY DISTRICT | 871203 | ?????? | 871205 | 1840PM | 5 | GPM | AMMUNITION | FALLBROOK | SD | SAN DIEGO | VANDALS THREW LOGS & STICKS INTO MANHOLE | Y | STREAM TO FALLBROOK CREEK |  |  | N | N | NA | CREW CLEANED AREA ON 12/06/87.
871210 | 1020AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871209 | 1000AM | 871209 | 1100AM | 120 | GAL | 3429 QUIMBY ST | SAN DIEGO | SD | MANHOLE | ROOTS & GREASE | NO | NONE |  |  | Y | N
871207 | 1130AM | DICK ARNOLD | 6194411658 | EL CAJON, CITY OF | 871207 | 0630AM | 871207 | 0730AM | 1700 | GAL | 1560 BROADWAY | EL CAJON | SD | MANHOLE | CAN & DEBRIS IN LINE | Y | FORRESTER CREEK |  |  | Y | N | NA
871214 | ?????? | CHARLES GOODMAN | 6192367340 | SAN DIEGO, CITY OF | 871209 | 1705PM | 871209 | 1905PM | 3000 | GAL | 4212 LOS PINOS AVE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y
871207 | 1515PM | DON GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871207 | 0900AM | 871207 | 1300PM | 120000 | GAL | 1400 MURRAY CANYON RD | SAN DIEGO | SD | MANHOLE | ROCKS | Y | SAN DIEGO RIVER TO OCEAN |  |  | Y | Y | ??
871210 | 1020AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871209 | 1300PM | 871209 | 1400PM | 1200 | GAL | SAN DIEGO ZOO HIPPO POND | SAN DIEGO | SD | MANHOLE | ROCKS | NO | NONE |  |  | Y | N
871210 | 1530PM | DON GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871210 | 1230PM | 871210 | 1330PM | 1800 | GAL | 2510 TORREY PINES RD. | SAN DIEGO | SD | MANHOLE | ROOTS | Y | OCEAN |  |  | Y | Y | ??
871215 | ?????? | BEADLE DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 871210 | 2145PM | 871210 | 2300PM | 375 | GAL | 3492 ADAMS AVE | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | N | N | NA
871216 | ?????? | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 871211 | 0820AM | 871211 | 0910AM | 150 | GAL | 600 BLK EAST 5TH AVENUE | SAN DIEGO | SD | MANHOLE 19 ATLAS PG 9 | ROOTS | NO | NONE |  |  | N | N | NA
871214 | 1400PM | PAT HOY |  | SAN DIEGO, CITY OF | 871211 | 1800PM | 871211 | 1900PM | 180 | GAL | 2100 HARBOR ISLAND DRIVE | SAN DIEGO | SD | MANHOLE | GREASE | Y | SAN DIEGO BAY |  |  | Y | Y | 02
871210 | 1100AM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 871209 | 1200 N | 871209 | 1330PM | 45 | GAL | 5255 KEARNY VILLA RD | SAN DIEGO | SD | SEWER LINE | GREASE & ROOTS | NO | NONE |  |  | Y | N
871214 | 1015AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871211 | 1038AM | 871211 | 1330PM | 3600 | GAL | 2040 HARBOR ISLAND DR | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
871217 | LETTER | DON GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871211 | 0930AM | 871211 | 1230PM | 10800 | GAL | 3783 TOMAHAWK LN | SAN DIEGO | SD | MANHOLE | ROCKS & DEBRIS | NO | NONE |  |  | Y
871214 | 0900AM | JIM MC CURLEY | 6195789772 | SAN DIEGO, CITY OF | 871211 | 1530PM | 871211 | 1830PM | 36000 | GAL | 3783 TOMAHAWK ST | SAN DIEGO | SD | SEWER LINE | ROCKS | NO | NONE |  |  | Y | N
871214 | 1015AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871212 | 2000PM | 871212 | 2400PM | 240 | GAL | 2455 CALLE GAVIOTA | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N
871214 | 1015AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871212 | 1000AM | 871212 | 1100AM | 120 | GAL | BRIGHTON & SPRAY | SAN DIEGO | SD | MANHOLE | SAND | NO | NONE |  |  | Y | N
871214 | 1015AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871212 | 1930PM | 871212 | 2130PM | 240 | GAL | 6794 ROSWELL ST | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N
871221 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871214 | 1830PM | 871214 | 1930PM | 300 | GAL | 4609 HAWLEY BLVD | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
871216 | 1425PM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871215 | 1719PM | 871215 | 1912PM | 120 | GAL | 1625 PLUMOSA WAY | SAN DIEGO | SD | MANHOLE | ROOTS ROCKS SLUDGE | NO | NONE |  |  | Y
871221 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871215 | 1330PM | 871215 | 1500PM | 45 | GAL | 4386 ARAGON DR | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
871216 | 0900AM | JIM MC CURLEY | 6195789772 | SAN DIEGO, CITY OF | 871215 | 1230PM | 871215 | 1330PM | 120 | GAL | 4361 MARLBOROUGH AVE | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N
871217 | 0930AM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871216 | 1300PM | 871216 | 1700PM | 2400 | GAL | 1900 TORREY PINES RD | SAN DIEGO | SD | MANHOLE | ROOTS | Y | OCEAN |  |  | Y | Y | ??
871217 | 0930AM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871216 | 1000AM | 871217 | 0200AM | 36000 | GAL | 3000 ROSEWOOD | SAN DIEGO | SD | MANHOLE | OVERLOAD ON LINE-RAIN-INFILTRATION | Y | MISSION BAY & OCEAN |  |  | Y | Y | ??
871221 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871216 | 0830AM | 871216 | 0930AM | 60 | GAL | 6142 CHENANGO PLACE | SAN DIEGO | SD | CLEANOUT | ROOTS
871216 | 1625PM | MAIN OFFICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 871216 | 1625PM | 871216 | 1750PM | 2 | GAL | 226 S. SUMMIT | FALLBROOK | SD | 6 INCH LINE | ROOTS | NO | NONE |  |  | N | N
871221 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871217 | 1730PM | 871217 | 1930PM | 1200 | GAL | 4608 BANCROFT ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE
871217 | 1600PM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871217 | 1000AM | 871217 | 1230PM | 30000 | GAL | 3000 ROSEWOOD ST | SAN DIEGO | SD | MANHOLE | RAIN INFILTRATION | Y | MISSION BAY & OCEAN |  |  | Y | Y | ??
871221 |  | CHARLES GOODMAN | 6192367340 | SAN DIEGO, CITY OF | 871218 | 0800AM | 871218 | 0900AM | 180 | GAL | 2625 ULRIC ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
871221 | 1115AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871218 | 1130AM | 871218 | 1200 N | 300 | GAL | 3519 QUIMBY ST | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N
871221 | 1115AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871220 | 0930AM | 871220 | 1230PM | 2700 | GAL | 6542 GARBER AVE | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N
871221 | 1115AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871220 | 1125AM | 871220 | 1225PM | 60 | GAL | 4367 REVILLO DR | SAN DIEGO | SD | CLEANOUT | ROOTS | NO | NONE |  |  | Y | N
871221 | 1115AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871220 | 1410PM | 871220 | 1510PM | 120 | GAL | MISSION BAY DR & GRAND AVE | SAN DIEGO | SD | MANHOLE | RAIN INFILTRATION | Y | DE ANZA COVE |  |  | Y | N
871223 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871221 | 1745PM | 871221 | 1945PM | 1200 | GAL | 5428 SANTA MARGARITA | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N
871222 | 1005AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871221 | 1140AM | 871221 | 1240PM | 300 | GAL | 32ND ST & GREELEY | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
871224 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871222 | 1200PM | 871222 | 1400PM | 600 | GAL | 7044 MOHAWK | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
871223 | 0920AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871222 | 1935PM | 871222 | 2135PM | 24 | GAL | 3745 1st AVE | SAN DIEGO | SD | MANHOLE | ROOTS & GREASE | NO | NONE |  |  | Y | N
871223 | 0920AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871222 | 1520PM | 871222 | 1620PM | 60 | GAL | 4236 VENUS ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
871222 | 1615PM | DALE HOFFLAND | 6196942132 | SPRING VALLEY SAN DIST. | 871222 | 1345PM | 871222 | 1445PM | 2000 | GAL | JAMACHA JUNCTION HWY 94 & 54 | SPRING VALLEY | SD | AIR RELEASE VALVE | VALVE FOUND OPEN/POSSIBLE VANDALISM | Y | SWEETWATER LAKE |  |  | Y | N
871223 | 1556PM | DON GRISSON | 6192367250 | SAN DIEGO, CITY OF | 871223 | ?????? | 871223 | ?????? | 600 | GAL | 1000 TORREY PINES RD | SAN DIEGO | SD | ??????? | GREASE | Y | OCEAN |  |  | Y | Y | ??
871224 | 0815AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871223 | 0930AM | 871223 | 1000AM | 450 | GAL | 3644 28TH ST | SAN DIEGO | SD | MANHOLE | GREASE & ROOTS | NO | NONE |  |  | Y
871228 | 1010AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871224 | 1150AM | 871225 | 1320PM | 90 | GAL | 3554 DALBERGIA ST | SAN DIEGO | SD | CLEANOUT | UNKNOWN STOPPAGE | NO | NONE |  |  | Y | N
871231 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 871224 | 0900AM | 871224 | 1100AM | 600 | GAL | FRIEDRICK & WHALEY | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N
871228 | 0800AM | FRANK PADUA | 6192366901 | SAN DIEGO, CITY OF | 871224 | 1030AM | 871224 | 1130AM | 75000 | GAL | MISSION CENTER RD N/O SEVAN CT | SAN DIEGO | SD | MANHOLE | STORM RUNOFF | Y | SAN DIEGO RIVER/OCEAN |  |  | Y | Y | 04
871228 | 1010AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871227 | 1330PM | 871227 | 1630PM | 4500 | GAL | HOUSE OF NATIONS BLDG 2171 | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
871229 | 0910AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871228 | 1430PM | 871228 | 1500PM | 3 | GAL | 4865 N. HARBOR DR | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
871229 | 0910AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871228 | 1949PM | 871228 | 2350PM | 480 | GAL | 8960 NEWMONT DR | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
871220 | 1520PM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 871228 | 2330PM | 871229 | 0230AM | 360 | GAL | 2962 NUTMEG ST IN CANYON | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y
871228 | 1530PM | JIM MC CURLEY | 6195789772 | SAN DIEGO, CITY OF | 871228 | 1300PM | 871228 | 1430PM | 180 | GAL | 4625 UTAH ST | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N
871228 | 1305PM | JOHN EIFLING | 6192216626 | SAN DIEGO, CITY OF | 871228 | 0920AM | 871228 | 0940AM | 300 | GAL | 1902 GATCHELL/POINT LOMA WWTP | SAN DIEGO | SD | SLUDGE DISPOSAL LINE | W.A.S. LINE RUPTURED BY CONTRACTOR WHILE DIGGING TRENCH | Y | OCEAN |  |  | Y | N | NA
880107 | LETTER | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 871228 | 0945AM | 871228 | 1130AM | 1500 | GAL | 1444 JUNIPER ST | SAN DIEGO | SD | CLEANOUT | ROOTS & GREASE | NO | NONE |  |  | N | N
871230 | 1530PM | JIM MC CURLEY | 6195789772 | SAN DIEGO, CITY OF | 871230 | 1030AM | 871230 | 1130AM | 120 | GAL | 4655 OHIO ST | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N
871231 | 0835AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871230 | 1725PM | 871230 | 1825PM | 60 | GAL | 2070 PACIFIC HWY | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
880106 | LETTER | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 871230 | 1025AM | 871230 | 1100AM | 500 | GAL | 1729 E. GRAND AVE | ESCONDIDO | SD | MH 30 ATLAS PAGE 46 | GREASE | NO | NONE |  |  | N | N
880104 | 1430PM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871231 | 1513PM | 871231 | 1713PM | 600 | GAL | 2079 ILEX AVE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
880104 | 1430PM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 871231 | 1743PM | 871231 | 1943PM | 3000 | GAL | AVE MARIA & PENASQUITOS | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
871230 | 1115AM | DEL HERNANDEZ | 6192365534 | SAN DIEGO, CITY OF | 871230 | 1115AM | 871230 | ?????? | 0 | ??? | 850 COAST BLVD | SAN DIEGO | SD | OVERFLOW PIPE STORM DRAIN | GREASE | Y | OCEAN |  |  | Y | Y | 03 | OVERFLOW WAS SEEN BY LIFEGUARD.
880107 | LETTER | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 880103 | 1245PM | 880103 | 1700PM | 3000 | GAL | 300 BLK W. WASHINGTON | ESCONDIDO | SD | MH25 ATLAS PAGE 6 | GREASE | NO | NONE |  |  | N | N
880104 | 0900AM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 880103 | 0930AM | 880103 | 1200 N | 300 | GAL | 1120 28TH ST | SAN DIEGO | SD | SEWER LINE | GREASE ROCKS & RAGS | NO | NONE |  |  | Y | N
880104 | 0900AM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 880103 | 1130AM | 880103 | 1500PM | 1050 | GAL | AFTON & EAMES ST | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N
880104 | 0900AM | JIMMCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 880103 | 1730PM | 880103 | 1900PM | 450 | GAL | 4927 QUINCY ST | SAN DIEGO | SD | SEWER LINE | ROOTS | NO | NONE |  |  | Y | N
880105 | 1540PM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880103 | 1900PM | 880105 | 1400PM | 103200 | GAL | CANYON NORTH OF ALLENHURST | SAN DIEGO | SD | MANHOLE | ROOTS | Y | TECOLOTE CREEK |  |  | Y | N |  | INTERCEPTOR IN TECOLOTE CREEK STOPPED FLOW FROM REACHING S.D. BAY.
880111 | LETTER | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 880105 | 1000AM | 880105 | 1100AM | 800 | GAL | P.S. 9 HAMILTON | ESCONDIDO | SD | AERATION VENT PIPE ON FORCE MA | CONTRACTOR DROVE TRACTOR OVER PIPE & BROKE IT. | NO | NONE |  |  | N | N
880106 | 0820AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880105 | 1200 N | 880105 | 1500PM | 360 | GAL | EL PRADO & PARK BLVD. | SAN DIEGO | SD | MANHOLE IN CANYON | ROOTS | NO | NONE |  |  | Y | N
880108 | LETTER | BEADLE/THOMPSON | 6192367030 | SAN DIEGO, CITY OF | 880105 | 1400PM | 880105 | 1700PM | 900 | GAL | 5205 LE BARRON RD | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
880107 | ?????? | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880106 | 1500PM | 880106 | 1700PM | 120 | GAL | 1545 EL CAMINO DEL TETRO | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y
880107 | 0800AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880106 | 0840AM | 880106 | 0940AM | 180 | GAL | PRESIDENTS WAY & PAN AMERICAN | SAN DIEGO | SD | MANHOLE IN PARKING LOT | ROOTS | NO | NONE |  |  | Y | N | NA
880108 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880106 | 0800AM | 880106 | 0930AM | 270 | GAL | 47TH & EL CAJON | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
880112 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880107 | 2000PM | 880107 | 2200PM | 1200 | GAL | 5TH & PENNSYLVANIA | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
880112 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880107 | 2245PM | 880108 | 0045AM | 360 | GAL | 4544 WINONA | SAN DIEGO | SD | MANHOLE | RAGS & GREASE | NO | NONE |  |  | N | N | NA
880108 | ?????? | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880107 | 1200 N | 880107 | 1400PM | 1800 | GAL | ROLFE & CLAIREMONT MESA BLVD. | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y
880111 | 0830AM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880110 | 1430PM | 880110 | 1530PM | 300 | GAL | 605 SAN ELIJO ST | SAN DIEGO | SD | MANHOLE | ROOTS | Y | SAN DIEGO BAY / OCEAN |  |  | Y | Y | ??
880108 | LETTER | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 880107 | 1100AM | 880108 | 1200 N | 7200 | GAL | 4600 OAKLEAF PT & 5360 OUTLOOK | SAN DIEGO | SD | SEWER LINE | ROOTS | NO | NONE |  |  | Y | N
880111 | 1255AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880108 | 1315PM | 880108 | 1715PM | 2400 | GAL | HWY 163 S/O ROBINSON | SAN DIEGO | SD | MANHOLE-BREAK IN MAIN | ROOTS | NO | NONE |  |  | Y | N
880111 | 1255AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880109 | 1030AM | 880109 | 1330PM | 3600 | GAL | 4419 PARK BLVD. | SAN DIEGO | SD | MANHOLE | GREASE & DEBRIS | NO | NONE |  |  | Y | N | NA
880114 | LETTER | BRADLEY | 7145822330 | SANTA MARGARITA WATER DISTRICT | 880109 | 1030AM | 880109 | 1115AM | 2000 | GAL | MARGUERITE PKWY & JERONIMO | MISSION VIEJO | OR | SEWER MAIN | UNKNOWN OBSTRUCTION | NO | NONE |  |  | Y | N
880114 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880111 | 1030AM | 880111 | 1230PM | 600 | GAL | 4617 30TH ST IN ALLEY | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | N | N | NA
880114 | LETTER | ????? | ????? | SANTA MARGARITA WATER DISTRICT | 880111 | 1000AM | 880111 | 1035AM | 900 | GAL | TRABUCO & PUERTA DE LUZ | MISSION VIEJO | OR | PUERTA DE LUZ LIFT STATION | BUBBLE COMPRESSOR FAILURE | NO | NONE |  |  | Y
880115 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880112 | 0900AM | 880112 | 1030AM | 450 | GAL | 4149 41ST | SAN DIEGO | SD | CLEANOUT | SLUDGE & GREASE | NO | NONE |  |  | N | N | NA
880113 | 0955AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880112 | 1100AM | 880112 | 1200 N | 1200 | GAL | GRAPE & PACIFIC HWY | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y
880114 | 0930AM | ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880113 | 1430PM | 880113 | 1700PM | 75 | GAL | 2024 JULIAN AVE | SAN DIEGO | SD | CLEANOUT | BROKEN MAIN | NO | NONE |  |  | Y | N | NA | DISINFECTANT APPLIED TO AREA & STORM DRAIN.
880114 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880113 | 1200 M | 880113 | 0300AM | 2940 | GAL | CASTANA & ESCUELA | SAN DIEGO | SD | MANHOLE | ROTS & GREASE | NO | NONE |  |  | Y
880120 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880114 | 0920AM | 880114 | 1120AM | 360 | GAL | 3224 DWIGHT ST | SAN DIEGO | SD | MANHOLE | ROOTS & GREASE | NO | NONE |  |  | N | N | NA
880122 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880114 | 1015AM | 880114 | 1215PM | 360 | GAL | 40TH ST & ALPHA ST | SAN DIEGO | SD | CLEANOUT | GREASE & SLUDGE | NO | NONE |  |  | N | N | NA
880119 | 0855AM | ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880115 | 1510PM | 880115 | 1640PM | 900 | GAL | FASHION VALLEY RD & HOTEL CIRC | SAN DIEGO | SD | MANHOLE | GREASE & DEBRIS | NO | NONE |  |  | Y | N
880119 | 0900AM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 880116 | 1300PM | 880116 | 1600PM | 45 | GAL | 5158 EAST BEDFORD DRIVE | SAN DIEGO | SD | SEWER LINE | ROOTS | NO | NONE |  |  | Y | N
880122 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880116 | 1226PM | 880116 | 1415PM | 525 | GAL | 5104 NORTH HARBOR DRIVE | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | N | N | NA
880119 | 1045AM | PHYLLIS CHALMERS | 6192362222 | SAN DIEGO, CITY OF | 880116 | ?????? | 880116 | ?????? | 11500 | GAL | 5100 N HARBOR DR | SAN DIEGO | SD | MANHOLE | UNKNOWN BLOCKAGE | Y | SAN DIEGO BAY |  |  | Y | Y | 02 | NO SAMPLING.
880119 | 1045AM | P. CHALMERS | 6192362222 | SAN DIEGO, CITY OF | 880117 | 1700PM | 880118 | 1500PM | 108000 | GAL | PUMP STA 22/FT. OF FERN GLENN. | SAN DIEGO | SD | PUMP STATION 22 | POWER FAILURE-STORM | Y | OCEAN |  |  | Y | Y | 02 | NO SAMPLING.
880119 | 1430PM | P. CHALMERS | 6192362222 | PINE VALLEY SANITATION DIST. | 880117 | 1230PM | 880117 | ?????? | 75000 | GAL | PINE VALLEY CO. PARK | SAN DIEGO | SD | PERCOLATION BED | OVERSPILL FROM RAIN STORM IN PERCOLATION BED. | NO | NONE |  |  | Y | N | NA
880121 | LETTER | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 880118 | 0800AM | 880118 | 1120AM | 15000 | GAL | 1700 BLK W COUNTRY CLUB DR | ESCONDIDO | SD | ATLAS PG 333 MANHOLE 32 | TROUGH IN TEMPORARY MANHOLE WAS FILLED WITH ROCKS CAUSING BLOCKAGE. | NO | NONE |  |  | N | N | NA | SPILL PUMPED TO SEWER SYSTEM NEARBY.
880118 | 0800AM | ANN ERICKSON | 6194994555 | SOUTH COAST WATER DISTRICT | 880118 | ?????? | 0 | ?????? | 150 | GPH | 16 LAGUNITA | LAGUNA BEACH | OR | SEWER LINE | STORM & HIGH SURF WASHED OUT 300 TO 400 FT OF 8"SEWER LINE. | Y | OCEAN |  |  | Y | Y | ?? | WILL REPAIR AS SOON AS SURF RECEEDS.
880120 | 0920AM | ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880119 | 0958AM | 880119 | 1300PM | 2700 | GAL | BALBOA GOLF FAIRWAY #3 | SAN DIEGO | SD | MANHOLE | ROOTS & DEBRIS | NO | NONE |  |  | Y | N
880120 | 0920AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880119 | 1300PM | 880119 | 1330PM | 30 | GAL | 28TH & VALLEY PLACE | SAN DIEGO | SD | MANHOLE | GREASE & RAGS | NO | NONE |  |  | Y | N | NA
880120 | 0920AM | ARNOLD |  | SAN DIEGO, CITY OF | 880119 | 0930AM | 880119 | 1000AM | 15 | GAL | 3146 1ST AVENUE | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | Y | N | NA
880122 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880119 | 1315PM | 880119 | 1515PM | 1200 | GAL | 3511 COLLEGE AVE | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | N | N | NA
880119 | 1045AM | P. CHALMERS | 6192362222 | SAN DIEGO, CITY OF | 880119 | 0900AM | 880119 | 0930AM | 120 | GAL | ALLEY BEHIND 3599 BAYSIDE WALK | SAN DIEGO | SD | PUMP STATION 16 | MAIN BREAK | Y | SAN JUAN COVE/ MISSION BAY |  |  | Y | Y | ?? | COUNTY HEALTH SAMPLING ON 1/20/88.
880119 | 1415PM | PETER HUHN | 6197281180 | FALLBROOK SANITARY DISTRICT | 880119 | 0330AM | 880119 | 0830AM | 1500 | GAL | 2857 SO. MISSION RD. T.P. #2 | FALLBROOK | SD | EARTHEN SLUDGE BED | ANIMAL BURROW HOLE PICKED UP FLOW AS IT WAS BEING PUMPED TO THE SLUDGE BED FROM THE ANAEROBIC DIGESTOR AT TRMT PLANT #2. | Y | OSTRIECH CREEK/SAN LUIS REY RI |  |  | Y | N | NA
880120 | 0850AM | P CHALMERS | 6192362222 | SAN DIEGO, CITY OF | 880119 | 1900PM | 880120 | 0300AM | 9600 | GAL | 3139 COLLURA ST | SAN DIEGO | SD | MANHOLE | BLOCKED SEWER LINE | Y | CHOLLAS CREEK/SAN DIEGO BAY |  |  | Y | Y | 02
880120 | 1240PM | P CHALMERS | 6192362222 | SAN DIEGO, CITY OF | 880120 | 0905AM | 880120 | 1005AM | 300 | GAL | 605 SAN ELIJO ST | SAN DIEGO | SD | MANHOLE | ROOTS | Y | SAN DIEGO BAY AT ROSECRANS |  |  | Y | Y | ?? | HAZ MAT SAMPLING ON 1/21/88.
880121 | 1510PM | GARY ORR | 6194397393 | OCEANSIDE, CITY OF | 880120 | 2030PM | 880121 | 1230AM | 300000 | GAL | 3817 PLAZA DRIVE | OCEANSIDE | SD | MANHOLE | VANDALS THREW BOULDERS INTO MANHOLE. | Y | BUENA VISTA CRK/LAGOON/OCEAN |  |  | Y | Y | ?? | FISH & GAME NOTIFIED.
880122 | 1455PM | DALE HOFFLAND | 6196942132 | PINE VALLEY SANITATION DIST. | 880122 | 1000AM | 880122 | 1130AM | 100000 | GAL | PINE VALLEY TREATMENT PLANT | PINE VALLEY | SD | PERCOLATION POND #4 | WIND BLEW BOAT INTO THE FRONT OF OUTFALL PIPE BLOCKING IT AND CAUSING WATER IN PERC POND TO OVERFLOW BERM TO MEADOW. | NO | NONE |  |  | N | N | NA | SPILL WAS SECONDARY TREATED EFFLUENT.
880125 | 0830AM | DON GRIFFIN |  | SAN DIEGO, CITY OF | 880123 | 2240PM | 880124 | 0100AM | 2100 | GAL | 7595 EADS AVE | SAN DIEGO | SD | CLEANOUT | GREASE | Y | OCEAN |  |  | Y | Y | 02 | POSTED BY COUNTY HEALTH
880125 | 0845AM | DALE HOFFLAND |  | SOLANA BEACH SANITATION DIST. | 880123 | 1130AM | 880123 | 1215PM | 20000 | GAL | NORTH END OF RIO ST. | SOLANA BEACH | SD | MANHOLE | GREASE | Y | SAN ELIJO LAGOON |  |  | Y | Y | ??
880117 | 1400PM | GEORGE LONG | 6196942133 | CARDIFF SANITATION DISTRICT | 880117 | 1230PM | 880117 | 1240PM | 35000 | GAL | 2695 MANCHESTER AVE | CARDIFF | CA | ????? | POWER FAILURE & MALFUNCTION OF FRESH WATER HYDRO STATION & AUXILURY POWER CAUSING EFFLUENT PUMP STATION TO OVERFLOW. | Y | SAN ELIJO LAGOON/ OCEAN |  |  | Y | ? | ?? | SPILL WAS DURING HEAVY RAINFALL. WAS ADVANCED PRIMARY TREATED WASTEWATER.
880125 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880120 | 0800AM | 880120 | 1000AM | 600 | GAL | 32ND ST & SAN MARCOS | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
880121 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880120 | 0940AM | 880120 | 1010AM | 1500 | GAL | 6535 TAIT ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y
880122 | 1005AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880121 | 1006AM | 880121 | 1206PM | 1200 | GAL | 330 BROOKS AVE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
880126 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880122 | 1200 N | 880122 | 1300PM | 300 | GAL | 39 TH & NATIONAL AVE | SAN DIEGO | SD | MANHOLE | ROOTS & GREASE | NO | NONE |  |  | N | N | NA
880125 | 0910AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880122 | 1200 N | 880122 | 1300PM | 120 | GAL | 172 PADRE TULLIO DRIVE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
880122 | 0800AM | ???????? | 7144965261 | CAPISTRANO BEACH SANITARY DIST | 880122 | ?????? | 880122 | 0900AM | 20 | GAL | 26101 VICTORIA BLVD. | CAPISTRANO BEACH | OR | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
880126 | 0950AM | PAT HOY | 6192365241 | SAN DIEGO, CITY OF | 880125 | 0800AM | 880125 | 1300PM | 7500 | GAL | 5387 CALUMET AVE | SAN DIEGO | SD | PUMP STATION 42 | PLUGGED MAIN | Y | OCEAN |  |  | Y | Y | ?? | CITY POSTED. CITY DID NOT CALL REG. BD. OR HAZ MAT IN 24HR DEADLINE.
880125 | 0700AM | RON ROSE | 6192365534 | SAN DIEGO, CITY OF | 880125 | 0700AM | 880125 | 0745AM | 450 | GAL | 15790 AVENIDA VENUSTO | SAN DIEGO | SD | STATION 73 WET WELL | #1 PUMP IMPELLOR BROKE OFF. NO BACK UP DUE TO COLLASPED ON SUCTION LINE ON #2. | Y | POND ON GOLF COURSE. |  |  | Y | Y | ?? | WILL BE POSTED FOR 24 HOURS.
880128 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880125 | 0921AM | 880125 | 1121AM | 1200 | GAL | 4808 TROJAN AVE | SAN DIEGO | SD | CLEANOUT | GREASE & SLUDGE | NO | NONE |  |  | N | N | NA
880127 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880126 | 1130AM | 880126 | 1400PM | 1500 | GAL | 2891 BROSNAN ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y
880127 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880126 | 2240PM | 880126 | 2340PM | 600 | GAL | 3475 KENYON ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y
880126 | 1100AM | OFFICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 880126 | 1045AM | 880126 | 1115AM | 15 | GAL | 1695 HILL ST | FALLBROOK | SD | CLEANOUT | UNKNOWN | NO | NONE |  |  | N | N | NA
880128 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880127 | 1130AM | 880127 | 1230PM | 300 | GAL | 7946 IVANHOE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y
880128 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880127 | 1030AM | 880127 | 1040AM | 500 | GAL | SOLEDAD RD & LOS ALTOS WAY | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y
880130 | 0830AM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 880128 | 0930AM | 880128 | 1130AM | 60 | GAL | HERALDRY & POMEROY ST | SAN DIEGO | SD | SEWER LINE | ROCKS & DIRT | NO | NONE |  |  | Y | N | NA
880128 | 1545PM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 880128 | 1120AM | 880128 | 1140AM | 400 | GAL | 1400 MURPHY CANYON ROAD | SAN DIEGO | SD | SEWER LINE | ROCKS WHILE BUCKETING SEWER MAIN | NO | NONE |  |  | Y | N
880201 | 1040AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880128 | 1200 N | 880128 | 1230PM | 15 | GAL | 4315 HAWK ST | SAN DIEGO | SD | CLEANOUT | ROOTS | NO | NONE |  |  | Y | N
880201 | 1040AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880129 | 1800PM | 880129 | 2100PM | 360 | GAL | 4316 ROLANDO BLVD. | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N
880201 | 1040AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880129 | 0830AM | 880129 | 0900AM | 15 | GAL | 1804 JULIAN AVE | SAN DIEGO | SD | CLEANOUT | GREASE & RAGS | NO | NONE |  |  | Y | N
880204 | LETTER | HERNANDEZ | 6192367340 | SAN DIEGO, CITY OF | 880129 | 1030AM | 880129 | 1030AM | 2160 | GAL | UNIV. OF CALIF. CAMPUS | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N
880201 | 1040AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880129 | 1400PM | 880129 | 1500PM | 300 | GAL | 2900 BLK MARKET ST | SAN DIEGO | SD | CLEANOUT | ROOTS & GREASE | NO | NONE |  |  | Y | N
880204 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880130 | 0900AM | 880130 | 1000AM | 120 | GAL | 4 TH AVE & ELM ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
880201 | 1040AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880131 | 1400PM | 880131 | 1500PM | 300 | GAL | MISSION BAY & ROSEWOOD | SAN DIEGO | SD | MANHOLE | OVERLOADED SEWER MAIN | NO | NONE |  |  | Y | N
880219 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880201 | 2100PM | 880201 | 2300PM | 6000 | GAL | LINDBERGH & BLERIOT AVE | SAN DIEGO | SD | MANHOLE | UNKNOWN | NO | NONE |  |  | N | N | NA
880204 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880201 | 1030AM | 880201 | 1230PM | 240 | GAL | 708 OLIVEWOOD TERRACE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
880204 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880201 | 1230PM | 880201 | 1430PM | 1200 | GAL | BOUNDARY & HALLER | SAN DIEGO | SD | MANHOLE | DEBRIS | NO | NONE |  |  | N | N | NA
880203 | 1615PM | ALICE BENSON | 6192216626 | SAN DIEGO, CITY OF | 880202 | 2100PM | 880202 | ?????? | 10 | GAL | VAULT7 MISSION BAY SLUDGE LINE | SAN DIEGO | SD | SLUDGE LINE | COMPRESSION FITTING BROKEN | Y | PACIFIC OCEAN |  |  | Y | N | NA | NO POSTING SINCE SPILL ON NAVY PROPERTY
880203 | 0920AM | M. ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880202 | 0330AM | 880202 | 1300PM | 8550 | GAL | SAN YSIDRO BL & COTTONWOOD | SAN DIEGO | SD | MAIN BREAK | COLLAPSED MAIN | Y | TIJUANA RIVER/OCEAN |  |  | Y | Y | ?? | PREVIOUSLY POSTED. DISINFECTANT APPLIED.
880202 | 1520PM | GARY ORR | 6194397164 | OCEANSIDE, CITY OF | 880202 | 0805AM | 880202 | 0810AM | 150 | GAL | INTERSEC MESA DR & GARRISON ST | OCEANSIDE | SD | MANHOLE | CONTRACTOR CONNECTING NEW BYPASS BETWEEN 24" MAIN AND 42" MAIN. | NO | NONE |  |  | N | N | NA | COPY OF RPT SENT TO DOHS.
880202 | 1655PM | GARY ORR | 6194397393 | OCEANSIDE, CITY OF | 880202 | 1330PM | 880202 | 1500PM | 9000 | GAL | SO. PACIFIC ST PUMP STATION | OCEANSIDE | SD | MANHOLE NEAR PUMP STATION | SDGE POWER OUTAGE TO PUMP STATION. | Y | OCEAN |  |  | Y | ? | ??
880203 | 1640PM | ALICE BENSON | 6192216626 | SAN DIEGO, CITY OF | 880202 | 0900AM | 880202 | 0915AM | 3000 | GAL | ???????? | SAN DIEGO | SD | ???????? | BROKEN COUPLING IN SLUDGE LINE.MOST CONTAINED IN THE VAULT. MINOR QUANTITY REACHED OCEAN. | Y | OCEAN |  |  | Y | N | NA | PAT HOY WAS CALLED TO VERIFY PROP65 RPT MADE.
880203 | 1100AM | PETER HUHN | 6197281180 | FALLBROOK SANITARY DISTRICT | 880202 | 1200 N | 880202 | 1300PM | 97000 | GAL | 1425 SOUTH ALTURAS RD. | FALLBROOK | SD | EFFLUENT JUNCTION BOX | PRESSURE VALVE IN CALTRANS VAULT MAY HAVE FAILED. POSSIBLE MALFUNCTION OF OTHER VALVES ALONG OUTFALL PIPELINE ALSO. | Y | FALLBROOK CRK/LAKE O'NEIL |  |  | Y | N | NA | EMER. BYPASS TO CREEK CHLORINATED.
880203 | 1930PM | CHERWINK | 6192365534 | SAN DIEGO, CITY OF | 880203 | 1730PM | 880203 | 1930PM | 1200 | GAL | 5387 CALUMET | SAN DIEGO | SD | PUMP STATION 42 | PLUGGED FORCE MAIN LEADING OUT OF STATION 42. | Y | OCEAN |  |  | Y | Y | 02
880203 | 1130AM | CHERWINK | 6192365534 | SAN DIEGO, CITY OF | 880203 | 1130AM | 880203 | 1530PM | 2400 | GAL | 5387 CALUMET | SAN DIEGO | SD | PUMP STATION 42 | PLUGGED FORCE MAIN LEADING FROM STATION 42. | Y | OCEAN |  |  | Y | Y | 02
880203 | 1630PM | PAT HOY | 6192362222 | SAN DIEGO, CITY OF | 880203 | 1500PM | 880204 | 0220AM | 10000000 | MG | NEAR BERDER ON MEXICO SIDE | TIJUANA, MEXICO | MX | 42" SEWER MAIN | DOZER BROKE MAIN. SHUT DOWN PUMP STATION. DIVERTED FLOW TO STEWARTS DRAIN. I.B. CLOSED INDEF. HAZ MAT SAMPLING. | Y | T.J. RIVER/OCEAN |  |  | Y | Y | 15 | STILL POSTED 2/9/88.
880203 | 1545PM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 880203 | 0700AM | 880203 | 1100AM | 6000 | GAL | 9906 MIRA MESA BLVD. | SAN DIEGO | SD | SEWER LINE | DEBRIS BLOCKAGE | NO | NONE |  |  | Y | N | NA
880209 | LETTER | LUIS HERNANDEZ | 6192367340 | SAN DIEGO, CITY OF | 880203 | 1055AM | 880203 | 1155AM | 60 | GAL | 3285 VIA BARTOLO | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
880203 | 0210AM | JOHN BURCHAM | 6197281178 | RAINBOW MUNICIPAL WATER DIST. | 880203 | 0100AM | 880203 | 0800AM | 25000 | GAL | OLD RIVER RD & GOPHER CANYON | BONSALL | SD | LIFT STATION 2 | BUBBLER SYSTEM FAILURE CAUSED FLOODING OF DRY WELL. | Y | SAN LUIS REY RIVER/OCEAN |  |  | Y | N | NA
880205 | 0940AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880204 | 0700AM | 880204 | 1230PM | 330 | GAL | 3664 HERBERT ST | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N | NA
880208 | LETTER | LUIS HERNANDEZ | 6192732021 | SAN DIEGO, CITY OF | 880205 | 1330PM | 880205 | 1430PM | 60 | GAL | 3500 COWLY WAY | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
880208 | 0925AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880206 | 1230PM | 880206 | 1500PM | 150 | GAL | 4196 MARCWADE DR | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
880208 | 0015AM | K L COYLE | 6197253567 | USMC CAMP PENDELTON | 880208 | 0015AM | 880208 | 0019AM | 4500 | GAL | BASILONE BLVD. | CAMP PENDELTON | SD | BLDG 51050 | MECHANICAL EQUIPMENT FAILURE | NO | NONE |  |  | Y | N | NA
880208 | 2000PM | CHERWINK | 6192365534 | SAN DIEGO, CITY OF | 880208 | 1700PM | 880208 | 2000PM | 20 | GAL | 1180 COAST BLVD. | SAN DIEGO | SD | PUMP STATION 33 | PUMP FAILED TO RUN ON AUTO. | N | NONE |  |  | Y | N | NA
880208 | 1530PM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880208 | 1040AM | 880208 | 1250PM | 3250 | GAL | 4343 OCEAN BLVD. IN ALLEY | SAN DIEGO | SD | MAIN | GREASE CAUSED OVERFLOW OF 3250 GAL. MOST FLOW CAPTURED BY VACTOR. 250 GAL ENTERED OCEAN AT 700 GRAND AVE. | Y | OCEAN |  |  | Y | N | NA
880208 | 1545PM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 880208 | 1000AM | 880208 | 1200 N | 2400 | GAL | 10955 CARMEL MOUNTAIN RD | SAN DIEGO | SD | SEWER LINE | VANDALISM & SLUDGE | NO | NONE |  |  | Y | N | NA
880209 | 0800AM | SENIOR | 6192367030 | SAN DIEGO, CITY OF | 880208 | 0800AM | 880208 | 1000AM | 600 | GAL | 4090 46TH | SAN DIEGO | SD | MANHOLE | SLUDGE & GREASE | NO | NONE |  |  | Y | N | NA
880209 | 0800AM | SENIOR | 6192367030 | SAN DIEGO, CITY OF | 880208 | 1000AM | 880208 | 1200 N | 120 | GAL | 5226 LA PAZ DR | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
880209 | 0800AM | SENIOR | 6192367030 | SAN DIEGO, CITY OF | 880208 | 0900AM | 880208 | 1100AM | 120 | GAL | BOUGAINVELLE RD & ALTA VIEW | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N | NA
880209 | 0800AM | SENIOR | 6192367030 | SAN DIEGO, CITY OF | 880209 | 1000AM | 880209 | 1200 N | 600 | GAL | 2268 COMSTOCK | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | Y | N | NA
880210 | 0920AM | ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880209 | 1200 N | 880209 | 1300PM | 300 | GAL | 28TH & L STREET. | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
880210 | 0008AM | C H MENKEN | 6197253567 | USMC CAMP PENDELTON | 880210 | 000000 | 880210 | 0010AM | 2000 | GAL | ALON20 & CARNES WIRE MTN AREA | CAMP PENDELTON | SD | MANHOLE | CRUSHED SEWER LINE | NO | NONE |  |  | Y | N | NA
880210 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880210 | 0815AM | 880210 | 1015AM | 1200 | GAL | 1441 QUIVERA RD/CONSTRN SITE | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | Y | N | NA
880211 | 0900AM | RICHARD ARNOLD | 6194411658 | EL CAJON, CITY OF | 880210 | 0700AM | 880211 | 1230PM | 5500 | GAL | 700FT S/O 2681 VALLEY LAKE DR. | EL CAJON | SD | SEWER MANHOLE | DEBRIS & GREASE | Y | FANITA CHANNEL/SAN DIEGO RIVER |  |  | Y | N | NA
880211 | 1000AM | GABE SHIPLEY | 6192366092 | SAN DIEGO, CITY OF | 880210 | 2130PM | 880211 | 0130AM | 21 | GAL | 5757 COLLEGE AVE | SAN DIEGO | SD | CLEANOUT | ROOTS | NO | NONE |  |  | Y | N | NA
880211 | 1000AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880210 | 2200PM | 880211 | 0015AM | 600 | GAL | 4465 MISSION BLVD | SAN DIEGO | SD | MANHOLE | DEBRIS FROM CONTRACTORS | Y | OCEAN |  |  | Y | Y | 04
880210 | 1520PM | SENIOR | 6192367030 | SAN DIEGO, CITY OF | 880210 | 0900AM | 880210 | 1100AM | 120 | GAL | 4708 BOUNDARY ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
880210 | 1520PM | SENIOR | 6192367030 | SAN DIEGO, CITY OF | 880210 | 1330PM | 880210 | 1530PM | 120 | GAL | 5341 EL CAJON BLVD | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
880210 | 1000AM | SHIPLEY | 6192366092 | SAN DIEGO, CITY OF | 880210 | 1055AM | 880210 | 1530PM | 4000 | GAL | 3705 ROBINSON | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
880210 | 1000AM | SHIPLEY | 6192366092 | SAN DIEGO, CITY OF | 880210 | 1730PM | 880210 | 1930PM | 2250 | GAL | 3705 ROBINSON PLACE | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N | NA
880212 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880211 | 1115AM | 880211 | 1215PM | 600 | GAL | KANTOR ST & KANTOR CT | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N | NA
880216 | 1100AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880211 | 0920AM | 880211 | 1300PM | 4200 | GAL | 6TH & NUTMEG | SAN DIEGO | SD | MANHOLE | ROOTS & RAGS | NO | NONE |  |  | Y | N | NA
880211 | 1500PM | TOM BRADLEY | 7145822330 | SANTA MARGARITA WATER DISTRICT | 880211 | 1030AM | 880211 | 1130AM | 1500 | GAL | AVENIDA DE LAS FLORES & LAUREL | ??????? | OR | MANHOLE | CONSTRUCTION DEBRIS | NO | NONE |  |  | Y | N | NA
880218 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880212 | 1100AM | 880212 | 1300PM | 120 | GAL | 3551 47TH ST. | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
880216 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880212 | 1515PM | 880212 | 1615PM | 60 | GAL | 7011 LINDA VISTA RD | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
880213 | 1125AM | JEFF LEADS | 6194383941 | ENCINA WPCF | 880213 | 0115AM | 880213 | 0200AM | 140000 | GAL | AGUA HEDIONDA PUMP STATION | CARLSBAD | SD | AGUA HEDIONDA PUMP STATION | PUMP STATION PUMPING SYSTEM FAILED TO KEEP OUTPUT FLOW EQUAL TO INFLOW. | Y | AGUA HEDIONDA LAGOON/OCEAN |  |  | Y | Y | ??
880222 | 0800AM | PETER HUHN | 6197281180 | FALLBROOK SANITARY DISTRICT | 880214 | 1230PM | 880214 | 1300PM | 6700 | GAL | 1425 S. ALTURAS RD. | FALLBROOK | SD | EFFLUENT JUNCTION BOX | PRESSURE VALVE IN CALTRANS VAULT MAY HAVE FAILED.ALSO MAY HAVE BEEN OTHER RELIEF VALVES ALONG OUTFALL PIPELINE. | NO | NONE |  |  | N | N | NA | PRESSURE VALVES HAVE BEEN CLEANED.
880216 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880214 | 0930AM | 880214 | 1130AM | 1200 | GAL | 1822 ELM ST IN CANYON | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
880216 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880214 | 0945AM | 880214 | 1145AM | 1200 | GAL | SHELTER ISLAND DR. | SAN DIEGO | SD | MANHOLE | GREASE | Y | SAN DIEGO BAY/OCEAN |  |  | Y | Y | NA
880216 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880214 | 1120AM | 880214 | 0120PM | 1200 | GAL | 2ND & NUTMEG ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
880216 | 1130AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880215 | 1422PM | 880215 | 1622PM | 6000 | GAL | 4977 MONROE AVE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
880216 | 1130AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880215 | 1110AM | 880215 | 1310PM | 600 | GAL | POLK & 43RD ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
880216 | 1130AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880215 | 1110AM | 880215 | 1310PM | 600 | GAL | 3350 KEMPER ST | SAN DIEGO | SD | MANHOLE | DEBRIS | NO | NONE |  |  | Y | N | NA
880216 | 1200 N | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880216 | 0910AM | 880216 | 1110AM | 6000 | GAL | LA FRANCE & RANDALL | SAN DIEGO | SD | MANHOLE | ROOTS | Y | MISSION BAY/OCEAN |  |  | Y | Y | ??
880219 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880216 | 0800AM | 880216 | 0900AM | 300 | GAL | RHOADES RD & RHOADES ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
880217 | 0920AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880216 | 0700AM | 880216 | 0900AM | 120 | GAL | 4476 HORTENSIA | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N | NA
880218 | 0905AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880217 | 1530PM | 880217 | 1930PM | 6000 | GAL | 3104 1ST AVE | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
880222 | ????? | TOM BRADLEY | 7145822330 | SANTA MARGARITA WATER DISTRICT | 880218 | 1600PM | 880222 | 1000AM | 45000 | GAL | MARGURIUTE & LABARCA | MISSION VIEJO | OR | MANHOLE | CONSTRUCTION DEBRIS | Y | OSO CRK BARRIER/OSO RESERVOIR |  |  | Y
880223 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880218 | 0830AM | 880218 | 1130AM | 900 | GAL | 4455 FEDERAL BLVD. | SAN DIEGO | SD | CLEANOUT | ROCKS | NO | NONE |  |  | N | N | NA
880219 | 1445PM | BILL BROWN | 6197253567 | USMC CAMP PENDELTON | 880219 | 1445PM | 880219 | 1530PM | 250 | GAL | 16 & A STREET | CAMP PENDELTON | SD | BLDG 1229 | BLOCKAGE | NO | NONE |  |  | Y | N | NA
880222 | 1105AM | ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880219 | 1000AM | 880219 | 1100AM | 120 | GAL | 2030 JULIAN AVE | SAN DIEGO | SD | MANHOLE | DEBRIS/VANDALISM | NO | NONE |  |  | Y | N | NA
880222 | 1000AM | PETER HUHN | 6197281180 | FALLBROOK SANITARY DISTRICT | 880220 | 1230PM | 880220 | 1400PM | 212000 | GAL | 1425 ALTURAS RD | FALLBROOK | SD | EFFLUENT JUNCTION BOX | OUTFALL LINE BACKED UP DUE TO FAILED PRESSURE SUSTAINING VALVE IN CALTRANS VAULT OR AIR & VACUUM RELIEF VALVES IN OUTFAL | Y | FALLBROOK CRK/LAKE O'NEIL |  |  | Y | N | NA
880224 | LETTER | BEADLE | 6192366092 | SAN DIEGO, CITY OF | 880220 | 0930AM | 880220 | 1130AM | 120 | GAL | 2550 VIA BARLETTA | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
880224 | LETTER | BEADLE | 6192366092 | SAN DIEGO, CITY OF | 880220 | 0830AM | 880220 | 1230PM | 480 | GAL | 521 LOS ANGELES PLACE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
880222 | 1100AM | DICK ARNOLD | 6194411658 | EL CAJON, CITY OF | 880221 | 0930AM | 880221 | 1630PM | 420 | GAL | 550 NORTH MOLLISON | EL CAJON | SD | LATERAL CLEANOUT | UNKNOWN-PROPERTY OWNERS RESPONSIBILITY. | Y | FORRESTER CREEK |  |  | Y | N | NA
880224 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880221 | 2200PM | 880222 | 0100AM | 1200 | GAL | 4027 EL CAJON BLVD | SAN DIEGO | SD | MANHOLE | GREASE & ROCKS | NO | NONE |  |  | N | N | NA
880223 | 1545PM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 880223 | 0830AM | 880223 | 1230PM | 3600 | GAL | 10105 AVENIDA MAGNIFICA | SAN DIEGO | SD | SEWER LINE | ROCKS | NO | NONE |  |  | Y | N | NA
880226 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880223 | 0900AM | 880223 | 1000AM | 60 | GAL | REDWOOD & FELTON | SAN DIEGO | SD | MANHOLE | GREASE & SLUDGE | NO | NONE |  |  | N | N | NA
880226 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880223 | 1130AM | 880223 | 1530PM | 480 | GAL | 5240 NARANJA ST | SAN DIEGO | SD | CLEANOUT | LATERAL BLOCKAGE | N | NONE |  |  | N | N | NA
880225 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880224 | 1315PM | 880224 | 1615PM | 9000 | GAL | GLIDDEN & VIA LAS CUMBRES | SAN DIEGO | SD | MANHOLE | ROCKS | NO | NONE |  |  | Y | N | NA
880226 | 1455PM | G. SHIPLEY | 6192366092 | SAN DIEGO, CITY OF | 880225 | 0741AM | 880225 | 0910AM | 18750 | GAL | ROSECRANS BET DUMAS & CURTIS | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N | NA
880226 | 0900AM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 880225 | 0800AM | 880225 | 1000AM | 1200 | GAL | PENASQUITOS DR & ALMAZON | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N | NA
880226 | 0800AM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 880226 | 0720AM | 880226 | 0810AM | 3 | GAL | 529 EAST MISSION | FALLBROOK | SD | 4" SEWER PIPE | ROOTS | NO | NONE |  |  | N | N | NA
880227 | 1640PM | GARY ORR | 6194397393 | OCEANSIDE, CITY OF | 880227 | 0930AM | 880227 | 1300PM | 2100 | GAL | 1508 SOUTH PACIFIC ST. | OCEANSIDE | SD | MANHOLE | BLOCKAGE BY RAGS,PAPER IN 8" SEWER MAIN IN FRONT OF SAND PIPER SNACK BAR. | Y | OCEAN |  |  | Y | Y | 02
880226 | 1730PM | ALICE BENSON | 6192216626 | SAN DIEGO, CITY OF | 880226 | 1100AM | 880226 | 1103AM | 10 | GAL | 1902 GATCHELL RD. | SAN DIEGO | SD | OUTLET BOX AT HYDRO FACILITY | BURP** BLOWN GASKET AROUND SLUICE GATE IN OUTLET BOX | Y | OCEAN |  |  | Y | N | NA
880229 | 1610PM | ALICE BENSON | 6192216626 | SAN DIEGO, CITY OF | 880226 | 1800PM | 880229 | 0200AM | 10 | GAL | 1902 GATCHELL RD | SAN DIEGO | SD | OUTLET BOX AT HYDRO FACILITY | BURP** FAULTY GASKET AROUND SLUICE GATE VAULT. OUTLET BOX ALLOWED INTERMITTENT BLOW BY OF TREATED SEWAGE AT HIGH FLOW. | Y | OCEAN |  |  | Y | N | NA
880229 | 2245PM | G SHIPLEY | 6192366092 | SAN DIEGO, CITY OF | 880226 | 1000AM | 880226 | 1200 M | 600 | GAL | VIA ENCANTADORAS & VISTA LANE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
880226 | 1545PM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 880226 | 1300PM | 880226 | 1430PM | 90 | GAL | MISSION CENTER RD NEAR RIVER | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N | NA
880302 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880226 | 1130AM | 880226 | 1330PM | 600 | GAL | 4920 DEFIANCE WAY | SAN DIEGO | SD | MANHOLE | ROCKS | NO | NONE |  |  | N | N | NA
880229 | 1045AM | G SHIPLEY | 6192366092 | SAN DIEGO, CITY OF | 880227 | 1500PM | 880227 | 1600PM | 300 | GAL | 3500 BLOCK OF ORANGE AVE. | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
880229 | 1045AM | G SHIPLEY | 6192366092 | SAN DIEGO, CITY OF | 880227 | 1010PM | 880227 | 1340PM | 1200 | GAL | 2362 ADIRONDAK ROW | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
880302 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880228 | 1300PM | 880229 | 1000AM | 630 | GAL | OLD MISSION DAM 780' W/O DAM | SAN DIEGO | SD | 42" STEEL SEWER PIPE | HOLE IN PIPE | NO | NONE |  |  | N | N | NA
880303 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880229 | 1230PM | 880229 | 1530PM | 1800 | GAL | SAN MARCOS & LAUREL | SAN DIEGO | SD | MANHOLE | POSSIBLE BROKEN 6" C.P. SEWER MAIN. OTHERWISE UNKNOWN. | NO | NONE |  |  | N | N | NA
880310 | LETTER | ????? | ????? | SANTA MARGARITA WATER DISTRICT | 880224 | 1530PM | 880224 | 1930PM | 15000 | GAL | CAMINO MONTANA | RANCHO SANTA MAR | OR | SEWER LINE | LINE BROKEN BY D9 CAT BULL DOZER RIPPERS. | NO | NONE |  |  | Y | ? | ??
880301 | 0930AM | PETER HUHN | 6197281180 | FALLBROOK SANITARY DISTRICT | 880229 | 0824AM | 880229 | 0840AM | 500 | GAL | SHADY LANE LIFT STATION | FALLBROOK | SD | SHADY LANE LIFT STATION | AIR BUBBLER LOST ITS WEIGHT.AIR LINE ROSE TO SURFACE. | NO | NONE |  |  | ? | N | NA
880301 | 0905AM | ANN ERICKSON | 7144994555 | SOUTH COAST COUNTY WATER DIST. | 880301 | 0830AM | 880301 | 0855AM | 25000 | GAL | 28303 ALICIA PARKWAY | LAGUNA NIGUEL | OR | LIFT STATION AT TREATMT PLANT | POWER FAILURE AT LIFT STATION IN MOULTON NIGUEL WATER DISTRICT. | Y | ALISO CREEK/PACIFIC OCEAN |  |  | Y | Y | ?? | POSTED UNTIL CO HEALTH SAMPLES ARE WITHIN ACCEPTABLE LIMITS
880302 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880302 | 0845AM | 880302 | 1045AM | 1200 | GAL | LA JOLLA SCENIC DRIVE | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y
880303 | 0900AM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880303 | 1330PM | 880303 | 1630PM | 540 | GAL | 727 SAN LUIS OBISPO | SAN DIEGO | SD | LATERAL | ROOTS | Y | MISSION BAY/OCEAN |  |  | Y | Y | ??
880308 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880304 | 0930AM | 880304 | 1030AM | 60 | GAL | 242 CALLE GAVIOTA | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
880307 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880304 | 1300PM | 880304 | 1400PM | 1200 | GAL | GRAND AVE AT MISSION BAY H.S. | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | Y | ??
880307 | 0930AM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 880305 | 1300PM | 880305 | 1800PM | 300 | GAL | MATURIN DR & REDBUD CT | SAN DIEGO | SD | SEWER LINE | GREASE & ROCKS | NO | NONE |  |  | Y | N | NA
880306 | 1500PM | SGT. WASHINGTON | 6197254981 | USMC CAMP PENDELTON | 880306 | 1445PM | 880306 | 1510PM | 100 | GAL | HAHN COURT | CAMP PENDELTON | SD | BLDG 238 #23 | STOPPAGE | NO | NONE |  |  | Y | N
880308 | 0810AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880307 | 1240PM | 880307 | 1340PM | 300 | GAL | 3623 3RD AVE | SAN DIEGO | SD | MANHOLE | ROOTS & GREASE | NO | NONE |  |  | Y | N | NA
880307 | 0810AM | DALE HOFFLAND | 6196942130 | SPRING VALLEY SANITATION DIST. | 880306 | 1130AM | 880306 | 1330PM | 13000 | GAL | 3536 SWEETWATER SPRINGS BLVD. | SPRING VALLEY | SD | MANHOLE | GREASE & DEBRIS | NO | NONE |  | DRAINAGE DITCH | Y | Y | 05
880307 | 1500PM | GARY ORR | 6194397164 | OCEANSIDE, CITY OF | 880307 | 1130AM | 880307 | 1230PM | 4200 | GAL | 510 JONES ROAD | OCEANSIDE | SD | FLAPPER VALVE OUTLET FROM M.H. | BLOCKAGE | Y | SAN LUIS REY RIVER |  |  | Y | ? | ??
880308 | 1345PM | V.T. BRADLEY | 7145822330 | SANTA MARGARITA WATER DISTRICT | 880307 | 1700PM | 880307 | 2130PM | 45000 | GAL | 24263 COTO DE CAZA | ??????? | OR | LIFT STATION | #1 PUMP WAS INADVERTANTLY LEFT IN OFF POSITION & #2 PUMP TRIPPED OUT. | NO | NONE |  |  | Y | N | NA
880308 | 1345PM | V.T. BRADLEY | 7145822330 | SANTA MARGARITA WATER DISTRICT | 880307 | 1925PM | 880307 | 1945PM | 1000 | GAL | TRABUCO & PUERTA DE LUZ | MISSION VIEJO | OR | LIFT STATION | PUMPS FAILED TO OPERATE DUE TO BUBBLER PROBLEM | NO | NONE |  |  | Y | N | NA
880308 | 0735AM | BILL BROWN | 6197254806 | USMC CAMP PENDELTON | 880307 | 1945PM | 880308 | 0100AM | 1800 | GAL | TALEGA ROAD | CAMP PENDELTON | SD | MANHOLE | SEWER LINE BLOCKAGE | NO | NONE |  |  | Y | N
880309 | 1430PM | G SHIPLEY | 6192366092 | SAN DIEGO, CITY OF | 880309 | 0900AM | 880309 | 1100AM | 120 | GAL | 2293 SAN JUAN RD | SAN DIEGO | SD | CLEANOUT | ROOTS | NO | NONE |  |  | Y | N | NA
880310 | 1400PM | GARY ORR | 6194397164 | OCEANSIDE, CITY OF | 880309 | 2000PM | 880309 | 2015PM | 250 | GAL | 1508 SOUTH PACIFIC ST | OCEANSIDE | SD | MANHOLE | UNKNOWN BLOCKAGE | Y | LOMA ALTA SLOUGH/OCEAN |  |  | Y | Y | 02
880309 | 1425PM | V.T. BRADLEY | 7145822330 | SANTA MARGARITA WATER DISTRICT | 880309 | 0915AM | 880309 | 0935AM | 4000 | GAL | 22698 FORMENTOR | MISSION VIEJO | OR | NORTH BEACH LIFT STATION | BUBBLER SYSTEM FAILURE | Y | OSO RESERVOIR |  |  | Y | N | NA
880311 | 0905AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880310 | 1305PM | 880310 | 1435PM | 450 | GAL | 4509 DEL MONTE AVE | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N | NA
880310 | 1400PM | GARY ORR | 6194397164 | OCEANSIDE, CITY OF | 880310 | 0745AM | 880310 | 0905AM | 1600 | GAL | 1508 SOUTH PACIFIC STREET | OCEANSIDE | SD | MANHOLES | BLOCKAGE | Y | LOMA ALTA SLOUGH & LAGOON |  |  | Y | Y | 04 | MOUTH OF SLOUGH BLOCKED FROM OCEAN BY SAND BAR PRESENTLY.
880311 | 0915AM | MONICA MAZUR,OR CO H | 7148346768 | EMERALD BAY H.O.A. (TO ALISO) | 880310 | ?????? | 880310 | ?????? | 2000 | GAL | PACIFIC COAST HWY PUMP STATION | EMERALD BAY | OR | PACIFIC COAST HWY PUMP STATION | PUMP STATION SWITCH FAILURE-EMERALD BAY HOA HIRED OR. CO. PUMP CO. TOCLEAN UP. PUMP CO. DISPOSED OF SEWAGE AT BEACH | Y | OCEAN |  |  | Y | Y | 04 | COMPLAINT FILED BY WJG. ENFORCEMENT ACTION SHOULD BE TAKEN;DISPOSAL TO OCEAN INTENTIONAL.
880314 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880311 | 1215PM | 880311 | 1115PM | 600 | GAL | 760 DODGE DRIVE | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N | NA
880311 | 1400PM | ANN ERICKSON | 7144994555 | SOUTH COAST COUNTY WATER DIST. | 880311 | 1010AM | 880311 | 1002AM | 400 | GAL | 33109BEACH CLUB DRIVE | LAGUNA NIGUEL | OR | PUMP STATION | POWER AT PUMP STA. TURNED OFF BY SDGE FOR REPAIRS. STANDBY GENERATOR FAILED TO START IMMEDIATELY CAUSING 2 MIN. SPILL. | NO | NONE |  |  | Y | N
880314 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880312 | 1045AM | 880312 | 1200 N | 7500 | GAL | JAMACHA & JOANNA | SAN DIEGO | SD | MANHOLE | ROCK BLOCKAGE | NO | NONE |  |  | Y | N | NA
880316 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880312 | 1930PM | 880312 | 2030PM | 1500 | GAL | 874 SAWTELL | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
880312 | 1605PM | STA 38 DEVLIN | 6192367030 | SAN DIEGO, CITY OF | 880312 | 1230PM | 880312 | 1430PM | 1800 | GAL | GRAVILLA & LA JOLLA BLVD | SAN DIEGO | SD | MANHOLE | ROOTS & GREASE | Y | OCEAN |  |  | Y | Y | 03
880314 | 0930AM | DICK ARNOLD | 6194411658 | EL CAJON, CITY OF | 880313 | 1000AM | 880313 | 1230PM | 5200 | GAL | JACKMAN ST 300FT S/O FLET.PKWY | EL CAJON | SD | MANHOLE | GREASE | Y | FORRESTER CREEK |  |  | Y | N | NA
880316 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880314 | 1015AM | 880314 | 1115AM | 120 | GAL | 8000 JAMACHA RD | SAN DIEGO | SD | MANHOLE | ROOTS & GREASE | NO | NONE |  |  | N | N | NA
880316 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880314 | 1100AM | 880314 | 1230PM | 180 | GAL | 3891 'Z' ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
880314 | 1530PM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880314 | 1345PM | 880314 | 1445PM | 3000 | GAL | 6000 LA HERMOSA AV | SAN DIEGO | SD | MANHOLE | ROOTS | Y | OCEAN |  |  | Y | Y | ??
880316 | 1000AM | PAT HOY | 6192362222 | SAN DIEGO, CITY OF | 880314 | AM HRS | 880315 | 1500PM | 500 | GPM | STATE ST & 'C' ST | SAN DIEGO | SD | 18'SEWER MAIN | CONTRACTOR DRILLING AT EXCAVATION SITE HIT SEWER LINE. DILLINGHAM CONSTRUCTION CO. SEWAGE PONDED IN EXCAVATION SITE. | NO | NONE |  | EXCAVATION SITE/YMCA/COURT HOU | Y | N | NA | EXCAV. SITE FENCED IN & 25 FEET DEEP. CO. HEALTH RESPONDED. JOHN CROWER OF CITY CALLED WJG
880316 | LETTER | GARY ORR | 6194397164 | OCEANSIDE, CITY OF | 880315 | 1515PM | 880315 | 1845PM | 21000 | GAL | 1330 SOUTH TAIT ST | OCEANSIDE | SD | SEWER MAIN | CONTRACTOR WORKING ON LA SALINA WWTP WITH BULL DOZER RIPPED UP 15" CAST IRON SEWER MAIN. | NO | NONE |  |  | N | N | NA | FLOW TO DEEP DEPRESSIONS FROM OLD OXIDATION PONDS & STORM RUNOFF DITCHES.
880316 | 1620PM | ALICE BENSON | 6192216626 | SAN DIEGO, CITY OF | 880316 | 1430PM | 880316 | 1515PM | 100 | GAL | CATALINA BLVD ON NAVY BASE | SAN DIEGO | SD | VAULT #9 MISSION BAY SLDG LINE | FAULTY AIR VALVE | NO | NONE |  |  | Y | N | NA
880318 | 0805AM | DONN GRIFFIN |  | SAN DIEGO, CITY OF | 880317 | 0845AM | 880317 | 1015AM | 180 | GAL | 1177 KNOXVILLE ST | SAN DIEGO | SD | MANHOLE | GREASE | Y | MISSION BAY NR. FIESTA ISLAND |  |  | Y | Y | ??
880304 | 1300PM | LACKEY CONSTRUCTION | 6197285591 | FALLBROOK SANITARY DISTRICT | 880303 | 1540PM | 880303 | 1700PM | 10000 | GAL | WEST OF POTTER ST | FALLBROOK | SD | 6 INCH SEWER LINE | CONTRACTOR BROKE LINE | NO | NONE |  |  | Y | N | NA | SEWAGE SATURATED DIRT REMOVED BY CONTRACTORS.
880315 | 1000AM | STEVEN MAURER | 6194662405 | LA MESA, CITY OF | 880314 | 1200 N | 880314 | 1600PM | 100000 | GAL | NAGEL ST BRIDGE & ALVARADO CHN | LA MESA | SD | 8 INCH SEWER PIPE | CONTRACTOR ERROR WHILE EXCAVATING FOR TROLLEY LINE CONSTRUCTION. | Y | ALVARADO CHNL/SAN DIEGO RIVER |  |  | Y | Y | 03
880316 | 0835AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880315 | 1120AM | 880315 | 1320PM | 1200 | GAL | WALLACE & CALHOUN | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
880318 | LETTER | GARY ORR | 6194397164 | OCEANSIDE, CITY OF | 880317 | 1530PM | 880317 | 1630PM | 300 | GAL | END OF LORETTA ST | OCEANSIDE | SD | MANHOLE | KIDS DUMPING ROCKS INTO UPSTREAM MANHOLE | Y | SAN LUIS REY RIVER/OCEAN |  |  | Y | N
880318 | 0900AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880317 | 0932AM | 880317 | 1100AM | 900 | GAL | SAN DIEGO ZOO | SAN DIEGO | SD | MANHOLE | CONCRETE BLOCKAGE | NO | NONE |  |  | Y | N
880322 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880318 | 1930PM | 880318 | 2130PM | 3600 | GAL | 9340 CARMEL MTN. ROAD | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
880321 | 1510PM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880318 | 2300PM | 880319 | 0200AM | 180 | GAL | 425 WEST B STREET | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
880322 | 1015AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880318 | 0915AM | 880318 | 1115AM | 600 | GAL | 3700 BLK CURLEW ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
880319 | 1835PM | DUTY NCO | 6197254981 | USMC CAMP PENDELTON | 880319 | 1830PM | 880319 | 1845PM | 5 | GAL | 252 OBERLIE #2 | CAMP PENDELTON | SD | CLEANOUT | STOPPAGE | NO | NONE |  |  | Y | N | NA
880322 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880319 | 1745PM | 880319 | 1845PM | 6000 | GAL | SAN DIEGO ZOO AT HIPPO PEN | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
880322 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880319 | 1400PM | 880319 | 1500PM | 60 | GAL | 3700 BLK CURLEW ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
880321 | 1510PM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880320 | 1030PM | 880321 | 1230PM | 2400 | GAL | 5958 MADRA ST | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N
880322 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880321 | 1415PM | 880321 | 1445PM | 150 | GAL | 3714 MISSION BLVD. | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y
880322 | 1015AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880321 | 1526PM | 880321 | 1700PM | 45 | GAL | 1437 TORRENCE ST | SAN DIEGO | SD | CLEANOUT | ROOTS | NO | NONE |  |  | Y | N
880322 | 1015AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880321 | 1230PM | 880322 | 0230AM | 12 | GAL | SAN DIEGO ZOO | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N
880324 | LETTER | GARY ORR | 6194397393 | OCEANSIDE, CITY OF | 880321 | 0630AM | 880321 | 0830AM | 480 | GAL | EL CAMINO CNTRY CLUB/VISTA WAY | OCEANSIDE | SD | MANHOLE @ GREEN #3 | UNKNOWN | NO | NONE |  |  | N | N
880328 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880323 | 1930PM | 880323 | 2130PM | 120 | GAL | ESTHER ST & ADAMS AVE | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
880328 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880323 | 1720PM | 880323 | 1820PM | 60 | GAL | 4202 NATIONAL AVE | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | N | N | NA
880324 | 1030AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880323 | 1343PM | 880323 | 1513PM | 450 | GAL | HAWK & HUNTER ST (CANYON) | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N | NA
880324 | 0900AM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 880323 | 0800AM | 880323 | 1100AM | 3600 | GAL | 14340 PENASQUITOS DR. | SAN DIEGO | SD | SEWER LINE | ROCKS | NO | NONE |  |  | Y | N
880325 | 0900AM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880324 | 1500PM | 880324 | 1600PM | 600 | GAL | MISSION CNTR RD/SAN DIEGO RIVE | SAN DIEGO | SD | MANHOLE | GREASE | Y | SAN DIEGO RIVER/OCEAN |  |  | Y | Y | ??
880324 | 1315PM | GARY ORR | 6194397164 | OCEANSIDE, CITY OF | 880324 | 0915AM | 880324 | 1100AM | 420 | GAL | LORETTA ST EXTENSION | OCEANSIDE | SD | MANHOLE ALONG SIDE ROAD | KIDS DROPPING ROCKS INTO MANHOLE/POSSIBLY RELATED TO LAST WEEKS OVERFLOW WITH SAME CAUSE(?). | Y | SAN LUIS REY RIVER/OCEAN |  |  | Y | N
880330 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880325 | 2130PM | 880325 | 2330PM | 600 | GAL | 4080 CHEROKEE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
880326 | 0300AM | MARK HAMMOND | 6194397393 | OCEANSIDE, CITY OF | 880325 | 2325PM | 880326 | 0005AM | 5250 | GAL | INTSEC. MESA DR & GARRISON ST | OCEANSIDE | SD | MANHOLE | CONTRACTOR DIVERTED SEWAGE FRON 42" MAIN TO 24" MAIN THAT WAS FULL OF AIR AND HAS NO PRESSURE RELEASE VALVES. | Y | LOMA ALTA CREEK/OCEAN |  |  | Y | Y | 06
880325 | 1015AM | GARY ORR | 6194397393 | OCEANSIDE, CITY OF | 880325 | 0710AM | 880325 | 1400PM | 61500 | GAL | INTSEC OF MESA DR & GARRISON | OCEANSIDE | SD | MANHOLE | CONTRACTOR DIVERTED SEWAGE FROM 42" MAIN TO 24" MAIN THAT WAS FULL OF AIR AND HAS NO PRESSURE RELIEF VALVES. | Y | LOMA ALTA CREEK/OCEAN |  |  | Y | Y | 06 | TOOK 2 DAYS TO BLEED ALL AIR OUT OF LINE.
880328 | 0950AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880325 | 0900AM | 880325 | 1030AM | 900 | GAL | FAMOSA BL & VALETA ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | U | U | 03
880328 | 0800AM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880326 | 1110AM | 880326 | 1310PM | 600 | GAL | 4603 MISSION BLVD | SAN DIEGO | SD | MANHOLE | GREASE | Y | OCEAN |  |  | Y | Y | ??
880330 | LETTER | GARY ORR | 6194397393 | OCEANSIDE, CITY OF | 880327 | 1440PM | 880327 | 1500PM | 20 | GAL | INTSEC CARMELO ST & RIVERSIDE | OCEANSIDE | SD | PUMP STATION WET WELL | STARTER COIL ON PUMP MOTOR BURNED OUT. | NO | NONE |  |  | N | N | NA
880401 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880329 | 2000PM | 880329 | 2200PM | 120 | GAL | 5400 BLK REDLAND PLACE | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
880330 | 1110AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880329 | 0951AM | 880329 | 1151AM | 360 | GAL | MYRTLE & WILSHIRE | SAN DIEGO | SD | MANHOLE | ROOTS & GREASE | NO | NONE |  |  | Y | N
880404 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880330 | 0830AM | 880330 | 0930AM | 120 | GAL | 65TH ST & BENSON AVE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
880404 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880330 | 1230PM | 880330 | 1430PM | 120 | GAL | 5069 EL CAJON BLVD | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
880331 | 0920AM | ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880330 | 0900AM | 880330 | 1030AM | 90 | GAL | 2414 SAN DIEGO AVE | SAN DIEGO | SD | HOUSE FLOODING | GREASE | NO | NONE |  |  | Y | N | NA
880401 | 0830AM | PETER HUHN |  | FALLBROOK SANITARY DISTRICT | 880331 | 1200 M | 880401 | 0730AM | 250000 | GAL | BEACH & ASH STS. | FALLBROOK | SD | ????? | VANDALISM | Y | FALLBROOK CREEK |  |  | ? | ? | ?? | LANCE TOOK REPORT.
880401 | 0800AM | GARY ORR | 6194397393 | OCEANSIDE, CITY OF | 880331 | 2344PM | 880331 | 2359PM | 3000 | GAL | INTSEC MESA DR & GARRISON ST | OCEANSIDE | SD | MANHOLE | CONTRACTOR MAKING CONNECTIONS TO NEW 42" MAIN MADE QUESTIONABLE DECISIONS. RESULT:INSUFFICIENT FLOW CAPACITY IN LINE. | Y | LOMA ALTA CREEK/OCEAN |  |  | Y | Y | 04 | AREA POSTED FROM PREVIOUS SPILLS OF 6 DAYS AGO.
880401 | 0830AM | PETER HUHN | 6197281180 | FALLBROOK SANITARY DISTRICT | 880401 | 0715AM | 880401 | 0730AM | 50000 | GAL | BETWEEN BEACH & ASH STREETS | FALLBROOK | SD | MANHOLE | VANDALISM | Y | FALLBROOK CRK/LAKE O'NEIL |  |  | Y | Y | 03
880401 | LETTER | ANSWERING SEVICE |  | SAN MARCOS COUNTY WATER DIST. | 880401 | 0530AM | 880401 | 1030AM | 1000 | GAL | VINEYARD AVE | SAN MARCOS | SD | MANHOLE | ROPE FROM CONSTRUCTION AREA LEFT IN LINE CAUSING BLOCKAGE. | NO | NONE |  |  | N | N | NA
880404 | 1030AM | JACK J WILLIAMS | 6192366092 | SAN DIEGO, CITY OF | 880401 | 2125PM | 880401 | 2325PM | 120 | GAL | 2222 SUNSET CLIFFS BLVD | SAN DIEGO | SD | ????? | GREASE | NO | NONE |  |  | Y | N | NA | AREA ZEPPED
880404 | 1045AM | JACK WILLIAMS | 6192366092 | SAN DIEGO, CITY OF | 880401 | 1745PM | 880401 | 2015PM | 750 | GAL | 4348 COPELAND AVE | SAN DIEGO | SD | MANHOLE | GREASE & DEBRIS | NO | NONE |  |  | Y | N
880404 | 1100AM | JACK WILLIAMS | 6192366092 | SAN DIEGO, CITY OF | 880402 | 1033AM | 880402 | 1400PM | 5250 | GAL | 3540 ACKWORTH AVE | SAN DIEGO | CA | MANHOLE | GREASE & DEBRIS | NO | NONE |  |  | Y | N | NA
880403 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880403 | 1150AM | 880403 | 1250PM | 6000 | GAL | 7137 JAMACHA RD | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | Y | ??
880412 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880404 | 0830AM | 880405 | 1230PM | 14400 | GAL | 7120 BULLOCK DR | SAN DIEGO | SD | MANHOLE | ROCKS & DEBRIS | NO | NONE |  |  | N | N | NA
880412 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880405 | 1030AM | 880405 | 1530PM | 3600 | GAL | 1777 BAYVIEW HGTS RD | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
880406 | 0715AM | BILL BROWN | 6197253567 | USMC CAMP PENDELTON | 880405 | 1800PM | 880406 | 0800AM | 20000 | GAL | BASILONE ROAD | CAMP PENDELTON | SD | SEWAGE LIFT STA/BLDG 51049 | ELECTRICAL POWER CUT OFF BY SDGE FOR REPAIRS | NO | NONE |  |  | Y | N | NA
880405 | 0830AM | ANN ERICKSON | 7144994555 | SOUTH COAST WATER DIST | 880405 | ????AM | 880405 | ????AM | 1000 | GAL | PACIFIC COAST HWY & 3 ARCH BAY | SOUTH LAGUNA | OR | 8" SEWER PIPE | LINE PLUGGED | NO | NONE |  |  | Y | N | NA
880411 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880406 | 1530PM | 880406 | 1730PM | 120 | GAL | 2020 31 STREET | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
880408 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880407 | 0640PM | 880407 | 0740PM | 1200 | GAL | 5200 MONTEZUMA RD | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y
880408 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880407 | 0715PM | 880407 | 0815PM | 360 | GAL | 2861 BROSNAN ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
880413 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880408 | 0700AM | 880408 | 0830AM | 270 | GAL | 6424 POTOMAC ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
880411 | 0900AM | JIM MCCURLY | 6195789772 | SAN DIEGO, CITY OF | 880409 | 2000PM | 880410 | 1800PM | 2640 | GAL | 3737 WIGHTMAN ST | SAN DIEGO | SD | SEWER LINE | MANHOLE | NO | NONE |  |  | Y | N | NA
880413 | 1145AM | JIM MCCURLY | 6195789772 | SAN DIEGO, CITY OF | 880412 | 1900PM | 880413 | 0700AM | 720 | GAL | 950 HOTEL CIRCLE | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N | NA
880413 | 1230PM | PATTI PLATT | 6197288319 | FALLBROOK SANITARY DISTRICT | 880412 | 1130AM | 880412 | 1145AM | 10 | GAL | 140 EAST KALMIA | FALLBROOK | SD | CLEANOUT | ROOTS | NO | NONE |  |  | N | N | NA
880412 | ?????? | PETER HUHN | 6197281180 | FALLBROOK SANITARY DISTRICT | 880412 | 0650AM | 880412 | 0700AM | 100 | GAL | 1425 S. ALTURAS | FALLBROOK | SD | LIFT STATION 5 | FLOAT GOT HUNG UP | NO | NONE |  |  | N | N | NA | LIFT STA LOCATED AT PLANT 1
880413 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880413 | 0800AM | 880413 | 0820AM | 200 | GAL | AMITY & PENDELTON ST | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N | NA
880413 | 0830AM | MR SIMMONS | 6197254773 | USMC CAMP PENDELTON | 880413 | 0800AM | 880413 | 1030AM | 100 | GAL | E STREET BLDG 11032 | CAMP PENDELTON | SD | MANHOLE | LINE PLUGGED | NO | NONE |  |  | Y | N | NA
880413 | 1530PM | FELIX DACOBO | 6197253567 | USMC CAMP PENDELTON | 880413 | 1330PM | 880413 | 1400PM | 5000 | GAL | VANDERGRIFT AVE BLDG 12109 | CAMP PENDELTON | SD | LIFT STATION | MECHANICAL FAILURE | Y | SANTA MARGARITA RIVER |  |  | Y
880418 | 0800AM | SENIOR | 6192367030 | SAN DIEGO, CITY OF | 880415 | 1000AM | 880415 | 1200 N | 240 | GAL | 555 FERGUS ST | SAN DIEGO | SD | CLEANOUT | ROOTS | NO | NONE |  |  | Y | N
880415 | LETTER | GARY ORR | 6194397393 | OCEANSIDE, CITY OF | 880415 | 1100AM | 880415 | 1145AM | 4500 | GAL | 4706 CANNON RD | OCEANSIDE | SD | LEISURE VILLAGE PUMP STA. #1 | POWER OUTAGE IN AREA.WHEN EMERGENCY POWER CAME ON, PUMP #3 DID NOT AND WET WELL OVERFLOWED. | NO | NONE |  |  | N | N | NA | THOM BROS 15-A-4.
880418 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880416 | 1200 N | 880416 | 1500PM | 9000 | GAL | 2100 ALTO VIEW DRIVE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
880417 | 1100AM | CINDI ZEIGLER | 6195617652 | SPRING VALLEY SANITATION DIST. | 880417 | 1100AM | 880417 | 1500PM | 5000 | GAL | 4100 CONRAD DR | SPRING VALLEY | SD | 8" LINE | ROOTS | NO | NONE |  |  | N | N | NA
880418 | 1530PM | PAT HOY | 6102365219 | SAN DIEGO, CITY OF | 880417 | 1830PM | 8804 | ?????? | 25 | GPM | BERNARDO HGTS GOLF COURSE | SAN DIEGO | SD | PUMP STATION 73 | BROKEN FORCE MAIN.****NOTE THAT VOLUME IS IN GPM, NOT TOTAL VOLUME.** | Y | POND ON GOLF COURSE |  |  | Y | N | NA | PRIVATE COUNTRY CLUB-GOLF COURSE.
880420 | 1125AM | TOM BRADLEY | 7145822330 | SANTA MARGARITA WATER DISTRICT | 880419 | 1700PM | 880419 | 2000PM | 2000 | GAL | 27142 SOLEDAD | MISSION VIEJO | OR | MANHOLE | ROOTS & DEBRIS | NO | NONE |  |  | Y | N
880420 | 1445PM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880420 | 1030AM | 880420 | 1300PM | 75000 | GAL | ROSEWOOD & MISSION BAY DR | SAN DIEGO | SD | MANHOLE | OVERLOADED MAIN DUE TO RAIN INFILTRATION AND OPEN INTERCEPTORS. | Y | DE ANZA COVE/ MISSION BAY |  | OCEAN | Y | Y | ??
880420 | 0930AM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880421 | 1000AM | 880421 | 1300PM | 5400 | GAL | 7217 COURTNEY DRIVE | SAN DIEGO | SD | MANHOLE | OVERLOADED MAIN | Y | SAN DIEGO RIVER/OCEAN |  |  | Y | N | NA
880421 | 1340PM | CHARLES GOODMAN | 6192367340 | SAN DIEGO, CITY OF | 880421 | 1000AM | 880421 | 1330PM | 105000 | GAL | MISSION BAY DR AT ROSEWOOD ST | SAN DIEGO | SD | MANHOLE | MAIN OVERLOAD | Y | MISSION BAY/OCEAN |  |  | Y | Y | ??
880422 | 0815AM | JAY SENIOR | 6192367030 | SAN DIEGO, CITY OF | 880421 | 0900AM | 880421 | 1100AM | 240 | GAL | 3300 REDWOOD | SAN DIEGO | SD | MANHOLE | HEAVY GREASE | NO | NONE |  |  | Y | N
880422 | 1430PM | D. GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880422 | 0940AM | 880422 | 1240PM | 90000 | GAL | ROSEWOOD & MISSION BAY DRIVE | SAN DIEGO | SD | MANHOLE | INFILTRATION OF RAIN | Y | DE ANZA COVE/MISSION BAY/OCEAN |  |  | Y | Y | ??
880425 | 0900AM | JIM MCCURLEY | 6195789772 | SAN DIEGO, CITY OF | 880422 | 1530PM | 880422 | 1730PM | 120 | GAL | 10942 BARBADOS WAY | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | ?
880425 | 0900AM | JIM MCCURLY | 6195789772 | SAN DIEGO, CITY OF | 880422 | 1930PM | 880422 | 2030PM | 0 | ??? | 2124 FROUD ST | SAN DIEGO | SD | SEWER LINE | GREASE & ROOTS | NO | NONE |  |  | Y
880423 | 1025AM | V T BRADLEY | 7145822330 | SANTA MARGARITA WATER DISTRICT | 880422 | 0900AM | 880422 | 1000AM | 10000 | GAL | 27656 CAMDEN | MISSION VIEJO | OR | FELIPE LIFT STATION | STATION FLOODED | NO | NONE |  |  | Y | N
880504 | 1400PM | PETER HUHN | 7197281180 | FALLBROOK SANITARY DISTRICT | 880421 | ?????? | 880422 | 0700AM | 184000 | GAL | N BOUND ON HILL ST RAMP AT I-5 | OCEANSIDE | SD | CALTRANS RECLAMATION IRRIG SYS | BROKEN LINE | Y | SAN LUIS REY RIVER/OCEAN |  |  | Y | N
880502 | 1000AM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 880423 | 0930AM | 880423 | 1020AM | 10 | GAL | E. KALMIA | FALLBROOK | SD | 4 INCH PIPE | ROOTS | NO | NONE |  |  | N | N
880427 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880424 | 0900AM | 880424 | 1100AM | 1200 | GAL | 5244 & 5248 WIGHTMAN | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
880425 | 0900AM | JIM MCCURLY | 6195789772 | SAN DIEGO, CITY OF | 880424 | 2100PM | 880424 | 2200PM | 600 | GAL | 39TH & LANDIS ST | SAN DIEGO | SD | SEWER LINE | ROOTS | NO | NONE |  |  | Y | N
880425 | 0830AM | G L ANDERSON | 6195227380 | CORONADO, CITY OF | 880425 | 0700AM | 880425 | 0830AM | 2700 | GAL | ADMIRALITY CROSS & THE POINT | CORONADO | SD | PUMP STATION | INLET LINE TO STATION PLUGGED. | Y | SAN DIEGO BAY/OCEAN |  |  | Y | Y | ??
880429 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880425 | 0910AM | 880425 | 1010AM | 300 | GAL | 4608 BANCROFT IN ALLEY | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N | NA
880427 | 0900AM | JIM MCCURLY | 6195789772 | SAN DIEGO, CITY OF | 880426 | 2300PM | 880426 | 2400PM | 60 | GAL | 5424 GENEVA ST | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N
880427 | 0900AM | JIM MCCURLY | 6195789772 | SAN DIEGO, CITY OF | 880426 | 0900AM | 880426 | 0930AM | 600 | GAL | CANYON LAKE DR & PINETREE DR | SAN DIEGO | SD | SEWER LINE | DEBRIS | NO | NONE |  |  | Y | N
880502 | 1000AM | HOME OWNER | 6197288319 | FALLBROOK SANITARY DISTRICT | 880427 | 1050AM | 880427 | 1157AM | 10 | GAL | 233 E. DOUGHERTY | FALLBROOK | SD | 4 INCH CLEANOUT | ROOTS | NO | NONE |  |  | N | N
880428 | 1100AM | TOM BRADLEY | 7145822330 | SANTA MARGARITA WATER DISTRICT | 880428 | 0805AM | 880428 | 1000AM | 1000 | GAL | CIPRES | MISSION VIEJO | OR | MANHOLE | ASPHALT IN MANHOLE | NO | NONE |  |  | Y | N
880509 | LETTER | GLENN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 880428 | 0500PM | 880429 | 0830AM | 15000 | GAL | 1100 FT N/O 1695 HAMILTON LANE | ESCONDIDO | SD | 6 INCH FORCE MAIN FROM PS 9 | CONTRACTOR HIT MAIN WHILE GRADING. | NO | NONE |  |  | N | N
880429 | 1300PM | PETER HUHN | 6197281180 | FALLBROOK SANITARY DISTRICT | 880428 | 1030AM | 880428 | 1045AM | 500 | GAL | 1425 ALTURAS | FALLBROOK | SD | CONCRETE SLUDGE BED UNDERDRAIN | BLOCKAGE | NO | NONE |  |  | N | N
880429 | 1330PM | PETER HUHN | 6197281180 | FALLBROOK SANITARY DISTRICT | 880428 | 1510PM | 880428 | 1540PM | 29000 | GAL | 1425 ALTURAS (PLANT 1) | FALLBROOK | SD | PRIMARY CLARIFIER | WIRING SHORT | NO | NONE |  |  | N | N
880503 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880428 | 1330PM | 880428 | 1530PM | 120 | GAL | 2021 30TH ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N
880503 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880428 | 2000PM | 880428 | 2400PM | 1200 | GAL | 9631 DISTRIBUTION AVE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N
880503 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880428 | 1900PM | 880428 | 2100PM | 240 | GAL | 3072 SUNCREST DR | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | N | N | NA
880502 | 1145AM | PETER HUHN | 6197288340 | FALLBROOK SANITARY DISTRICT | 880429 | 1500PM | 880429 | 1515PM | 15000 | GAL | 1425 S ALTURAS | FALLBROOK | SD | PRIMARY CLARIFIER | WIRE SHORT | NO | NONE |  |  | N | N | NA
880502 | 0830PM | STEVEN MAURER | 6194662405 | SAN DIEGO, CITY OF | 880501 | 2000PM | 880502 | 1700PM | 1200000 | GAL | ALVARADO DRAINAGE CHANNEL | LA MESA | SD | 12INCH CLAY SEWER MAIN | CONTRACTOR WORKING IN AREA KNOCKED MANHOLE LOOSE & ROCKS FILLED MAIN & MANHOLE | Y | SAN DIEGO RIVER |  |  | N | Y | 03
880502 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880501 | 1800PM | 880502 | 0500AM | 660 | GAL | AVE DE LOS LOBOS | SAN DIEGO | SD | MANHOLE | DIRT & ROCKS | NO | NONE |  |  | Y
880502 | 1600PM | J WILLIAMS | 6192366092 | SAN DIEGO, CITY OF | 880502 | 1400PM | 880502 | 1600PM | 600 | GAL | 314 SAN ELIJO ST | SAN DIEGO | SD | MANHOLE | GREASE | Y | SAN DIEGO BAY AT KELLOGG ST. |  |  | Y | Y | 03
880502 | 0945AM | PAUL WILSON | 6197281180 | FALLBROOK SANITARY DISTRICT | 880502 | 0945AM | 880502 | 1015AM | 500 | GAL | DOUGLAS DR AT SAN LUIS REY BRG | OCEANSIDE | SD | AIR/VACUUM RELIEF VALVE/OUTFAL | VANDAL OPENED 1/2 INCH DRAIN VALVE ON ASSEMBLY WHILE UNIT WAS IN SERVICE. | NO | NONE |  |  | N | N | NA | WATER WAS SECO EFFL.
880503 | 1530PM | JIM MCCURLY | 6195789772 | SAN DIEGO, CITY OF | 880503 | 0900AM | 880503 | 1000AM | 60 | GAL | 10761 CARIUTO CT. | SAN DIEGO | SD | SEWER LINE | GREASE/ROOTS | NO | NONE |  |  | Y | N
880509 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880503 | 2300PM | 880504 | 0500AM | 1800 | GAL | CANYON W/O 111 W PENNSYLVANIA | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y
880507 | 1245PM | BOB CESARZ | 6196966014 | SAN DIEGO, CITY OF | 880504 | 1200 N | 880506 | 1200 N | 2000 | GAL | 8TH ST & I-5 | NATIONAL CITY | SD | MANHOLE SURCHARGED | LINE BLOCKAGE | Y | PUELLITA CRK/SAN DIEGO BAY |  |  | Y | N
880504 | 0500AM | KEN COYLE | 6197253567 | USMC CAMP PENDELTON | 880504 | 0800AM | 880504 | 0902AM | 500 | GAL | LIFT STA. AT BLDG 22188 | CAMP PENDELTON | SD | LIFT STATION | MECHANICAL EQUIPMENT FAILURE | NO | NONE |  |  | Y | N
880505 | 1130AM | PATTI PLATT | 6197288319 | FALLBROOK SANITARY DISTRICT | 880505 | 0905AM | 880505 | 0920AM | 25 | GAL | 232 E. KALMIA | FALLBROOK | SD | CLEANOUT | ROOTS | NO | NONE |  |  | N | N | NA
880505 | 1540PM | DEL HERNANDEZ |  | SAN DIEGO, CITY OF | 880505 | 0830AM | 880505 | 1400PM | 16500 | GAL | 15790 AVENIDA VENUSTO | SAN DIEGO | SD | FORCE MAIN | MAIN BREAK | Y | POND ON GOLF COURSE |  |  | Y | Y | ??
880505 | 1510PM | KEN SIMON |  | VALLEY CENTER MUN WATER DIST | 880505 | 1000AM | 880505 | ?????? | 250000 | GPD | MOOSA CANYON TRMT PLANT |  | SD | EFFLUENT LINE | BROKEN METER | ?? | ????? |  |  | Y | N
880510 | 1250AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880506 | 1430PM | 880506 | 1630PM | 1200 | GAL | 3821 SPORTS ARENA | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
880506 | 0830AM | RON ROSE | 6192365534 | SAN DIEGO, CITY OF | 880506 | 0830AM | 880506 | 1400PM | 16500 | GAL | 15790 AVENIDA VENUSTO | RANCHO BERNARDO | SD | WET WELL | BROKEN FORCE MAIN | Y | POND ON GOLF COURSE |  |  | Y | Y | 05
880510 | 1250AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880506 | 1130AM | 880506 | 1230PM | 180 | GAL | 2359 AIRLANE RD | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
880510 | 1250AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880507 | 1000AM | 880507 | 1100AM | 60 | GAL | 1551 SHELTER ISLAND DR | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
880511 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880507 | 1800PM | 880507 | 1900PM | 60 | GAL | 970 WEST MUIRLAND DR | SAN DIEGO | SD | CLEANOUT | ROOTS | NO | NONE |  |  | N | N | NA
880510 | 1250PM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880508 | 1330PM | 880508 | 1530PM | 1200 | GAL | 6507 TAIT ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
880508 | 0625PM | NCPD | 6193364455 | NATIONAL CITY, CITY OF | 880508 | 1800PM | 880508 | 1900PM | 400 | GAL | 800 BLK SO. EUCLID AVE | NATIONAL CITY | SD | MANHOLE NUMBER 1402 | ROOT GROWTH IN MAIN | NO | NONE |  |  | N | N
880512 | 0905AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880511 | 0800AM | 880511 | 0900AM | 180 | GAL | 3RD & BROOKS | SAN DIEGO | SD | MANHOLE | ROOTS/GREASE | NO | NONE |  |  | Y | N
880512 | 1530PM | KEN COYLE | 6197253567 | USMC CAMP PENDELTON | 880512 | 0400AM | 880512 | 0845AM | 50 | GAL | MESS HALL-BLDG 1283 | CAMP PENDELTON | SD | BLDG 1283 CLEANOUT | CLEANOUT BLOCKAGE | NO | NONE
880512 | 1530PM | KEN COYLE | 6197253567 | USMC CAMP PENDELTON | 880511 | 1800PM | 880512 | 1330PM | 50000 | GAL | NEAR TRIPLE LAKES | CAMP PENDELTON | SD | LIFT STATION | ELECTRICAL PROBLEM-OLD EQUIPMENT | NO | NONE |  |  | Y | N
880511 | 1430PM | JOHN BURCHAM | 6197281178 | RAINBOW MUNICIPAL WATER DIST. | 880511 | 0730AM | 880511 | 1230PM | 1000 | GAL | CAMINO DEL CIELO | BONSALL | SD | MANHOLE NO. 3 | PLUG CAME OUT OF LINE UNDER CONSTRUCTION & LODGED IN MAIN. | Y | SAN LUIS REY RIVER |  |  | Y | N
880513 | 1015AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880512 | 2130PM | 880513 | 0130AM | 6000 | GAL | 6442 CAM LISTO | SAN DIEGO | SD | MANHOLE | ROOTS/GREASE | NO | NONE |  |  | Y | N
880513 | 1015AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880512 | 0800AM | 880512 | 1400PM | 21600 | GAL | 4282 WHITTIER ST | SAN DIEGO | SD | MANHOLE | DEBRIS | Y | SAN DIEGO FLOOD CHANNEL |  |  | Y | Y | 04
880513 | 0800AM | SENIOR | 6192367030 | SAN DIEGO, CITY OF | 880512 | 0700AM | 880512 | 0900AM | 360 | GAL | 8746 COMPLEX DR | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
880513 | 1000AM | BRADLEY | 7145822330 | SANTA MARGARITA WATER DISTRICT | 880512 | 1200 N | 880512 | 1500PM | 5000 | GAL | END OF MONTANA | RANCHO SANTA MAR | OR | SEWER LINE | CONTRACTOR BROKE LINE | NO | NONE |  |  | Y
880513 | 1600PM | KEN COYLE |  | USMC CAMP PENDELTON | 880513 | 1400PM | 880513 | 1500PM | 100 | GAL | LAS PULGAS AREA | CAMP PENDELTON | SD | CLEANOUT AT BLDG 43354 | STOPPAGE | NO | NONE |  |  | ? | N | NA
880517 | 0855AM | ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880514 | 1830PM | 880514 | 2000PM | 270 | GAL | 4100 FLORIDA ST | SAN DIEGO | SD | MANHOLE | ROOTS/GREASE | NO | NONE |  |  | Y | N
880517 | 0855AM | ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880514 | 2100PM | 880514 | 2200PM | 30 | GAL | 6900 NAVAJO RD | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | Y | N
880518 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880515 | 1230PM | 880515 | 1530PM | 540 | GAL | 5476 REBOLLA LN | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
880506 | 1000AM | KEN SIMON | 6197491600 | VALLEY CENTER MWD | 880506 | 1000AM | 880506 | ?????? | 10000 | GAL | LOWER MOOSA CANYON FACILITY | VALLEY CENTER | SD | ????? | BLOCKED EFFLUENT METER | NO | NONE |  |  | ? | ? | ??
880516 | 0930AM | BOB MANRY |  | RANCHO CALIF. WATER DISTRICT | 880514 | ?????? | 880514 | ?????? | 15000 | GAL | INTSEC. CLINTON KEITH/CALLE OS | TEMECULA | RI | FORCE MAIN | CONTRACTOR BROKE AIR RELIEF LINE ON 12 INCH EFFLUENT FORCE MAIN TO BEAR CREEK GOLF COURSE IRRIGATION MIX TANK. | NO | NONE |  |  | Y | N | NA
880518 | 0800AM | SENIOR | 6192367030 | SAN DIEGO, CITY OF | 880517 | 1845PM | 880517 | 2145PM | 3600 | GAL | 3800 LANDIS ST | SAN DIEGO | SD | MANHOLE | VANDALISM | NO | NONE |  |  | Y
880518 | 0800AM | SENIOR | 6192367030 | SAN DIEGO, CITY OF | 880517 | 0730AM | 880517 | 0930AM | 1200 | GAL | 6255 RADIO DR | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N
880518 | 0900AM | JIM MCCURLY | 6195789772 | SAN DIEGO, CITY OF | 880517 | 1100AM | 880517 | 1300PM | 360 | GAL | 4672 35TH ST IN ALLEY | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N
880518 | 1030AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880517 | 0840AM | 880517 | 0940AM | 300 | GAL | 4300 MARCWADE ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
880519 | 1150AM | ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880518 | 0800AM | 880518 | 1100AM | 1800 | GAL | BANNING & WHITTIER | SAN DIEGO | SD | MANHOLE | ROCKS & SLUDGE | NO | NONE |  |  | Y | Y | 04
880519 |  | GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880518 | 0930AM | 880518 | 0945AM | 75 | GAL | 5000 SOLEDAD MTN. ROAD | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y
880519 |  | GRIFFIN |  | SAN DIEGO, CITY OF | 880518 | 1200 N | 880518 | 1245PM | 450 | GAL | PARKING LOT-7901 FROST ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y
880524 | LETTER | SAM NICOSIA | 6197553294 | DEL MAR, CITY OF | 880518 | 0830PM | 880518 | 1000PM | 50 | GAL | 9TH ST & CAMINO DEL MAR | DEL MAR | SD | SEWER MAIN | GREASE | NO | NONE |  |  | ?
880519 | 0100AM |  | 6197253645 | USMC CAMP PENDELTON | 880519 | 0800AM | 880519 | 1015AM | 500 | GAL | BLDG 2483/POWDER MAGAZINE ROAD | CAMP PENDELTON | SD | CLEANOUT BELOW BARRACKS | SLIME STOPPAGE | NO | NONE |  |  | Y | N
880519 | 0640AM | ALLEN KENT | 6194619389 | SPRING VALLEY SANITATION DIST. | 880519 | 0640AM | 880519 | 0730AM | 2000 | GAL | 5823 LAMAR ST | SPRING VALLEY | SD | MAIN | ROCKS & ROOTS | Y | SPRING VALLEY CREEK |  |  | Y | Y | 02 | CHLORINATED.
880519 | 0315AM | ROSADO | 6194628504 | SPRING VALLEY SANITATION DIST. | 880519 | 0315AM | 880519 | 0325AM | 4000 | GAL | THOMAS BROS. 67-D4 | SPRING VALLEY | SD | MAIN | CONTRACTOR DIVERTING FLOW, PLUG BROKE BLOCKING FLOW OUT OF MH 7. | Y | SWEETWATER RIVER |  |  | Y | N | NA | PART OF FLOW TO RIVER. CHLORINATION & SAMPLING.
880526 |  | GRIFFIN |  | SAN DIEGO, CITY OF | 880520 | 0745PM | 880520 | 0945PM | 1200 | GAL | BEHIND 4251 FOSTER | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y
880523 | 0800AM | ANN ERICKSON | 7144994555 | SOUTH COAST WATER DISTRICT | 880521 | 1205PM | 880522 | 1100AM | 1000000 | GAL | 515 FOREST AVE | LAGUNA BEACH | OR | PUMP STATION | FUSE CONTROLLING ALARMS WENT OUT. NO ALARMS WERE SENT. SEWAGE FLOWED INTO SEWER & INTO OUTFALL. | Y | OCEAN |  |  | Y | Y | ??
880523 | 1000AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880521 | 0900AM | 880521 | 1200 N | 35 | GAL | 999 SOUTH 43RD ST | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
880523 | 1000AM | M ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880521 | 0900AM | 880521 | 1030AM | 1800 | GAL | 28TH ST & COMMERCIAL | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
880521 | 1045AM | NATIONAL CITY POLICE | 6193364455 | NATIONAL CITY, CITY OF | 880521 | 1045AM | 880521 | 1330PM | 4000 | GAL | 8TH ST 400 BLOCK EASEMENT | NATIONAL CITY | SD | MANHOLE NOS. 817-830-816-0 | SOURCE UNKNOWN NO SPIGOT END AVAILIBLE | Y | CHANNEL/SAN DIEGO BAY |  |  | N | N
880526 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880522 | 1600PM | 880523 | 1140AM | 1140 | GAL | 4314 BONILLO DR | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
880526 |  | GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880522 | 1530PM | 880522 | 1940PM | 240 | GAL | 4314 BONILLO | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y
880526 |  | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880522 | 1255PM | 880522 | 1455PM | 2400 | GAL | AMPUDIA & WHITMAN | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y
880525 |  | GARY ORR | 6194397393 | OCEANSIDE, CITY OF | 880524 | 1330PM | 880524 | 1400PM | 250 | GAL | LORETTA ST. EXTENSION | OCEANSIDE | SD | MANHOLE ALONGSIDE ROAD | SOMEONE DROPPED DEBRIS INTO MANHOLE | Y | SAN LUIS REY RIVER/OCEAN |  |  | N | N | NA
880526 |  | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880524 | 0830AM | 880524 | 0930AM | 3000 | GAL | MISSION CENTER RD & S.D. RIVER | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y
880527 | 0810AM | LARRY MONTOYA | 7144965261 | CAPISTRANO BEACH SANITARY DIST | 880527 | 0800AM | 880527 | 1000AM | 100 | GAL | CALIFORIA & VIA CATALINA | CAPISTRANO BEACH | OR | MANHOLE | GREASE | NO | NONE |  |  | Y | N | NA
880602 |  | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880528 | 1400PM | 880528 | 2200PM | 480 | GAL | 4469 REVILLO DRIVE | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
880602 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880528 | 1245PM | 880528 | 1445PM | 1200 | GAL | SAN DIEGO ZOO-HIPPO PENS | SAN DIEGO | SD | MANHOLE | DEBRIS FROM FEED | NO | NONE |  |  | N | N | NA
880531 | 0900AM | HOLODNAK | 6195789772 | SAN DIEGO, CITY OF | 880528 | 0900AM | 880528 | 1400PM | 600 | GAL | 4267 33RD ST | SAN DIEGO | SD | SEWER MAIN | GREASE | NO | NONE |  |  | Y | N | NA
880531 | 0900AM | HOLODNAK | 6195789772 | SAN DIEGO, CITY OF | 880528 | 1400PM | 880528 | 1700PM | 2700 | GAL | ADOLPHIA ST AT MORAN WAY | SAN DIEGO | SD | SEWER MAIN | ROCKS & DIRT | NO | NONE |  |  | N | N | NA
880531 | 0900AM | HOLODNAK | 6195789772 | SAN DIEGO, CITY OF | 880528 | 0800AM | 880528 | 1000AM | 3600 | GAL | DANA LANDING BOAT LAUNCH | SAN DIEGO | SD | SEWER MAIN | GREASE | Y | MISSION BAY |  |  | Y | Y | 04
880602 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880529 | 1915PM | 880530 | 0315PM | 2400 | GAL | 13084 POLVERA AVE | SAN DIEGO | SD | PRIVATE PUMP STATION | PUMP STOPPED RUNNING | Y | SYCAMORE CREEK -LAKE HODGES |  |  | Y | N | NA
880602 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880529 | 1630PM | 880529 | 1830PM | 1800 | GAL | 3404 CHEROKEE | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N
880602 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880529 | 1145PM | 880529 | 1345PM | 1200 | GAL | SAN DIEGO ZOO/HIPPO PENS | SAN DIEGO | SD | MANHOLE | ANIMAL WASTE | NO | NONE |  |  | N | N | NA
880531 | 0930AM | DALE HOFFLAND | 6196942132 | BUENA SANITATION DISTRICT | 880530 | 1000AM | 880530 | 1130AM | 2000 | GAL | LIVE OAK RD/SHDW RDG GOLF CRSE | VISTA | SD | MANHOLE | CONSTRUCTION DEBRIS(LUMBER/PLASTIC PIPE BLOCKAGE | NO | NONE |  |  | N | N | NA
880531 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880530 | 0630AM | 880530 | 0800AM | 1800 | GAL | 15250 PENASQUITOS DR | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
880531 | 0900AM | HOLODNAK | 6195789772 | SAN DIEGO, CITY OF | 880530 | 1100AM | 880530 | 1400PM | 180 | GAL | 4072 ADAMS AVE | SAN DIEGO | SD | MAIN | GREASE | NO | NONE |  |  | N | N | NA | AREA ZEPPED
880531 | 0900AM | HOLODNAK | 6195789772 | SAN DIEGO, CITY OF | 880530 | 1200 N | 880530 | 1400PM | 240 | GAL | 4906 PACIFICA DR | SAN DIEGO | SD | MAIN | ROOTS | NO | NONE |  |  | N | N | NA
880531 | 0900AM | HOLODNAK | 6195789772 | SAN DIEGO, CITY OF | 880530 | 2200PM | 880530 | 2330PM | 450 | GAL | 69TH AT SYCHAR | SAN DIEGO | SD | MAIN | ROOTS | NO | NONE |  |  | N | N | NA | AREA ZEPPED
880606 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880531 | 1230PM | 880531 | 1730PM | 600 | GAL | 3751 37TH ST | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
880601 | LETTER | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880531 | 1000AM | 880531 | 1530PM | 16500 | GAL | 4241 JUTLAND (IN REAR) | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | ? | ??
889691 | 1915AM | JOHN CONTRERAS | 7144994555 | SOUTH COAST WATER DISTRICT | 880531 | ?????? | 88 | ?????? | 0 | ??? | S LA SENDA(86-92-94-96)4 RESDT | SOUTH LAGUNA | OR | 6" PVT LATERAL SEWER MAIN | SEWER MAIN PULLED AWAY FROM CLIFF ALLOWING SEWAGE TO FLOW ONTO PVT BCH AT THREE ARCH BAY.(HOME OWNERS ASSOC.) | Y | OCEAN |  |  | Y | N
880601 | 1645PM | ZAMISCH PLUMBING | 6195750822 | NATIONAL, CITY OF | 880601 | 1645PM | 880601 | 1800PM | 50 | GAL | 1705 EAST 16TH ST | NATIONAL CITY | SD | CLEANOUT PVT PROPERTY | ROOTS | NO | NONE |  |  | N | N
880602 | 1600PM | J CROWDER | 6192367089 | SAN DIEGO, CITY OF | 880602 | 0830AM | 880602 | 0930AM | 3000 | GAL | 2802 CANON ST | SAN DIEGO | SD | MANHOLE | GREASE | Y | SAN DIEGO BAY |  |  | Y | Y | 04
880606 | 1445PM | ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880604 | 1345PM | 880604 | 1745PM | 3600 | GAL | CORONADO AVE & HAWAII AVE | SAN DIEGO | SD | MANHOLE | ROCKS | NO | NONE |  |  | Y | Y | 03
880607 | 1650PM | GLENN | 6192365534 | SAN DIEGO, CITY OF | 880605 | 1650PM | 880605 | 1800PM | 14000 | GAL | 3255 LA JOLLA DR | SAN DIEGO | SD | STA 30 OVERFLOW MANHOLE | MAIN CIRCUT BREAKER TRIPPED FOR UNKNOWN REASON. | NO | NONE |  |  | Y | N
880607 | 0940AM | ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880605 | 1146AM | 880605 | 1230PM | 0 | ??? | 1381 PALM AVE | SAN DIEGO | SD | CLEANOUT | PUMP FAILURE | NO | NONE |  |  | Y | N
880606 | 1300PM | MICHAEL GARNER | 7149257676 | EASTERN MUNICIPAL WATER DIST | 880606 | 0200AM | 880606 | 0715AM | 50000 | GAL | 30185 STATE HIGHWAY 71 | TEMECULA | RI | PALA LIFT STATION | CONTRACTOR LEFT PLANT SITE UNSECURED RESULTING IN VANDALS CUTTING CONTROL/TELEMETRY POWER TO PUMPS. | NO | NONE |  |  | N | N
880607 | LETTER | GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880606 | 1700PM | 880606 | 1900PM | 1800 | GAL | 5480 UNIVERSITY AVE | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N
880607 | LETTER | GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880606 | 2030PM | 880607 | 0230AM | 18000 | GAL | CANYON AT 6442 CAMTO LISTO | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N
880607 | LETTER | GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880606 | 1130AM | 880606 | 1230PM | 300 | GAL | 2930 BAYSIDE LANE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | Y | N
880607 | 0800AM | BOB WADE | 6197891330 | RAMONA MUNICIPAL WATER DIST | 880606 | 0600AM | 880606 | 0800AM | 500000 | GAL | 26758 SAN VICENTE ROAD | RAMONA | SD | IRRIGATION POND/RECLAIMED H2O | EQUIPMENT FAILURE:VALVE ON IRRIG LINE IN POND BLEW OFF WHEN PUMP SHUT OFF & POND FILLED & OVERFLOWED. | Y | SAN VICENTE CREEK/RESERVOIR |  |  | Y | N
880609 | 1200 N | ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880608 | 1700PM | 880608 | 2100PM | 720 | GAL | 200 BLOCK OF 30TH ST | SAN DIEGO | SD | MANHOLE | GREASE & DEBRIS | NO | NONE |  |  | Y | N
880608 | 1320PM | TOM BRADLEY | 7145822330 | SANTA MARGARITA WATER DIST. | 880608 | 0900AM | 880608 | 1000AM | 10000 | GAL | AVE DE LOS FUNDADORES | RANCHO SANTA MAR | OR | MANHOLE | CONSTRUCTION DEBRIS | NO | NONE |  |  | Y | N
880614 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880609 | 1530PM | 880609 | 1630PM | 60 | GAL | 60TH ST & FEDERAL BLVD. | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N
880610 | 1020AM | ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880609 | 1150AM | 880609 | 1750PM | 180 | GAL | 4310 RANDOLPH ST | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N
880615 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880610 | 1700PM | 880610 | 1900PM | 600 | GAL | 2912 CHAMOUNE AVE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N
880615 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880610 | 2000PM | 880610 | 2200PM | 120 | GAL | BURGANDY & CRAWFORD | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N
880610 | 1530PM | PHYLLIS CHALMERS | 6192365220 | SAN DIEGO, CITY OF | 880610 | 1218PM | 880610 | 1248PM | 300 | GAL | 7964 PRINCESS ST | SAN DIEGO | SD | FIXTURES IN 7964 PRINCESS ST | ROOTS | Y | OCEAN AT LA JOLLA COVE |  |  | Y | Y | 01 | 100 FT OF COVE CLOSED
880615 | 1030AM | BETTY LEASH |  | FALLBROOK SANITARY DISTRICT | 880610 | 1920PM | 880610 | 1925PM | 5 | GAL | 644 MINNISOTA ST | FALLBROOK | SD | 4" CLAY PIPE | ROOTS | NO | NONE |  |  | N | N
880613 | 0900AM | JIM MCCURLY | 6195789772 | SAN DIEGO, CITY OF | 880611 | 0130AM | 880611 | 0330AM | 600 | GAL | 600 BUSH ST | SAN DIEGO | SD | MAIN | GREASE | NO | NONE |  |  | Y | N
880615 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880612 | 1100AM | 880612 | 1400PM | 180 | GAL | 4324 RANDOLPH ST | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N
880615 | LETTER | BEADLE |  | SAN DIEGO, CITY OF | 880612 | 1430PM | 880612 | 1530PM | 120 | GAL | CANON ST & SHAFTER ST | SAN DIEGO | SD | MANHOLE | ROOTS & GREASE | NO | NONE |  |  | N | N
880612 | 2230PM | M BEDARD | 6192365534 | SAN DIEGO, CITY OF | 880612 | 1400PM | 880613 | 0730AM | 20 | GAL | 13634 OLD CAMINO REAL | SAN DIEGO | SD | MANHOLE | BAD AIR VALVE ON FORCE MAIN CONNECTED TO STATION 79 | NO | NONE |  |  | Y | N
880614 | 1010AM | ARNOLD | 6192366092 | SAN DIEGO, CITY OF | 880613 | 1355PM | 880613 | 1655PM | 1800 | GAL | 3412 KENYON ST | SAN DIEGO | SD | MANHOLE | GREASE & DEBRIS | NO | NONE |  |  | Y | N
880614 | 0900AM | JIM MCCURLY | 6195789772 | SAN DIEGO, CITY OF | 880613 | 1830PM | 880613 | 2000PM | 45 | GAL | 1702 NATIONAL AVE | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N
880615 | 1030AM | PATTI PLATT | 6197288319 | FALLBROOK SANITARY DISTRICT | 880613 | 1215PM | 880613 | 1223PM | 5 | GAL | 410 W. FALLBROOK ST | FALLBROOK | SD | 6" CLEANOUT | FOREIGN MATERIALS IN LINE | NO | NONE |  |  | N | N
880614 | 0900AM | JIM MCCURLY | 6195789772 | SAN DIEGO, CITY OF | 880614 | 0330AM | 880614 | 0500AM | 45 | GAL | 3360 SPORTS ARENA BLVD | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N
880616 | LETTER | PETER HUHN | 6197281180 | FALLBROOK SANITARY DISTRICT | 880615 | 1000AM | 880615 | 1230PM | 250 | GAL | 514 HAWTHORNE ST | FALLBROOK | SD | HAWTHORNE LIFT STATION | PUMP CLOGGED | NO | NONE |  |  | N | N
880621 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880616 | 0830AM | 880616 | 1030AM | 240 | GAL | 445 GLORIA ST | SAN DIEGO | SD | CLEANOUT | GREASE | NO | NONE |  |  | N | N
880623 | LETTER | BEADLE |  | SAN DIEGO, CITY OF | 880617 | 1600PM | 880617 | 1800PM | 6000 | GAL | 1955 SAIPAN | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N
880621 | 0955AM | ARNOLD |  | SAN DIEGO, CITY OF | 880620 | 0945AM | 880620 | 1045AM | 1200 | GAL | SAN ELIJO & JENKINS | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | Y | N
880620 | 1545PM | JIM MCCURLY | 6195789772 | SAN DIEGO, CITY OF | 880620 | 0830AM | 880620 | 0930AM | 60 | GAL | 4888 RONSON CT. | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N
880627 | LETTER | BEADLE |  | SAN DIEGO, CITY OF | 880621 | 1430PM | 880621 | 1630PM | 600 | GAL | 5359 AUBURN DR | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N
880622 | 1619PM | JAMES SMITH | 7146432006 | MOULTON NIGUEL WATER DISTRICT | 880622 | 1000AM | 880622 | 1015AM | 5000 | GAL | COASTAL TREATMENT PLANT | SOUTH LAGUNA | OR | LIFT STATION WET WELL | MAJOR ELECTRICAL REPAIRS AT REGIONAL LIFT STA. CAUSED THE WET WELL AT THE COASTAL LIFT STA TO OVERFLOW DURING PEAK FLOWS | Y | ALISO CREEK/OCEAN |  |  | Y | Y | ??
880627 | LETTER | BEADLE |  | SAN DIEGO, CITY OF | 880622 | 1430PM | 880622 | 1630PM | 120 | GAL | 8297 LAKE ANDRITA AVE | SAN DIEGO | SD | CLEANOUT | ROOTS | NO | NONE |  |  | N | N
880627 | LETTER | GLEN PETERSON | 6197414668 | ESCONDIDO, CITY OF | 880622 | 1030AM | 880622 | 1330PM | 15000 | GAL | EASEMENT LINE HARMONY GROVE RD | ESCONDIDO | SD | MANHOLE 2, ATLAS PG. 35 | ROOTS & DEBRIS | NO | NONE |  |  | N | N
880620 |  | PETER HUHN | 6197281180 | FALLBROOK SANITARY DISTRICT | 880620 | 0500AM | 880620 | 0630AM | 100 | GAL | 1425 S. ALTURAS RD | FALLBROOK | SD | LIFT STATION 5 | THE ON/OFF FLOAT GOT HUNG UP & THE WET WELL OVERFLOWED.INSPECTED & GREASED THE FLOAT. | NO | NONE |  |  | N | N
880623 |  | PETER HUHN |  | FALLBROOK SANITARY DISTRICT | 880622 | 0600AM | 880622 | 0700AM | 200 | GAL | 1425 S. ALTURAS RD | FALLBROOK | SD | LIFT STATION 5 | THE ON/OFF FLOAT GOT HUNG UP & THE WET WELL OVERFLOWED. INSPECTED FLOAT & MADE SOME MODIFICATIONS TO THE FLOAT. | NO | NONE |  |  | N | N |  | NEW BACKUP PUMP & FLOAT INSTALLED ON 6/23/88.
880625 | 1730PM | DUTY NCO | 6197254981 | USMC CAMP PENDELTON | 880625 | 1700PM | 880625 | 1900PM | 5000 | GAL | SAN ONOFRE BEACH RD | CAMP PENDELTON | SD | LIFT STATION | CONTROL SYSTEM FAILURE | NO | NONE |  |  | Y | N
880701 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880625 | 1000AM | 880625 | 1100AM | 60 | GAL | 5959 BALMORAL ST | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N | NA
880701 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880625 | 1200 N | 880625 | 1400PM | 120 | GAL | 3980 BROADWAY | SAN DIEGO | SD | CLEANOUT | ROOTS | NO | NONE |  |  | N | N | NA
880627 | 0900AM | DONN GRIFFIN | 6192367340 | SAN DIEGO, CITY OF | 880625 | 1530PM | 880625 | 2130PM | 288000 | GAL | 54TH ST. SOUTH OF MARKET ST. | SAN DIEGO | SD | MANHOLE | VANDALISM-TIRES & ROCKS IN MANHOLE | Y | SAN DIEGO BAY// OCEAN |  |  | Y | Y | ??
880701 | 0800AM | JAMES E. SMITH | 7146432006 | MOULTON NIGUEL WATER DISTRICT | 880626 | 1700PM | 880626 | 1800PM | 8400 | GAL | LAGUNA NIGUEL REGIONAL PARK | LAGUNA NIGUEL | OR | 4 INCH AIR & VACUUM RELIEF VAL | VANDALISM | Y | SULFER CREEK/OCEAN |  |  | Y | Y | 05
880627 | 1505PM | WILLIAM ORTIZ | 6196915021 | CHULA VISTA, CITY OF | 880627 | 1030AM | 880627 | 1035AM | 200 | GAL | INT EAS MAPLE & MONSERAT | CHULA VISTA | SD | FIRE HOSE | HOSE USED TO DIVERT SEWAGE AT CONSTRUCTION SITE RUPTURED DUE TO CONTRACTOR ERROR | NO | NONE |  |  | N | N
880627 | 1530PM | JIM MCCURLY | 6195789772 | SAN DIEGO, CITY OF | 880627 | 0830AM | 880627 | 1030AM | 600 | GAL | COLINA DORADO DR & TIERRASANTA | SAN DIEGO | SD | SEWER LINE | GREASE | NO | NONE |  |  | Y | N
880701 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880628 | 1230PM | 880628 | 1330PM | 60 | GAL | 6607 BROADWAY | SAN DIEGO | SD | CLEANOUT | ROOTS | NO | NONE |  |  | N | N | NA
880629 | 1415PM | PUBLIC WORKS DEPT | 6193364360 | NATIONAL CITY, CITY OF | 880629 | 1400PM | 880629 | 1440PM | 250 | GAL | 1200 BLOCK PALM AVE | NATIONAL CITY | SD | MH #1348 | GREASE & ROOTS | NO | NONE |  |  | N | N | NA
880606 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880630 | 0900AM | 880630 | 1200 N | 180 | GAL | 3284 NATIONAL AVE | SAN DIEGO | SD | MANHOLE | GREASE | NO | NONE |  |  | N | N
880706 | LETTER | BEADLE | 6192367030 | SAN DIEGO, CITY OF | 880630 | 1430PM | 880630 | 1606PM | 12 | GAL | 5612 SAN ONOFRE TERR | SAN DIEGO | SD | MANHOLE | ROOTS | NO | NONE |  |  | N | N