## Drop-down lists
Sewer Agency List | County | SSO Cause Short | Yes or No
Buena Sanitary District | OC | BLOCKAGE | Y
Carlsbad Municipal Water District | RV | CONSTRUCTION | N
City of Chula Vista | SD | DEBRIS
City of Coronado |  | FLOOD DAMAGE
City of Del Mar |  | GREASE
City of El Cajon |  | INFILTRATION
City of Encinitas |  | LINE BREAK
City of Escondido |  | MANHOLE FAILURE
City of Imperial Beach |  | OTHER
City of La Mesa |  | POWER FAILURE
City of Laguna Beach |  | PRIVATE PROPERTY
City of Lemon Grove |  | PUMP STATION FAILURE
City of National City |  | ROCKS
City of Oceanside |  | ROOTS
City of Poway |  | UNKNOWN
City of San Clemente |  | VANDALISM
City of San Diego
City of San Juan Capistrano
City of Solana Beach
City of Vista
County of San Diego
Eastern Municipal Water District
Elsinore Valley Municipal Water District
El Toro Water District
Emerald Bay Community Services District
Fairbanks Ranch Community Services District
Fallbrook Public Utilities District
Irvine Ranch Water District
Leucadia County Water District
Moulton Niguel Water District
Murrieta County Water District
Olivenhain Municipal Water District
Otay Water District
Padre Dam Municipal Water District
Pauma Valley Community Services District
Rainbow Municipal Water District
Ramona Municipal Water District
Rancho Santa Fe Community Services District
Rancho California Water District
Santa Margarita Water District
South Coast County Water District
Trabuco Canyon Water District
U.S. Marine Corps, Camp Pendleton
U.S. Navy Public Works Center
Vallecitos Water District
Valley Center Municipal Water District
Whispering Palms Community Services District
Private Party

## Quarterly Summary Rpt Template
RB-Assigned SSO ID No. | RB-Assigned Tracking No. | RB-entered Reporting Agency | RB-entered Responsible Agency | RB-entered Start Date | RB-entered End Date | RB-entered Total Volume | RB-entered Recovered Volume | RB-entered Cause - Short Description | RB-entered Warning signs posted | Place an "X" here if this is definitely a private spill | Place an "P", "R", "S", "O" here if it is a Plant, Recycled, Secondary, or Other non SSO | Tracking No. | Regional Board Contact Notified (Name, or "VOICE MAIL", or "FAX") | Date & Time Reported | Reported By | Phone No. | Reporting Agency | Responsible Agency | Start Date & Time | End Date & Time | Estimated Overflow Flow Rate (gallons per minute) | Total Overflow Volume (Gallons) | Overflow Volume Recovered (Gallons) | Overflow Volume Released to Environment (Gallons) | SSO Location -- Street Address | SSO Location -- City | SSO Zip Code | SSO County (SD, RV, OR) | SSO Structure I.D. | No. of Overflows within 1000 ft. of this location in past 12 months | Dates of Overflows within 1000 ft. of this location in past 12 months | SSO Cause (Short Description) | SSO Cause (Detailed Description) | SSO Correction and Prevention | 72-hour period measurable precipitation? (Y or N) | Entered Storm Drain? (Y or N) | Reached surface waters other than storm drain? (Y or N) | Initial Receiving Waters | Secondary Receiving Waters | Final Sewage Destination | Local Health Services Agency Notified (Y or N) | OES Notified (Y or N) | Warning Signs Posted (Y or N) | Location of Posting | No. of Days Signs Posted | Remarks | RB staff review comments
| 67001 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 7/5/2006 11:00 |  |  |  | PRIVATE PROPERTY | N | X |  | 67001 | FAX (858) 571-6972 | 7/5/2006 14:50 | Patti S. Page | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 7/5/2006 11:00 | [5 empty] | 323 Retreat Court | Fallbrook | 92028- | SD | 4" lateral from house | 0 | NA | PRIVATE PROPERTY | 4" ABS pipe missing approximately 4' section into 6' x 17 foot hole between house and sidewalk. Don't know how long this has been going on. No evidence of washout. Might be old waterwell. | Informed renter to contact owner. | N | N | N |  |  | Not sure, maybe old water well, soaked into ground. | Y | N | N |  | 0 | PRIVATE PROPERTY. Also notified County SD, Storm Water Division, Complaint Investigation. FPUD employee Jim Whisnand called us out to look at problem. Hole is between house and side walk in front yard. Hole is approximately 6 feet wide and 17 feet dee
| 67002 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 7/10/2006 11:00 | 7/10/2006 14:00 | 45 | 40 | PRIVATE PROPERTY | N | X |  | 67002 | QUARTERLY REPORT |  |  | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 7/10/2006 11:00 | 7/10/2006 14:00 | 0.25 | 45 | 40 | 5 | 809 Vanita Street | Fallbrook | 92028- | SD | 4" DIP Lateral | 0 | NA | PRIVATE PROPERTY | Two small holes in ductile iron pipe attached to concrete wall. Concrete gutter below wall that flows into storm drain. | FPUD installed temporary coupling to stop flow. Owner will need to be contacted for permanent repair. Washed down concrete gutter and vacuumed down stream. | N | Y | N | None. | None. | Stopped in concrete gutter. | Y | N | N |  | 0 | PRIVATE PROPERTY. Have had problems with 809 and 817 Vanita in the past. County Health required them to replace old pipe with D.I.P. about 2 or 3 years ago. Owner needs to be contacted to have pipe fixed in a permanent manner. Concrete gutter is on FP
1990 | N/A | City of San Clemente | City of San Clemente | 2006-08-01 13:24 | 2006-08-01 13:45 | 42 | 0 | PRIVATE PROPERTY | Y | X |  |  | Fax | 2006-08-01 16:00 | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2006-08-01 13:24 | 2006-08-01 13:45 | 2 | 42 | 0 | 42 | 415 Ave Pico | San Clemente | 92672 | OC | Private lateral | 0 | 0 | BLOCKAGE | Private Lateral | Private Lateral | n | y | y | Pacific Ocean |  | Pacific Ocean | y | n | y | North Beach San Clemente | 4 | Private Lateral
1994 | 67001 | City of San Clemente | City of San Clemente | 2006-08-28 13:30 | 2006-08-28 15:00 | 13500 | 13500 | CONSTRUCTION | N |  |  | 67001 | Voice Mail | 2006-08-29 15:30 | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2006-08-28 13:30 | 2006-08-28 15:00 | 150 | 13500 | 13500 | 0 | Mariposa Beach Access | San Clemente | 92672 | OC | 8" Gravity Sewer | 0 | 0 | CONSTRUCTION | Contractor Broke Line | Contractor Broke Line During Construction. Sewer Line was Marked Before Work Began. | n | n | n | None | None | Sewer System | y | y | n | N/A
N/A | N/A | City of San Clemente | City of San Clemente | 2006-09-20 12:49 | 2006-09-20 13:30 | 50 | 50 | PRIVATE PROPERTY | N | X |  |  | Fax | 2006-09-20 16:40 | Chris Fike | 949-366-1553 | City of San Clemente | City of San Clemente | 2006-09-20 12:49 | 2006-09-20 13:30 | 1 | 50 | 50 | 0 | 800 Ave Pico | San Clemente | 92672 | OC | Private Sewer System | 0 | 0 | BLOCKAGE | Private Lateral | Private Lateral | n | n | n | None | None | Sewer System | y | n | n | N/A |  | Private Lateral
3031 | N/A | City of San Clemente | City of San Clemente | 2006-09-21 10:45 | 2006-09-21 11:15 | 100 | 100 | PRIVATE PROPERTY | N | X |  |  | Fax | 2006-09-21 13:30 | Chris Fike | 949-366-1553 | City of San Clemente | City of San Clemente | 2006-09-21 10:45 | 2006-09-21 11:15 | 3 | 100 | 100 | 0 | 256 Ave. Victoria | San Clemente | 92672 | OC | Private Lateral | 0 | 0 | BLOCKAGE | Private Lateral | Private Lateral | n | y | n | None | None | Sewer System | y | n | n | N/A |  | Private Lateral
1993 | 67001 | Trabuco Canyon Water District | Trabuco Canyon Water District | 2006-08-05 08:45 | 2006-08-05 09:15 | 200 | 0 | LINE BREAK | N |  |  | 56001 | Joanne Cofrancesco | 8/5/2006 1200 | Kris Hanberg | 949-858-0277 | Trabuco Canyon Water District | Trabuco Canyon Water District | 2006-08-05 08:45 | 2006-08-05 09:15 | 6 | 200 | 0 | 200 | 21014 Plano Trabuco Road | Trabuco Canyon | 92679 | OC | n/a | 0 | n/a | Line Break | 1" lateral to Air Vac sprung a hole | Replace lateral to Air Vac | n | y | y | Tieras creek | none | Tieras creek | y | y | n | N/A | 0
1948 | N/A | South Coast County Water District | South Coast County Water District | 2006-07-07 21:30 | 2006-07-07 21:35 |  |  | PRIVATE PROPERTY | N | X |  | 76001 | FAX 858-571-6972 | 2006-07-13 14:05 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2006-07-07 21:30 | 2006-07-07 21:35 | 0 | 0 | 0 | 0 | 31721 Sea Cliff | Laguna Beach | 92651 | OC | Private lateral | 0 | NONE | LINE BREAK | SCWD personnel responded to a call about a broken service lateral at 31721 Sea Cliff, Laguna Beach, CA. Upon arriving at the site, District personnel found a 4" PVC lateral had separated next to the address at 31719 Sea Cliff and was being suspended to the side of the cliff. No spill or residual was seen by District personnel when they arrived at the site. The spill report was based on eyewitness account by homeowners at 31719 Sea Cliff. Accoridng to the homeowners the spill saturated into the ground next to their house. | SCWD personnel advised homeowner that water service would be turned off until necessary repairs to the service lateral were made. Homeowner said that he would get a plumber to make the necessary repairs. | N | N | N | n/a | n/a | Spill saturated into the ground. | Y | N | n/a | n/a | 0 | Private System Overflow Incident
1987 | N/A | South Coast County Water District | South Coast County Water District | 2006-07-22 11:12 | 2006-07-22 11:30 | 30 | 30 | PRIVATE PROPERTY | N | X |  | 76002 | FAX 858-571-6972 | 2006-07-26 12:10 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2006-07-22 11:12 | 2006-07-22 11:30 | 0 | 30 | 30 | 0 | 25325 Dana Point Harbo Drive | Dana Point | 92629 | OC | Private Cleanout | 0 | NONE | BLOCKAGE | SCWD personnel received a call regarding a spill at the Dana Point Harbor Inn. When SCWD personnel arrived at the site the spill had stopped. The owner of the hotel indicated that the service lateral to one of the hotel rooms backed up due to heavy amounts of tissue disposed into the system, causing the lateral to back up and spill over. The back-up occurred in one of the rooms that were located at the rear of the hotel complex. | The owner had a plumber run a snake at the 4" cleanout. Plumber cleared the blockage. The majority of the overflow spilled into the flower bed. A small amount spilled over the flower bed and onto the parking lot where SCWD personnel were able to contain wash down and vacuum up the SSO. District crews vacuumed the remaining debris, which saturated inot the flower bed. The SSO didi not enter the storm drain. | N | N | N | n/a | n/a | Spill saturated into the ground. | Y | N | n/a | n/a | 0 | Private System Overflow Incident
2029 | N/A | South Coast County Water District | South Coast County Water District | 2006-09-08 13:00 | 2006-09-08 13:25 | 50 | 50 | PRIVATE PROPERTY | N | X |  | 76003 | FAX 858-571-6972 | 2006-09-14 08:55 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2006-09-08 13:00 | 2006-09-08 13:25 | 0 | 50 | 50 | 0 | 34052 Doheny Park Road | Dana Point | 92629 | OC | Prvate Cleanout | 0 | NONE | GREASE | SCWD personnel was driving by and saw the cleanout overflowing. SCWD personnel ran jetter hose from District manhole into private system inside the mobile home park. At approximately 18 ft. from the manhole they hit an obstruction, which appeared to be heavy grease buildup. A debris trap was used to contain and remove the grease and grit. The SSO did not reach the storm drain. | SCWD personnel responded with two combination jetter trucks. One truck was used to clear the blockage while the other was used to contain the SSO at the cleanout. SCWD personnel washed down the spill site and used a combination truck to vacuum the contained spill. A plumber called in by the property manager cleaned out the remaining debris left inside the lines. A video camera was used by the plumber to video the main line inside the mobile home park to determine if the private line was in good condition. | N | N | N | n/a | n/a | Spill saturated into the ground. | Y | N | n/a | n/a | 0 | Private System Overflow Incident
1989 | 67001 | Santa Margarita Water District | Santa Margarita Water District | 2006-08-03 08:00 | 2006-08-03 09:15 | 375 | 0 | ROOTS | N |  |  | 67001 | FAX (858) 571-6972 | 2006-08-03 13:30 | Gerre Bedell | (949) 459-6541 | Santa Margarita Water District | Santa Margarita Water District | 2006-08-03 08:00 | 2006-08-03 09:15 | 5 | 375 | 0 | 375 | 158 La Puerta | Rnch Santa Margarita | 92688 | OC | Manhole | 0 | 0 | ROOTS | Roots from a private property entered the manhole barrel through the grade rings in to the eight-inch sewer line channel blocking the flow. | Revoved the roots from the manhole barrel and cleaned the channel with the Rodder truck. | N | Y | Y | Trabuco Creek | None | Dry creek bed | Y | Y | N | N/A | 0 | Trabuco Creek was dry. No secondary water were impacted. The overflow soaked in to the dry creek bed. OES #06-4617
2027 | 67001 | Moulton Niguel Water District | Moulton Niguel Water District | 2006-09-06 11:40 | 2006-09-06 12:00 | 600 | 200 | OTHER | Y |  |  | 67001 | FAX (858) 571-6972 | 2006-09-06 14:30 | Brad Bruington | (949) 425-3543 | Moulton Niguel Water District | Moulton Niguel Water District | 2006-09-06 11:40 | 2006-09-06 12:00 | 30 | 600 | 200 | 400 | Aliso Creek & Horizon | Aliso Viejo | 92656 | OR | Manhole #23, Sectional Book Page D14 | 0 | 0 | Other | Overflow caused by excessive flow due to Kana Pipeline Construction pumping pipeline test water into 8" gravity sewer. Flow could not be handled in 90 degree turn at Manhole No. 23. | City of Aliso Viejo & Kana Pipeline Construction will be notified of damages caused by their actions. 8" sewer will be video inspected 9/7/06 for debris. (Note: 9/7/06 video inspection found clear lines). | N | Y | Y | Aliso Creek | Pacific Ocean, A. Creek Beach |  | Y | N | Y | 150' south & north of river at Aliso Creek Beach | 4 | Contractor did not contact water district prior to using the sewer for dumping.
2094 | 67001 | City of Solana Beach | City of Solana Beach | 2006-11-24 13:30 | 2006-11-24 23:00 | 2000 | 2000 | BLOCKAGE | N | X |  | 67001 | Michelle Mata FAX 858 571-6972 | 2006-11-27 | Danny King | 858 720-2477 | City of Solana Beach | City of Solana Beach | 2006-11-24 13:30 | 2006-11-24 | 3.5 | 2000 | 2000 | 0 | 315 S. Sierra | Solana Beach | 92075 | SD | Cleanout | 0 | N/A | Blockage | Blockage in Private lateral (Long's Drugs) | Cleared blocage, checked low flow diverter, all discharge returned to sewer system and gutters were cleaned by a vac-con truck | N | Y | N | None | None | Low Flow diverter/back sto sewer system | Y | N | N | N/A | 0
2062 | 67002 | City of San Clemente | City of San Clemente | 2006-10-02 20:30 | 2006-10-02 20:55 | 250 | 0 | VANDALISM | Y |  |  | 67002 | Voice Mail | 2006-10-03 08:30 | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2006-10-02 20:30 | 2006-10-02 20:55 | 10 | 250 | 0 | 250 | Calle Pastadero | San Clemente | 92672 | OC | 8" Gravity line | 0 |  | VANDALISM | Grout Poured into the Sewer Line | Remove Grout | n | y | y |  |  | Pacific Ocean | y | n | y | North Beach | 3
2099 | 67003 | City of San Clemente | City of San Clemente | 2006-11-02 21:10 | 2006-11-02 21:50 | 800 | 280 | ROOTS | N |  |  | 67003 | Fax | 2006-11-02 23:30 | Chris Fike | 949-366-1553 | City of San Clemente | City of San Clemente | 2006-11-02 21:10 | 2006-11-02 21:50 | 20 | 800 | 280 | 520 | 115 Ave. Presidio | San Clemente | 92672 | OC | 8" Gravity line | 0 |  | ROOTS | Root Intrusion | Root Removed | n | y | n | None |  | Canyon Floor | y | n | n
2139 | 67004 | City of San Clemente | City of San Clemente | 2006-12-23 08:00 | 2006-12-23 08:15 | 1000 | 0 | ROOTS | Y |  |  | 67004 | Fax | 2006-12-23 11:30 | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2006-12-23 08:00 | 2006-12-23 08:15 | 66 | 1000 | 0 | 1000 | Portico Del Sur | San Clemente | 92672 | OC | 8" Gravity line | 0 |  | ROOTS | Root Intrusion | Root Removed | n | y | y |  |  | Pacific Ocean | y | y | y | Poche Beach | 5
2067 |  | City of San Clemente | City of San Clemente | 2006-10-22 20:00 | 2006-10-22 20:30 |  |  | PRIVATE PROPERTY | N | x |  |  | Fax | 2006-10-23 16:00 | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2006-10-22 20:00 | 2006-10-22 20:30 |  |  |  |  | 104 El Camino Real | San Clemente | 92672 | OC | Private System | 0 |  | PRIVATE PROPERTY | Private System |  | n | n | n |  |  | N/A | y | n |  |  |  | Private System
2129 |  | City of San Clemente | City of San Clemente | Unknown | 2006-12-13 13:26 |  |  | PRIVATE PROPERTY | Y | x |  |  | Fax | 2006-12-13 13:50 | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente |  | 2006-12-13 13:26 |  |  |  | 250 | 158 Calle Redondel | San Clemente | 92672 | OC | Private System | 0 |  | PRIVATE PROPERTY | Private System |  | n | y | y | None |  | Pacific Ocean | y | n | y | North Beach |  | Private System
2130 | 67001 | El Toro Water District | El Toro Water District | 2006-12-15 10:55 | 2006-12-15 11:30 | 175 | 0 | GREASE | N |  |  | 67001 | Joann Cofrancesco | 2006-12-15 10:55 | Renzo Marin | (949) 837-7050 | El Toro Water District | El Toro Water District | 2006-12-15 10:55 | 2006-12-15 11:30 | 5 | 175 | 0 | 175 | Alicia Pkwy & Charlinda | Mission Viejo | 92691 | OC | ETWD atlas page MB- 503 | 0 | N-A | Grease | Gease blockage in 8" sewer line. | Set up containment while using the Hydrocleaner to break the blockage and clean the line. Washed down contaminated area, contained and recovered all wash down water. Will Video inspect sewer line on 12/18/2006 to assess line conditions. | N | Y | Y | Catch basin | Storm drain | Aliso Creek | Y | N | N | N-A |  | Emailed report to Regulatory Agencies and City of Mission Viejo 12/15/06.
| 67002 | El Toro Water District | El Toro Water District | 2006-12-19 18:15 | 2006-12-19 19:20 | 98 | 0 | GREASE | N |  |  | 67002 | VIOICE MAIL | 2006-12-19 20:00 | Renzo Marin | (949) 837-7050 | El Toro Water District | El Toro Water District | 2006-12-19 18:15 | 2006-12-19 19:20 | 1.5 | 98 | 0 | 98 | Laguna Hills Malll & Calle Louisa | Laguna Hills | 92630 | OC | ETWD Atlas page MA-496 | 0 | N-A | Grease | Gease blockage in 8" sewer line. | Set up traffic control & containment while using the Hydrocleaner to break the blockage and clean the line. Used Vactor to vaccum sewage from manhole in oder to stop overflow. Washed down contaminated area, contained and recovered all wash down water. Will Video inspect sewer line on 12/20/2006 to assess line conditions. Inspection confirmed line to be in good conditions. | Y | Y | Y | Storm drain | Aliso Creek | Aliso Creek | Y | N | N | N-A |  | Emailed report to Regulatory Agencies and City of Laguna Hills 12/20/06.
2101 | 67010 | City of Laguna Beach | City of Laguna Beach | 2006-11-15 09:15 | unknown | 700 | 0 | BLOCKAGE | Y |  |  | 67010 |  | 2006-11-15 10:55 | Paul Ferrell |  |  |  | 2006-11-15 09:15 |  | 35 | 700 | 0 | 700 | 1741 Ocean Way |  |  |  | Private Sewer Lateral Cleanout | 0 |  | Debris | A plumbers test plug (used to seal a sewer lateral for testing purposes) and an accumulation of debris which was caught around this test plug causing the City sewer mainline to surgecharge. | Staff proceeded to set up at the downstream manhole (F25-118) and using a high pressure jetting truck, jetted upstream to manhole (F25-119) to relieve the surcharged condition from the system, this restoring the flow to the collection system. | N | Y | N | Pacific Ocean | None | Pacific Ocean | Y | N | Y | Bluebird Canyon Beach to Center Street | 2 | The resulting overflow, which was estimated at seven hundred gallons (700) was based upon the residents report of the time of the spill and from our visual observations at the site. The overflow entered a storm drain, which drains directly onto Agate Street Beach below the home. Efforts by staff to contain and recover the spill from the beach was not feasible due to the high tides which were occurring at this time.
2064 | 67001 | City of San Juan Capistrano | City of San Juan Capistrano | 2006-10-08 08:45 | 2006-10-08 10:31 | 5300 | 0 | BLOCKAGE | N |  |  | 67001 | FAX 858-517-6972 | 2006-10-09 12:58 | David Hubler | 949-443-6365 | City of San Juan Capistrano | City of San Juan Capistrano | 2006-10-08 08:45 | 2006-10-08 10:31 | 50 | 5300 | 0 | 5300 | ORTEGA HWY IN FRONT OF 27500 | San Juan Capistrano | 92675 | OC | Manhole | 0 | 0 | ROOTS/DEBRIS | Roots and other debris (rags, mp heads) caused blockage in the line. | 1)Cleared line of blockage and captured debris, which caused blockage; 2)System in area was scheduled for cleaning during 10/9-10/20/06 | N | Y | Y | San Juan Creek | Pacific Ocean | San Juan Creek | Y | Y | N
| 67003 | City of Oceanside | City of Oceanside | 10/07/06 21:45 | 10/07/06 22:20 | 80 | 0 | PRIVATE PROPERTY | N | X |  | 67003 | n/a | n/a | Harbor Police | 435-4044 | City of Oceanside | City of Oceanside | 2145 10/07/06 | 2220 10/07/06 | 0 | 80 | 0 | 80 | 1325 Harbor dr | Oceanside | 92054 | SD | Private cleanout | 1 | 1/00/06 | GREASE | The grease trap for the restaurant backed up causing a spill | Had ode enforcement issue a citation to the restaurant for discharging into the harbor. City will inspect the restaurant as part ot our grease trap program. Corrective actions will be issued as required. | N | Y | Y | Storm Drain | Oceanside Harbor | Pacific Ocean | N | Y | N | N/A | 0 | The grease trap at the Monteray Bay Canner Resaurant overflowed due to excessive grease buildup. The grease blocked their lateral and the sewer cleanout in the resaurant parking lot overflowed. This lot drains into the harbor. A plumber was called by the restaurant and the lateral was cleaned by flow Master Plumbing using a hand rodder @10:30pm on October 7, 06. The citywas not notified at this time. At 950 am on October 8, 06 Brian Sundberg, Oceanside harbor Police, Observed the sewage in the parking lot around the cleanout. The restaurant explains that the flow was caused by the activity of the jetting the line by the plumbers that morning. The overflow volume in this report is the number provided by the management of the restaurant. Brian filed a report with the National Response Center on October9, 06. This is their standard practice with any released material into the Harbor waters. he did not indicate any volume numbers in his report. The water Utilities Department was not notified until we received a call from the RWQCB asking about the spill several days later. DEH was not notified becouse the Water Utilities Department was not involved with this incident. We have informed the Harbor Police and Maintenance Dept that in future, the water department should be notified if any private or city owned facilities are experiencing a sewer overflow. I have investigated the incident as fully as possible and provide this report for your records.
| 67004 | City of Oceanside | City of Oceanside | 12/10/06 09:20 | 12/10/06 10:30 | 700 | 0 | CONSTRUCTION | Y |  |  | 67004 | Voice mail | 12/11/06@0725 | Jeremy Kemp | 4355842 | City of Oceanside | City of Oceanside | 0920 12/10/06 | 1030 12/10/06 | 10 | 700 | 0 | 700 | 562 Hoover st | Oceanside | 92054 | SD | Manhole | 0 | n/a | CONSTRUCTION | contractor working for the city left sand bags in the manhole over the weekend causing the city line to back-up and spill. | While it is the respponsibility of the contractor to remove downstream protective devices like sandbags, the city inspectors have been told to make sure the contractors remove these in the future. | Y | Y | Y | Loma alto Creek | Pacific Ocean | Pacific Ocean | Y | N | Y | 300' North and South of Loma Alta opening at Buccaneer Beach. | 3 | Sand bags were placed downstream of the pipeline replacement project in a manhole to prevent debris from entering the collection system. At the completion of the project, the sand bags should have been removed. The contractor overlooked this and the pipeline system was put back in sevice. the city used a vactor to clear the stoppage. An entry into the manhole was necessary to determine the cause of the blockage and for the removal of the sand bags. Under the circumstances, the city crews worked as fast as safely possible. The storm drains were closed by which daylight about 1000' away into Loma Alta Creek , creek entry point is approximately 4.5 miles from the Ocean.
| 67006 | City of Oceanside | City of Oceanside | 12/31/06 12:20 | 12/31/06 16:18 | 369000 | 366000 | LINE BREAK | Y |  | S | 67006 | voicemail | 12/31/06@2035 | Guss Pennell | 535-0393 | City of Oceanside | City of Oceanside | 1220 12/31/06 | 1618 12/31/06 | 1500 | 369000 | 366000 | 3000 | Oceanside blvd & greenbrier | Oceanside | 92054 | SD | San Luis Rey WWTP Treated effluent outfall | 0 | n/a | LINE BREAK | Failure of the 24" SLRWWTP treated effluent land outfall from what appears to be corrosion. Two 2" holes were found on the bottom side of the pipe. | Secctions of the 24" ductile iron land outfall will be potholed to determine if additional sections have corrosion. Excavation will be necessary to inspect sections of the pipe. | N | Y | Y | Loma Alta Creek | Pacific Ocean | Pacific Ocean | Y | Y | Y | Loma Alta Creek and Pacific Ocean | 4 | The city collections crew was called by a NCTD railroad employee at 1220 on 12/31/06. The city determined that the spill was from the San Luis Rey WWTP treated effluent land outfall and shut down the plant effluent pumps at 1320 on 12/31/06. The flow continued until 1618 on 12/31/06 due to gravity emptying the line. Of the line. Of the 369,000 gallons of secondary treated effluent spilled from the land outfall 137,050 gallons were recovered by city vactor and pumper trucks from thechannel along Oceanside BLVD. The remaining 231,950 gallons flowed into Loma Alta Creek. Approximately 3,000 gallons of water flowed from loma Alta Lagoon at Buccaneer Beach before the opaning of the lagoonwas bermed off with sand. The inital estimate of 6,000 gallons reported to DEH was determined to be incrrect. The lagoon dry weatherr diverion pumps were activated at 2020 on 12/31/06. Any flow reaching the lagoon is being pumped into theocean outfall. This will continue until there is a rain event. Precautionary KEEP OUT signs were placed on the beach at 1615 on 12/31/06 every 50 feet for 300 feet north and south of the lagoon openingat Buccaneer Beach. City crews worked through the night and completed the repairs to the pipeline. The land outfall line went back in service at 0100 on 01/01/07. During the repair period all effluent flow from the San Luis Rey WWTP was stored in the emergency pond at the plant.
| 67003 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 10/11/2006 10:30 | 10/11/2006 11:00 | 50 | 5 | PRIVATE PROPERTY | N | X |  | 67003 | Fax (858) 571-6972 | 10/16/2006 07:00 | Patti S. Page | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 10/11/2006 10:30 | 10/11/2006 11:00 | 1.7 | 50 | 5 | 45 | 229 West Alvarado Street | Fallbrook | 92028- | SD | 4" Cleanout | 0 |  | PRIVATE PROPERTY | Roots in cleanout. | Ran cleanout brought back small amount of roots. Root-X, cleaned up area. | N | Y | N | None | None | Storm drain. | Y | N | N |  | 0 | COURTESY NOTIFICATION. Private Sewer. Previously reported on #18, one overflow in past 12 months on 2/21/06. This was an inadvertent error, because the 2/21/06 spill was within 1000 ft., rather than at the exact address, as is deemed appropriate when r
| 67004 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 10/29/2006 17:30 | 10/29/2006 17:50 | 40 | 10 | PRIVATE PROPERTY | Y | X |  | 67004 | FAX (858) 571-6972 | 10/30/2006 11:00 | Patti S. Page | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 10/29/2006 17:30 | 10/29/2006 17:50 | 2 | 40 | 10 | 30 | 739 E. Mission Road | Fallbrook | 92028- | SD | 6" Cleanout | 0 | NA | PRIVATE PROPERTY | Grease and rags in lateral. | Rodded open about 40 ft. Washed down area and vacuumed. Disinfected area. | N | Y | Y | Fallbrook Creek | Santa Margarita, Lake O'Neil, Pacific Ocean | NA | Y | N | Y | Along creek down Brandon Street | 3 | Will visit restaurant and go over BMP's with owner.
| 67005 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 12/20/2006 12:00 | 12/20/2006 12:30 | 30 | 0 | PRIVATE PROPERTY | Y | X |  | 67005 | QUARTERLY REPORT |  | Patti S. Page | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 12/20/2006 12:00 | 12/20/2006 12:30 | 1 | 30 | 0 | 30 | 745 De Luz | Fallbrook | 92028- | SD | Cleanout | 0 | NA | PRIVATE PROPERTY | Possible paper products causing blockage. | Rodded cleanout, opened about 15 feet in to remove blockage | N | N | N | None | None | Along the side of the road. | Y | N | Y | Along the side of the road. | 3 | Cleaned up the area and used disinfectant.
| 67006 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 12/26/2006 09:30 | 12/26/2006 10:15 | 45 | 0 | GREASE | Y |  |  | 67006 | QUARTERLY REPORT |  | Patti S. Page | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 12/26/2006 09:30 | 12/26/2006 10:15 | 1 | 45 | 0 | 45 | 1338 E. Fallbrook Street | Fallbrook | 92028- | SD | Manhole | 0 |  | GREASE | Grease and grit. | Flushed the sewer line. Vactored grease and grit out of the manhole. | N | N | N | None | None | Along side of road. | Y | N | Y | Along side of road. | 3 | Cleaned up area and used disinfectant.
2135 | 67002 | Santa Margarita Water District | Santa Margarita Water District | 2006-12-15 10:00 | 2006-12-16 15:30 | 700 | 600 | PRIVATE PROPERTY | N | X |  | 67002 | FAX (858) 571-6972 | 2006-12-16 16:55 | Gerre Bedell | (949) 459-6541 | Santa Margarita Water District | Santa Margarita Water District | 2006-12-15 10:00 | 2006-12-16 15:30 | 0.4 | 700 | 600 | 100 | 27721 Via Alberti | Mission Viejo | 92690 | OC | Customer's Clean Out | 0 | 0 | Construction | Customer had sewer lateral re-lined by a private plumbing company. A portion of the new line was protruding in to SMWD's main line collecting debris which caused a partial blockage. | Cut out the excess portion of the sewer lateral with a root cutter. | Y | Y | Y | Oso Creek | None | Soaked in to ground between 27721 and 27711 Via Aberti | Y | Y | N | N/A | 0 | OES Tracking #06-7429 The blockage was due to downstream sewer lateral that was recently re-lined by a private plumbing company. Excess lining protruding in to the main, collected debris which caused a partial blockage in the main line. The spill was from the customer's lateral. Approx. 600 gallons reached the storm drain and 100 gallons soaked in to the ground. The storm drain goes to Oso Creek. Oso Creek Barrier PS recovers all of the creek water and pumps to Oso Creek Water Reclamation Plant.
2100 | 67004 | South Coast County Water District | South Coast County Water District | 2006-11-07 06:50 | 2006-11-07 07:20 | 150 | 150 | BLOCKAGE | N |  |  | 67004 | FAX 858-571-6972 | 2006-11-09 16:20 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2006-11-07 06:50 | 2006-11-07 07:20 | 5 | 150 | 150 | 0 | Ave Las Palmas | Dana Point | 92624 | OC | manhole | 0 | NONE | BLOCKAGE | District personnel received a call from contractor in charge of a storm drain construction project near the intersection of Ave. Las Palmas and Camino Capistrano that sewage was coming out of the pavement near the District manhole. The cause of the spill appeared to be from asphalt being dropped into the manhole when the rings and covers were removed and a round metal plate was placed over the manholes and paved over until the contractor would come back to raise and install rings and covers as part of the street paving. A large amount of asphalt was seen on the manhole shelf when the flow was vacuumed from the manhole. | District personnel placed sand bags in front of the storm drain to contain the SSO and prevent additional sewage entering the storm drain. They proceeded to use another combination jetter truck to vacuum the SSO from inside of MH #547. The jetter hose was then placed inside the line and heading dowstream with the flow, hitting the obstruction at 3 ft. from manhole #547. The video camera was used to video upstream. No problems were found. The camera then ran downstream and a large section of pipe was broken and missing 3 ft. downstream of manhole #547. A contractor was called to excavate and make the necessary repairs to the broken secion of 6" clay pipe. | N | Y | N | n/a | n/a | SSO entered into the storm diversion and into LS #13 | Y | N | n/a | n/a | 0
2413 | 67005 | South Coast County Water District | South Coast County Water District | 2006-12-26 10:00 | 2006-12-26 10:25 | 150 | 150 | PRIVATE PROPERTY | N | X |  | 67005 | FAX 858-571-6972 | 2006-12-28 09:45 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2006-12-26 10:00 | 2006-12-26 10:25 | 0 | 150 | 150 | 0 | 25411 Sea Bluff Drive | Dana Point | 92629 | OC | private lateral | 0 | NONE | BLOCKAGE | District personnel received a call from a customer about an overflowing cleanout. District personnel responded to the site and found the cleanout was overflowing into the storm drain. They closed the CDS unit. The spill was contained and fully recovered. | A combination jetter truck was used to run the high pressure hose in the cleanout that was overflowing. An obstruction was found at approximately 60 ft. from the cleanout. A debris trap was set at the downstream manhole to catch any heavy debris that might be dislodged. At the CDS unit, a jetter truck was used to wash down the storm drain culvert while a combination jetter truck vacuumed the debris and standing water from inside the CDS unit. | N | Y | N | n/a | n/a | SSO was diverted into CDS unit. CDS unit is connected to SCWD collection system | Y | N | n/a | n/a | 0 | Private System Overflow Incident
2412 | 67006 | South Coast County Water District | South Coast County Water District | 2006-12-28 11:05 | 2006-12-28 11:35 | 300 | 0 | LINE BREAK | N |  |  | 67006 | FAX 858-571-6972 | 2006-12-28 17:15 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2006-12-28 11:05 | 2006-12-28 11:35 | 10 | 300 | 0 | 300 | Ceanothus | Laguna Beach | 92651 | OC | 8" sewer line | 0 | NONE | LINE BREAK | District personnel were cleaning the 8" sewer line in the easement at Laguna Sur from MH #1283 (near Ceanothus and Alta Loma) with combination jetter truck. Abount 29 ft. from manhole #1283 the jetting hose got stuck and could not be removed. After pulling on it for several minutes, District personnel noticed sewage coming from the slope under the pipe. It appeared that while the jetting was taking place, the mortar lining came off the inside of the pipe exposing several feet of corrosion in the pipe and a break | District personnel located and excavated the break on the ductile iron pipe (DIP). The pipe was exposed and a section of pipe was cut out at the top to provide access to the sewer line to do video inspection. At this point, the flow was diverted back into the DIP by highlining a temporary sewer line until repairs were made. A contractor was also called to expedite completion of the repairs. District personnel ran the video camera upstream to visually inspect the pipe condition. Heavy scale buildup was observed downstream. The line was again jetted to remove loose scale that remained inside the pipe. Approximately 14 ft. of 8" DIP was replaced with 8" C-900 PVC to prevent additional leaks. The remaining section of sewer pipe will be inspected and excavated and/or lined as necessary starting the week of January 2, 2007. | N | N | N | n/a | n/a | SSO seeped into soil downstream of break | Y | N | n/a | n/a | 0
| 50620 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 07/07/06 - 9:00 | 07/07/06 - 10:00 | 900 | 2000 | Roots | N |  |  | 50620 | Clay Clifton | 07/10/06 - 9:30 | Mario Remillard | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 07/07/06 - 9:00 | 07/07/06 - 10:00 | 15 | 900 | 2000 | 0 | 7017 Nutmeg Way | Carlsbad | 92009 | SD | Manhole | 0 | N/A | Roots | Roots blocking flow in sewer main | Vactored out roots to let flow go through in main. | N | Y | N | Storm drain inlet on Nutmeg | Storm drain system | Storm drain box | Y | N | N | N/A | 0 | None
| 50621 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 07/13/06 - 8:15 | 07/13/06 - 9:45 | 45 | 45 | Debris | N | X |  | 50621 | Clay Clifton | 07/14/06 - 10:30 | Mario Remillard | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 07/13/06 - 8:15 | 07/13/06 - 9:45 | 0.5 | 45 | 100 | 0 | 1860 Marron | Carlsbad | 92008 | SD | Private lateral cleanout | 0 | N/A | Debris | Debris in lateral blocked sewage from passing to main | Private company snaked out lateral. Recommend that Restaurant cleans their private lateral more often. | N | Y | N | Storm drain box | None | Storm drain box | Y | N | N | N/A | 0 | Private lateral
| 50622 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 08/24/06 - 8:00 | 08/24/06 - 9:00 | 60 | 60 | Unknown | N |  |  | 50622 | Clay Clifton | 08/24/06 - 16:00 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 08/24/06 - 8:00 | 08/24/06 - 9:00 | 1 | 60 | 60 | 0 | 3601 Monroe St | Carlsbad | 92008 | SD | Backed up inside swim complex building | 0 | N/A | Unknown | Unknown cause of blockage caused sewer lateral to back up into swim complex. *All of the back up was vacuumed up and returned to sewer. | Televised lateral, take appropriate steps to replace or rehab. | N | N | N | None | None | Recaptured with shop vac | Y | N | N | N/A | 0 | None
| 50623 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 09/09/06 - 11:00 | 09/09/06 - 13:00 | 600 | 0 | Roots | N |  |  | 50623 | Clay Clifton | 09/11/06 - 10:00 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 09/09/06 - 11:00 | 09/09/06 - 13:00 | 5 | 600 | 0 | 600 | 3500 Catalina | Carlsbad | 92010 | SD | Inside of residence | 0 | N/A | Roots | Roots in sewer main caused back up | Investigate overflow cause, televise it. Inform resident that they should remove tree from over our sewer easement. | N | Y | N | Storm drain box | Storm Drain | Storm drain | Y | N | N | N/A | 0 | Minor spill in bathroom of 3500 Catalina, clean up was done. Strom drain outlet was not flowing. Stagnant water standing there.
| 50624 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 09/25/06 - 11:00 | 09/25/06 - 11:30 | 30 | 30 | Roots | N |  |  | 50624 | Clay Clifton | 09/26/06 - 13:30 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 09/25/06 - 11:00 | 09/25/06 - 11:30 | 1 | 30 | 100 | 0 | 3500 Roosevelt | Carlsbad | 92008 | SD | Property line cleanout | 0 | N/A | Roots | Root intrusion at main caused overflow | Rehab or replace 4" sewer lateral | N | N | N | Gutter | None | Recaptured overflow in gutter | Y | N | N | N/A | 0 | None
| 67001 | City of Encinitas | City of Encinitas | 2006-08-14 11:00 | 2006-08-14 11:30 | 200 | 200 | Vandalism | N |  |  | 67001 | Bob Morris VOICEMAIL | 2006-08-14 14:30 | Shawn Atherton | 760-633-2871 | City of Encinitas | City of Encinitas | 2006-08-14 11:00 | 2006-08-14 11:30 | 6 | 200 | 200 | 0 | 95 N. Vulcan | Encinitas | 92024 | SD | F-96 | 0 | NA | Vandalism | Someone removed manhole cover, then threw pieces of manhole cement and rocks into manhole, then replaced cover | All concrete removed from manhole, total flow restored, all manholes were locked | N | N | N | none | none | Water puddled on dirt easement | Y | N | N | none | 0 | This was a partial blockage, some flow still going through, causing slight backup
| 67001 | City of Escondido | City of Escondido | 2006-08-16 11:25 | 2006-08-16 14:30 | 370 | 240 | PRIVATE PROPERTY | N | X |  | 67001 | Fax 858-571-6972 Eric Becker | 2006-08-16 14:30 | John Vaught | (760)839-4323 | City of Escondido | City of Escondido | 2006-08-16 11:25 | 2006-08-16 14:30 | 2 | 370 | 240 | 130 | 2855 Wanek Rd. | Escondido | 92027 | SD | Private cleanout | 0 |  | PRIVATE PROPERTY | Unknown Private Cleanout | City pretreatment inspector investigated and may issue the property manager a Notice of Correction. | N | Y | Y | Escondido Creek | San Elijo Lagoon |  | Y | N | N
| 67002 | City of Escondido | City of Escondido | 2006-08-22 08:00 | 2006-08-22 14:30 | 780 | 80 | CONSTRUCTION | Y |  |  | 67002 | Fax 858-571-6972 Eric Becker | 2006-08-22 16:30 | Ron Canfield | (760)839-4599 | City of Escondido | City of Escondido | 2006-08-22 08:00 | 2006-08-22 14:30 | 2 | 780 | 80 | 700 | 200 E. Via Rancho Pkwy. | Escondido | 92029 | SD | City manhole 4531 | 0 |  | CONSTRUCTION | Trench backfill from an incorrectly installed private sewer lateral caused a blockage in City mainline. | Private contractor repaired sewer lateral. City crews cleaned & vacuumed mainline, captured runoff, pulled water samples for testing and posted warning signs. | N | Y | Y | Natural Creek | Lake Hodges |  | Y | N | Y | Sunset Dr. & Lake Hodges east of I-15 | 3 | The point of discharge into Lake Hodges east of I-15 has been dammed up by CalTrans contractors working on the freeway expansion project.
| 67003 | City of Escondido | City of Escondido | 2006-08-30 10:20 | 2006-08-30 11:00 | 440 | 440 | CONSTRUCTION | N |  |  | 67003 | Fax 858-571-6972 Eric Becker | 2006-08-30 14:00 | John Vaught | (760)839-4323 | City of Escondido | City of Escondido | 2006-08-30 10:20 | 2006-08-30 11:00 | 11 | 440 | 440 | 0 | 812 Felicita Rd. | Escondido | 92025 | SD | City of Escondido sewer Forcemain #6 | 0 |  | CONSTRUCTION | Excavating contractor damaged city 4" sewer forcemain. | City Public Works crews performed repair and recovery operations. Contractor failed to notice Dig-alert marks in area to be excavated. | N | Y | N | None | None | Captured & returned to the collection system. | Y | N | N
| 67004 | City of Escondido | City of Escondido | 2006-09-17 16:00 | 2006-09-17 16:50 | 100 | 100 | ROOTS | N |  |  | 67004 | Fax 858-571-6972 Eric Becker | 2006-09-18 10:30 | Ron Canfield | (760)839-4599 | City of Escondido | City of Escondido | 2006-09-17 16:00 | 2006-09-17 16:50 | 2 | 100 | 100 | 0 | 1010 Cheastnut Dr. | Escondido | 92025 | SD | City mainline cleanout 2001 | 0 |  | ROOTS | Root intrusion into city main and private laterals. | City main was inspected and roots removed. Future cleaning will included root cutting equipment. | N | Y | N | None | None | Vacuumed from catch basin and returned to collection system. | Y | N | N
| 67001 | City of Laguna Beach | City of Laguna Beach | 2006-07-10 10:30 | 2006-07-10 10:45 | 3 | 2.99 | Debris | N | X |  | 67001 | VOICE MAIL | 2006-07-11 09:00 | Paul Ferrell | 949-497-0765 | City of Laguna Beach | City of Laguna Beach | 2006-07-10 10:30 | 2006-07-10 10:45 | 0.2 | 3 | 2.99 | 0.01 | 783 Summit Drive | Laguna Beach | 92651 | OR | Private clean out | 0 |  | Debris | City staff went down to the clean out and noticed that about 2-3 gallons had overflowed from the cleanout caused by a plugged lateral servicing the resident's property of 783 Summit Drive. | City staff informed the resident directly at 783 Summit Drive, (Tim Healy ) phone 949-715-2611, that he could not use water or the bathroom until a plumber has fixed the problem. It was also determined that the City mainline was fine. City staff followed up later in the day to this address and to make sure there was no further problem at the residence. The plumber arrived the following day and corrected the problem. | N | N | N | None | None | Soaked into the ground at the property. | Y | N | N |  | 0 | Courtesy Notice, Private System overflow
| 67002 | City of Laguna Beach | City of Laguna Beach | 2006-07-11 12:25 | 2006-07-11 14:00 | 20 | 20 | Debris | N | X |  | 67002 | Bob Morris | 2006-07-11 14:00 | Paul Ferrell | 949-497-0765 | City of Laguna Beach | City of Laguna Beach | 2006-07-11 12:25 | 2006-07-11 14:00 | 1.33 | 20 | 20 | 0 | 222 Arch St. | Laguna Beach | 92651 | OR | Private clean out | 0 |  | Debris | City staff went to the clean out and noticed that about 20 gallons had overflowed from the cleanout which was caused by a blocked lateral next to the building. The overflow stayed on the property of 222 Arch St. | We informed the property manager (Nikie Fadel) at 949 278-6300 that she could not use water or the bathroom until a plumber has fixed the problem. It was also determined that the City mainline was fine. City staff did a follow up later in the day to this address to make sure there was no further problem at this building. We did a follow up at the building, Orange Coast Plumbing was on scene and restored the service back to the city's collection system. | N | N | N | None | None | Overflow was contained in the planter box of the property at 222 Arch Street | Y | N | N |  | 0 | Courtesy Notice, Private System overflow
| 67003 | City of Laguna Beach | City of Laguna Beach | 2006-07-23 12:15 | 2006-07-23 12:35 | 150 | 5 | Line Break | N | X |  | 67003 | VOICE MAIL | 2006-07-23 12:50 | Paul Ferrell | 949-497-0765 | City of Laguna Beach | City of Laguna Beach | 2006-07-23 12:15 | 2006-07-23 12:35 | 7.5 | 150 | 5 | 145 | 340 S. Coast Hwy | Laguna Beach | 92651 | OR | Private clean out | 0 |  | Line Break | On Sunday, July 23, 2006 at 12:10 p.m. the Wastewater Division Staff was notified that a sewer lateral servicing the ‘White House’ restaurant at 340 South Coast Highway was overflowing. The sewer lateral appeared to be broken as the plumber was pulling mud from the lateral. | Staff placed sandbags around the lateral cleanout to contain the spill. Using a vacuum truck, staff washed and recovered the overflow from the sidewalk and from the gutterline of the street. Staff contacted the Laguna Beach County Water District who turned the water off to the building until repairs could be made. Staff did a follow-up to the site on the afternoon of July 25, 2006 and corrective measures had been taken to restore the sewer lateral to an operation condition. | N | Y | N | None | None | Overflow recovery efforts from the storm drain were limited due to sand which covers the end of the flood control outlet on the Main Beach in the summer months. | Y | N | N |  | 0 | Courtesy Notice, Private System overflow
| 67004 | City of Laguna Beach | City of Laguna Beach | 2006-08-06 15:00 | 2006-08-07 08:15 | 500 | 0 | Roots | N |  |  | 67004 | VOICE MAIL | 2006-08-07 11:30 | Paul Ferrell | 949-497-0765 | City of Laguna Beach | City of Laguna Beach | 2006-08-06 15:00 | 2006-08-07 08:15 | 0.69 | 500 | 0 | 500 | 743 Davis Way | Laguna Beach | 92651 | OR | Clean out | 0 |  | Roots | Homeowner, Andy Siegenfeld (949) 499-0482 informed Staff member Mike that he had noticed the downstairs toilet was bubbling and started to overflow. His plumber removed the sewer lateral cleanout cap which immediately stopped the overflow into bathroom. Staff removed tree roots from the City mainline about 60 feet down from an upstream manhole. | Mike advised the resident to refrain from using any water in the house and that a City crew would be back first thing in the morning to determine what coarse should be taken. On Monday morning, August 7, Staff responded and arrived on scene at 7:45 a.m. Using roding equipment, Staff rodded from the upstream manhole I21-043 down 60 feet to remove tree roots from the city mainline. This restored flow to the collection system. | N | N | N | None | None | An open canyon area. Efforts for any recovery of the spill were restricted due to the steep terrain heavy vegetation. | Y | N | N |  | 0 | Based upon the duration of time from the reported time of spill, Staff estimated that 500 gallons of sewage had spilled from the cleanout and into a open canyon area. Efforts for any recovery of the spill were restricted due to the steep terrain heavy vegetation.
| 67005 | City of Laguna Beach | City of Laguna Beach | 2006-08-16 09:00 | 2006-08-16 10:30 | 50 | 0 | Line Break | Y | X |  | 67005 | VOICE MAIL | 2006-08-24 14:00 | Paul Ferrell | 949-497-0765 | City of Laguna Beach | City of Laguna Beach | 2006-08-16 09:00 | 2006-08-16 10:30 | 0.56 | 50 | 0 | 50 | 309 Cliff Drive | Laguna Beach | 92651 | OR | Private sewer lateral | 0 |  | Line Break | Las Brisas, a restaurant located at 309 Cliff Drive, next door to the Laguna Art Museum, was in the process of major sewer line repair work by the company ‘Plumbing Master’ (909)683-4840. City officials comfirmed that the private sewer lateral to the restaurant was broken by the construction causing the water to soak into the ground. The water that soaked into the ground surfaced in the lower level of the museum next door. | As a follow up on Monday August 21st it was noted that the Museum was still discharging ground water into the gutter line rather then the sewer system. City officials concluded that the sewer lateral servicing the Las Brisas restaurant was damaged and leaking. The water was soaking into the ground. Repairs were made to the private sewer lateral which services the restuarant and the museum took our recommendation by pumping all ground water into the sewer system. | N | Y | N | None | None | Staff removed approximately two yards of wet sand from the small pond area on the beach with the remaining water soaking into the ground. | Y | N | Y | Main Beach outlet of storm drain near North Lifeguard station. | 3
| 67006 | City of Laguna Beach | City of Laguna Beach | 2006-09-07 16:15 | 2006-09-08 09:00 | 50 | 50 | Line Break | N | X |  | 67006 | Email | 2006-09-14 14:45 | Leah Nealon | 949-497-0342 | City of Laguna Beach | City of Laguna Beach | 2006-09-07 16:15 | 2006-09-08 09:00 | 0.05 | 50 | 50 | 0 | 790 N. Coast Hwy | Laguna Beach | 92651 | OR | Broken sewer lateral and potable water line. | 0 |  | Line Break | Staff determined that the sewer lateral servicing a toilet in the lower level of the home was cracked and leaking under the house. The investigation also revealed a potable water leak under the house which was contributing to the problem and causing the water to surface on the hillside below the property. | Staff using a vacuum truck, washed and recovered the estimated fifty gallons of water and tracing dye from the sidewalk down the hillside from the property and advised the resident not to use any water until repairs could be made. A plumbing company (name unknown) made all neccessary repairs to the sewer lateral and to the broken water line. | N | N | N | None | None | Staff using a vacuum truck, washed and recovered the estimated fifty gallons of water and tracing dye from the sidewalk down the hillside from the property. | Y | N | N |  | 0 | Courtesy Notice, Private System overflow
| 67007 | City of Laguna Beach | City of Laguna Beach | 2006-09-13 07:45 | 2006-09-13 08:05 | 300 | 150 | Grease | N |  |  | 67007 | VOICE MAIL | 2006-09-13 07:45 | Graham Wright | 949-497-0765 | City of Laguna Beach | City of Laguna Beach | 2006-09-13 07:45 | 2006-09-13 08:05 | 15 | 300 | 150 | 150 | 647 S. Coast Hwy | Laguna Beach | 92651 | OR | Sewer Lateral | 0 |  | Grease | The cause of the blockage in the City mainline was attributed to grease. The last time this line was cleaned was May 11, 2006. | Using a high pressure jetting machine, Staff cleaned the City Sewer mainline from Cleo Street lift station (#9) jetting upstream to manhole number E24-20 to break the stoppage. The flow was restored to the collection system at 8:05 a.m. | N | N | N | None | None | Efforts to recover the estimated 300 gallons, which had previously spilled, had soaked into the sand and Staff using a front-end loader, removed one yard of wet sand. | Y | N | N |  | 0 | Wastewater Division Staff were dispatched to the scene and arrived at 7:55 a.m. Confirming that a sewer problem was occurring, Staff, immediately bermed the area with sand to contain the spill. Monica Mazur of the OCHCA advised me that posting signs would not be required after the sand removal.
2095 | 86001 | County of San Diego | County of San Diego | 8/9/06 17:30 | 8/9/06 18:05 | 175 | 0 | GREASE | N |  |  | 86001 | Clay Clifton | 2006-08-10 08:30 | Bill Wiltse | 619-660-2007 | County of San Diego | County of San Diego | 8/9/06 5:30pm | 8/9/06 6:05pm | 5 | 175 | 0 | 175 | Wild Oats Lane | Bonita | 91902 | SD | 590-381-309E | 0 | 0 | GREASE | Stoppage caused by grease and paper in mainline. | Mainline was cleaned and televised … this line segment will be put on accelerated maintenance (cleaned quarterly). | N | N | N | None | None | Wastewater perked into field next to manhole. | Y | N | N | N/A | 0 | No public contact was made to wastewater that perked into the ground. Sanitizing and odor agents were applied to effected area.
| 62002 | Eastern Municipal Water District | Eastern Municipal Water District | 2006-07-06 16:30 | 2006-07-06 18:30 | 50 | 0 | DEBRIS | N |  |  | 62002 | N/A | N/A | N/A | N/A | Eastern Municipal Water District | Eastern Municipal Water District | 07/06/06 1630 | 07/06/06 1830 | 0 | 50 | 0 | 0 | 32220 Highway 79 | Temecula | 92592 | RV | Manhole/Clean-out | 0 | N/A | DEBRIS | Unknown debris causing blockage | Clean-out manhole and customer clean-out | N | N | N | N/A | N/A | Dried on street | N | N | N | N/A | 0 | Customer responsible
| 67001 | City of Vista | City of Vista | 2006-09-08 | 2006-09-09 02:00 | 6000 | 0 | OTHER | Y |  |  | 67001 | faxed | 2006-09-19 10:30 | David Brookbank | 760.726.6328 | City of Vista | City of Vista | 2006-09-08 | 2006-09-09 02:00 | 50 | 6000 | 0 | 6000 | S. Melrose Bridge @ Green Oak Ranch Road | Vista | 92081 | SD | V33 MH 173-174 | 0 | N/A | Other | Shut down of Buena Creek Pump Station to connect old force main to new force main on Faraday Avenue @ S. Melrose Drive; crack in top of sewer main and head pressure caused spill | Expose sewer main, patch hole in pipe and install 4 foot by 4 foot concrete lug around main and remove contaminated soil and import fresh, clean soil | N | N | Y | Agua Hedionda Creek | Agua Hedionda Creek | N/A | Y | Y | Y | All of Buena Vista Park | 4 | Signs were posted at 15:00 Monday, September 11, 2006
| 67001 | Rainbow Municipal Water District | Rainbow Municipal Water District | 2006-09-02 06:30 | 2006-09-02 09:00 | 3000 | 0 | PUMP STATION FAILURE | Y |  |  | 67001 | VOICEMAIL | 2006-09-02 09:11 | Ramon Zuniga | (760) 728-1178 | Rainbow Municipal Water District | Rainbow Municipal Water District | 2006-09-02 06:30 | 2006-09-02 09:00 | 20 | 3000 | 0 | 3000 | 4650 Dulin Road Space # 225 | Fallbrook | 92028 | SD | Sewage lift station failure | 0 | None | PUMP STATION FAILURE | Rainbow Municipal Water District air compressor at lift station # 4 Rancho Monserate failed.Causing bubbler line to fail and pumps to stop pumping and created a high level surcharged 8'' line backing up sewage and releasing sewage at lower end. | Rainbow Municipal Water District technician Brian Fonseca responded to sewage spill/overflow at lift station, came across pump station not pumping and responding.Technician immediately switches H.O.A controls into hand to overide system will not work,then resets electrical breakers and suts of H.O.A controls and lift station begins pumping wet well down,as well as sewage spill at relief valve stops. Crew at spill site begin to disenfect area by applying RDX44 germicide solution around spill area and set up warning sign to keep public away from sewage release.Electrician re installs new back up compressor at lift station and purges out condensation in bubbler tube , physicall opens wet well cover and watches pumps cycles levels alternate and test floats in wet well making sure they work correctly .After 4 pump cycles sewage lift station is back to normal operations.Rancho Monserate notified of sewage release advised to keep people and pets away from sewage spill at 1-760-740-2368 spoke to Laura. | N | N | N | None | None | Soaked into ground / evaporated at open field | Y | Y | Y | Around sewage soaked area | 3 | Ms. Laura Toms at 4650 Dulin Road space # 225 Fallbrook California says she wakes up at 6:30 a.m. to take a coffee break,today 09-02-2006 she heard a noise at her yard so she examined area and saw sewage being released at R.M.W.D relief valve.She then calls Rainbow Water at 7:08 a.m. to report spill and then answering service dispatches sewer duty man to respond . Brian arrives at customer property and notices sewage being dumped out of valve;Brian resets electrical breakers and H.O.A controls and then pumps start to pump wet well down as well as sewage spill stopped.District sewage compressor failed caused 3,000 gallon sewage spill.
| 65009 | Rancho California Water District | Rancho California Water District | 7/23/06, 11:30 | 7/25/06, 8:00 | 93450 | 0 | OTHER | N |  |  | 65009 | Joann Lynn, left message | 7/25/06, 9:00am | David Holguin | (909)772-5047 | Rancho California Water District | Rancho California Water District | 7/23/06, 11:30am | 7/25/06, 8:00am | 35 | 93450 | 0 | 93450 | 34295 Vailranch Parkway | Temecula, Ca. | 92590 | RV | Redhawk recycled pump station. | 0 |  | OTHER | Hole develpoed in pipe on discharge manifold. | Closed discharge valve and dug up pipe to make necessary repairs. | Y | Y | Y | Temecula Creek | none | Temecula Creek | Y | Y | N | n/a |  | OES# 06-4407
| 65388 | Rancho California Water District | Rancho California Water District | 09/08/06, 20:00 | 09/08/06, 21:00 | 600 | 0 | OTHER | Y |  |  | 65388 | Left messange | 09/09/06, 12:00 pm | Mike Horn | (951)296-6900 | Rancho California Water District | Rancho California Water District | 09/08/06, 8:00pm | 09/08/06, 9:00pm | 10 | 600 | 0 | 600 | 27370 Diaz Rd. | Temecula, Ca. | 92590 | RV | Winchester Park Sewage Lift Station | 0 |  | OTHER | Temporary Ph meter supply hose dislodged from its secured position. | Ph meter was properly scured and storm drain was blocked with absorbent socks to catch flow. | N | Y | Y | Murrieta Creek | none | Murrieta Creek | Y | Y | Y | Murrieta Creek | 5 | OES# 06-2233
| 67002 | MCB CAMP PENDLETON | MCB CAMP PENDLETON | 2006-07-13 08:00 | 2006-07-13 09:10 | 250 | 225 | Blockage | N |  |  | 67002 | Joann Lim | 2006-07-13 14:01 | Teya K. Daniel | (760) 725-9762 | MCB CAMP PENDLETON | MCB CAMP PENDLETON | 2006-07-13 08:00 | 2006-07-13 09:10 | 3.57 | 250 | 225 | 25 | 41 Area, Fisher St, Building 41371,41372 | MCB CAMP PENDLETON | 92055-5008 | SD | Clean out | 3 | 5/11/06;5/16/06 | Blockage | Two clean outs in 41 Area overflowed due to blockage in the sewer line. | The water supply to the building was temporarily shutdown to prevent more sewage flowing out of the clean outs. A vactor was placed next to the storm drain and prevented more sewage entering the storm drain. In addition, a drain mat was placed over the strom drain to ensure wastewater intrusion. The concrete deck was wash down with water. Natural disinfection(sunlight) followed. A request was made to use CCTV to inspect the sewer line to identify the problem. | N | Y | N | None | None | Overflow entered a storm drain but did not reach actual receiving waters. | Y | NA | N | N/A | N/A | The spill from both clean outs flowed towards the center of the parade deck and converged. The spill flowed westward and entered a storm drain but did not reachg actual receiving water. Total distance traveled: App 150 feet No epected public contact.
| 67003 | MCB CAMP PENDLETON | MCB CAMP PENDLETON | 7/30/2006; unknown | 2006-07-30 17:30 | 3500 | 0 | Grease | N |  |  | 67003 | Joann Lim | 2006-07-31 10:15 | Luis Ledesma | (760) 725-0141 | MCB CAMP PENDLETON | MCB CAMP PENDLETON | 7/30/2006; unknown | 2006-07-30 17:30 |  | 3500 | 0 | 3500 | 14 Area, Building 140212 | MCB CAMP PENDLETON | 92055-5008 | SD | MH14-Y-144; MH14-Y-144A;MH14-Y-144D | 0 |  | Grease blockage | A line blockage prior to manhole number 14-Y-139 forced a backup into MH 14-Y-144, 14-Y-144A, 14-Y-144D and parking lot at Building 140210 140211,140212 and into the oil-water separator by Bldg 140209. | The response team used a water jetter to remove the grease blockage in the line between MH 14-Y-139 and 14-Y-144. Spill flowed into adjacent dry culvert and percolated into the ground. Areas were secured to contain washdown drainage. The parking lot area was washed down with fresh water. Drain barriers were used to ensure that washdown water did not enter the stormdrains. All washdown water was recovered. | N | Y | N | None | None | Overflow reach a dry culvert adjacent to Bldg 140210 but did not reach actual receiving water. | Y | Y | N | NA | 0 | The spill did not reach Urine Lake or Lake O'Neill. The spill travelled along a dry culvert at the end of Bldg 140210 before percolating into the ground. . Total distance traveled: 1200 feet No expected public contact.
| 67004 | MCB CAMP PENDLETON | MCB CAMP PENDLETON | 2006-08-08 09:40 | 2006-08-08 09:50 | 20 | 10 | OTHER | N |  |  | 67004 | Quarterly Report |  |  | (760) 725-6762 | MCB CAMP PENDLETON | MCB CAMP PENDLETON | 2006-08-08 09:40 | 2006-08-08 09:50 | 0.33 | 20 | 10 | 10 | 52 Area, Building 520422 | MCB CAMP PENDLETON | 92055-5008 | SD | MH11-Y-55 | 0 |  | A sudden release of huge vollume of wastewater to the sewer line. | New plumbing fixtures were installed at building no. 520422. To check for leakage, contractor flushed out the lines. Due to a huge volume of water released into the sewer line, the manhole overflowed.Sewage overflowed from manhole 11-Y-55. | Water supply to the building was cut off to prevent more sewage overflowing in to the sewer line. A vactor recovered 10 gallons of sewage from the manhole. The remaining percolated into the ground. Sewer lines were jetted in case of possible blockage. During the process, maintenance crew felt that there was no blockage. Impacted area was flushed with clean water. Root killer was also applied to rid of roots in case there are any. | N | N | N | None | None | About ten gallons of wastewater was recovered and the rest percolated into the ground. | N |  | N | N/A |  | Sewage overflowed from a manhole when the contractor flushed out water from building 520422 to check leakage from the new plumbing fixtures installed. Total distance traveled: 10 feet No expected public contact.
| 67005 | MCB CAMP PENDLETON | MCB CAMP PENDLETON | 2006-08-08 19:00 | 2006-08-08 19:50 | 800 | 0 | PUMP STATION FAILURE | N |  |  | 67005 | Quarterly Report |  |  | (760) 725-0141 | MCB CAMP PENDLETON | MCB CAMP PENDLETON | 2006-08-08 19:00 | 2006-08-08 19:50 | 16 | 800 | 0 | 800 | 22 Area | MCB CAMP PENDLETON | 92055-5008 | SD | MH3-Y-01;MH-Y-02;MH3-Y-03 | 0 |  | Influent pump failure | Influent pump #1 and #2 shut down when the electronic component for the pump control failed. As a result MH3-Y01, MH3-Y-02 and MH3-Y-03 overflowed. | To stop the overflow, the pumps were activated after setting the control in hand operation. The impacted area was allowed to dry naturally. An electronic technician will replace the electronic component (PLC) of the pump control and will also check the float control to determine why it did not activated when the PLC failed. | N | N | N | None | None | Overflow percolated into the ground. | Y |  | N |  | 0 | The wastewater flowed along the northside of Vandergrift Rd. Total distance traveled: 200 feet No expected public contact.
| 67006 | MCB CAMP PENDLETON | MCB CAMP PENDLETON | 2006-08-17 10:50 | 2006-08-17 12:30 | 35 | 34 | Blockage | N |  |  | 67006 | Quarterly Report |  |  | (760) 725-9762 | MCB CAMP PENDLETON | MCB CAMP PENDLETON | 2006-08-17 10:50 | 2006-08-17 12:30 | 0.35 | 35 | 34 | 1 | 41 Area, Bldg 41731-2, Building 41371-2 | MCB CAMP PENDLETON | 92055-5008 | SD | Clean Out | 4 | 5/11/06;5/16/06 | Blockage | Blockage in the lateral caused sewage overflow from two clean outs. | The water supply to the building was turned off temporarily to avoid further sewage spillage from the two clean outs. The lateral was jetted to clear the blockage. Absorbent socks and dikes prevented the spill to flow further. After isolating the spill It was recovered with a vactor. The impacted concrete deck was flushed with clean water. A CCTV to the lateral has been performed by MAC Tech. FMD will review the photos to determine the problem. | N | N | N | None | None | Wastewater did not enter the storm drain this time. It was captured by a vactor. | Y |  | N |  |  | The spill from two clean outs flowed towards the center of the parade deck. Total distance traveled: 150 feet No expected public contact.
| 67007 | MCB CAMP PENDLETON | MCB CAMP PENDLETON | 2006-09-19 08:20 | 2006-09-19 08:40 | 1500 | 500 | PumpStationFailure | N |  |  | 67007 | Charles Cheng | 2006-09-19 14:46 | Teya K. Daniel | (760) 725-9762 | MCB CAMP PENDLETON | MCB CAMP PENDLETON | 2006-09-19 08:20 | 2006-09-19 08:40 | 10 | 1500 | 500 | 1000 | 22 Area, Building PS220205 | MCB CAMP PENDLETON | 92055-5008 | SD | Wet Well | 0 |  | PumpStationFailure | A fuse in the control panel of the pump station burnt out causing the pumps to fail. When the pumps failed, the wet well overflowed. | The fuse was replaced and the pumps went back on line. When the pumps went back on line, the wet well stopped overflowing. The ponded effluent along the grassy area was collected with the vactor. The concrete area was washed down and the grassy area was limed. The contractor to this newly repaired pump station was contacted and requested to further inspect the system for possible deficiencies. | N | N | N | None | None | Overflow percolated into the ground. | Y | Y | N |  |  | From the wet well, sewage flowed out on the concrete stage and moved westward. The flow continued to glide south of the structure towards the grassy area and went further south along the tall bushes. Total distance traveled: 110 feet. No expected public contact.
| 67008 | MCB CAMP PENDLETON | MCB CAMP PENDLETON | 2006-09-29 13:00 | 2006-09-29 15:40 | 3100 | 2500 | CONSTRUCTION | N |  |  | 67008 | Charles Cheng | 2006-09-29 16:40 | Luis Ledesma | (760) 725-9762 | MCB CAMP PENDLETON | MCB CAMP PENDLETON | 2006-09-29 13:00 | 2006-09-29 15:40 | 19.37 | 3100 | 2500 | 600 | 41 Area, railroad track parallel to Stuart Mesa Rd. | MCB CAMP PENDLETON | 92055-5008 | SD | Force Main | 0 |  | Construction error | An AMTRAK contractor hit a sewer line when excavating the slope for the new railroad trak. | The lift station located at one of the CALTRANS rest stop was turned off to stop the flow of wastewater in the force main. Base maintenance crew recovered the wastewater with their vactor. A full circle repair clamp was installed on the damaged section of the pipe. Impacted area was limed. | N | N | N | None | None | About 3100 gallons was recovered and about 600 percolated into the ground. | Y | Y | N |  | 0 | The wastewater was contained into the excavation ditch and was recovered by the vactor. From the force main, effluent ponded about 4 feet northward and about 30 feet southward. Total distance traveled: 34 feet No expected public contact.
| 67001 | Olivenhain Municipal Water District | Olivenhain Municipal Water District | 2006-09-07 16:30 | 2006-09-07 17:30 | 300 | 300 | ROOTS | N |  |  | 67001 | QUARTERLY REPORT | 2006-11-01 08:00 | CHAD DAVISSON | (858) 451-7837 | Olivenhain Municipal Water District | Olivenhain Municipal Water District | 2006-09-07 16:30 | 2006-09-07 17:30 | 5 | 300 | 300 | 0 | THORNMINT ROAD | SAN DIEGO | 92127 | SD | MANHOLE | 0 | 0 | ROOTS | Root obstruction resulted in manhole overflow | wastewater was contained and removed via pumper truck. Subsequent line cleaning, root removal and video was conducted. | N | N | N | None | None | Collected wastewater disposed of at District's Sewer Pump Station | N | N | N | None | 0
| 60701 | City of Chula Vista | City of Chula Vista | 2006-07-26 08:00 | 2006-07-26 08:30 | 5 | 5 | ROOTS | N | X |  | 60701 | 1 (858) 495-5579 | 2006-07-26 08:15 | City of Chula Vista PW dispatch | (619) 397-6000 | City of Chula Vista | City of Chula Vista | 07/26/06 8:00 AM (Approx) | 2006-07-26 08:30 | 0.16 gallons per minute | 5 | 5 | 0 | 73 East Oxford St. | Chula Vista | 91911 | SD | Private Cleanout | 0 | None | ROOTS | Roots at the tap-in | Rod out lateral and placed in repair list. Will monitor lateral until repair is made | No | No | No | None | None | Sewage trickled 15 feet down curb line, first responding unit contained spill by placing geo-logs to prevent spill from spreading. Flusher came after and vacuumed spill and decontaminated area with bleach. | Yes | N/A | Not necessary | N/A | N/A | Spill was very minimal and fully recovered
| 60702 | City of Chula Vista | City of Chula Vista | 2006-09-01 08:00 | 2006-09-01 10:15 | 50 | 50 | GREASE | N | X |  | 60702 | 1 (858) 495-5579 | 2006-09-01 09:47 | City of Chula Vista | (619) 397-6000 | City of Chula Vista | City of Chula Vista | 09/01/06 8:00 AM (Approx) | 2006-09-01 10:15 | 0.37 gallons per minute | 50 | 50 | 0 | 577 Oxford Ave. | Chula Vista | 91911 | SD | Private Cleanout | 0 | None | Grease and Debris | Grease and debris in private sewer lateral, 27 feet of sag on sewer lateral | Rod out , TV sewer lateral and place on repair list | No | Yes | No | None | None | Sewer overflow from private lateral spilled into the curb and gutter for an estimated two hours, final destination was at the catch basin (S/E corner of Broadway and Oxford). Footage of travel was 480 feet from cleanout to catch basin, due to the paper and rocks along the gutter and inside the catch basin; spill was contained to the catch basin. Two sewer flushers were used to vacuum and decontaminate spill area. | Yes | N/A | No | N/A | N/A | With the estimated information gathered for flow time, length of spill travel and the debris along the gutter and catch basin, the estimated overflow rate was concluded. 1>. Flow time - 2 hours 15 minutes (135 minutes) 2>.Length of spill travel - 480 feet 3>. Rocks and trash along gutter and catch basin 4>. 50 gals divided 135 minutes = 0.37 gals per minute
| 60703 | City of Chula Vista | City of Chula Vista | 2006-09-26 12:30 | 2006-09-26 14:30 | 12 | 12 | OTHER | N | X |  | 60703 | 1 (858) 495-5579 | 2006-09-26 13:10 | City employee | (619) 397-6000 | City of Chula Vista | City of Chula Vista | 09/26/06 12:30 PM (Approx) | 09/26/06 2:30 PM (Approx) | 0.10 gallon per minute | 12 | 12 | 0 | 720 Third Ave. (Albertson's grocery market) | Chula Vista | 91910 | SD | Private Cleanout | 0 | None | Other - collapsed lateral | According to the private plumber, there is a collapsed section of the sewer lateral. It is approximately six feet from the private cleanout towards the building where the clay pipe and the cast iron pipe connect | A private plumber repair the collapsed section of the sewer lateral | No | No | No | None | None | The destination of the sewer overflow traveled 177 feet form the private lateral, which is located in a gated area behind the building (Albertson's grocery store). Due to heavy debris in the gutter such as pine needles, dirt and overgrowth of shrubs hanging in the gutter prevented the sewage from flowing into a storm drain inlet, which is approximately 15 feet further. BMP's (4) and absorbent materials were placed in the gutter for containment. The store manager was notified of his responsibility of hiring a private plumber and to clean up the sewage overflow. | Yes | N/A | No | N/A | N/A | The graffiti crew of City of Chula Vista was removing graffitti on Albertson's gated back wall and notice a trail of sewage on the ground slowly coming out of the private sewage clean out. They immediately notified the Wastewater supervisor at 1:00 pm. Wastewater crew were on site at 1:15 pm, they investigated the problem and determined that it was a private lateral. The crew placed BMP's (4) on the gutter and notified the store manager of the situation. A private plumber, RC Store Maintenance rodded and televised the lateral and discovered that the lateral was collapsed about six feet before their cleanout. Sewer lateral repair schedulded 9/27/06 according to the plumber. The spillage was vacuumed and was able to avoid any sewage from entering the store drain inlet, which is located about 15 feet downstream. With the estimated information gathered for flow time, length of spill traveled and debris along the gutter line, the estimated overflow rate was concluded. 1>. Flow rate - 2 hours (120 minutes) 2>. Length of spill travel - 177 feet 3>. Debris - pine needles, dirt and overgrowth of shrubs 4>. 12 gallons divided 120 minutes = 0.10 gal/min
| 67001 | City of Coronado | City of Coronado | 2006-08-03 12:00 | 2006-08-03 14:30 | 800 | 0 | OTHER | N |  | O | 67001 | Voice Mail 858-467-2952 | 2006-08-03 14:50 | J Ramirez | 619-522-7380 | City of Coronado | City of Coronado | 2006-08-03 12:00 | 2006-08-03 14:30 |  | 800 | 0 | 800 | 176 C Avenue | Coronado | 92118 | SD | Potable Water Meter | 0 |  | OTHER | Private contractor broke valve on water meter. | CalAm Water shut off water supply and replaced broken water valve | N | Y | Y | San Diego Bay |  |  | Y | N | N |  |  | Courtesy notice only, potable water entered storm drain and bay
| 67002 | City of Coronado | City of Coronado | 2006-08-04 13:00 | 2006-08-04 14:20 |  | 30 | BLOCKAGE | N | X |  | 67002 | Voice Mail 858-467-2952 | 2006-08-04 15:25 | S Jones | 619-522-7380 | City of Coronado | City of Coronado | 2006-08-04 13:00 | 2006-08-04 14:20 |  |  | 30 |  | 90 Trinidad Bend | Coronado | 92118 | SD | Sewer Lateral | 0 |  | BLOCKAGE | Blockage in private sewer lateral caused overflow which flowed into storm drain and bay. Unknown when stoppage occurred or how much sewage entered storm drain. We were notified at 1:00 p.m. | Property owner called plumbing contractor to clear/repair lateral. WWO staff removed overflow from street and storm drain | N | Y | Y | San Diego Bay |  |  | Y | N | N
| 67003 | City of Coronado | City of Coronado | 2006-08-09 18:00 | 2006-08-10 01:15 | 220000 | 6000 | LINE BREAK | N |  | O | 67003 | Quarterly Report |  |  |  | City of Coronado | City of Coronado | 2006-08-09 18:00 | 2006-08-10 01:15 | 500 | 220000 | 6000 | 214000 | 1121 Star Park Circle | Coronado | 92118 | SD | Water Main | 0 |  | LINE BREAK | Water main line break under pavement | CalAm Water repaired line break, City staff assisted with cleanup | N | Y | N |  |  |  | Y | N | N |  |  | Courtesy notice only, potable water entered storm drain, diverted to sewer
| 67004 | City of Coronado | City of Coronado | 2006-08-29 23:22 | 2006-08-30 01:30 | 20 | 20 | BLOCKAGE | N |  |  | 67004 | Quarterly Report |  |  |  | City of Coronado | City of Coronado | 2006-08-29 23:22 | 2006-08-30 01:30 |  | 20 | 20 | 0 | 900 blk J/Alameda alley | Coronado | 92118 | SD | Sewer Main Line | 1 | 2006-04-16 | BLOCKAGE | Tree roots from private property tree in City main line | Used Vactor to clear roots, CCTV line to check for other intrusions | N | Y | N |  |  |  | Y | N | N
| 67005 | City of Coronado | City of Coronado | 2006-09-04 | 2006-09-05 07:30 | 20 | 20 | BLOCKAGE | N |  |  | 67005 | Quarterly Report |  |  |  | City of Coronado | City of Coronado | 2006-09-04 | 2006-09-05 07:30 |  | 20 | 20 | 0 | 922 Olive Avenue | Coronado | 92118 | SD | Sewer Main Line/lateral | 0 |  | BLOCKAGE | Roots from private tree in City main line, caused backup to private lateral | WWO staff cleared main line, called plumbing contractor to clear lateral | N | N | N |  |  |  | Y | N | N
| 67006 | City of Coronado | City of Coronado | 2006-09-07 | 2006-09-07 13:00 | 10 | 10 | BLOCKAGE | N |  |  | 67006 | Quarterly Report |  |  |  | City of Coronado | City of Coronado | 2006-09-07 | 2006-09-07 13:00 |  | 10 | 10 | 0 | 753 Orange Avenue | Coronado | 92118 | SD | Sewer Main Line | 0 |  | BLOCKAGE | Rags in 6" main line | Jetted line and cleared blockage | N | N | N |  |  |  | Y | N | N
| 67007 | City of Coronado | City of Coronado | 2006-09-18 | 2006-09-19 07:30 | 20 | 20 | BLOCKAGE | N |  |  | 67007 | Quarterly Report |  |  |  | City of Coronado | City of Coronado | 2006-09-18 | 2006-09-19 07:30 |  | 20 | 20 | 0 | 849 Orange Avenue | Coronado | 92118 | SD | Sewer Main Line | 1 | 2006-09-07 | BLOCKAGE | Roots from private property trees/grease in sewer main line | Jetted line and cleared blockage | N | N | N |  |  |  | Y | N | N
| 67008 | City of Coronado | City of Coronado | 2006-09-21 19:00 | 2006-09-21 21:00 | 20 | 20 | BLOCKAGE | N |  |  | 67008 | Quarterly Report |  |  |  | City of Coronado | City of Coronado | 2006-09-21 19:00 | 2006-09-21 21:00 |  | 20 | 20 | 0 | 1135 Isabella Avenue | Coronado | 92118 | SD | Sewer Main Line | 0 |  | BLOCKAGE | Debris/sand buildup in sewer main line | Cleared line | N | N | N |  |  |  | Y | N | N
| 67001 | City of Del Mar | City of Del Mar | 2006-07-12 07:20 | 2006-09-12 10:40 | 100 | 100 | BLOCKAGE | N |  |  | 67001 | QUARTERLY REPORT | 2006-09-12 07:20 | Reported by Kip Curry, utility worker of City of Del Mar Public Works Dept | (858) 755-3294 | City of Del Mar | City of Del Mar | 2006-07-12 07:20 | 2006-09-12 10:40 | 0.5 | 100 | 100 | 0 | 1300 Block of Camino Del Mar southbound in #1 (left) lane | Del Mar | 92014 | SD | 6" sewer main between Manhole MH B7-89 to MH B8-12, see GIS Map page B7 and B8 | 2 | 11/21/2005 03/09/06 (both were private lateral stoppage & SSO) | BLOCKAGE | Blockage in wastewater main in 1300 Blk of Camino Del Mar, caused by rags (nylon stockings), grease, small roots | Rodded 6" wastewater main 300 feet, from manhole (Del Mar GIS Map) B7-89 to B8-12. Rodded main twice with 2" and 4" auger. Cleared blockage. | N | Y | N | none | none | Evaporation from road surface and partly absorption in asphalt surface, the rest swept up with City street sweeper | Y | Y | N | N/A | 0 | ±100 gallons was cleared from street surface through evaporation + rest removed with street sweeper. The overflow was initially thought to be water main leak. At 7:20 AM there was only a small spot seepi ng from underground. At ±8:00 AM it had grown to a small puddle. Sewer line was video-ed, one week after incident and showed line clear, some grease built-up and small roots.
| 67001 | City of El Cajon | City of El Cajon | 2006-08-27 22:25 | 2006-08-27 23:00 | 300 | 50 | DEBRIS | Y |  |  | 67001 | fax 858-571-6972 | 2006-08-28 07:00 | Patrick Jackson | 619-441-1658 | City of El Cajon | City of El Cajon | 2006-08-27 22:25 | 2006-08-27 23:00 | 8.6 | 300 | 50 | 250 | 707 Graves Ave. | El Cajon | 92020 | SD | MH 12-073 | 0 | N/A | DEBRIS | Recovered pieces of clay pipe and rocks which caused grease to build up. | This line will be added to our 3 month trouble list. The upstream line is scheduled to be lined by a contractor. | N | Y | Y | Forrester Creek | San Diego River | none | Y | N | Y | Mission Trails Park | 3 | none
| 67002 | City of El Cajon | City of El Cajon | 2006-09-26 06:30 | 2006-09-26 08:15 | 4000 | 2000 | LINE BREAK | N |  |  | 67002 | VOICEMAIL Melissa Valdovinos | 2006-09-26 08:30 | Patrick Jackson | 619-441-1658 | City of El Cajon | City of El Cajon | 2006-09-26 06:30 | 2006-09-26 08:15 | 38 | 4000 | 2000 | 2000 | 502 Patrica Ln. | El Cajon | 92020 | SD | MH 14-80S and 14-81S | 0 | N/A | LINE BREAK | A water main belonging to Helix Water District broke and damaged a City 8" sewer main. Rocks and debris infiltrated the sewer main causing a blockage. A 12 foot section of sewer main was replaced. | none | N | Y | Y | County Ditch | Forrester Creek | San Diego River | Y | Y | N | N/A | 0 | None
| 67001 | City of Imperial Beach | City of Imperial Beach | 9/19/06 0625 | 9/19/06 0635 | 2 | 2 | PUMP STATION FAILURE | N |  |  | 67001 | Quarterly Report | 9/19/06 0630 | Tim Taylor | (619) 627-1374 | City of Imperial Beach | City of Imperial Beach | 9/19/06 0625 | 9/19/06 0635 | 1 | 2 | 2 | 0 | 814 Cypress Ave | City of Imperial Beach | 91932 | SD | P.S.#10 | 0 | N/A | PUMP STATION FAILURE |  | Pump Station #10 is an above ground station. The air relief for pump #1 vibrated loose and sprayed in a downward direction into the station when the pump cycled. The station has a six inch lip inside to contain and drain to the wet well all effluent during maintenance. The angular spray from the air relief line directed effluent towards the floor and the lip causing a small amount of splash to escape between the upper lip and the door bottom. | N | Y | [6 empty] | N | N/A | 0 | There is a storm drain catch basin directly adjacent to the pump station. The effluent had just made it to the storm drain, but the pipe was dry. Since the city is in the process of annual storm drain cleaning, the pipe will be cleaned as a precaution and reported as part of the annual storm drain cleaning
| 2944348 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-08-27 10:32 | 2006-08-27 11:00 | 5 | 140 | ROOTS | Y |  |  | 2944348 | Fax (858) 571-6972 (RWQCB) | 2006-08-29 09:30 | Jose L Oropeza | (858) 654-4142 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-08-27 10:32 | 2006-08-27 11:00 | 5 | 140 | 140 | 0 | 5925 Baja Dr | San Diego | 92115 | SD | 8'' PVC | 1 | 05/05/2006 | ROOTS | Roots & Rocks Blockage | Relieved Root & Rocks Blockage refer it to area supervisor & CCTV to tv after 733 as per policy. | N | N | N | None | None | Street Gutter | Y | Y | N |  | 0 | After Continuing to flush we remove a huge rock out of main and lots of rocks.
| 2944775 | City of San Diego MWWD/WWC | City of San Diego MWWD/O&M | 2006-08-29 08:15 | 2006-08-29 08:43 | 0.01 | 0.3 | OTHER | Y |  |  | 2944775 | Fax (858) 571-6972 (RWQCB) | 2006-08-30 10:15 | Jean Fernandes | (858) 614-5772 | City of San Diego MWWD/WWC | City of San Diego MWWD/O&M | 2006-08-29 08:15 | 2006-08-29 08:43 | 0.01 | 0.3 | 0 | 0.3 | 2800 Dairy Mart Road | San Diego, CA | 92154 | SD | 30"DI | 1 | 8/8/2006 | OTHER | Vac relief valve had debris in it that pervented it from closing completely | Replaced valve with a repaired valve | N | N | N | None | None | Dryed in river bed | Y | Y | N |  | 0 | None
| 2945334 | City of San Diego MWWD/WWC | City of San Diego MWWD/O&M | 2006-08-30 08:00 | 2006-08-30 10:15 | 0.01 | 1.35 | OTHER | Y |  |  | 2945334 | Fax (858) 571-6972 (RWQCB) | 2006-08-31 08:45 | Jean Fernandes | (858) 614-5772 | City of San Diego MWWD/WWC | City of San Diego MWWD/O&M | 2006-08-30 08:00 | 2006-08-30 10:15 | 0.01 | 1.35 | 1.1 | 0.2 | 2800 Dairy Mart Road | San Diego, Ca | 92154 | SD | 30"DI | 2 | 08/08/2006 08/29/2006 | OTHER | Vac relief valve had debris in it that pervented it from closing completely | Isolated valve till replacement valve arrives. | N | N | N | None | None | Dryed in river bed | N | Y | N |  | 0 | None
| 2945356 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-08-31 10:10 | 2006-08-31 10:42 | 25 | 800 | ROOTS | Y |  |  | 2945356 | Fax (858) 571-6972 (RWQCB) | 2006-08-31 18:40 | Jean Fernandes | (858) 615-5772 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-08-31 10:10 | 2006-08-31 10:42 | 25 | 800 | 800 | 0 | 2586 Azure Coast Dr | San Diego, CA | 92037 | SD | 8" VC | 0 | 0 | ROOTS | Roots in manhloe FSN# 70998 caused blockage.` | Rodded 8" vc main relieved root blockage rodded two section up and two down with full size blade. | N | Y | N | None | None | Recoverd at interceptor at La Jolla Shores & Avnda de La Playa | Y | Y | N |  | 0 | Referred to area supervisor and cctv to tv fsn' 2802,2801,2789,2788 and 2783
| 2945580 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-09-02 08:21 | 2006-09-02 09:20 | 3 | 177 | GREASE | Y |  |  | 2945580 | Fax (858) 571-6972 (RWQCB) | 2006-09-02 15:00 | Jose L Oropeza | (858) 654-4142 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-09-02 08:21 | 2006-09-02 09:20 | 3 | 177 | 157 | 20 | 1460 Altadena Av | San Diego | 92105 | SD | 8'' VC | 0 | N/A | GREASE | Heavy Grease Blockage | Flushed 8'' VC Main relieved heavy grease blockage refer to area supervisor & cctv. | N | Y | N | None | None | Soak into Dirt | Y | Y | N |  | 0
| 2945584 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-09-02 09:12 | 2006-09-02 11:35 | 100 | 14300 | GREASE | Y |  |  | 2945584 | Fax (858) 571-6972 (RWQCB) | 2006-09-02 14:00 | Jose L Oropeza | (858) 654-4142 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-09-02 09:12 | 2006-09-02 11:35 | 100 | 14300 | 7500 | 6800 | Munda Rd X Alleghany St | San Diego | 92139 | SD | 10'' VC | 0 | N/A | GREASE | Heavy Grease Blockage | Flushed 10'' VC Main to relieved Grease Blockageat fsn# 60884 refer to area supervisor & cctv | N | Y | N | None | None | Soil & Vegetation Open Space | Y | Y | N |  | 0 | Refer to CCTV fsn's 60884,60883,60661,60654 & 5443698.
| 2945629 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-09-03 15:41 | 2006-09-03 17:00 | 1 | 79 | ROOTS | Y |  |  | 2945629 | Fax (858) 571-6972 (RWQCB) | 2006-09-03 17:30 | Jose L Oropeza | (858) 654-4142 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-09-03 15:41 | 2006-09-03 17:00 | 1 | 79 | 79 | 0 | 13984 Mango Dr | San Diego | 92014 | SD | 8'' PVC | 0 | N/A | ROOTS | Root Blockage | Flusher relieved root blockage in 8'' pvc main refer it to area supervisor & cctv. | N | N | N | None | None | Street Gutter | Y | Y | N |  | 0 | Refer 2 up & 2 Down fsn's to cctv after a 733.
| 2945670 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-09-04 13:56 | 2006-09-04 16:00 | 0.5 | 62 | ROOTS | Y |  |  | 2945670 | Fax (858) 571-6972 (RWQCB) | 2006-09-04 18:30 | Eddie Salinas | (858) 654-4152 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-09-04 13:56 | 2006-09-04 16:00 | 0.5 | 62 | 62 | 0 | 5260 Stone Ct | San Diego | 92115 | SD | 8'' VC | 0 | N/A | ROOTS | Roots Blockage | Flushed 8'' VC Mains relieved root blockage refer to area supervisor & CCTV | N | N | N | None | None | Street Gutter | Y | Y | N |  | 0 | Refer to cctv fsn's 50866,50867,50868,50914 & 50913.
| 2946203 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-09-07 11:11 | 2006-09-07 11:55 | 10 | 440 | GREASE | Y |  |  | 2946203 | Fax (858) 571-6972 (RWQCB) | 2006-09-07 14:45 | Jean Fernandes | (858) 614-5772 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-09-07 11:11 | 2006-09-07 11:55 | 10 | 440 | 440 | 0 | Banning St & Whittier St | San Diego,CA | 92107 | SD | 8"VC | 0 | 0 | GREASE | Grease blockage in 8'vc main | set up containment at overflowing man hole and flushed Fsn 9924 to clear stopage. Also flushed two sections up and two down. | N | Y | N | None | None | Recoverd at diversion valve @ W Point loma & Nimitz Bl | Y | Y | N |  | 0 | Referd fsn# 9924,9929,9928,9923 & 9922 to cctv and area supervisor
| 2946500 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-09-09 17:22 | 2006-09-09 18:30 | 5 | 340 | ROOTS | Y |  |  | 2946500 | Fax (858) 571-6972 (RWQCB) | 2006-09-10 10:00 | Jose L Oropeza | (858) 654-4142 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-09-09 17:22 | 2006-09-09 18:30 | 5 | 340 | 325 | 15 | Richeth Rd X S. Valencia PY | San Diego | 92114 | SD | 8'' PVC | 0 | N/A | ROOTS | Heavy Root Blockage | Set containment next to manhole # 459 at gutter, flushed fsn# 53245 to relieved root blockage.Refer it to area supervisor & cctv. | N | Y | N | None | None | Soak into Dirt Canyon | Y | Y | N |  | 0 | SSO Data Report was faxed on 09/10/2006 due to System down on 09/09/2006. Refer fsn's 53245,53266,53270,53239 & 53246 to cctv.
| 2947401 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-09-15 14:19 | 2006-09-15 15:00 | 50 | 2050 | ROOTS | Y |  |  | 2947401 | Fax (858) 571-6972 (RWQCB) | 2006-09-15 16:30 | Jose L Oropeza | (858) 654-4142 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-09-15 14:19 | 2006-09-15 15:00 | 50 | 2050 | 0 | 2050 | Airoso Av X Dartford Way | San Diego | 92120 | SD | 8'' VC | 0 | N/A | ROOTS | Root Blockage | Machine Rodded 8'' VC Main relieved blockage removed heavy roots rwefer to area supervisor & cctv. | N | Y | N | None | None | Soak into Dirt Canyon | Y | Y | N |  | 0 | Refer to cctv fsn's 58026,58028,57639,58025 & 58024 to tv after 733.
| 2947534 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-09-17 14:30 | 2006-09-17 15:30 | 0.5 | 30 | ROOTS | Y |  |  | 2947534 | Fax (858) 571-6972 (RWQCB) | 2006-09-17 17:00 | Jose L Oropeza | (858) 654-4142 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-09-17 14:30 | 2006-09-17 15:30 | 0.5 | 30 | 0 | 30 | 1754 W. Arbor Dr | San Diego | 92103 | SD | 6'' PVC | 0 | N/A | ROOTS | Root Blockage | flushed 6'' PVC Main to relieved root blockage, Refer to area supervisor & cctv. | N | N | N | None | None | Canyon Behind 1754 W. Arbor Dr. | Y | Y | N |  | 0 | Refer fsn's 23300,23299,23298,23301, & 23302 to CCTV to tv after a 733.
| 2948663 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-09-24 21:18 | 2006-09-24 22:40 | 2 | 164 | ROCKS | Y |  |  | 2948663 | Fax (858) 571-6972 (RWQCB) | 2006-09-25 13:40 | Jean Fernandes | (858) 614-5772 | City of San Diego MWWD/WWC | City of San Diego MWWD/WWC | 2006-09-24 21:18 | 2006-09-24 22:40 | 2 | 164 | 164 | 0 | Afton Rd & Iverson St | San Diego, Ca | 92123 | SD | Unknown | 0 | 0 | ROCKS | Rocks from construction devlopment | Contained spill and removed blockage cleaned two section up and two down and started to clean area. Developer was notified in the am and will finish cleaning mains in area. | N | Y | N | None | None | Contained at storm drain inlet | Y | Y | N |  | 0 | New Construction development no fsn# assigned in the system. Sewer mains are still under developer responsiblity.Fsn# 32519 is for tracking purpose only. City will bill containment and clean up (Clark Realty Builders) Pat Petrell 858-268-8007 x207
| 67001 | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2006-08-09 11:15 | 2006-08-09 15:10 | 170 | 70 | FLOOD DAMAGE | N |  |  | 67001 | After Hours. Voicemail (858) 467-2952 and fax (858) 571-6972. | 2006-08-09 15:25 | Jackie Oravitz | 619-556-7349 | NAVFAC Southwest | NAVFAC Southwest | 2006-08-09 11:15 | 2006-08-09 15:10 | 3 | 170 | 70 | 100 | SUBASE, Sylvester Rd | San Diego | 92152 | SD | Manhole | 2 | 12/20/2005 8/18/05 | Overflow | Line plugged with debris. Debris cleared. | Debris cleared. | N | N | N | San Diego Bay | Pacific Ocean | Flow diverted to sewer manhole. | Y | Y | N | N/A | N/A | Spill evaporated. Site was cleaned up as per PWC sewer spill clean up SOP.
| 67002 | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2006-09-04 01:06 | 2006-09-04 02:00 | 2000 | 0 | PUMP STATION FAILURE | Y |  |  | 67002 | Melissa Valdovinos, fax (858) 467-2952 | 09/04/2006 0700 | Joe Patrias | 619-556-8946 | NAVFAC Southwest | NAVFAC Southwest | 09/04/2006 0106 | 09/04/2006 0200 | 50-100 | 2000 | 0 | 2000 | NASNI, Kilo Pier | Coronado | 92135 | SD | Pump Station | 0 | na | pump station failure | Pump motor electrical overload/breaker tripped. Electrical/control problems. Sewage from lift station overflowed onto the pier and into a storm drain and into San Diego Bay. | Contractor/Electrician investigating pump station and substation. | n | n | Y | San Diego Bay | Pacific Ocean | Pier and was cleaned and sanitized by PWC | Y | Y | Y | Pier | 2 | Site was cleaned up as per PWC sewer spill clean up SOP.
| 67003 | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2006-09-06 01:15 | 2006-09-06 02:00 | 1800 | 0 | PUMP STATION FAILURE | Y |  |  | 67003 | Melissa Valdovinos, fax (858) 467-2952 | 09/06/2006 0600 | Joe Patrias | 619-556-8946 | NAVFAC Southwest | NAVFAC Southwest | 09/06/2006 0115 | 09/06/2006 0200 | 30-50 | 1800 | 0 | 1800 | NASNI, Kilo Pier | Coronado | 92135 | SD | Pump Station | 1 | 2006-09-04 01:06 | pump station failure | Pump motor electrical overload/breaker tripped. Electrical/control problems. Sewage from lift station overflowed onto the pier and into a storm drain and into San Diego Bay. | Contractor/Electrician investigating pump station and substation. | n | n | Y | San Diego Bay | Pacific Ocean | Pier and was cleaned and sanitized by PWC | Y | Y | Y | Pier | 2 | Site was cleaned up as per PWC sewer spill clean up SOP.
| 67004 | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2006-09-15 14:30 | 2006-09-16 17:00 | 50 | 0 | LINE BREAK | Y |  |  | 67004 | Melissa Valdovinos, fax (858) 467-2952 | 09/15/2006 1747 | Jackie Oravitz | 619-556-7964 | NAVFAC Southwest | NAVFAC Southwest | 09/15/2006 1430 | 09/16/2006 1700 | 100 | 50 | 0 | 0 | NASNI, Breakers Beach | Coronado | 92135 | SD | Lift Station | 0 | na | lift station pipe broken | Lift station discharge pipe broken in wet well. | NAVFAC repaired pipe. | n | n | n | San Diego Bay | Pacific Ocean | Discharge soaked into dirt. Wet area was disinfected by spray with bleach solution. Spill also had some evaporation | Y | N | Y | Breakers Beach | 2 | Site was cleaned up as per PWC sewer spill clean up SOP.
| 67005 | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2006-09-25 15:00 | 2006-09-25 15:50 | 630 | 0 | OTHER | N |  |  | 67005 | Melissa Valdovinos, fax (858) 467-2952 | 09/25/2006 1800 | Jackie Oravitz | 619-556-7964 | NAVFAC Southwest | NAVFAC Southwest | 09/25/2006 1500 | 09/25/2006 1550 | 2 | 630 | 0 | 630 | NAVSTA Pier 6 | San Diego | 92136 | SD | Coupling | 2 | 12/2/2005 & 1/25/2006 | Leaking coupling | Coupling was leaking. 600 gallons of the 630 gallons released during repair. | Repaired coupling. Inspect piers more often. | n | n | Y | San Diego Bay | Pacific Ocean | Discharged directly into the bay. Sanitized outside of coupling. | Y | Y | N | na (under pier) | na | Site was cleaned up as per PWC sewer spill clean up SOP.
| 60706 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 10/11/06 - 9:00 | 10/11/06 - 9:30 | 1500 | 100 | Roots | N |  |  | 60706 | Clay Clifton | 10/11/06 - 14:00 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 10/11/06 - 9:00 | 10/11/06 - 9:30 | 50 | 1500 | 100 | 1400 | Aviara Golf Course | Carlsbad | 92009 | SD | Manhole | 0 | N/A | Roots | Roots in manhole caused back up | Routine cleaning and inspections of manholes | N | Y | Y | Desilt basin | None | Desilt Basin | Y | Y | N | N/A | 0 | Desilt basin not accessible to human contact
| 60707 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 10/11/06 - 09:00 | 10/11/06 - 09:30 | 1500 | 12000 | Roots | N |  |  | 60707 | Clay Clifton | 10/12/06 - 15:00 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 10/11/06 - 09:00 | 10/11/06 - 09:30 | 50 | 1500 | 12000 | 0 | Aviara Golf Course | Carlsbad | 92009 | SD | Manhole | 0 | N/A | Roots | Roots in manhole caused back up | We pumped out desilt basin to recapture overflow from yesterday, pumped back into sewer system. | N | Y | Y | Desilt basin | None | Desilt Basin | Y | Y | N | N/A | 0 | Revised final
| 60708 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 10/06/06 - 19:15 | 10/06/06 - 19:45 | 7 | 7 | Debris | N | X |  | 60708 | Clay Clifton | 10/12/06 - 16:15 | Eric Sanders | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 10/06/06 - 19:15 | 10/06/06 - 19:45 | 0.25 | 7 | 7 | 0 | 752 Grand Ave | Carlsbad | 92008 | SD | Sewer lateral cleanout | 0 | N/A | Debris | Seemed to be toilet paper that got blocked in lateral | Used router to clear, will research replacing lateral | N | N | N | None | None | Sidewalk | Y | N | N | N/A | 0 | None
| 60709 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 12/18/06 - 16:00 | 12/18/06 - 16:30 | 30 | 200 | Unknown | N |  |  | 60709 | Clay Clifton | 12/20/06 - 11:30 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 12/18/06 - 16:00 | 12/18/06 - 16:30 | 1 | 30 | 200 | 0 | College Blvd/Palomar Point | Carlsbad | 92011 | SD | Sewer manhole | 0 | N/A | Unknown | Newly constructed manhole overflowed | Instruct contractor to televise the sewer system to determine overflow cause | Y | N | N | Gutter along College Blvd | None | We recaptured small overflow along with wash down water | Y | N | N | N/A | 0 | None
| 60710 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 12/21/06 - 11:15 | 12/21/06 - 11:35 | 10 | 10 | Roots | N |  |  | 60710 | Clay Clifton | 12/21/06 - 1:00 | Marco Castillo | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 12/21/06 - 11:15 | 12/21/06 - 11:35 | 0.25 | 10 | 10 | 20 | 3831 Sierra Morena | Carlsbad | 92008 | SD | Manhole | 0 | N/A | Roots | Roots blocking flow in sewer main | Routed out roots to let sewer flow go through in main, pulled root out | N | N | N | Brow ditch | None | We vacuumed overflow at brow ditch | Y | N | N | N/A | 0 | None
| 60711 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 12/22/06 - 13:30 | 12/22/06 - 15:00 | 180 | 400 | Construction | N |  |  | 60711 | Clay Clifton | 12/22/06 - 16:00 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 12/22/06 - 13:30 | 12/22/06 - 15:00 | 2 | 180 | 400 | 0 | 1800 Block of Aston | Carlsbad | 92009 | SD | Manhole | 1 | 2006-12-18 | Construction | Several different construction projects on Aston. Probably cause, construction debris | Televise main. Instruct contractors to keep debris out of sanitary sewer system | Y | Y | N | Storm drain box on Aston | None | We flushed out and recaptured out of the storm drain system | Y | N | N | N/A | 0 | Crew recaptured overflow.
| 60704 | City of Chula Vista | City of Chula Vista | 2006-10-05 19:00 | 2006-10-05 20:45 | 50 | 50 | UNKNOWN | N | X |  | 60704 | 1 (858) 495-5579 | 2006-10-05 19:30 | City of Chula Vista Police Dispatch | (619) 691-5151 | City of Chula Vista | City of Chula Vista | 10/05/06 7:00 PM Approximate Time | 2006-10-05 20:45 | 2.75 gallons per minute (See remark) | 50 | 50 | 0 | 278 Madrona Street | Chula Vista | 91910 | SD | Private Cleanout | 0 | None | UNKNOWN | Private plumber rodded out 100 feet of private lateral and unplugged line going towards sewer main. Unknown the cause of over flow | Private plumber has temporary corrected problem by unplugging sewer lateral. Any further repairs will need to be done by owner | No | Yes | No | None | None | About half of the spill (estimate 25 gallons) was contained in the parking lot of this property before it entered a private storm drain. Another estimated 30 gallons was contained in a city storm drain channel in the rear of this property. The excessive dirt build up in the channel contained the spill from spreading any further | Yes | N/A | N/A | N/A | N/A | Flusher was used to clean and decontaminate the parking lot and storm drain channel. Dirt and water that were affected in the channel and parking lot were vacuumed up with flusher, 100% recovery due to the exessive build up of dirt in the channel and placement of BMP. When crew arrived on site, spill was self-contained by the indentation of the asphalt in the parking lot of the property, one foot before entering a private storm drain (one BMP was placed on that location). Crew adviced all tenants to stop use of water until the sewer lateral could be cleared. One of the tenants started washing clothes while crew was looking for the clean out that suppose to be closer to the street. We estimated that the washer operated for twenty minutes and fifty gallons of water was used in one cycle (Washer capacity). This is how the estimated overflow rate was concluded. 1>- Time of washer usage - 20 minutes 2>- Capacity of washer - estimate 50 gallons 3>- Five gallons of sewage already spilled 4>- 55 gallons divided 20 minutes = 2.75 gallons per minute
| 60705 | City of Chula Vista | City of Chula Vista | 2006-10-10 07:30 | 2006-10-10 09:30 | 300 | 300 | Roots | N | X |  | 60705 | 1 (858) 495-5579 | 2006-10-10 09:00 | City of Chula Vista Dispatch | (619) 397-6000 | City of Chula Vista | City of Chula Vista | 10/10/06 7:30 AM (Approximate Time) | 2006-10-10 09:30 | 2.50 gallons per minute | 300 | 300 | 0 | 551-581 Mcintosh St. | Chula Vista | 91910 | SD | Private Cleanout | 0 | None | Roots | Roots in lateral causing blockage | Private plumber has temporary corrected problem by unplugging sewer lateral. Owner has been given a citation to make the proper repair to this lateral and avoid another spill | No | No | No | None | None | The estimated 300 gallons spilled into a private concrete brow ditch which length was 700 ft from clean out to private inlet; spill was contained (berm) by a caltrans worker five feet before reaching private drop inlet. City crews were able to vacuum and decontaminate the affected area and 100% containment and recovery was possible. | Yes | N/A | No | N/A | N/A | Estimated overflow rate was concluded in with the following assumptions. 1>. Time of spillage - 120 minutes (estimated) 2>. Ten units affected - estimated 30 gallons per unit (two hour period) 3>. 30 gallons multiply 10 units = 300 gallons total 4>. 300 gallons divided by 120 minutes = 2.50 gallons per minute
| 60706 | City of Chula Vista | City of Chula Vista | 2006-11-04 11:35 | 2006-11-04 12:30 | 10 | 10 | PRIVATE PROPERTY | N | X |  | 60706 | County after hour 858 -565-5255 Haz Mat duty Specialist Responder Jim Paged | 2006-11-04 11:35 | City of Chula Vista Police Dispatch | (619) 397-6000 | City of Chula Vista | City of Chula Vista | 2006-11-04 11:35 | 2006-11-04 12:30 | See Notes #34 | 10 | 10 | 0 | 71 East L Street | Chula Vista | 91911 | SD | Sewer Lateral Cleanout | 0 | None | Roots in lateral | Root in lateral 15 feet from clean out | Worker cleaned up area, area disinfected curb washed down and vacuumed up. Line will be televised ASAP and put on repair list to remove root intrusion. | No | No | No | None | None | Along curb line contained with Geo Logs | Yes | N/A | N/A | N/A | N/A | Homeowner notice water seeping out of clean out located in his front yard. Spill was contained in front yard. City crews arrived and set up Geo Logs along curb line and vacuum truck (Vactor) before unscrewing clean out cap. Spill was captured along curb line before reaching Geo-Logs. Estimated ten gallons was released when cap was remove to rod out line.
| 60707 | City of Chula Vista | City of Chula Vista | 2006-11-09 12:30 | 2006-11-09 13:00 | 200 | 200 | CONSTRUCTION | N |  |  | 60707 | 1 (858) 495-5579 | 2006-11-09 12:45 | City of Chula Vista Police Dispatch | (619) 397-6000 | City of Chula Vista | City of Chula Vista | 11/09/06 12:30 PM Approximate Time | 2006-11-09 13:00 | 6.7 gallons per minute (See remark) | 200 | 200 | 0 | Birch Street and Mater Dei Dr. | Chula Vista | 91914 | SD | Sewer Main | 0 | None | Construction debris/Siphon still in pipe | Private contractors failed to remove the siphon in the manhole. Broken pieces of plastic PVC pipe were also lodged in the mouth of the manhole causing a blockage. This area has not been fully accepted of Public Improvements by the City of Chula Vista | Contained the entire sewer spill. Removed the siphon and broken pieces of PVC pipe and concrete in the sewer main. Cleaned the sewer line segment until all debris was removed. Then proceeded to clean sewer line segments upstream and downstream. CCTV the sewer line segments. Notify the private contractor. | No | No | No | None | None | The estimated 200 gallons spilled onto the street, down the gutter. The sewer spill did not reach the storm drain inlet. The storm drain inlet was 420 feet downstream, with the three BMPS preventing any foreign substance from entering the inlet. In addition to this, the sewer plug level reduced three feet from the manhole lid when arriving on the scene, The city crews were able to vacuum and decontaminate the affected area and obtain 100% containment and a full recover of the sewer spill. | Yes | N/A | N/A | N/A | N/A | Estimated overflow rate was concluded in such manner 1>. Time of spillage - 30 minutes 2>. Estimate 200 gallons 3>. 200 gallons divided by 30 minutes = 6.70 gallons per minute
| 60708 | City of Chula Vista | City of Chula Vista | 2006-12-15 09:15 | 2006-12-15 09:45 | 150 | 150 | Grease | N | X |  | 60708 | 1 (858) 495-5579 | 2006-12-15 09:15 | City of Chula Vista Dispatch | (619) 397-6000 | City of Chula Vista | City of Chula Vista | 12/15/06 9:15 AM (Approximate Time) | 2006-12-15 09:45 | 5 gallons per minute | 150 | 150 | 0 | 700 East Naples Ct. | Chula Vista | 91911 | SD | Private Sewer Main | 0 | None | Heavy grease, rocks and rags | The cause of the overflow was due to heavy grease, rocks and some rags in the sewer main. A lack of a routine sewer system maintenance program on this private sewer system (Veterans Home of California - Chula Vista) is the main cause | City of Chula Vista's Storm Drain Compliance Officer provided the Stationary Engineer the need of establishing a regular sewer maintenance program and provides education to all residents and employees on the premise. The City of Chula Vista would also privide any additional information if needed to their program. | No | Yes | No | None | None | The estimated 150 gallons went onto the private street; some went down the gutter into the City's storm drain inlet. The storm drain inlet was approximately 100 feet downstream; city crews placed eight BMPS (Geo-Logs) along the gutter capturing and preventing most of foreign substance from entering the inlet. A combination vehicle set up at this storm drain inlet to vacuum the spillage and another vehicle was set up several storm drain inlets downstream before the spill reached this area. This was in order to fully contain and vacuum all the spillage. Sewage was fully contained and vacuumed on the street and storm drains; For preventive measures, crews cleaned approximately 450 feet of storm drain downstream from the incident. | Yes | N/A | N/A | N/A | N/A | Estimated assumption overflow rate was concluded in such manner. 1>. Time of spillage - 30 minutes 2>. Estimate 150 gallons 3>. 150 gallons divided by 30 minutes = 5 gallons per minute
| 60709 | City of Chula Vista | City of Chula Vista | 2006-12-21 13:30 | 2006-12-21 14:00 | 500 | 500 | Grease | N | X |  | 60709 | 1 (858) 495-5579 | 2006-12-21 14:00 | City of Chula Vista Public Works | (619) 397-6000 | City of Chula Vista | City of Chula Vista | 12/21/06 1:30 PM (Approximate Time) | 2006-12-21 14:00 | 16-17 gallons per minute | 500 | 500 | 0 | 895 East H St. | Chula Vista | 91911 | SD | Private Sewer Lateral | 0 | None | Heavy grease | The cause of the overflow was due to heavy grease. The following caused the SSO: - Costco's lack of regular maintenance to their private sewer laterals. - According to Costco employees the private plumber inserted the hydraulic jetter in the wrong cleanout causing the sewage to overflow out the sewer lateral cleanout. | City of Chula Vista's Storm Drain Compliance Officer provided Costco a NOV (Notice of Violation) for failing to perform regular maintenance on their private laterals. This NOV will provide the actions of starting the regular sewer maintenance program and education to all employees working for the company. The Compliance Officer will also issue a fine to the private plumber (S.O.S Rooter) for negligence of securing the area without using BMPs and allowing the sewage to enter the storm drain. | No | Yes | No | None | None | The estimated 500 gallons went onto the private road behind Costco; approximately 400 gallons went down the gutter into the storm drain inlet and another 100 gallons was contained and captured by a private company, J & M keystone Inc. (apparently they were called by the private plumber (S.O.S Rooter) to vacuum and contain the spillage after it occurred and before the City of Chula Vista was awared of the incident). Upon arrival city crews tracked the spillage from where it entered the storm drain inlet (northeast corner of building and approx 100 ft from the sewer lateral cleannouts.). City crew did the following steps to secure 100% containment: 1>. A combination vehicle set up behind the K-mart Store (875 East H St.), approximately 1463 feet downstream and west of the incident before the spill had reached this area and began to contain and vacuum. 2>. Another combination vehicle began to clean and decontaminate the upstream line segments and manholes 3>. Next, city crews washed down a concrete area (approximatley 160ft x 93ft = 14,880 sq ft). where the sewer spill occurred. They decotaminated and vacuumed the remnants of grease on the private road. 4>. Sewage was fully contained and vacuumed on the street and in storm drains by city crews. | Yes | N/A | N/A | N/A | N/A | It is estimated 500 gallons came out of the private sewer lateral within that 30 minute time period. The private plumber (S.O.S Rooter) used a hydraulic jetter to clear the sewer blockage. When retrieving the jetter line, that is when all the raw sewage came out of the private sewer laterals. The private plumber did not have any BMPs (i.e. geo-logs and or sandbags) around the area to contain the spill while jetting.
| 67009 | City of Coronado | City of Coronado | 2006-12-06 19:30 | 2006-12-06 20:30 | 200 | 200 | GREASE | N |  |  | 67009 | Quarterly Report |  |  |  | City of Coronado | City of Coronado | 2006-12-06 19:30 | 2006-12-06 20:30 | 3.33 | 200 | 200 | 0 | 1500 Orange Avenue | Coronado | 92118 | SD | Sewer main line | 1 | 2005-11-04 | GREASE | Grease blockage in City main line caused overflow onto construction site, sewer lines were connected to main but not capped | Cleared blockage, scheduled more frequent grease trap inspections of hotel's grease traps | N | N | N | None |  |  | Y | N | N
| 67010 | City of Coronado | City of Coronado | 2006-12-12 16:30 | 2006-12-12 17:00 | 4 | 4 | PRIVATE PROPERTY | N | X |  | 67010 | Quarterly Report |  |  |  | City of Coronado | City of Coronado | 2006-12-12 16:30 | 2006-12-12 17:00 |  | 4 | 4 | 0 | 659 B Avenue | Coronado | 92118 | SD | Sewer lateral cleanout | 0 |  | PRIVATE PROPERTY | Plumber working at residence left cleanout cap unsecured | Cleanout cap secured. Overflow contained in garage, cleaned up by City staff | N | N | N | None |  |  | Y | N | N
| 67003 | City of El Cajon | City of El Cajon | 2006-11-10 14:00 | 2006-11-10 14:30 | 100 | 0 | DEBRIS | N |  |  | 67003 | Fax 858-571-6972 | 2006-11-10 16:30 | Chris Agundes | 619-441-1658 | City of El Cajon | City of El Cajon | 2006-11-10 14:00 | 2006-11-10 14:30 | 3.3 | 100 | 0 | 100 | 550 Graves Ave. | El Cajon | 92021 | SD | 4 inch sewer cleanout at 550 Graves Ave. | 1 | 2006-08-27 | DEBRIS | Sewer main was partially stopped up with a piece of broken clay pipe. Sewer main was running with half the normal flow. Four manholes were filled up half way, two on Graves Ave. and two on Madison Ave. | This sewer line was cleaned on 11-03-06. This section of sewer main is going to be lined by a contractor. When we cleaned the sewer main, we may have dislodged the piece of clay pipe in the main. | N | Y | N | Forrester Creek | San Diego River | San Diego River | Y | N | N | n/a | 0 | none
| 67005 | City of Escondido | City of Escondido | 2006-10-17 12:00 | 2006-10-17 13:00 | 60 | 60 | PRIVATE PROPERTY | N | X |  | 67005 | Fax 858-571-6972 Eric Becker | 2006-10-18 11:00 | Mike Mayfield | (760) 839-4599 | City of Escondido | City of Escondido | 2006-10-17 12:00 | 2006-10-17 13:00 | 1 | 60 | 60 | 0 | 1700 N AutoPark Way | Escondido | 92025 | SD | Private cleanout | 0 |  | PRIVATE PROPERTY | Unknown - Private Sewer | City Environmental Compliance Inspector issued a Notice of Correction requiring the business to clean and CCTV all lines in question. The owner will then provide a video tape of the inspection to determine further course of action. | N | N | N | None | None | Recovered & returned to sanitary sewer. | Y | N | N
| 67006 | City of Escondido | City of Escondido | 2006-10-26 10:00 | 2006-10-26 11:30 | 90 | 90 | PRIVATE PROPERTY | N | X |  | 67006 | Fax 858-571-6972 Eric Becker | 10/26/2006 1530 | Keith Hayashi | (760) 839-4599 | City of Escondido | City of Escondido | 2006-10-26 10:00 | 2006-10-26 11:30 | 1 | 90 | 90 | 0 | 505 B W. Washington Ave | Escondido | 92025 | SD | Private cleanout | 0 |  | PRIVATE PROPERTY | Unknown - Private Sewer | City Environmental Compliance Inspector is investigating and has issued a Notice of Correction requiring the business to have a qualified plumber clean & CCTV the service lateral in question. | N | Y | N | None | None | Dry catch basin near southeast corner of Quince St. & Washington Ave. 660 feet from discharge. | Y | N | N
| 67007 | City of Escondido | City of Escondido | 2006-11-24 12:00 | 2006-11-24 16:00 | 200 | 0 | PRIVATE PROPERTY | N | X |  | 67007 | Fax 858-571-6972 Eric Becker | 11/24/2006 2051 | Jim Miller | (760) 839-4323 | City of Escondido | City of Escondido | 2006-11-24 12:00 | 2006-11-24 16:00 | 0.83 | 200 | 0 | 200 | 512 E. 2nd. St. | Escondido | 92025 | SD | Private cleanout | 0 |  | PRIVATE PROPERTY | Unknown - Private Sewer | The property will be issued a Notice of Correction by our Environmental Compliance Inspector. | N | Y | Y | Escondido Creek | San Elijo Lagoon |  | Y | N | N
| 67008 | City of Escondido | City of Escondido | 2006-12-07 09:20 | 2006-12-07 09:45 | 25 | 0 | PRIVATE PROPERTY | N | X |  | 67008 | Fax 858-571-6972 Eric Becker | 12/07/2006 1400 | Ron Canfield | (760) 839-4599 | City of Escondido | City of Escondido | 2006-12-07 09:20 | 2006-12-07 09:45 | 1 | 25 | 0 | 25 | 505 B W. Washington Ave | Escondido | 92025 | SD | Private cleanout | 1 | 2006-10-26 | PRIVATE PROPERTY | Private lateral had an offset joint & debris. | Business owner was issued a Notice of Correction to repair the lateral in question. | N | Y | Y | Reidy Creek | San Elijo Lagoon |  | Y | N | N
| 67009 | City of Escondido | City of Escondido | 2006-12-18 06:00 | 2006-12-18 10:35 | 550 | 200 | PRIVATE PROPERTY | Y | X |  | 67009 | Fax 858-571-6972 Eric Becker | 12/18/2006 1330 | John Vaught | (760) 839-4323 | City of Escondido | City of Escondido | 2006-12-18 06:00 | 2006-12-18 10:35 | 2 | 550 | 200 | 350 | 2680 S. Escondido Blvd. | Escondido | 92025 | SD | Private cleanout | 1 | 2006-01-19 | PRIVATE PROPERTY | Private overflow from Centre City Café sewer lateral. Cause unknown. | A Notice of Correction will be issued to the manager of the Centre City Café to clean & inspect their service lateral. | Y | Y | Y | South Esc. Blvd Creek | None | Creek flows underground. | Y | N | Y | Verda Ave. La Trieste Pl. La Verona Pl.
| 67010 | City of Escondido | City of Escondido | 2006-12-18 13:30 | 2006-12-18 14:55 | 425 | 425 | PRIVATE PROPERTY | N | X |  | 67010 | Fax 858-571-6972 Eric Becker | 12/18/2006 1530 | John Vaught | (760) 839-4323 | City of Escondido | City of Escondido | 2006-12-18 13:30 | 2006-12-18 14:55 | 5 | 425 | 425 | 0 | 624 E. Mission Ave | Escondido | 92025 | SD | Private cleanout | 0 |  | PRIVATE PROPERTY | Apartment overflow due to blockage in private sewer lateral. | City Environmental Compliance Inspector will issue a Notice of Correction to the property manager. | Y | Y | N | None | None | Recovered & returned to sanitary sewer. | Y | N | N
| 67011 | City of Escondido | City of Escondido | 2006-12-19 11:30 | 2006-12-19 11:40 | 600 | 600 | ROOTS | N |  |  | 67011 | Fax 858-571-6972 Eric Becker | 12/19/2006 1500 | John Vaught | (760) 839-4323 | City of Escondido | City of Escondido | 2006-12-19 11:30 | 2006-12-19 11:40 | 60 | 600 | 600 | 0 | 159 W. 5th Ave | Escondido | 92025 | SD | City manhole #5395 | 0 |  | ROOTS | Overflow due to heavy root intrusion into 8" main line. | Main line was cleaned and will be put on a six month cleaning schedule to ensure reliability. | Y | Y | N | None | None | Recovered & returned to sanitary sewer. | Y | N | N
| 67002 | City of Imperial Beach | City of Imperial Beach | 2006-10-12 10:00 | 2006-10-12 11:45 | 5 | 5 | PRIVATE PROPERTY | N | X |  | 67002 | Quarterly Report | 10/12/06 1000 | Sonia Galaviz | (619) 423-8311 | City of Imperial Beach | City of Imperial Beach | 10/12/06 1000 | 10/12/06 1145 | 1 | 5 | 5 | 0 | 945 13th Street | City of Imperial Beach | 91932 | SD | Private Lateral | 0 | N/A | PRIVATE PROPERTY |  | An unknown caller reported sewerage coming from the property at 945 13th Street. Anthony Sorano and the city Vactor crew were dispatched to asess the problem. The Vactor was stationed downstream to protect the storm drain system. A washdown was performed while the owner of the duplex was contacted. The property owner called for a plumber to fix the private property issue. | N | N | [6 empty] | N | N/A | 0 | The spillage from the lateral was intermittant. The one gals per minute was measured at the peak flow. Total Gals reported was based on what was viewed in the gutter. The response by city personel was fantastic. The spill was cleaned up in very short order. This was clearly a private property issue.
| 67003 | City of Imperial Beach | City of Imperial Beach | 2006-11-09 09:05 | 2006-11-09 09:10 | 5 | 5 | BLOCKAGE | N |  |  | 67003 | Quarterly Report | 11/09/06 0910 | Sonia Galaviz | (619) 423-8311 | City of Imperial Beach | City of Imperial Beach | 11/09/06 0905 | 11/9/2006 0910 AM | 1 | 5 | 5 | 0 | 490 Emory Street | City of Imperial Beach | 91932 | SD | Manhole #211 | 0 | N/A | BLOCKAGE |  | The public works secretary received a call from a maintenance person for the south bay school district stating there was an overflowing manhole in their parking lot. The Vactor truck was on the same block and responded immediately. The blockage had self relieved and the manhole was flowing free. There appaered to be a spill of apx that had run ten feet through the parking lot into an a storm drain. Tidal infulence allowed 250 gallons of ocean water to be vacuumed from the storm drain, ensuring the entire spill volume had been recovered. The upstrem and downstream lines were cleaned using the vator truck. The recovered effluent and ocean water was decanted into the sewer system. | N | Y | [6 empty] | N | N/A | 0 | The spill had self relieved. All effluent was recovered. Quick response was due to the Vactor being on the same block. This sewer line is on the monthly jetting program to ensure it is maintained on a frequent basis. The jetting program is behind this year due to a fifty percent turnover of sewer division personnel.
| 67008 | City of Laguna Beach | City of Laguna Beach | 2006-10-01 17:35 | 2006-07-10 10:45 | 35 | 0 | Blockage | N | X |  | 67008 | VOICE MAIL | 2006-10-01 18:40 | Jason Walker | 949-497-0765 | City of Laguna Beach | City of Laguna Beach | 2006-10-01 17:35 | 2006-07-10 10:45 | 1 | 35 | 0 | 35 | 274 Grand View St. | Laguna Beach | 92651 | OR | Private clean out | 0 |  | Blockage | On scene at 6:10 p.m., and after meeting with the residents (renters of the property), it was determined that the sewer lateral servicing the property was plugged. | As a precautionary measure, I jetted the City mainline from manhole # D22-51 upstream to manhole # D22-41 to rule out the possibility of this being a City mainline problem. I advised the residents to refrain from using any water until repairs were made. A follow-up inspection was performed today, Monday October 2nd and it appeared that a plumber had cleared the line which corrected the problem. | N | N | N | None | None | I estimated that approximately 30-35 gallons had spilled prior to my arrival and had evaporated and or soaked into the pavement. | Y | N | N |  | 0 | Courtesy Notice, Private System overflow
| 67009 | City of Laguna Beach | City of Laguna Beach | 2006-10-02 10:10 |  | 15 | 15 | Debris | N |  |  | 67009 |  | 2006-10-05 12:37 | Leah Nealon |  |  |  | 2006-10-02 10:10 |  | 1.5 | 15 | 15 | 0 | 230 High Drive |  |  |  | Clean out | 0 |  | Debris | Staff arrived on scene at 10:20 a.m. and after meeting with the resident (Mrs. Nancy Wallace 494-8985) confirmed that the sewer lateral servicing her home was plugged and running over. | Staff inspected a City manhole, number E22-025, which is located directly in front of Mrs. Wallace’s property. Staff proceeded to clean what appeared to be a City Mainline. Staff cleaned what was thought to be a City Six- inch sewer mainline but after checking the City district maps, it was determined that this line is a private sewer lateral servicing this property. | N | N | N | None | None | Overflow was contained at the planter box in front of the residents at 230 High Drive | Y | N | N |  | 0 | Courtesy Notice, Private System overflow
| 67004 | City of Oceanside | City of Oceanside | 2006-12-10 09:20 | 12/10/06 10:30 | 700 | 0 | CONSTRUCTION | Y |  |  | 67004 | Voice mail | 12/11/06@0725 | Jeremy Kemp | 435-5842 | City of Oceanside | City of Oceanside | 0920 12/10/06 | 1030 12/10/06 | 10 | 700 | 0 | 700 | 562 Hoover st | Oceanside | 92054 | SD | Manhole | 0 | n/a | CONSTRUCTION | contractor working for the city left sand bags in the manhole over the weekend causing the city line to back-up and spill. | While it is the respponsibility of the contractor to remove downstream protective devices like sandbags, the city inspectors have been told to make sure the contractors remove these in the future. | Y | Y | Y | Loma alto Creek | Pacific Ocean | Pacific Ocean | Y | N | Y | 300' North and South of Loma Alta opening at Buccaneer Beach. | 3 | Sand bags were placed downstream of the pipeline replacement project in a manhole to prevent debris from entering the collection system. At the completion of the project, the sand bags should have been removed. The contractor overlooked this and the pipeline system was put back in sevice. the city used a vactor to clear the stoppage. An entry into the manhole was necessary to determine the cause of the blockage and for the removal of the sand bags. Under the circumstances, the city crews worked as fast as safely possible. The storm drains were closed by which daylight about 1000' away into Loma Alta Creek , creek entry point is approximately 4.5 miles from the Ocean.
| 67005 | City of Oceanside | City of Oceanside | 12/18/06 11:15 | 12/18/06 11:30 | 70 | 70 | ROOTS | N |  |  | 67005 | Bob | 12/18/06@1410 | Jeremy Kemp | 435-5842 | City of Oceanside | City of Oceanside | 1115 12/18/06 | 1130 12/18/06 | 0 | 70 | 70 | 0 | 3528 college BLVD | Oceanside | 92054 | SD | Manhole | 0 | n/a | ROOTS | A large root mass let loose and wedged itself in a manhole channel with a 60degree turn which began to collect rags and debris behind it causing a partal stoppage. | We are tving a nearby lateral that maybe abandoned, which we believe is where the roots are affecting the city line. If so, we are planning to dynamite off the lateral in question. | Y | Y |  | Storm Drain | Storm Drain | n/a | Y | N | N | N/A | 0 | The flow rate is unknown due to spill not constantly flowing. Spill was reported and nearby crew ersponded quikly finding wet pavement but no spilling manhole. Upon futher investigation, partial root mass was removed returning manhole to normal flow. Spill was determined to exist only when pumps from a local privat lift station at a shopping center turned on in which the line couldn't handle with obstruction in the channel. Spill amont was calculated by the size of the puddled water under the bridge.
| 66001 | City of Poway | City of Poway | 2006-12-12 09:15 | 2006-12-12 09:35 | 100 | 0 | OTHER | N |  |  | 66001 | Fax | 2006-12-12 15:30 | Brad Voorhees | (858) 668-4719 | City of Poway | City of Poway | 2006-12-12 09:15 | 2006-12-12 09:35 | 5 | 100 | 0 | 100 | 12913 Avenida La Valencia | Poway | 92064 | SD | Manhole | 0 | N/A | OTHER | 6" piece of pipe recoverd in downstream manhold, assume this pipe to be the cause | Video inspection performed after blockage revieas no defects or infiltration in the 8" main. Pipe recovered during c leanup believed to be the cause. 100 gallons lost in Green Valley creekbed which was dy at the time. | Y | N | Y | Green Vallely Creek bed | None | dry creek bed - Green Valley Creek | Y | N | N | N/A | 0 | No signs were posted due to limited public access and contact.
| 45002 | City of San Juan Capistrano | City of San Juan Capistrano | 2004-12-07 15:55 | 2004-12-07 16:28 | 1600 | 0 | ROOTS | N |  |  | 45002 | FAX 858-571-6972 | 2004-12-08 10:00 | Michelle Perea | (949) 487-4315 | City of San Juan Capistrano | City of San Juan Capistrano | 2004-12-07 15:55 | 2004-12-07 16:28 | 50 | 1600 | 0 | 1600 | Intersection of Ortega Hwy/Belford Dr | San Juan Capistrano | 92675 | OC | Manhole | 0 | 0 | ROOTS | Roots in sewer line caused grease to build up, which in turn, caused the overflow. | City Contractor removed obstruction of roots and jetted the line several times. Sewer line will be cleaned in Feb/March 2005. | Y | Y | Y | San Juan Creek | Pacific Ocean | Pacific Ocean | Y | Y | N
| 45003 | City of San Juan Capistrano | City of San Juan Capistrano | 2004-10-19 08:30 | 2004-10-19 10:00 | 792 | 0 | CONSTRUCTION | N |  |  | 45003 | Quarterly Report | Quarterly Report | Phil Falzarano | (949) 443-6396 | City of San Juan Capistrano | City of San Juan Capistrano | 2004-10-19 08:30 | 2004-10-19 10:00 | 8.8 | 792 | 0 | 792 | Via Cristal | San Juan Capistrano | 92675 | OC | Manhole | 0 | 0 | CONSTRUCTION | Rocks and debris in mainline blocking flow, which appears to be due to construction debris. | Jetted mainline before and after blockage; cctv videotaping of mainline; | Y | Y | Y | San Juan Creek | Pacific Ocean | San Juan Creek | N | N | N
| 67003 | Eastern Municipal Water District | Eastern Municipal Water District | 10/04/06 1625 | 10/04/06 1800 | 600 | 500 | OTHER | N |  |  | 67003 | Voice | 10/5/06 1140 | Al Javier | (951) 928-3777 | Eastern Municipal Water District | Eastern Municipal Water District | 10/04/06 1625 | 10/04/06 1800 | 5 | 600 | 500 | 100 | Auld Rd & Pourroy Rd | Murrieta | 92596 | RV | Force Main 1" Air Vac | 0 | NA | OTHER | Leaking Air Vac | Repair Air Vac | N | Y | N | NA | NA | Storm Catch Basin | Y | N | N | NA |  | Storm catch basin was initially dry; all 100 gallon spilled into dirt basin percolated.
| 67006 | Eastern Municipal Water District | Eastern Municipal Water District | 10/09/2006 1000 | 10/09/06 1115 | 70 | 0 | DEBRIS | N |  |  | 67006 | Quarterly Report | NA | NA | NA | Eastern Municipal Water District | Eastern Municipal Water District | 10/09/2006 1000 | 10/09/06 1115 | 2.5 | 70 | 0 | 70 | Willow Ave & San | Murrieta | 92563 | RV | Manhole #32228 | 0 | NA | DEBRIS | Swimming pool grout and lg rock | Cleared line | N | N | N | NA | NA | Area of Spill | Y | N | N | NA |  | Ground soaked up spill
| 67004 | Eastern Municipal Water District | Eastern Municipal Water District | 11/14/06 1025 | 11/14/06 1730 | 1070000 | 93000 | LINE BREAK | Y |  |  | 67004 | Brian Kelley | 11/14/06 1055 | Al Javier | (951) 928-3777 | Eastern Municipal Water District | Eastern Municipal Water District | 11/14/06 1025 | 11/14/06 1730 | 2378 | 1070000 | 93000 | 977000 | 28079 Diaz Rd | Temecula | 92592 | RV | 10" Force Main | 0 | NA | LINE BREAK | Line was hit during excavation | Repair pipeline | N | N | Y | Murrieta Creek | NA | Murrieta Creek | Y | Y | Y | Along Murrieta Creek | 5 | See reports issued to SD RWQCB associated with spill
| 67005 | Eastern Municipal Water District | Eastern Municipal Water District | 12/20/06 1235 | 12/20/06 1330 | 1000 | 500 | OTHER | Y |  |  | 67005 | Brian Kelley | 12/20/06 1515 | Al Javier | (951) 928-3777 | Eastern Municipal Water District | Eastern Municipal Water District | 12/20/06 1235 | 12/20/06 1330 | 15 | 1000 | 500 | 500 | 28801 Pujol St | Temecula | 92592 | RV | Manhole/Pipe Valve | 0 | NA | OTHER | Leaking Valve | Diverted flow to another pipe and repaired valve | N | N | N | NA | NA | Area of Spill | Y | Y | Y | Roadway access | 5 | Ground soaked up spill
| 67002 | City of Vista | City of Vista | 2006-11-29 | 2006-11-29 | Unknown | 0 | UNKNOWN | N | X |  | 67002 | faxed | 2006-11-29 11:06 | Cirilo Mariscal | 760.726.6328 | City of Vista | City of Vista | 2006-11-29 | 2006-11-29 | Unknown | Unknown | 0 | Unknown | 668 Matagual | Vista | 92083 | SD | Private Lateral | N/A | N/A | Unknown | Two private laterals spilled from private lateral cleanouts, one at 664 Matagual & the other from 561 Vale View Drive. Both cleanouts are at the Matagual easement. They are about 30 feet apart from each other. The cause is unknown. The resident's are to contact plumbers. | Jetted the city mainline & it was clear. Line had been televised about two weeks before the spill. Performed a dye test to determine ownership of private sewer laterals. Residents are to contact plumber to eliminate blockages on their private laterals. | N | N | N | None | None | soaked into ground & no signs of runoff | Y | N | N | N/A | N/A | Residents at 664 Matagual & 561 Vale View were notified of the spills & were advised to get plumbers at site as soon as possible to take care of the problem. Both residents were to contact plumbers of their choice. Neither private laterals were spilling at time of city crews arrival. Spill had soaked into ground & just traces of toilet paper remained behind. Crews arrived at 10:29 a.m.
|  | Rainbow Municipal Water District | Rainbow Municipal Water District | 2006-10-17 14:37 | 2006-10-18 15:00 | 761 | 0 | PRIVATE PROPERTY | Y | X |  |  | VOICEMAIL | 2006-10-17 16:21 | Brian Fonseca | 760-728-1178 | Rainbow Municipal Water District | Rainbow Municipal Water District | 2006-10-17 14:37 | 2006-10-18 15:00 | 0.5 | 761 | 0 | 761 | 4586 Orange Hill Rd | Fallbrook | 92028 | SD | Private sewer latteral | 0 | 0 | PRIVATE PROPERTY | Found blockage at customer sewer latteral.Upon arrival to property noticed toilet paper on ground next to clean out and yard.Customer has a steep 200' run of 4'' abs pipe causing debris to get tangled also customer needs to locate clean outs at property and perform an annual maintenace cleaning of sewer latteral. | Wastewater staff used shovels and buckets to clean up private sewage release.Recovered 2 5 gallon buckets of waste and disenfected spill area with 3 2 1/2 gallons of RDX44 solution around spill release to disenfect site.Crew placed 4 barricades with warning signs to warn people living at house and guest.Staff built a temporary dirt berm to contain sewage released from sewer latteral. - waiting on plumber to arrive at spill site to make repairs.Plumber arrived at property on 10-18-2006 at 2:30 p.m. sewage stopped at 3:00 p.m. | N | N | N | None | None | Soaked into ground/ evaporated at open lot | Y | N | Y | Around sewage soaked area | 1 | 10-18-2006 Plumber arrived at 4586 Orange Hill Rd Las Colinas Plumbing & Rooter Services 1-714-528-8100 took care of sewer overflow at 3:00 p.m.
| 65010 | Rancho California Water District | Rancho California Water District | 2006-10-18 11:50 | 2006-10-18 17:30 | 150000 | 0 | Line Break | N |  |  | 65010 | Charles Chang/Voicemail | 10/19/06 8:30a.m. | David Holguin | 951-296-6900 | Rancho California Water District | Rancho California Water District | 10/18/06 11:50a.m. | 10/18/06 5:30p.m. | 500 | 150000 | 0 | 150000 | Diaz Rd.cross st. Rancho Way | Temecula | 92589 | RV | 20" reclaimed water pipe | 0 | 0 | Line Break | Small hole developed on the 20"reclaimed water pipe. | The valves upstream and downstream of the leak were secured. Repair band was welded on. | N | Y | N | Small tributary | none | Small tributary | Y | Y | N |  |  | OES# 06-6193
| 65011 | Rancho California Water District | Rancho California Water District | 2006-10-25 10:44 | 2006-10-25 11:12 | 181527 | 160000 | LINE BREAK | N |  |  | 65011 | Charles Chang/Voicemail | 2006-10-26 08:00 | David Holguin | 951-296-6900 | Rancho California Water District | Rancho California Water District | 2006-10-25 10:44 | 2006-10-25 11:12 | 6500 | 181527 | 160000 | 21527 | 26879 Diaz Rd. | Temecula | 92589 | RV | 8 " reclaimed water pipeline | 0 | 0 | LINE BREAK | Arizone pipline bored horizontally through 8" reclaimed water mainline | The valves upstream and downstream were secured, used 4" pump to dewater into manhole. | N | N | N | none | none | none | Y | Y | N |  |  | OES# 06-6347
| 67009 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2006-10-12 15:30 | 2006-10-12 16:30 | 25 | 0 | Blockage | N |  |  | 67009 | Quarterly Report |  |  | (760) 725-9762 | MCB CAMP PENDLETON | MCB CAMP PENDLETON | 2006-10-12 15:30 | 2006-10-12 16:30 | 0.42 | 25 | 0 | 25 | 53 Area, Building 53311 | MCB CAMP PENDLETON | 92055-5008 | SD | Sewage leaked from a crack of a concrete swale adjacent to a manhole. | 1 | 4/7/2006 (Inc #820) | Blockage | App. 25 gallons of wastewater leaked out from a crack of a concrete swale. To determine the cause, the manhole adjacent to the concrete swale was inspected. It was noted that it was full of wastewater to about 2/3 its capacity. A vactor collected the wastewater but it continued to fill up. Several manholes were inspected and it was observed that they were about half filled with wastewater. FMD crew discovered a blockage in the main gravity line between MH10-Y-14 and MH10-Y15. When the root blockage was cleared, standing wastewater from the manholes subsided and normal flow was restored. | When the wastewater from manhole no. 10-Y-7 was recovered, the leakage stopped. The spill remained in the concrete swale until it evaporated. FMD crew cleared the blockage in the main gravity line between MH10-Y-14 and MH10-Y-15. Water level from the manholes in the vicinity subsided and normal flow was restored. Disinfection was not necessary since public contract not expected. The spill evaporated overtime and natural disinfection was aided by the sunlight. | N | N | N | None | None | Overlfow stayed in the concrete swale until it evaporated. | Y | NA | N |  | N/A | The sewage flowed westward from the clean out to the culvert and percolated into the dirt downhill. Total distance traveled: 160 feet Expected public contact:No
| 67010 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2006-10-31 07:00 | 2006-10-31 10:00 | 700 | 400 | LineBreak | N |  |  | 67010 | Quarterly Report | 2006-10-31 15:14 | Teya K. Daniel | (760) 725-9762 | MCB CAMP PENDLETON | MCB CAMP PENDLETON | 2006-10-31 07:00 | 2006-10-31 10:00 | 3.9 | 700 | 400 | 300 | 51 Area, San Onofre Beach | MCB CAMP PENDLETON | 92055-5008 | SD | Force main Line Type: PVC Line Size: 4 in | 0 |  | LineBreak | About 700 gallons of sewage seeped above ground due to a cracked force main. | Pump Station 51849 was shut off to stop the flow of sewage into the force main. Sewage was recovered by a vactor. The ground was excavated to locate the distressed section of the line. Cracked section was cut and replaced with identical size and secured by coupling on both ends. Lime was applied to disinfect impacted area. | N | N | N | None | None | Overflow did not reach surface water. About 400 was recovered, and the unrecovered portion percolated into the ground. | Y | NA | N |  | 0 | A slow seepage of wastewater from the ground created a pond of sewage water in one of the parking lot at San Onofre Beach. From the ponded effluent, the wastewaster flowed northwards to about 36 feet from the point source. Total distance traveled: app 75 feet Expected public contact:
| 67011 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2006-11-06 21:00 | 2006-11-06 22:50 | 1200 | 0 | Blockage | N |  |  | 67011 | Charles Cheng | 2006-11-07 08:35 | Teya K. Daniel | (760) 390-0784 | MCB CAMP PENDLETON | MCB CAMP PENDLETON | 2006-11-06 21:00 | 2006-11-06 22:50 | 11 | 1200 | 0 | 1200 | A St., 53 Area, Camp Horno, Building 53436 | MCB CAMP PENDLETON | 92055-5008 | SD | Manhole no 10-Y-10 | 1 | 10/12/2006 (Inc #959) | Blockage | Manhole no 10-Y-10 overflowed due to blockage of debris and roots. | Water supply to the adjacent buildings was turned off to prevent more wastewater flow in the sewer line. The main sewerline was cleared with a high pressure water jetter. The impacted concrete area was washed down with clean water. Standing water from the wash down was collected by a vactor truck. FMD will use root killer to rid of roots in the sewer line. A work request will be placed to remove trees near the sewage line. | N | Y | N |  |  | Overflow did not surface waters but: Spill percolated into the ground. | Y | Y | N |  | 0 | Addendum to Spill path: Along bldg 53433, it was noted that sewage flowed on south and north direction until it reached the storm drain located along A St. From MH 10-Y10, sewage flowed east towards bldg 53420 and 53421. Evidence of overflow was also noted between north and south direction between bldg 53420 / 53421 and 53435/ 53436 and flowed at a down grade rate west toward building 53433. Total distance traveled: 500 feet Expected public contact: No
| 67012 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2006-11-14 | 2006-11-14 09:05 | 450 | 50 | Blockage | Y |  |  | 67012 | Charles Cheng | 2006-11-14 12:23 | Teya K. Daniel | (760) 390-0784 | MCB CAMP PENDLETON | MCB CAMP PENDLETON | 2006-11-14 | 2006-11-14 09:05 |  | 450 gallons | 50 | 400 | 12 Area, Bldg MH 1-Y-111 | MCB CAMP PENDLETON | 92055-5008 | SD | Manhole 1-Y-111 | 0 |  | Blockage | An estimated 450 gallons of sewage overflowed from a manhole. | The manhole was no longer overflowing when the crew arrrived. The impacted side of the road was washed down. Washdown water was collected by a vactor. Blockage was cleared with a high pressure water jetter. Roots blocking the main gravity line was recovered. Lime was applied throughout the impacted dirt including the slope where wastewater flowed. FMD recommends that the trees along the sewer line be removed. | N | Y | N | None | None | Overflow did not reach actual receiving waters.The liquid part of the sewage percolated into the ground and the thick part stayed on the ground and was recovered. | Y |  | Y | Signs were posted on both sides of the bus stop. | 7 days | Dark colored wastewater spilled out of the manhole and flowed downhill. When it reached the bottom of the hill, it flowed northeast and streamed down off the road and entered the storm drain. Total distance traveled: 525 feet Expected public contact: Yes
| 67014 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2006-12-14 10:05 | 2006-12-14 10:45 | 70 | 20 | Blockage | N |  |  | 67014 | Quarterly Report |  |  |  | MCB CAMP PENDLETON | MCB CAMP PENDLETON | 2006-12-14 10:05 | 2006-12-14 10:45 | 1.75 | 70 | 20 | 50 | Bldg 1342,13 Area | MCB CAMP PENDLETON | 92055-5008 | SD | Clean out | 0 |  | Blockage | The clean out overflowed due to obstruction of roots in the main line. | The blockage was cleared with a high pressure water jetter and a vactor. | N | N | N | None | None | Sewage flowed downhill through a culvert and percolated into the dirt. | Y | NA | N | N/A | N/A | Sewage flowed 40 feet from the clean out to the culvert and flowed further 30 feet downhill.
| 67006 | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2006-11-01 08:56 | 2006-11-02 12:00 | 22600 | 0 | LINE BREAK | Y |  |  | 67006 | After Hours. Voicemail (858) 467-2952 and fax (858) 571-6972. | 2006-11-02 11:36 | Jackie Oravitz | 619-556-7964 | NAVFAC Southwest | NAVFAC Southwest | 2006-11-01 08:56 | 2006-11-02 12:00 | 13.9 | 22600 | 0 | 22600 | NAVSTA Pier 6 | San Diego | 92136 | SD | Pipe | 3 | 09/25/2006 09/13/2006 12/2/2005 | Hole in pipe | Corroded lateral pipe | Pipe Repaired | N | N | Y | San Diego Bay | Pacific Ocean | San Diego Bay | Y | Y | Y | Pier | 2 | Pipe repaired.
| 67007 | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2004-11-01 | 2006-11-17 09:00 | 14200000 | 0 | LINE BREAK | Y |  |  | 67007 | After Hours. Voicemail (858) 467-2952 and fax (858) 571-6972. | 2006-11-17 09:30 | Jackie Oravitz | 619-556-7964 | NAVFAC Southwest | NAVFAC Southwest | 2004-11-01 | 2006-11-17 09:00 | Variable | 14.2 Million | 0 | 14.2 Million | NAVSTA, Bldg 3621, Palmer Hall, Norman Scott Rd., 92132 | San Diego | 92132 | SD | Connection | 0 |  | Sewer connection to Storm drain | Connection of sewer lateral to storm drain | Sewer lateral connected to sewer main. | N | Y | Y | Chollas Creek | San Diego Bay | Pacific Ocean | Y | Y | Y | Chollas Creek | 2 | Sewer lateral disconected from strom drain, storm drain cleaned in accordance with NAVFAC spill clean up SOP. Sewer lateral reconnected to sewer main.
| 67008 | U.S. Navy Public Works Center | U.S. Navy Public Works Center | 2006-12-11 12:30 | 2006-12-11 13:00 | 150 | 0 | OTHER | Y |  |  | 67008 | Melisaa Valdovinos Voicemail (858) 467-2724 and fax (858) 571-6972. | 12/11/2006 14:35:00 PM | Jackie Oravitz | 619-556-7349 | NAVFAC Southwest | NAVFAC Southwest | 2006-12-11 12:30 | 12/11/2006 13:00:00 PM | 5 | 150 | 0 | 150 | SUBASE, Sylvester Rd | San Diego | 92152 | SD | Manhole | 2 | 8/9/06 12/20/05 8/18/05 | Overflow | Line plugged with roots and debris. Debris cleared and roots cleared with root cutter. | Debris cleared. Conducting engineering evaluation to upgrade manhole. | N | Y | Y | San Diego Bay | Pacific Ocean | San Diego Bay | Y | Y | Y | Outfall | 2 | Debris cleared. Conducting engineering evaluation to upgrade manhole. Site was cleaned up as per PWC sewer spill clean up SOP.
| 67001 | City of Oceanside | City of Oceanside | 07/25/06 0906 | 2006-07-25 10:00 | 1350 | 1350 | GREASE | N |  |  | 67001 | Bob / message | 7/25/06 1217 | Jeremy Kemp | 760-435-5842 | City of Oceanside | City of Oceanside | 07/25/06 0906 | 2006-07-25 10:00 | 25 | 1350 | 1350 | 0 | 4347 Avenida Soledad | oceanside | 92054 | SD | Manhole | 0 | 0 | GREASE | Heavy Grease in city line caused line to over flow | cctv line to check for possible sag put run on a semi-annual vactor cleaning program. | N | Y | N | storm drain on Avenida Soledad | Storm Drain on Rancho Del Oro | Storm Drain on Rancho Del Oro | Y | Y | N | N/A | 0 | Spill entered a storm drain which daylighted into an open flood channel where full recovery was made. Three vactor trucks recovered the sewer spill mixed with irrigation runoff.
| 67002 | City of Oceanside | SDG&E | Unknown | 2006-09-14 10:40 | 700 | 0 | PRIVATE PROPERTY | N | X |  | 67002 | Sassio | 09/14/06 1613 | Jeremy Kemp | 760-435-5842 | City of Oceanside | SDG&E | Unknown | 2006-09-14 10:40 | 1 | 700 | 0 | 700 | 1400 Blk Downs | Oceanside | 92054 | SD | Private Lateral | 0 | 0 | PRIVATE PROPERTY | A SDG&E power pole was driven straight through customers lateral at 2165 Grandview | Took samples and dyed customers lateral to verify SDG&E responsibility before digging around the power pole. Vactor crew was on site until repairs where made. | N | N | Y | Open flood channel | Loma Alta Creek | Loma Alta Creek | Y | N | N | N/A | 0 | On Monday sept 11 We received a call of an unknown liquid leaking from the ground near a construction site. The city line was flowing fine and there was no obvious problem in the rural area so we took samles to try to determine the substance. Test came back with high fecal matter. We tved the city line which was clear but found a single lateral tie-in about 500' in length to a home on a hill. We dyed their line which in-turn came bubbling up around the pole. The spill totals were estimated at 280 gpd at two an a half days (700 gallons total). An open flood channel was cleaned 100 ft down strem of the pole. The remainning section of flood channel was dry down to loma alta creek. *Update- SDG&E moved the power pole and completed the necessary repairs to the lateral @6pm on thursday. City crews recovered about 300 gallons of sewage and debris from 1040 to 1800.