## Sheet1
FILE # | DATE REPT | TIME REPTD | REPORT BY | PHONE | AGENCY | START DATE | START TIME | END DATE | END TIME | LATE | VOL SPILL | UNITS | VOL RECVR | SPILL LOCATION | CITY | COUNTY | STRUCT ID | CAUSE | RCH SRF WTR | PRIMWTR | SECWTR | DEST | PUBLIC HEALTH NOTI | AREA POSTED | DAYS | ACTION TAKEN | FILE # | AGENCY | START DATE | START TIME | END DATE | END TIME | VOL SPILL | UNITS | SPILL LOCATION | CITY | COUNTY | STRUCT ID | CAUSE | PRIMWTR | ACTION TAKEN
| 930623 | 1400PM | DAVE SEYMOUR | 7145822330 | SANTA MARGARITA WATER DISTRICT | 93/06/22 | 0900AM | 930622 | 0945AM |  | 67500 | GAL |  | LOS ALISOS & MARGUERITE | MISSION VIEJO | OR | WATER MAIN | CONTRACTOR DAMAGED WATER LINE CAUSING RELEA | NO | NONE |  | CONTRACTORS DESILTING BASIN | Y | N
| 930716 | ?????? | JOSE GALINZOGA | 6195277456 | SAN DIEGO, CITY OF | 93/06/28 | 1350PM | 930628 | 1400PM |  | 1800 | GAL |  | 3255 LA JOLLA VILLAGE DRIVE | SAN DIEGO | SD | SEWER PUMP STATION #30 | BUBBLER TUBE IN WETWELL NOT ANCHORED TO BOT | NO | NONE |  | INTERCEPTOR STATION I-1 | N | N |  | SEWER DIVERTED TO STORM DRAIN THEN TO INTERCEP | FILE # | AGENCY | START DATE | START TIME | END DATE | END TIME | VOL SPILL | UNITS | SPILL LOCATION | CITY | COUNTY | STRUCT ID | CAUSE | PRIMWTR | ACTION TAKEN
| 930716 | ?????? | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 93/06/28 | 1030AM | 930628 | 1330PM |  | 900 | GAL |  | 7850 VISTA HILL AVENUE | SAN DIEGO | SD | 8" VC | GREASE | NO | NONE |  | DISSIPATED IN STORM DRAIN | Y | N |  | SEWAGE DRIED IN STORM DRAIN. |  | SANTA MARGARITA WATER DISTRICT | 93/06/22 | 0900AM | 930622 | 0945AM | 67500 | GAL | LOS ALISOS & MARGUERITE | MISSION VIEJO | OR | WATER MAIN | CONTRACTOR DAMAGED WATER LINE CAUSING RELEA | NONE
| 930716 | ?????? | MARK STROHMAN | 6915258682 | SAN DIEGO, CITY OF | 93/06/29 | 1153AM | 930629 | 1300PM |  | 30 | GAL |  | 5505 TEXAS STREET | SAN DIEGO | SD | 8" VC MAIN | ROOTS | NO | NONE |  | STORM DRAIN | Y | N |  | RODDED BY MACHINE. |  | SAN DIEGO, CITY OF | 93/06/28 | 1350PM | 930628 | 1400PM | 1800 | GAL | 3255 LA JOLLA VILLAGE DRIVE | SAN DIEGO | SD | SEWER PUMP STATION #30 | BUBBLER TUBE IN WETWELL NOT ANCHORED TO BOT | NONE | SEWER DIVERTED TO STORM DRAIN THEN TO INTERCEP
| 930716 | ?????? | R.L. WILLIAMS | 6915258686 | SAN DIEGO, CITY OF | 93/06/30 | 1830PM | 930701 | 1830PM |  | 72000 | GAL |  | 3675 BELLING AVENUE | SAN DIEGO | SD | 8" VC SEWER MAIN | VANDALISM | NO | NONE |  | SOAKED IN DRY CREEK BED. | Y |  |  | OVERFLOW DIVERTED BACK TO SYSTEM UNTIL MORE RE |  | SAN DIEGO, CITY OF | 93/06/28 | 1030AM | 930628 | 1330PM | 900 | GAL | 7850 VISTA HILL AVENUE | SAN DIEGO | SD | 8" VC | GREASE | NONE | SEWAGE DRIED IN STORM DRAIN.
| 930716 | ?????? | RONOALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 93/07/02 | 1400PM | 930702 | 1500PM |  | 60 | GAL |  | 24TH & BROADWAY | SAN DIEGO | SD | 6" CP | GREASE | NO | NONE |  | STORM DRAIN | Y |  |  | FLOWED INTO STORM DRAIN WHERE IT SETTLED. |  | SAN DIEGO, CITY OF | 93/06/29 | 1153AM | 930629 | 1300PM | 30 | GAL | 5505 TEXAS STREET | SAN DIEGO | SD | 8" VC MAIN | ROOTS | NONE | RODDED BY MACHINE.
| 930716 | ?????? | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 93/07/03 | 1100AM | 930703 | 1200PM |  | 600 | GAL |  | ALDINE DR. * FAIRMONT AVE. | SAN DIEGO | SD | 8" VC | ROCKS | NO | NONE |  | DIRT IN CULVERT | Y |  |  | FLOWED INTO CULVERT AND SOAKED INTO DIRT. |  | SAN DIEGO, CITY OF | 93/06/30 | 1830PM | 930701 | 1830PM | 72000 | GAL | 3675 BELLING AVENUE | SAN DIEGO | SD | 8" VC SEWER MAIN | VANDALISM | NONE | OVERFLOW DIVERTED BACK TO SYSTEM UNTIL MORE RE
| 930716 | ?????? | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 93/07/05 | 1500PM | 930705 | 1630PM |  | 450 | GAL |  | 3202 CAMINITO QUIXOTE | SAN DIEGO | SD | 8" VC | GREASE | NO | NONE |  | CONTAINED IN CANYON | Y | N |  | SEWAGE CONTAINED IN CANYON. |  | SAN DIEGO, CITY OF | 93/07/02 | 1400PM | 930702 | 1500PM | 60 | GAL | 24TH & BROADWAY | SAN DIEGO | SD | 6" CP | GREASE | NONE | FLOWED INTO STORM DRAIN WHERE IT SETTLED.
| 930716 | ?????? | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 93/07/05 | 1045AM | 930705 | 1335PM |  | 750 | GAL |  | 1511 REQULUS STREET | SAN DIEGO | SD | 8" VC | GREASE | NO | NONE |  | STORM DRAIN TO CANYON | Y | N |  | SEWAGE CONTAINED IN CANYON. |  | SAN DIEGO, CITY OF | 93/07/03 | 1100AM | 930703 | 1200PM | 600 | GAL | ALDINE DR. * FAIRMONT AVE. | SAN DIEGO | SD | 8" VC | ROCKS | NONE | FLOWED INTO CULVERT AND SOAKED INTO DIRT.
| 930716 | ?????? | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 93/07/05 | 1830PM | 930705 | 2030PM |  | 450 | GAL |  | 2365 VANCOUVER AVENUE | SAN DIEGO | SD | 8" CP | ROOTS | NO | NONE |  | DEAD END ST. TO STORM DRAIN | Y | N |  | SEWAGE CONTAINED IN CANYON. |  | SAN DIEGO, CITY OF | 93/07/05 | 1500PM | 930705 | 1630PM | 450 | GAL | 3202 CAMINITO QUIXOTE | SAN DIEGO | SD | 8" VC | GREASE | NONE | SEWAGE CONTAINED IN CANYON.
| 930706 | 0730AM | RICHARD PRIETO | 6197414854 | ESCONDIDO, CITY OF | 93/07/05 | 0850AM | 930705 | 1010AM |  | 12680 | GAL |  | 1340 ORANGE STREET | ESCONDIDO | SD | SEWER ATLAS PAGE 28 MANHOLE 5 | GREASE | Y | ESCONDIDO CREEK/SAN EL |  |  | Y | N | 04 | AREA WAS TREATED WITH DISINFECTANT AND WASHED |  | SAN DIEGO, CITY OF | 93/07/05 | 1045AM | 930705 | 1335PM | 750 | GAL | 1511 REQULUS STREET | SAN DIEGO | SD | 8" VC | GREASE | NONE | SEWAGE CONTAINED IN CANYON.
| 930716 | ?????? | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 93/07/06 | 1521PM | 930706 | 1700PM |  | 90 | GAL |  | CONDE & JEFFERSON | SAN DIEGO | SD | 6" CP | GREASE | NO | NONE |  | STORM DRAIN AT CONDE & JEFRSN. | Y | N |  | RODDED MAIN. SECTION OF MAIN WILL BE ON A 3-M |  | SAN DIEGO, CITY OF | 93/07/05 | 1830PM | 930705 | 2030PM | 450 | GAL | 2365 VANCOUVER AVENUE | SAN DIEGO | SD | 8" CP | ROOTS | NONE | SEWAGE CONTAINED IN CANYON.
| 930716 | ?????? | M. S. STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 93/07/08 | 1330PM | 930708 | 1830PM |  | 2400 | GAL |  | BAJA DR. CAMPANILE | SAN DIEGO | SD | 8" VC | ROCKS | NO | NONE |  | STORM DRAIN | N | O |  | AREA DEODORIZED. |  | ESCONDIDO, CITY OF | 93/07/05 | 0850AM | 930705 | 1010AM | 12680 | GAL | 1340 ORANGE STREET | ESCONDIDO | SD | SEWER ATLAS PAGE 28 MANHOLE 5 | GREASE | ESCONDIDO CREEK/SAN EL | AREA WAS TREATED WITH DISINFECTANT AND WASHED
| 930716 | ?????? | M. S. STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 93/07/08 | 0841AM | 930708 | 0941AM |  | 300 | GAL |  | BALBOA PARK MORELY FIELD | SAN DIEGO | SD | 8" VC | ROOTS | NO | NONE |  | STORM DRAIN | Y |  |  |  |  | SAN DIEGO, CITY OF | 93/07/06 | 1521PM | 930706 | 1700PM | 90 | GAL | CONDE & JEFFERSON | SAN DIEGO | SD | 6" CP | GREASE | NONE | RODDED MAIN. SECTION OF MAIN WILL BE ON A 3-M
| 930716 | ?????? | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 93/07/09 | 1200PM | 930709 | 1830PM |  | 390 | GAL |  | AERO SPACE MUSEUM, BALBOA PARK | SAN DIEGO | SD | 8" VC | ROOTS | NO | NONE |  | GRASS AROUND MANHOLE | Y |  |  | RODDED BY TRUCK. |  | SAN DIEGO, CITY OF | 93/07/08 | 1330PM | 930708 | 1830PM | 2400 | GAL | BAJA DR. CAMPANILE | SAN DIEGO | SD | 8" VC | ROCKS | NONE | AREA DEODORIZED.
| 930712 | 0815AM | MARK A. STOFFER | 6197254806 | USMC CAMP PENDLETON | 93/07/09 | 2000PM | 930709 | 2315PM |  | 3000 | GAL |  | STEWART MESA | CAMP PENDLETON | SD | 31520 LIFT STATION | PUMP AIR LOCKED. | NO | NONE |  | FIELD | Y | N |  | REPRIMED PUMP. CLEANED UP AND APPLIED LIME ON |  | SAN DIEGO, CITY OF | 93/07/08 | 0841AM | 930708 | 0941AM | 300 | GAL | BALBOA PARK MORELY FIELD | SAN DIEGO | SD | 8" VC | ROOTS | NONE
| 930709 | 1100AM | MARK A. STOFFER | 6197254806 | USMC CAMP PENDLETON | 93/07/09 | 1000AM | 930709 | 1040AM |  | 200 | GAL |  | MEADOWLARK | CAMP PENDLETON | SD | 343 | PUMP FAILURE IN LIFT STATION NUMBER 51049. | NO | NONE |  | LAWN | Y | N |  | RESET PUMPS. CLEANED UP AND APPLIED LIME ON T |  | SAN DIEGO, CITY OF | 93/07/09 | 1200PM | 930709 | 1830PM | 390 | GAL | AERO SPACE MUSEUM, BALBOA PARK | SAN DIEGO | SD | 8" VC | ROOTS | NONE | RODDED BY TRUCK.
| 930811 | ?????? | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 93/07/11 | 1345PM | 930711 | 1415PM |  | 60 | GAL |  | 3792 WARD ROAD | SAN DIEGO | SD | 8" CP | ROOTS | NO | NONE |  | DRIED IN ADJACENT CANYON. | Y | N |  | SEWAGE DRIED UP IN CANYON. |  | USMC CAMP PENDLETON | 93/07/09 | 2000PM | 930709 | 2315PM | 3000 | GAL | STEWART MESA | CAMP PENDLETON | SD | 31520 LIFT STATION | PUMP AIR LOCKED. | NONE | REPRIMED PUMP. CLEANED UP AND APPLIED LIME ON
| 930716 | ?????? | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 93/07/11 | 1545PM | 930711 | 1615PM |  | 450 | GAL |  | PARK BLVD. & UPAS ST. | SAN DIEGO | SD | 6" CP | ROOTS | NO | NONE |  | DRIED UP IN ADJACENT CANYON. | Y | N |  | SEWAGE DRIED UP IN ADJACENT CANYON. |  | USMC CAMP PENDLETON | 93/07/09 | 1000AM | 930709 | 1040AM | 200 | GAL | MEADOWLARK | CAMP PENDLETON | SD | 343 | PUMP FAILURE IN LIFT STATION NUMBER 51049. | NONE | RESET PUMPS. CLEANED UP AND APPLIED LIME ON T
| 930716 | ?????? | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 93/07/11 | 1000AM | 930711 | 1030AM |  | 30 | GAL |  | ALTA VIEW & WOODMAN | SAN DIEGO | SD | 8" VC | ROOTS | NO | NONE |  | STORM DRAIN WERE IT SETTLED. | Y | N |  | SEWAGE DRIED UP IN STORM DRAIN. |  | SAN DIEGO, CITY OF | 93/07/11 | 1345PM | 930711 | 1415PM | 60 | GAL | 3792 WARD ROAD | SAN DIEGO | SD | 8" CP | ROOTS | NONE | SEWAGE DRIED UP IN CANYON.
| 930713 | 0830AM | ROBERT F. ROBERTS | 6196602008 | RANCHO DEL CAMPO | 93/07/13 | 0830AM | 930713 | 0930AM |  | 85000 | GAL |  | HIGHWAY 94, CAMPO CREEK | CAMPO | SD | #1 PERC BED NORTH END | #1 PERC BED BACK BERM GAVE WAY CAUSING SPIL | Y | CAMPO CREEK |  |  | Y | N |  |  |  | SAN DIEGO, CITY OF | 93/07/11 | 1545PM | 930711 | 1615PM | 450 | GAL | PARK BLVD. & UPAS ST. | SAN DIEGO | SD | 6" CP | ROOTS | NONE | SEWAGE DRIED UP IN ADJACENT CANYON.
| 930715 | 0900AM | DISTRICT OFFICE | 6197288319 | FALLBROOK SANITARY DISTRCIT | 93/07/15 | ?????? | 930715 | 1000AM |  | 5 | GAL |  | 710 GOLDEN LANE | FALLBROOK | SD | 4" CLAY CLEANOUT | ROOTS | NO | NONE |  | FOILAGE AROUND CLEANOUT. | N | O |  | AT 0910AM, OPENED CLEANOUT. RODDED MANHOLES. |  | SAN DIEGO, CITY OF | 93/07/11 | 1000AM | 930711 | 1030AM | 30 | GAL | ALTA VIEW & WOODMAN | SAN DIEGO | SD | 8" VC | ROOTS | NONE | SEWAGE DRIED UP IN STORM DRAIN.
| 930811 | ?????? | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 93/07/16 | 1130AM | 930716 | 1400PM |  | 25 | GAL |  | 28TH IVY GOLF COURSE | SAN DIEGO | SD | 8" CP | ROOTS | NO | NONE |  | DRIED AROUND MANHOLE | Y |  |  | RODDED BY MACHINE. |  | RANCHO DEL CAMPO | 93/07/13 | 0830AM | 930713 | 0930AM | 85000 | GAL | HIGHWAY 94, CAMPO CREEK | CAMPO | SD | #1 PERC BED NORTH END | #1 PERC BED BACK BERM GAVE WAY CAUSING SPIL | CAMPO CREEK
| 930811 | ?????? | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 93/07/16 | 1900PM | 930716 | 2030PM |  | 90 | GAL |  | 4729 CASTANA STREET | SAN DIEGO | SD | 8" VC | GREASE | NO | NONE |  | SOAKED INTO GROUND. | Y |  |  | FLOWED INTO CANYON AND SOAKED INTO GROUND NORT |  | FALLBROOK SANITARY DISTRCIT | 93/07/15 | ?????? | 930715 | 1000AM | 5 | GAL | 710 GOLDEN LANE | FALLBROOK | SD | 4" CLAY CLEANOUT | ROOTS | NONE | AT 0910AM, OPENED CLEANOUT. RODDED MANHOLES.
| 930720 | 1500PM | CLINT R. BAZE | 6197281178 | RAINBOW MUNICIPAL WATER DIST. | 93/07/16 | 2330PM | 930717 | 0100AM |  | 7500 | GAL |  | OLD RIVER RD. & GOPHER CYN. | BONSALL | SD | LIFT STATION #2 | BUBLER SYSTEM MALFUNCTION | Y | SAN LUIS REY RIVER/PAC |  |  | Y | N |  | AN ALTERNATE SYSTEM IS CURRENTLY BEING INVESTI |  | SAN DIEGO, CITY OF | 93/07/16 | 1130AM | 930716 | 1400PM | 25 | GAL | 28TH IVY GOLF COURSE | SAN DIEGO | SD | 8" CP | ROOTS | NONE | RODDED BY MACHINE.
| 930726 | ?????? | RONALD D. ROBY | 6915258685 | SAN DIEGO, CITY OF | 93/07/17 | 1930PM | 930717 | 2030PM |  | 60 | GAL |  | 6542 GARBER WAY | SAN DIEGO | SD | 8" VC | ROOTS | NO | NONE |  | STORM DRAIN | Y |  |  | FLOWED INTO STORM DRAIN WHERE IT SETTLED. |  | SAN DIEGO, CITY OF | 93/07/16 | 1900PM | 930716 | 2030PM | 90 | GAL | 4729 CASTANA STREET | SAN DIEGO | SD | 8" VC | GREASE | NONE | FLOWED INTO CANYON AND SOAKED INTO GROUND NORT
| 930726 | ?????? | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 93/07/18 | 1830PM | 930718 | 1930PM |  | 600 | GAL |  | CASS ST. & VAN NUYS CANYON | SAN DIEGO | SD | 8" VC | VANDALISM & ROCKS | NO | NONE |  | CANYON | Y |  |  | FLOW NEVER GOT OUT OF VAN NUYS CANYON. IT SET |  | RAINBOW MUNICIPAL WATER DIST. | 93/07/16 | 2330PM | 930717 | 0100AM | 7500 | GAL | OLD RIVER RD. & GOPHER CYN. | BONSALL | SD | LIFT STATION #2 | BUBLER SYSTEM MALFUNCTION | SAN LUIS REY RIVER/PAC | AN ALTERNATE SYSTEM IS CURRENTLY BEING INVESTI
| 930719 | 1430PM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 93/07/19 | 0945AM | 930719 | 1045AM |  | 3000 | GAL |  | VAN NUYS | SAN DIEGO | SD | 8" VC | ROCK IN MANHOLE DUE TO VANDALISM. | Y | STORM DRAIN/PACIFIC OC |  | CANYON TO STORM DRAIN TO OCEAN | Y | Y | 07 | SIGNS POSTED AT MOUTH AND 3 EACH WAY 50 FEET A |  | SAN DIEGO, CITY OF | 93/07/17 | 1930PM | 930717 | 2030PM | 60 | GAL | 6542 GARBER WAY | SAN DIEGO | SD | 8" VC | ROOTS | NONE | FLOWED INTO STORM DRAIN WHERE IT SETTLED.
| 930730 | ?????? | JOHN GIFFORD | 9099257676 | EASTERN MUNICIPAL WATER DIST. | 93/07/19 | 0830AM | 930719 | 0900AM |  | 60000 | GAL |  | HWY 79 AT PALA ROAD | TEMECULA | RI | 12" RECLAIMED WATER LINE | PIPE COUPLING FAILURE | Y | TEMECULA CRK./ST. MARG |  |  | N | N |  | WATER WAS TERTIARY TREATED EFFLUENT. |  | SAN DIEGO, CITY OF | 93/07/18 | 1830PM | 930718 | 1930PM | 600 | GAL | CASS ST. & VAN NUYS CANYON | SAN DIEGO | SD | 8" VC | VANDALISM & ROCKS | NONE | FLOW NEVER GOT OUT OF VAN NUYS CANYON. IT SET
| 930720 | 1645PM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 93/07/20 | 0900AM | 930720 | 1000AM |  | 3000 | GAL |  | VAN NUYS CANYON | SAN DIEGO | SD | 8" VC SEWER MAIN | ROCK IN MANHOLE DUE TO VANDALISM. | Y | STORM DRAIN TO PACIFIC |  |  | Y | N |  | POSTED SIGN ON 7/19/93. |  | SAN DIEGO, CITY OF | 93/07/19 | 0945AM | 930719 | 1045AM | 3000 | GAL | VAN NUYS | SAN DIEGO | SD | 8" VC | ROCK IN MANHOLE DUE TO VANDALISM. | STORM DRAIN/PACIFIC OC | SIGNS POSTED AT MOUTH AND 3 EACH WAY 50 FEET A
| 930720 | 1300PM | CLINT R. BAZE | 6197281178 | RAINBOW MUNICIPAL WATER DIST. | 93/07/20 | 1200AM | 930720 | 1245PM |  | 7650 | GAL |  | OLD RIVER ROAD & GOPHER CYN. | BONSALL | SD | LIFT STATION #2 | MALFUNCTIONED BUBBLER SYSTEM | Y | SAN LUIS REY RIVER/PAC |  |  | Y | N |  | INVESTIGATING ALTERNATE SYSTEM. INSTALLED DUAL |  | EASTERN MUNICIPAL WATER DIST. | 93/07/19 | 0830AM | 930719 | 0900AM | 60000 | GAL | HWY 79 AT PALA ROAD | TEMECULA | RI | 12" RECLAIMED WATER LINE | PIPE COUPLING FAILURE | TEMECULA CRK./ST. MARG | WATER WAS TERTIARY TREATED EFFLUENT.
| 930720 | 1640PM | KEN, OPERATOR #4 | 6195277660 | SAN DIEGO, CITY OF | 93/07/20 | 0900AM | 930720 | 1000AM |  | 3000 | GAL |  | VAN NUYS ST. CYN. EST OF CASS | SAN DIEGO | SD | ???? | ROCKS AND DEBRIS IN LINE DUE TO VANDALISM. | Y | PACIFIC OCEAN NEAR TOU |  |  | Y |  |  | DEPARTMENT OF HEALTH SERVICES WILL BE NOTIFIED |  | SAN DIEGO, CITY OF | 93/07/20 | 0900AM | 930720 | 1000AM | 3000 | GAL | VAN NUYS CANYON | SAN DIEGO | SD | 8" VC SEWER MAIN | ROCK IN MANHOLE DUE TO VANDALISM. | STORM DRAIN TO PACIFIC | POSTED SIGN ON 7/19/93.
| 930721 | 1030AM | CATHY STONE | 6193382386 | SAN DIEGO, CITY OF | 93/07/20 | ?????? | 930720 | ?????? |  | 3000 | GAL |  | TOURMALINE SURF PARK | SAN DIEGO | SD | MANHOLE | VANDALISM | Y | PACIFIC OCEAN |  |  | Y |  |  |  |  | RAINBOW MUNICIPAL WATER DIST. | 93/07/20 | 1200AM | 930720 | 1245PM | 7650 | GAL | OLD RIVER ROAD & GOPHER CYN. | BONSALL | SD | LIFT STATION #2 | MALFUNCTIONED BUBBLER SYSTEM | SAN LUIS REY RIVER/PAC | INVESTIGATING ALTERNATE SYSTEM. INSTALLED DUAL
| 930720 | 1126AM | CAMINO PT. APARTMENT | 6194346075 | CARLSBAD, CITY OF | 93/07/20 | 1100AM | 930720 | 1300PM |  | 100 | GAL |  | 2280 AVENIDA MAGNIFICA | CARLSBAD | SD | 8" MAIN LINE | ROOTS ENTERING MAIN | NO | NONE |  | APARTMENT PERIMETER GROUNDS | N | N |  |  |  | SAN DIEGO, CITY OF | 93/07/20 | 0900AM | 930720 | 1000AM | 3000 | GAL | VAN NUYS ST. CYN. EST OF CASS | SAN DIEGO | SD | ???? | ROCKS AND DEBRIS IN LINE DUE TO VANDALISM. | PACIFIC OCEAN NEAR TOU | DEPARTMENT OF HEALTH SERVICES WILL BE NOTIFIED
| 930722 | 1330PM | FRANK ANDERSON | 6197414660 | ESCONDIDO, CITY OF | 93/07/21 | 1600PM | 930721 | 1615PM |  | 30 | GAL |  | BARHAM DR. X ST. OPPES ST. | ESCONDIDO | SD | WEST OF MH #8 - ATLAS PG. 103 | CONTRACTOR BROKE SEWER MAIN. SEE ATTACHED S | Y | ST.MARCOS CRK./LAKE SA |  |  | Y | Y |  | AREA WAS TREATED WITH DISINFECTANT AND POTABLE |  | SAN DIEGO, CITY OF | 93/07/20 | ?????? | 930720 | ?????? | 3000 | GAL | TOURMALINE SURF PARK | SAN DIEGO | SD | MANHOLE | VANDALISM | PACIFIC OCEAN
| 930811 | ?????? | DAVID BEST | 6195258686 | SAN DIEGO, CITY OF | 93/07/23 | 1130AM | 930723 | 1330PM |  | 600 | GAL |  | GLENLEA LANE & OVERLAKE AVE. | SAN DIEGO | SD | 8" VC | VANDALISM | NO | NONE |  | 100 FEET DOWN CANYON. | Y |  |  | SEWAGE DISSOLVED 100 FEET DOWN CANYON INTO DIR |  | CARLSBAD, CITY OF | 93/07/20 | 1100AM | 930720 | 1300PM | 100 | GAL | 2280 AVENIDA MAGNIFICA | CARLSBAD | SD | 8" MAIN LINE | ROOTS ENTERING MAIN | NONE
| 930729 | ?????? | DWIGHT G. SMITH | 6196943974 | SAN DIEGO, COUNTY OF | 93/07/23 | 1100AM | 930723 | 1230PM |  | 300 | GAL |  | 4418 VISTA WAY | LA MESA | SD | 4430 VISTA WAY MANHOLE | BLOCKAGE IN MAIN LINE DUE TO DEBRIS AND PIE | Y | DRAINAGE DITCH |  |  | N |  |  | RODDED THE MAIN LINE CLEARING STOPPAGE. CHLORI |  | ESCONDIDO, CITY OF | 93/07/21 | 1600PM | 930721 | 1615PM | 30 | GAL | BARHAM DR. X ST. OPPES ST. | ESCONDIDO | SD | WEST OF MH #8 - ATLAS PG. 103 | CONTRACTOR BROKE SEWER MAIN. SEE ATTACHED S | ST.MARCOS CRK./LAKE SA | AREA WAS TREATED WITH DISINFECTANT AND POTABLE
| 930811 | ?????? | JIM MC CURLEY | 6195258687 | SAN DIEGO, CITY OF | 93/07/24 | 2200PM | 930724 | 2400PM |  | 600 | GAL |  | 2961 GABRIELSON AVENUE | SAN DIEGO | SD | 8" VC SEWER LINE | GREASE | NO | NONE |  | INTO STORM DRAIN CHANNEL | Y | N |  | AREA WAS DEODORIZED. |  | SAN DIEGO, CITY OF | 93/07/23 | 1130AM | 930723 | 1330PM | 600 | GAL | GLENLEA LANE & OVERLAKE AVE. | SAN DIEGO | SD | 8" VC | VANDALISM | NONE | SEWAGE DISSOLVED 100 FEET DOWN CANYON INTO DIR
| 930811 | ?????? | JIM MC CURLEY | 6195258687 | SAN DIEGO, CITY OF | 93/07/25 | 0300AM | 930725 | 0200AM |  | 900 | GAL |  | CLEVELAND & TYLER AVENUES | SAN DIEGO | SD | 8" PVC SEWER LINE | GREASE | NO | NONE |  | INTO ALLEY AND DISSIPATED | Y | N |  | AREA WAS DEODORIZED, VACTERED UP AND WASHED DO |  | SAN DIEGO, COUNTY OF | 93/07/23 | 1100AM | 930723 | 1230PM | 300 | GAL | 4418 VISTA WAY | LA MESA | SD | 4430 VISTA WAY MANHOLE | BLOCKAGE IN MAIN LINE DUE TO DEBRIS AND PIE | DRAINAGE DITCH | RODDED THE MAIN LINE CLEARING STOPPAGE. CHLORI
| 930811 | ?????? | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 93/07/25 | 1200PM | 930725 | 1400PM |  | 120 | GAL |  | 17940 MIRASOL DRIVE | SAN DIEGO | SD | 8" VC | ROOTS | NO | NONE |  | STORM DRAIN | Y |  |  | FLOWED INTO STORM DRAIN WHERE IT SETTLED. |  | SAN DIEGO, CITY OF | 93/07/24 | 2200PM | 930724 | 2400PM | 600 | GAL | 2961 GABRIELSON AVENUE | SAN DIEGO | SD | 8" VC SEWER LINE | GREASE | NONE | AREA WAS DEODORIZED.
| 930727 | 1435PM | ANSWERING SERVICE | 6917288319 | FALLBROOK SANITARY DISTRICT | 93/07/25 | 1435PM | 930725 | 1505PM |  | 20 | GAL |  | 817 LA PALMA | FALLBROOK | SD | 4" CLEANOUT | PAPER TOWELS | NO | NONE |  | NEAR CLEANOUT IN YARD & DRIVWY | N | N |  | AT 1650PM, OPENED CLEANOUT. COMPLETED AT 1720 |  | SAN DIEGO, CITY OF | 93/07/25 | 0300AM | 930725 | 0200AM | 900 | GAL | CLEVELAND & TYLER AVENUES | SAN DIEGO | SD | 8" PVC SEWER LINE | GREASE | NONE | AREA WAS DEODORIZED, VACTERED UP AND WASHED DO
| 930811 | ?????? | DAVID BEST | 6195258686 | SAN DIEGO, CITY OF | 93/07/26 | 0946AM | 930726 | 1319PM |  | 210 | GAL |  | 5990 UNIVERSITY AVENUE | SAN DIEGO | SD | 8" VC | ROCKS IN MAIN. | NO | NONE |  | SEEPED IN AREA AROUND MANHOLD. | Y |  |  | 300 FEET OF MAIN WAS FLUSHED. |  | SAN DIEGO, CITY OF | 93/07/25 | 1200PM | 930725 | 1400PM | 120 | GAL | 17940 MIRASOL DRIVE | SAN DIEGO | SD | 8" VC | ROOTS | NONE | FLOWED INTO STORM DRAIN WHERE IT SETTLED.
| 930811 | ?????? | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 93/07/27 | 1045AM | 930727 | 1145AM |  | 180 | GAL |  | 6933 LA JOLLA BLVD. | SAN DIEGO | SD | 6" CP | GREASE | NO | NONE |  | RETURNED FLOW TO SEWER | Y | N |  | SEWAGE WENT BACK INTO MANHOLE. |  | FALLBROOK SANITARY DISTRICT | 93/07/25 | 1435PM | 930725 | 1505PM | 20 | GAL | 817 LA PALMA | FALLBROOK | SD | 4" CLEANOUT | PAPER TOWELS | NONE | AT 1650PM, OPENED CLEANOUT. COMPLETED AT 1720
| 930727 | 2100PM | DENIS POLLAK | 6197530155 | LEUCADIA COUNTY WATER DISTRICT | 93/07/27 | 2100PM | 939727 | 2230PM |  | 2250 | GAL |  | 1960 LA COSTA AVENUE | CARLSBAD | SD | LEUCADIA PUMP STATION | FAILED CHLORINE SOLUTION LINE CONNECTED TO | Y | SAN MARCOS CREEK |  |  | Y | Y | 07 | SPILL FLOWED TO A STORM DRAIN TO SAN MARCOS CR |  | SAN DIEGO, CITY OF | 93/07/26 | 0946AM | 930726 | 1319PM | 210 | GAL | 5990 UNIVERSITY AVENUE | SAN DIEGO | SD | 8" VC | ROCKS IN MAIN. | NONE | 300 FEET OF MAIN WAS FLUSHED.
| 930730 | 1400PM | TRISH BUTLER | 6192987127 | DEL MAR FAIR/RACETRACK | 93/07/28 | 1700PM | 930728 | 1830PM |  | 0 | ??? |  | DEL MAR RACETRACK PUMP STATION | DEL MAR | SD | PUMP STATION AT RACETRACK | NEW TOILETS RUNNING CONSTANTLY CAUSED HYDRA | NO | UNKNOWN |  |  | Y | N |  | IT IS UNKNOWN IF ANY OF THE FLOW REACHED A STO |  | SAN DIEGO, CITY OF | 93/07/27 | 1045AM | 930727 | 1145AM | 180 | GAL | 6933 LA JOLLA BLVD. | SAN DIEGO | SD | 6" CP | GREASE | NONE | SEWAGE WENT BACK INTO MANHOLE.
| 930729 | 0825AM | MARK A. STOFFER | 6197254806 | USMC CAMP PENDLETON | 93/07/29 | 0104AM | 930729 | 0330AM |  | 350 | GAL |  | SAN MATEO | CAMP PENDLETON | SD | 62431 | PLUGGED LATERAL & BROKEN RISER WHICH HAD BE | NO | NONE |  | CONSTRUCTION SITE | Y | N |  | UNPLUGGED LATERAL AND APPLIED LIME TO THE AREA |  | LEUCADIA COUNTY WATER DISTRICT | 93/07/27 | 2100PM | 939727 | 2230PM | 2250 | GAL | 1960 LA COSTA AVENUE | CARLSBAD | SD | LEUCADIA PUMP STATION | FAILED CHLORINE SOLUTION LINE CONNECTED TO | SAN MARCOS CREEK | SPILL FLOWED TO A STORM DRAIN TO SAN MARCOS CR
| 930730 | 1530PM | MICHAEL BARDIN | 6197530155 | LEUCADIA COUNTY WATER DISTRICT | 93/07/30 | 0800AM | 930730 | 1000AM |  | 3000 | GAL |  | 2007 LA COSTA DEL MAR | CARLSBAD | SD | MANHOLE #11-0550 | ROOT INTRUSION IN MANHOLE WALL ENTERED DOWN | NO | NONE |  | HALF CONTAINED.REST SOAKED IN. | Y |  |  |  |  | DEL MAR FAIR/RACETRACK | 93/07/28 | 1700PM | 930728 | 1830PM | 0 | ??? | DEL MAR RACETRACK PUMP STATION | DEL MAR | SD | PUMP STATION AT RACETRACK | NEW TOILETS RUNNING CONSTANTLY CAUSED HYDRA | UNKNOWN | IT IS UNKNOWN IF ANY OF THE FLOW REACHED A STO
| 930730 | 1150AM | CHULA VISTA, CITY OF | 6196915027 | PRIVATE PLUMBER | 93/07/30 | 1150AM | 930730 | 1430PM |  | 200 | GAL |  | BROADWAY & NAPLES | CHULA VISTA | SD | PRIVATE CLEANOUT CARLS JR REST | PAPER | NO | NONE |  | STORM DRAIN/NAPLE & JEFFERSON | Y | N |  | AREA BLOCKED OFF UNTIL STOPPAGE WAS CLEARED. |  | USMC CAMP PENDLETON | 93/07/29 | 0104AM | 930729 | 0330AM | 350 | GAL | SAN MATEO | CAMP PENDLETON | SD | 62431 | PLUGGED LATERAL & BROKEN RISER WHICH HAD BE | NONE | UNPLUGGED LATERAL AND APPLIED LIME TO THE AREA
| 930802 | 0930AM | JAY ELSTOR | 7143661553 | SAN CLEMENTE DISTRICT | 93/07/31 | 1000AM | 930731 | 1330PM |  | 8000 | GAL |  | RIVIERA STREET | SAN CLEMENTE | SD | LIFT STATION | AN SDG&E TRANSFORMER EXPLODED RESULTING IN | NO | NONE |  | SAND ON THE BEACH | Y | Y |  | COVERED THE SPILL SITE; CHLORINATED AND HOSED |  | LEUCADIA COUNTY WATER DISTRICT | 93/07/30 | 0800AM | 930730 | 1000AM | 3000 | GAL | 2007 LA COSTA DEL MAR | CARLSBAD | SD | MANHOLE #11-0550 | ROOT INTRUSION IN MANHOLE WALL ENTERED DOWN | NONE
| 930811 | ?????? | RONALD D. ROBY | 6195258684 | SAN DIEGO, CITY OF | 93/08/01 | 1230PM | 930801 | 1430PM |  | 120 | GAL |  | 2181 ALTA VIEW DRIVE | SAN DIEGO | SD | 8"VC | GREASE | NO | NONE |  | DRIED IN STREET | Y |  |  | FLOW DRIED IN STREET |  | PRIVATE PLUMBER | 93/07/30 | 1150AM | 930730 | 1430PM | 200 | GAL | BROADWAY & NAPLES | CHULA VISTA | SD | PRIVATE CLEANOUT CARLS JR REST | PAPER | NONE | AREA BLOCKED OFF UNTIL STOPPAGE WAS CLEARED.
| 930811 | ?????? | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 93/08/02 | 0830AM | 930802 | 1030AM |  | 600 | GAL |  | CHOLLAS RD. & QUINCE ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE | NO | NONE |  | DISSIPATED IN STORM DRAIN | Y | N |  | RODDED MAIN BY MACHINE TO RELEASE STOPPAGE. |  | SAN CLEMENTE DISTRICT | 93/07/31 | 1000AM | 930731 | 1330PM | 8000 | GAL | RIVIERA STREET | SAN CLEMENTE | SD | LIFT STATION | AN SDG&E TRANSFORMER EXPLODED RESULTING IN | NONE | COVERED THE SPILL SITE; CHLORINATED AND HOSED
| 930811 | ?????? | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 93/08/02 | 1830PM | 930803 | 1130PM |  | 510 | GAL |  | 46TH ST. & MYRTLE AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE | NO | NONE |  | IN CANYON |  |  |  | OVERFLOW DISSIPATED IN CANYON. DEODORIZED ARE |  | SAN DIEGO, CITY OF | 93/08/01 | 1230PM | 930801 | 1430PM | 120 | GAL | 2181 ALTA VIEW DRIVE | SAN DIEGO | SD | 8"VC | GREASE | NONE | FLOW DRIED IN STREET
| 930811 | ?????? | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 93/08/03 | 0830AM | 930803 | 0930AM |  | 1800 | GAL |  | 5852 KANTOR COURT | SAN DIEGO | SD | 8" VC | ROOTS | NO | NONE |  | SOAKED IN SAN CLEMENTE CANYON | Y | N |  | SEWAGE SOAKED INTO GROUND IN CANYON. |  | SAN DIEGO, CITY OF | 93/08/02 | 0830AM | 930802 | 1030AM | 600 | GAL | CHOLLAS RD. & QUINCE ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE | NONE | RODDED MAIN BY MACHINE TO RELEASE STOPPAGE.
| 930811 | ?????? | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 93/08/03 | 1500PM | 930803 | 1630PM |  | 180 | GAL |  | 5786 LA JOLLA BLVD. | SAN DIEGO | SD | 6" CP | GREASE | NO | NONE |  | STORM DRAIN AND DRIED UP | Y | N |  | SEWAGE DRIED UP IN STORM DRAIN. |  | SAN DIEGO, CITY OF | 93/08/02 | 1830PM | 930803 | 1130PM | 510 | GAL | 46TH ST. & MYRTLE AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE | NONE | OVERFLOW DISSIPATED IN CANYON. DEODORIZED ARE
| 930803 | 0830AM | ALAN WILLIAMS | 6195227380 | CORONADO, CITY OF | 93/08/03 | 0825AM | 930803 | 0930AM |  | 455 | GAL |  | 1330 ORANGE AVENUE | CORONADO | SD | PUMP STATION | DISCHARGE LINE PLUGGED FROM PRIVATE BUSINES | NO | NONE |  | CORONADO BEACH | Y | N |  | SEWER FLOW DISCHARGED INTO STORM INLET WHOSE O |  | SAN DIEGO, CITY OF | 93/08/03 | 0830AM | 930803 | 0930AM | 1800 | GAL | 5852 KANTOR COURT | SAN DIEGO | SD | 8" VC | ROOTS | NONE | SEWAGE SOAKED INTO GROUND IN CANYON.
| 930803 | 1301PM | ORVAL SALISBURY | 6197440460 | VALLECITOS WATER DISTRICT | 93/08/03 | 0900AM | 930803 | 0920AM |  | 1000 | GAL |  | SOUTH OF LOS POSAS IN FIELD | SAN MARCOS | SD | THOMAS BRO. PG. 21, A1 | WHILE REPAIRING SEWER LINE, KEWIT CONSTRUCT | NO | NONE |  | FIELD NEXT TO SAN MARCOS CRK. | Y |  |  | EXCESS SPILL WAS CONTAINED AND DIVERTED TO MAN |  | SAN DIEGO, CITY OF | 93/08/03 | 1500PM | 930803 | 1630PM | 180 | GAL | 5786 LA JOLLA BLVD. | SAN DIEGO | SD | 6" CP | GREASE | NONE | SEWAGE DRIED UP IN STORM DRAIN.
| 930804 | 1000AM | DISTRICT OFFICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 93/08/04 | 1000AM | 930804 | 1030AM |  | 20 | GAL |  | 509 TERAN DRIVE | FALLBROOK | SD | CLEANOUT | ROOTS | NO | NONE |  | AROUND CLEANOUT | N | N |  | AT 1000AM OPENED CLEANOUT. COMPLETED AT 1040AM |  | CORONADO, CITY OF | 93/08/03 | 0825AM | 930803 | 0930AM | 455 | GAL | 1330 ORANGE AVENUE | CORONADO | SD | PUMP STATION | DISCHARGE LINE PLUGGED FROM PRIVATE BUSINES | NONE | SEWER FLOW DISCHARGED INTO STORM INLET WHOSE O
| 930826 | ?????? | M. A.WHELAN | 6195258687 | SAN DIEGO, CITY OF | 93/08/04 | 1530PM | 930804 | 1630PM |  | 30 | GAL |  | INTSECT. BOYCE LN./CHOLLAS PY. | SAN DIEGO | SD | 8" PVC SEWER MAIN | VANDALISM. SOMEONE BROKE PVC PIPE. FILLED | NO | NONE |  | SOAKED INTO CREEK BED. | N | Y | ? | RODDED 210' SECTION MAIN IS 7-24, RELIEVED STO |  | VALLECITOS WATER DISTRICT | 93/08/03 | 0900AM | 930803 | 0920AM | 1000 | GAL | SOUTH OF LOS POSAS IN FIELD | SAN MARCOS | SD | THOMAS BRO. PG. 21, A1 | WHILE REPAIRING SEWER LINE, KEWIT CONSTRUCT | NONE | EXCESS SPILL WAS CONTAINED AND DIVERTED TO MAN
| 930826 | ?????? | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 93/08/05 | 0830AM | 930893 | 1130AM |  | 900 | GAL |  | 4704 PANARAMA DRIVE | SAN DIEGO | SD | 6" CP MAIN | GREASE | NO | NONE |  | STORM DRAIN | Y |  |  | RODDED BY MACHINE. |  | FALLBROOK SANITARY DISTRICT | 93/08/04 | 1000AM | 930804 | 1030AM | 20 | GAL | 509 TERAN DRIVE | FALLBROOK | SD | CLEANOUT | ROOTS | NONE | AT 1000AM OPENED CLEANOUT. COMPLETED AT 1040AM
| 930806 | 0850AM | MARK A. STOFFER | 6197254806 | USMC CAMP PENDLETON | 93/08/06 | 0420AM | 930806 | 0440AM |  | 150 | GAL |  | BASILONE | CAMP PENDLETON | SD | 51053 | SUCTION LINE LEAK FILLED DRY WELL OF LIFT S | NO | NONE |  | GROUND BY 51053 |  |  |  | SET UP PORTABLE PUMPS TO PUMP WET WELL TO ADJA |  | SAN DIEGO, CITY OF | 93/08/04 | 1530PM | 930804 | 1630PM | 30 | GAL | INTSECT. BOYCE LN./CHOLLAS PY. | SAN DIEGO | SD | 8" PVC SEWER MAIN | VANDALISM. SOMEONE BROKE PVC PIPE. FILLED | NONE | RODDED 210' SECTION MAIN IS 7-24, RELIEVED STO
| 930806 | 2100PM | JEFF BEENKEN | 6194385021 | CA DEPT. OF PARKS & REC. | 93/08/06 | 1400PM | 930806 | 1700PM |  | 100 | GAL |  | 7200 BLOCK OF CARLSBAD BLVD. | CARLSBAD | SD | SOUTH CARLSBAD LIFT STATION 3 | SHORT IN ELECTRICAL SERVICE BETWEEN MAIN DI | Y | UNKNOWN |  |  | Y | N |  | AREA AFFECTED WAS FLUSHED WITH POTABLE WATER. |  | SAN DIEGO, CITY OF | 93/08/05 | 0830AM | 930893 | 1130AM | 900 | GAL | 4704 PANARAMA DRIVE | SAN DIEGO | SD | 6" CP MAIN | GREASE | NONE | RODDED BY MACHINE.
| 930809 | ?????? | MARK A. STOFFER | 6197254806 | USMC CAMP PENDLETON | 93/08/07 | 11AM93 | 930807 | 1300AM |  | 300 | GAL |  | BASILONE | CAMP PENDLETON | SD | LIFT STATION #51053 | PUMPS NEED TO BE REPLACED OR IN PROGRESS OF | NO | NONE |  | DRAINAGE DITCH | Y | N |  | PUMP REPAIR IN PROGRESS. APPLIED LIME TO AREA |  | USMC CAMP PENDLETON | 93/08/06 | 0420AM | 930806 | 0440AM | 150 | GAL | BASILONE | CAMP PENDLETON | SD | 51053 | SUCTION LINE LEAK FILLED DRY WELL OF LIFT S | NONE | SET UP PORTABLE PUMPS TO PUMP WET WELL TO ADJA
| 930809 | 1340PM | ORV SALISBURY | 6197440460 | VALLECITOS WATER DISTRICT | 93/08/08 | 0930AM | 930809 | 1030AM |  | 4000 | GAL |  | BROKEN ROCK/RANCHO SANTA FE | SAN MARCOS | SD | 545-021-MH 20, THOMAS P20, E2 | VANDALIZED MANHOLE, FOUND KIDS TOYS BLOCKIN | Y | STORM DRAIN/LAKE SAN M |  |  | Y | Y | 05 | STORM RUNOFF IS THROUGH GOLF COURSE THRU OPENE |  | CA DEPT. OF PARKS & REC. | 93/08/06 | 1400PM | 930806 | 1700PM | 100 | GAL | 7200 BLOCK OF CARLSBAD BLVD. | CARLSBAD | SD | SOUTH CARLSBAD LIFT STATION 3 | SHORT IN ELECTRICAL SERVICE BETWEEN MAIN DI | UNKNOWN | AREA AFFECTED WAS FLUSHED WITH POTABLE WATER.
| 930810 | 0820AM | MARK A. STOFFER | 6197254806 | USMC CAMP PENDLETON | 93/08/09 | 0915AM | 930809 | 0925AM |  | 100 | GAL |  | BEACH CLUB ROAD | CAMP PENDELTON | SD | LIFT STATION #51849 | PLUGGED LINE-USED PUMPER TO KEEP FLOW DOWN | NO | NONE |  | SAND AREA BY MANHOLE. | Y | N |  | LIMED AREA. |  | USMC CAMP PENDLETON | 93/08/07 | 11AM93 | 930807 | 1300AM | 300 | GAL | BASILONE | CAMP PENDLETON | SD | LIFT STATION #51053 | PUMPS NEED TO BE REPLACED OR IN PROGRESS OF | NONE | PUMP REPAIR IN PROGRESS. APPLIED LIME TO AREA
| 930826 | ?????? | JOHNNY L. PEAY | 6195258686 | SAN DIEGO, CITY OF | 93/08/09 | 0730AM | 930809 | 1130AM |  | 1200 | GAL |  | 3181 ASH STREET | SAN DIEGO | SD | 10" VC SEWER MAIN | ROOTS IN 10" MAIN | NO | NONE |  | DISIPATED IN DIRT 100" SO. MH | N | N |  | RODDED 176' SECTION MAIN 10" VC TO RELIEVE STO |  | VALLECITOS WATER DISTRICT | 93/08/08 | 0930AM | 930809 | 1030AM | 4000 | GAL | BROKEN ROCK/RANCHO SANTA FE | SAN MARCOS | SD | 545-021-MH 20, THOMAS P20, E2 | VANDALIZED MANHOLE, FOUND KIDS TOYS BLOCKIN | STORM DRAIN/LAKE SAN M | STORM RUNOFF IS THROUGH GOLF COURSE THRU OPENE
| 930810 | 1435PM | BOB WADE | 6197891330 | RAMONA MUNICIPAL WATER DIST. | 93/08/10 | 1435PM | 930810 | 1445PM |  | 4000 | GAL |  | END OF HUNTER ST. MH #13 | RAMONA | SD | MANHOLE | UNKNOWN SOURCE STOPPED PUMPS. POSSIBLY A P | NO | NONE |  | DRY CREEK BED. | Y | Y | 01 | AREA IS BEING IMMEDIATELY DISINFECTED. |  | USMC CAMP PENDLETON | 93/08/09 | 0915AM | 930809 | 0925AM | 100 | GAL | BEACH CLUB ROAD | CAMP PENDELTON | SD | LIFT STATION #51849 | PLUGGED LINE-USED PUMPER TO KEEP FLOW DOWN | NONE | LIMED AREA.
| 930810 | 1230PM | ORV SALISBURY | 6197440460 | VALLECITOS WATER DISTRICT | 93/08/10 | 0940AM | 930810 | 0950AM |  | 300 | GAL |  | ENTRADA DEL LAGO | SAN MARCOS | S | 53B-Q6-MH7, THOMASP20-2F | GREASE BLOCKAGE IN A 10" GRAVITY SEWER MAIN | Y | LAKE SAN MARCOS |  |  | Y | Y | 05 | BLOCKAGE LOCATED BETWN. MH & LIFT STA. BLOCK |  | SAN DIEGO, CITY OF | 93/08/09 | 0730AM | 930809 | 1130AM | 1200 | GAL | 3181 ASH STREET | SAN DIEGO | SD | 10" VC SEWER MAIN | ROOTS IN 10" MAIN | NONE | RODDED 176' SECTION MAIN 10" VC TO RELIEVE STO
| 930811 | 0815AM | JOHN GIFFORD | 9099257676 | EASTERN MUNICIPAL WATER DIST. | 93/08/11 | 0630AM | 930811 | 0830AM |  | 13000 | GAL |  | LEON RD. & SALT CREEK | WINCHESTER | RV | PRE-IRRIGATION SPRINKLER SYS. | PIPE FAILURE AT 12" SOURCE PIPE. | NO | NONE |  |  | N | N |  | WATER WAS TERTIARY TREATED EFFLUENT. SPILL OCC |  | RAMONA MUNICIPAL WATER DIST. | 93/08/10 | 1435PM | 930810 | 1445PM | 4000 | GAL | END OF HUNTER ST. MH #13 | RAMONA | SD | MANHOLE | UNKNOWN SOURCE STOPPED PUMPS. POSSIBLY A P | NONE | AREA IS BEING IMMEDIATELY DISINFECTED.
| 930812 | 2000PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 93/08/12 | 2000PM | 930812 | 2130PM |  | 20 | GAL |  | 611 VILLAGE VIEW | FALLBROOK | SD | CLEANOUT | ROOTS | NO | NONE |  |  | N | N |  | AT 2030 PM, OPENED 5 - 10 FT. OF LATERAL. COMP |  | VALLECITOS WATER DISTRICT | 93/08/10 | 0940AM | 930810 | 0950AM | 300 | GAL | ENTRADA DEL LAGO | SAN MARCOS | S | 53B-Q6-MH7, THOMASP20-2F | GREASE BLOCKAGE IN A 10" GRAVITY SEWER MAIN | LAKE SAN MARCOS | BLOCKAGE LOCATED BETWN. MH & LIFT STA. BLOCK
| 930826 | ?????? | FRANK YTURRALEZ | 6195277456 | SAN DIEGO, CITY OF | 93/08/12 | 1850PM | 930812 | 1925PM |  | 4500 | GAL |  | 3255 LA JOLLA VILLAGE DRIVE | SAN DIEGO | SD | OVERLOW MHS. 32569 & 32570 | MAIN POWER BREAKER TRIPPED. | NO | NONE |  | INTERCEPTOR RETURNED TO SEWER. | Y | N |  | SPILL DIVERTED TO SEWER SYSTEM AT INTERCEPTOR |  | EASTERN MUNICIPAL WATER DIST. | 93/08/11 | 0630AM | 930811 | 0830AM | 13000 | GAL | LEON RD. & SALT CREEK | WINCHESTER | RV | PRE-IRRIGATION SPRINKLER SYS. | PIPE FAILURE AT 12" SOURCE PIPE. | NONE | WATER WAS TERTIARY TREATED EFFLUENT. SPILL OCC
| 930816 | 0900AM | BOB MANRY | 7146764101 | RANCHO CALIFORNIA WATER DIST. | 93/08/16 | 0900AM | 930816 | 1100AM |  | 1200 | GAL |  | BALLESTROS AND MANDRA | MURRIETA | RV | RAW SEWAGE MANHOLE | ROCKS, RAGS, ASPHALT BLOCKED LINE. | Y | STORM DRAIN |  |  | Y |  |  | FLUSHED RAW SEWAGE FROM STREET/GUTTER. CHLORIN |  | FALLBROOK SANITARY DISTRICT | 93/08/12 | 2000PM | 930812 | 2130PM | 20 | GAL | 611 VILLAGE VIEW | FALLBROOK | SD | CLEANOUT | ROOTS | NONE | AT 2030 PM, OPENED 5 - 10 FT. OF LATERAL. COMP
| 930830 | ?????? | WILIAM HAMPTON | 6195258687 | SAN DIEGO, CITY OF | 93/08/16 | 1630PM | 930816 | 1730PM |  | 30 | GAL |  | 4350 35TH STREET | SAN DIEGO | SD | SEWER LINE 8" CP | ROOTS | NO | NONE |  | SEWAGE DRIED UP IN GUTTER. | Y | N |  | AREAS WAS DEODORIZED. |  | SAN DIEGO, CITY OF | 93/08/12 | 1850PM | 930812 | 1925PM | 4500 | GAL | 3255 LA JOLLA VILLAGE DRIVE | SAN DIEGO | SD | OVERLOW MHS. 32569 & 32570 | MAIN POWER BREAKER TRIPPED. | NONE | SPILL DIVERTED TO SEWER SYSTEM AT INTERCEPTOR
| 930820 | 1600PM | ROBERT ESPINOSA | 6195452906 | CORONADO, CITY OF | 93/08/16 | 0800AM | 930816 | 1200PM |  | 300 | GAL |  | ALLEY PERPENDICULAR TO 2ND ST. | CORONADO | SD | BUILDING 334 | CLEAN OUT ON TOP OF 4" PIPE BURST OFF DUE T | NO | NONE |  | UNDER CONCRETE LOADING DOCKS | Y | N |  | PIPE HAS BEEN REPAIRED. INDUSTRIAL HYGIENIST M |  | RANCHO CALIFORNIA WATER DIST. | 93/08/16 | 0900AM | 930816 | 1100AM | 1200 | GAL | BALLESTROS AND MANDRA | MURRIETA | RV | RAW SEWAGE MANHOLE | ROCKS, RAGS, ASPHALT BLOCKED LINE. | STORM DRAIN | FLUSHED RAW SEWAGE FROM STREET/GUTTER. CHLORIN
| 930817 | 1330PM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 93/08/17 | ?????? | 930817 | 0740AM |  | 2500 | GAL |  | 4706 CANNON DRIVE | OCEANSIDE | SD | PUMP STATION (LEISURE VILLAGE) | INOPERATIVE COMPRESSOR PUMP | Y | IRRIGATION RUNOFF CHAN |  |  | Y | N |  | NO SOLIDS DISCHARGED. WASTEWATER FLOWED TO DIT |  | SAN DIEGO, CITY OF | 93/08/16 | 1630PM | 930816 | 1730PM | 30 | GAL | 4350 35TH STREET | SAN DIEGO | SD | SEWER LINE 8" CP | ROOTS | NONE | AREAS WAS DEODORIZED.
| 930818 | 1300PM | JOHN VAUGHT | 6197414854 | ESCONDIDO, CITY OF | 93/08/18 | 0800AM | 930818 | 0910AM |  | 1750 | GAL |  | 200 BLOCK OF FERNWOOD | ESCONDIDO | SD | SEWER ATLAS PG. 47, MH 15 | LARGE CONCENTRATION OF GREASE DEPOSIT CAUSE | Y | ESCONDIDO CREEK/SAN EL |  |  | Y | Y | 04 | TREATED AREA WITH DISINFECTANT AND WASHED DOWN |  | CORONADO, CITY OF | 93/08/16 | 0800AM | 930816 | 1200PM | 300 | GAL | ALLEY PERPENDICULAR TO 2ND ST. | CORONADO | SD | BUILDING 334 | CLEAN OUT ON TOP OF 4" PIPE BURST OFF DUE T | NONE | PIPE HAS BEEN REPAIRED. INDUSTRIAL HYGIENIST M
| 930820 | ?????? | RESIDENT | 6194273875 | CHULA VISTA, CITY OF | 93/08/20 | 1729PM | 930820 | 1930PM |  | 700 | GAL |  | MONSERATE & MAPLES | CHULA VISTA | SD | BATH TUB & OUTSIDE CLEANOUT | PLUG MAIN; ROOTS, GREASE | NO | NONE |  | STORM DRAIN | Y | N |  | STORM DRAIN FLUSHED WITH WATER. |  | OCEANSIDE, CITY OF | 93/08/17 | ?????? | 930817 | 0740AM | 2500 | GAL | 4706 CANNON DRIVE | OCEANSIDE | SD | PUMP STATION (LEISURE VILLAGE) | INOPERATIVE COMPRESSOR PUMP | IRRIGATION RUNOFF CHAN | NO SOLIDS DISCHARGED. WASTEWATER FLOWED TO DIT
| 930830 | ?????? | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 93/08/22 | 1200PM | 930822 | 1300PM |  | 60 | GAL |  | ADAMS AVE. & HINSON PL. | SAN DIEGO | SD | 6" CP | ROOTS | NO | NONE |  | STORM DRAIN | Y |  |  | FLOWED INTO STORM DRAIN WHERE IT SETTLED. |  | ESCONDIDO, CITY OF | 93/08/18 | 0800AM | 930818 | 0910AM | 1750 | GAL | 200 BLOCK OF FERNWOOD | ESCONDIDO | SD | SEWER ATLAS PG. 47, MH 15 | LARGE CONCENTRATION OF GREASE DEPOSIT CAUSE | ESCONDIDO CREEK/SAN EL | TREATED AREA WITH DISINFECTANT AND WASHED DOWN
| 930830 | ?????? | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 93/08/25 | 1230PM | 930825 | 1430PM |  | 600 | GAL |  | 40TH/ELCAJON BL. | SAN DIEGO | SD | 6" VC SEWER MAIN | ROCKS | NO | NONE |  | DISSIPATED IN STORM DRAIN. | Y |  |  | FLUSHED MAIN DEODERIZED AREA. |  | CHULA VISTA, CITY OF | 93/08/20 | 1729PM | 930820 | 1930PM | 700 | GAL | MONSERATE & MAPLES | CHULA VISTA | SD | BATH TUB & OUTSIDE CLEANOUT | PLUG MAIN; ROOTS, GREASE | NONE | STORM DRAIN FLUSHED WITH WATER.
| 930830 | 0815AM | LUCKY BISHOP IV | 6197414854 | ESCONDIDO, CITY OF | 93/08/29 | 1605PM | 930829 | 1530PM |  | 450 | GAL |  | ALLEY BTWN. 4TH & 5TH | ESCONDIDO | SD | SEWER ATLAS PG. 9; MANHOLE 9 | ROOTS AND GREASE IN MAIN LINE. | Y | ESCONDIDO CRK./SAN ELI |  |  | Y | Y | 04 | AREA WAS TREATED WITH DISINFECTANT AND WASHED |  | SAN DIEGO, CITY OF | 93/08/22 | 1200PM | 930822 | 1300PM | 60 | GAL | ADAMS AVE. & HINSON PL. | SAN DIEGO | SD | 6" CP | ROOTS | NONE | FLOWED INTO STORM DRAIN WHERE IT SETTLED.
| 930829 | 1240PM | RESIDENT | ?????????? | CHULA VISTA, CITY OF | 93/08/29 | 1240PM | 930829 | 1450PM |  | 200 | GAL |  | MELROSE & OXFORD | CHULA VISTA | SD | MANHOLE | GREASE AND PAPER | NO | NONE |  | STORM DRAIN PIPE | Y | N |  | AREA WASHED DOWN WITH WATER. |  | SAN DIEGO, CITY OF | 93/08/25 | 1230PM | 930825 | 1430PM | 600 | GAL | 40TH/ELCAJON BL. | SAN DIEGO | SD | 6" VC SEWER MAIN | ROCKS | NONE | FLUSHED MAIN DEODERIZED AREA.
| 930901 | ?????? | R. ROBY | 6195258685 | SAN DIEGO, CITY OF | 93/08/29 | 1215PM | 930829 | 1315PM |  | 300 | GAL |  | 1600 BLOCK 42ND STREET | SAN DIEGO | SD | 6" CP | GREASE | NO | NONE |  | DRIED IN DIRT. | Y |  |  | DRIED IN DIRT AT SITE. |  | ESCONDIDO, CITY OF | 93/08/29 | 1605PM | 930829 | 1530PM | 450 | GAL | ALLEY BTWN. 4TH & 5TH | ESCONDIDO | SD | SEWER ATLAS PG. 9; MANHOLE 9 | ROOTS AND GREASE IN MAIN LINE. | ESCONDIDO CRK./SAN ELI | AREA WAS TREATED WITH DISINFECTANT AND WASHED
| 930901 | ?????? | R. ROBY | 6195258685 | SAN DIEGO, CITY OF | 93/08/29 | 1600PM | 930829 | 1900PM |  | 900 | GAL |  | IMPERIAL AVE. & VISTA HORIZON' | SAN DIEGO | SD | 6" CP | GREASE | NO | NONE |  | STORM DRAIN | Y |  |  | FLOWED INTO STORM DRAIN WHERE IT SETTLED. |  | CHULA VISTA, CITY OF | 93/08/29 | 1240PM | 930829 | 1450PM | 200 | GAL | MELROSE & OXFORD | CHULA VISTA | SD | MANHOLE | GREASE AND PAPER | NONE | AREA WASHED DOWN WITH WATER.
| 930831 | 0730AM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 93/08/30 | 1545PM | 9308 | 1800PM |  | 4050 | GAL |  | INGRAHAM ST. UNDR SEA WRLD. DR | SAN DIEGO | SD | 8" CI FORCE MAIN BREAK | FORCE MAIN BREAK | Y | MISSION BAY/PACIFIC OC |  |  | Y | Y |  | FIVE SIGNS POSTED AT DOG BEACH; FIVE SIGNS POS |  | SAN DIEGO, CITY OF | 93/08/29 | 1215PM | 930829 | 1315PM | 300 | GAL | 1600 BLOCK 42ND STREET | SAN DIEGO | SD | 6" CP | GREASE | NONE | DRIED IN DIRT AT SITE.
| 930901 | 0730AM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 93/08/31 | 1800PM | 930831 | 1945PM |  | 2250 | GAL |  | INGRAHAM ST. UNDR. SEA WRLD DR | SAN DIEGO | SD | 8" CI FORCE MAIN | FORCE MAIN BREAK | Y | MISSION BAY/PACIFIC OC |  |  | Y | Y |  | SIGNS STILL POSTED FROM PREVIOUS OVERFLOW ON 8 |  | SAN DIEGO, CITY OF | 93/08/29 | 1600PM | 930829 | 1900PM | 900 | GAL | IMPERIAL AVE. & VISTA HORIZON' | SAN DIEGO | SD | 6" CP | GREASE | NONE | FLOWED INTO STORM DRAIN WHERE IT SETTLED.
| 930831 | 0650AM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 93/08/31 | 0650AM | 930831 | 0720AM |  | 200 | GAL |  | 422 MINNESOTA STREET | FALLBROOK | SD | MAINLINE | ROOTS | NO | NONE |  | OWNER'S YARD | N | N |  | AT 0700AM, OPENED MANHOLE. COMPLETED AT 0720A |  | SAN DIEGO, CITY OF | 93/08/30 | 1545PM | 9308 | 1800PM | 4050 | GAL | INGRAHAM ST. UNDR SEA WRLD. DR | SAN DIEGO | SD | 8" CI FORCE MAIN BREAK | FORCE MAIN BREAK | MISSION BAY/PACIFIC OC | FIVE SIGNS POSTED AT DOG BEACH; FIVE SIGNS POS
| 930901 | 1400PM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 93/09/01 | 1030AM | 930901 | 1130AM |  | 1800 | GAL |  | INGRAHAM & SEA WORLD OVERPASS | SAN DIEGO | SD | 8" CI FORCE MAIN BREAK | FORCE MAIN BREAK | Y | SAN DIEGO RIVER & MISS |  |  | Y | Y | 05 | SIGNS WERE PREVIOUSLY POSTED FROM OVERLW ON 8/ |  | SAN DIEGO, CITY OF | 93/08/31 | 1800PM | 930831 | 1945PM | 2250 | GAL | INGRAHAM ST. UNDR. SEA WRLD DR | SAN DIEGO | SD | 8" CI FORCE MAIN | FORCE MAIN BREAK | MISSION BAY/PACIFIC OC | SIGNS STILL POSTED FROM PREVIOUS OVERFLOW ON 8
| 930902 | 0900AM | JOEL HOLT | 6197288319 | FALLBROOK SANITARY DISTRICT | 93/09/01 | 1030PM | 930902 | 1230AM |  | 5000 | GAL |  | OSTRICH CREEK | FALLBROOK | SD | NEW RECLAIM WATER LINE | RECLAIM WATER LINE BROKE | Y | OSTRICH CRK./SAN LUIS |  |  | Y |  |  | THE BREAK WAS ISOLATED AND BEING REPAIRED. |  | FALLBROOK SANITARY DISTRICT | 93/08/31 | 0650AM | 930831 | 0720AM | 200 | GAL | 422 MINNESOTA STREET | FALLBROOK | SD | MAINLINE | ROOTS | NONE | AT 0700AM, OPENED MANHOLE. COMPLETED AT 0720A
| 930901 | 1250AM | AMUEL HILLIARD | 6196602007 | SAN DIEGO, COUNTY PUBLIC WORKS | 93/09/01 | 1250AM | 930901 | 0350AM |  | 200 | GAL |  | ESTRELLA DR. & LOMA DEL SUR | SPRING VALLEY | SD | EIGHT INCHES | ROOTS AND DEBRIS | NO | NONE |  | STREET & GUTTER | N | N |  |  |  | SAN DIEGO, CITY OF | 93/09/01 | 1030AM | 930901 | 1130AM | 1800 | GAL | INGRAHAM & SEA WORLD OVERPASS | SAN DIEGO | SD | 8" CI FORCE MAIN BREAK | FORCE MAIN BREAK | SAN DIEGO RIVER & MISS | SIGNS WERE PREVIOUSLY POSTED FROM OVERLW ON 8/
| 930903 | 0820AM | MARK A. STOFFER | 6197254806 | USMC, CAMP PENDLETON | 93/09/02 | 1745PM | 930902 | 2000PM |  | 3000 | GAL |  | STEWART MESA | CAMP PENDLETON | SD | ONE EIGHTH FROM 410251 | 8' CRACK IN FORCE MAIN | NO | NONE |  | FIELD | Y | N |  | REPAIR CREW REPAIRED LINE KEEPING FLOW FROM SP |  | FALLBROOK SANITARY DISTRICT | 93/09/01 | 1030PM | 930902 | 1230AM | 5000 | GAL | OSTRICH CREEK | FALLBROOK | SD | NEW RECLAIM WATER LINE | RECLAIM WATER LINE BROKE | OSTRICH CRK./SAN LUIS | THE BREAK WAS ISOLATED AND BEING REPAIRED.
| 930907 | 1200PM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 93/09/04 | 1000AM | 930904 | 1123AM |  | 600 | GAL |  | 2875 EMERALD DRIVE | OCEANSIDE | SD | MANHOLE IN CROWN OF STREET | GREASE & RAGS BLOCKING CITY MAIN LINE | NO | NONE |  | STORM DRAIN IN WESTSIDE GUTTER | Y | N |  | DOMESTIC WASTEWATER WITH NO OBSERVABLE SOLIDS |  | SAN DIEGO, COUNTY PUBLIC WORKS | 93/09/01 | 1250AM | 930901 | 0350AM | 200 | GAL | ESTRELLA DR. & LOMA DEL SUR | SPRING VALLEY | SD | EIGHT INCHES | ROOTS AND DEBRIS | NONE
| 930909 | 0500PM | JAMES E. SMITH | 7146432006 | MOULTON NIGUEL WATER DISTRICT | 93/09/04 | 0900AM | 930904 | 0200PM |  | 8000 | GAL |  | EL NIGUEL COUNTRY CLUB EAST 9 | LAGUNA NIGUEL | OR | ABANDONED SIPHON | BLOCKAGE IN SEWER REDIRECTED FLOW INTO AN A | Y | SALT CREEK/PACIFIC OCE |  |  | Y | Y |  |  |  | USMC, CAMP PENDLETON | 93/09/02 | 1745PM | 930902 | 2000PM | 3000 | GAL | STEWART MESA | CAMP PENDLETON | SD | ONE EIGHTH FROM 410251 | 8' CRACK IN FORCE MAIN | NONE | REPAIR CREW REPAIRED LINE KEEPING FLOW FROM SP
| 930913 | ?????? | D. EVANS | 6195258685 | SAN DIEGO, CITY OF | 93/09/04 | 1030AM | 930904 | 1130AM |  | 60 | GAL |  | 1935 FLORIDA STREET | SAN DIEGO | SD | 6" CP SEWER MAIN | DEBRIS BLOCKAGE | NO | NONE |  | DRIED IN STORM DRAIN | [5 empty] | OCEANSIDE, CITY OF | 93/09/04 | 1000AM | 930904 | 1123AM | 600 | GAL | 2875 EMERALD DRIVE | OCEANSIDE | SD | MANHOLE IN CROWN OF STREET | GREASE & RAGS BLOCKING CITY MAIN LINE | NONE | DOMESTIC WASTEWATER WITH NO OBSERVABLE SOLIDS
| 930913 | ?????? | G. D. EVANS | 6195258685 | SAN DIEGO, CITY OF | 93/09/04 | 1230PM | 930904 | 1330PM |  | 60 | GAL |  | CAM.ESTRELLADO & NAVAJO RD. | SAB DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | NO | NONE |  | DRIED IN STORM DRAIN | Y | N |  |  |  | MOULTON NIGUEL WATER DISTRICT | 93/09/04 | 0900AM | 930904 | 0200PM | 8000 | GAL | EL NIGUEL COUNTRY CLUB EAST 9 | LAGUNA NIGUEL | OR | ABANDONED SIPHON | BLOCKAGE IN SEWER REDIRECTED FLOW INTO AN A | SALT CREEK/PACIFIC OCE
| 930907 | 1130AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 93/09/06 | 1015AM | 930906 | 1630PM |  | 23250 | GAL |  | 18265 MOON SONG CT. | SAN DIEGO | SD | SEWER PUMP STATION | PUMP STATION. NEW PUMP STATION - UNKNOWN NU | Y | LAKE HODGES |  |  | Y | Y | ?? | CREW UNABLE TO LOCATE OVERFLOW ON 9/6/93. NO O |  | SAN DIEGO, CITY OF | 93/09/04 | 1030AM | 930904 | 1130AM | 60 | GAL | 1935 FLORIDA STREET | SAN DIEGO | SD | 6" CP SEWER MAIN | DEBRIS BLOCKAGE | NONE
| 930906 | 1900PM | MS. BANKS/HOME OWNER | ?????????? | CARLSBAD, CITY OF | 93/09/06 | 1900PM | 930906 | 2030PM |  | 100 | GAL |  | BACK YARD OF HOUSE | CARLSBAD | SD | 8" VCP | SEWER MAIN STOPPAGE | NO | NONE |  | ABSORED IN THE DIRT YARD | N | N |  | WATER CAME OUT OF A CLEANOUT IN BACK OF HOUSE. |  | SAN DIEGO, CITY OF | 93/09/04 | 1230PM | 930904 | 1330PM | 60 | GAL | CAM.ESTRELLADO & NAVAJO RD. | SAB DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | NONE
| 930913 | ?????? | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 93/09/06 | 0930AM | 930906 | 1130AM |  | 1200 | GAL |  | 3800 TORREY PINE RD. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOTS BLOCKAGE | NO | NONE |  | SOAKED INTO DIRT STORM DRAIN | Y | N |  | MACHINE RODDED TO RELIEVE BLOCKAGE. DEODORIZED |  | SAN DIEGO, CITY OF | 93/09/06 | 1015AM | 930906 | 1630PM | 23250 | GAL | 18265 MOON SONG CT. | SAN DIEGO | SD | SEWER PUMP STATION | PUMP STATION. NEW PUMP STATION - UNKNOWN NU | LAKE HODGES | CREW UNABLE TO LOCATE OVERFLOW ON 9/6/93. NO O
| 930907 | 1350PM | MARK A. STOFFER | 6197253567 | USMC, CAMP PENDLETON | 93/09/07 | 1100AM | 920907 | 2100PM |  | 100000 | GAL |  | LAS PULGAS | CAMP PENDLETON | SD | PLANT #9 - 4383 | VACTOR TRUCK RAN OVER POWER TRANSFORMER. BR | NO | NONE |  | PRIMARY TREATMENT TO PONDS | N | N |  | THIS WAS NOT A SPILL. LOSS OF SECONDARY TREAT |  | CARLSBAD, CITY OF | 93/09/06 | 1900PM | 930906 | 2030PM | 100 | GAL | BACK YARD OF HOUSE | CARLSBAD | SD | 8" VCP | SEWER MAIN STOPPAGE | NONE | WATER CAME OUT OF A CLEANOUT IN BACK OF HOUSE.
| 930913 | ?????? | D. BEST | 6195258686 | SAN DIEGO, CITY OF | 93/09/08 | 0800AM | 930908 | 0900AM |  | 300 | GAL |  | 4000 BL MAYBERRY STREET | SAN DIEGO | SD | 8" PVC SEWER MAIN | GREASE BLOCKAGE | NO | NONE |  | DISSIPATED IN STORM DRAIN] | Y | N |  | MACHINE RODDED. SEWAGE DISSIPATED IN STORM DR |  | SAN DIEGO, CITY OF | 93/09/06 | 0930AM | 930906 | 1130AM | 1200 | GAL | 3800 TORREY PINE RD. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOTS BLOCKAGE | NONE | MACHINE RODDED TO RELIEVE BLOCKAGE. DEODORIZED
| 930915 | ?????? | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 93/09/09 | 1900PM | 930910 | 1130AM |  | 9900 | GAL |  | 4606 HURON AVE. IN CANYON | SAN DIEGO | SD | 8" VC SEWER MAIN | GRAVITY SEWER MAIN BREAK IN CANYON. | NO | NONE |  | DRIED UP IN CANYON | Y | N |  | SEWAGE DRIED UP IN CANYON. |  | USMC, CAMP PENDLETON | 93/09/07 | 1100AM | 920907 | 2100PM | 100000 | GAL | LAS PULGAS | CAMP PENDLETON | SD | PLANT #9 - 4383 | VACTOR TRUCK RAN OVER POWER TRANSFORMER. BR | NONE | THIS WAS NOT A SPILL. LOSS OF SECONDARY TREAT
| 930913 | ?????? | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 93/09/09 | 2230PM | 930910 | 0300AM |  | 120 | GAL |  | 4700 BLK. VOLTAIRE, ALLEY NO. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | NO | NONE |  | DRIED UP IN ALLEY | N | N |  | RODDED MAIN BY MACHINE. |  | SAN DIEGO, CITY OF | 93/09/08 | 0800AM | 930908 | 0900AM | 300 | GAL | 4000 BL MAYBERRY STREET | SAN DIEGO | SD | 8" PVC SEWER MAIN | GREASE BLOCKAGE | NONE | MACHINE RODDED. SEWAGE DISSIPATED IN STORM DR
| 930913 | ?????? | MARK A. STOFFER | 6197254806 | USMC, CAMP PENDLETON | 93/09/09 | 1900PM | 930909 | 1930PM |  | 400 | GAL |  | 33 AREA | CAMP PENDLETON | SD | 33605 LIFT STATION | FLOAT STUCK | NO | NONE |  | GROUND BY LIFT STATION | Y | N |  | UNSTUCK FLOAT & LIMED THE AREA. |  | SAN DIEGO, CITY OF | 93/09/09 | 1900PM | 930910 | 1130AM | 9900 | GAL | 4606 HURON AVE. IN CANYON | SAN DIEGO | SD | 8" VC SEWER MAIN | GRAVITY SEWER MAIN BREAK IN CANYON. | NONE | SEWAGE DRIED UP IN CANYON.
| 930911 | 1725PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 93/09/11 | 1710PM | 930911 | 1820PM |  | 10 | GAL |  | 731 N. MAIN STREET | FALLBROOK | SD | 4" CLEANOUT | ROOTS IN MAIN LINE | NO | NONE |  | SOAKED IN YARD AROUND CLEANOUT | N | N |  | COMPLETED CLEANOUT AT 1825PM. |  | SAN DIEGO, CITY OF | 93/09/09 | 2230PM | 930910 | 0300AM | 120 | GAL | 4700 BLK. VOLTAIRE, ALLEY NO. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | NONE | RODDED MAIN BY MACHINE.
| 930916 | ?????? | D. BEST | 6195258686 | SAN DIEGO, CITY OF | 93/09/13 | 0800AM | 930913 | 1000AM |  | 120 | GAL |  | 2183 MANZANA WAY | SAN DIEGO | SD | 8" PVC SEWER MAIN | DEBRIS IN MAIN | NO | NONE |  | DISSIPATED IN STORM DRAIN | Y | N |  | DEODORIZED AROUND MANHOLE. SEWAGE DISSIPATED I |  | USMC, CAMP PENDLETON | 93/09/09 | 1900PM | 930909 | 1930PM | 400 | GAL | 33 AREA | CAMP PENDLETON | SD | 33605 LIFT STATION | FLOAT STUCK | NONE | UNSTUCK FLOAT & LIMED THE AREA.
| 930922 | ?????? | RONALD ROBY | 6195258685 | SAN DIEGO, CITY OF | 93/09/17 | 0700AM | 930917 | 0830AM |  | 90 | GAL |  | 7055 VIA VALUERDE | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE | NO | NONE |  | DRIED IN STREET | Y |  |  | FLOWED ONTO STREET WHERE IT DRIED UP. |  | FALLBROOK SANITARY DISTRICT | 93/09/11 | 1710PM | 930911 | 1820PM | 10 | GAL | 731 N. MAIN STREET | FALLBROOK | SD | 4" CLEANOUT | ROOTS IN MAIN LINE | NONE | COMPLETED CLEANOUT AT 1825PM.
| 930922 | ?????? | DAVID BEST | 6195258686 | SAN DIEGO, CITY OF | 93/09/17 | 0900AM | 930917 | 1000AM |  | 300 | GAL |  | 5011 WARING ROAD | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE IN MAIN | NO | NONE |  |  | Y |  |  | MACHINE RODDED SOME OVERFLOW IN BACK OF HOUSE |  | SAN DIEGO, CITY OF | 93/09/13 | 0800AM | 930913 | 1000AM | 120 | GAL | 2183 MANZANA WAY | SAN DIEGO | SD | 8" PVC SEWER MAIN | DEBRIS IN MAIN | NONE | DEODORIZED AROUND MANHOLE. SEWAGE DISSIPATED I
| 930920 | 1200PM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 930918 | 1200PM | 930918 | 1600PM |  | 200 | GAL |  | 445 GARRISON STREET | OCEANSIDE | SD | SEWER CLEANOUT IN PRIV. LATRL. | UNKNOWN BLOCKAGE IN PRIVATE LATERAL. | Y | GARRISON CRK/LOMA ALTA |  |  | Y | Y |  | DOMESTIC WASTEWTR W/NO APPARENT SOLIDS ESCAPED |  | SAN DIEGO, CITY OF | 93/09/17 | 0700AM | 930917 | 0830AM | 90 | GAL | 7055 VIA VALUERDE | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE | NONE | FLOWED ONTO STREET WHERE IT DRIED UP.
| 930918 | 1530PM | MITCH PIERSON | 6197281180 | FALLBROOK SANITARY DISTRICT | 930918 | 1300PM | 930918 | 1400PM |  | 800 | GAL |  | PLANT #1 STP | FALLBROOK | SD | LIFT STATION #5 | CONTROL PANEL FAILURE | Y | FALLBRK.CRK/ST. MARGAR |  |  | Y | N |  | LEFT MESSAGE AT 1530PM TO CRWQCB ON 930918. |  | SAN DIEGO, CITY OF | 93/09/17 | 0900AM | 930917 | 1000AM | 300 | GAL | 5011 WARING ROAD | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE IN MAIN | NONE | MACHINE RODDED SOME OVERFLOW IN BACK OF HOUSE
| 930922 | ?????? | RONALD ROBY | 6195258685 | SAN DIEGO, CITY OF | 930919 | 1300PM | 930919 | 1330PM |  | 60 | GAL |  | 1635 BROOKES AVE. | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOTS | NO | NONE |  | FLOW DRIED IN STREET. | Y |  |  | FLOW DRIED IN STREET. |  | OCEANSIDE, CITY OF | 930918 | 1200PM | 930918 | 1600PM | 200 | GAL | 445 GARRISON STREET | OCEANSIDE | SD | SEWER CLEANOUT IN PRIV. LATRL. | UNKNOWN BLOCKAGE IN PRIVATE LATERAL. | GARRISON CRK/LOMA ALTA | DOMESTIC WASTEWTR W/NO APPARENT SOLIDS ESCAPED
| 930921 | 0655AM | JOHN KING, CITIZEN | 6197535018 | SAN ELIJO JOINT POWERS AUTH. | 930921 | 0330AM | 930921 | 0715AM |  | 75000 | GAL |  | SO. E. CORNER 3RD & B ST. | ENCINITAS | SD | MOONLIGHT BEACH PUMA STATION | LEAD & LAG PUMPS TRIPPED. IMPELLER OFF ON L | Y | MOONLIGHT BEACH/PACIFI |  |  | Y | Y |  | STANDBY PERSONNEL NOT NOTIFIED.INVESTIGATING T |  | FALLBROOK SANITARY DISTRICT | 930918 | 1300PM | 930918 | 1400PM | 800 | GAL | PLANT #1 STP | FALLBROOK | SD | LIFT STATION #5 | CONTROL PANEL FAILURE | FALLBRK.CRK/ST. MARGAR | LEFT MESSAGE AT 1530PM TO CRWQCB ON 930918.
| 930927 | ?????? | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 930922 | 1850PM | 930922 | 2100PM |  | 660 | GAL |  | 1740 SO. 43RD ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE | NO | NONE |  | STORM DRAIN EPSILON & DELTA | Y | N |  | RODDED MAIN. |  | SAN DIEGO, CITY OF | 930919 | 1300PM | 930919 | 1330PM | 60 | GAL | 1635 BROOKES AVE. | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOTS | NONE | FLOW DRIED IN STREET.
| 930927 | ?????? | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 930922 | 1630PM | 930922 | 1800PM |  | 450 | GAL |  | 4202 EL CAJON BLVD. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE | NO | NONE |  | STORM DRAIN EL CAJON/COPELAND | Y | N |  | RODDED RELIEVING STOPPAGE ABOUT 310' INTO MAIN |  | SAN ELIJO JOINT POWERS AUTH. | 930921 | 0330AM | 930921 | 0715AM | 75000 | GAL | SO. E. CORNER 3RD & B ST. | ENCINITAS | SD | MOONLIGHT BEACH PUMA STATION | LEAD & LAG PUMPS TRIPPED. IMPELLER OFF ON L | MOONLIGHT BEACH/PACIFI | STANDBY PERSONNEL NOT NOTIFIED.INVESTIGATING T
| 930924 | 0800AM | I. JENKINS | 6195258682 | SAN DIEGO, CITY OF | 930923 | 0930AM | 930923 | 1030AM |  | 1200 | GAL |  | 28TH BTWN. HARBOR DR./MAIN ST. | SAN DIEGO | SD | 12" VC MAIN | GREASE | Y | FLD. CTRL. CHAN./SAN D |  |  | Y | Y | 02 |  |  | SAN DIEGO, CITY OF | 930922 | 1850PM | 930922 | 2100PM | 660 | GAL | 1740 SO. 43RD ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE | NONE | RODDED MAIN.
| 930923 | 1130AM | LUIS HERNANDEZ | 6195258682 | SAN DIEGO, CITY OF | 930923 | 0930AM | 930923 | 1000AM |  | 20 | GAL |  | MANHOLE AT 28TH ST. | SAN DIEGO | SD | MANHOLE | GREASE | Y | ?????????????????????? |  |  | ? | ? |  | WASHED THE STREET. |  | SAN DIEGO, CITY OF | 930922 | 1630PM | 930922 | 1800PM | 450 | GAL | 4202 EL CAJON BLVD. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE | NONE | RODDED RELIEVING STOPPAGE ABOUT 310' INTO MAIN
| 930930 | 0953AM | ISSAC JENKINS | 6195258682 | SAN DIEGO, CITY OF | 930923 | 1000PM | 930929 | 1300PM |  | 9000 | GAL |  | W/SIDE 163 S/O ROBINSON AVE. | SAN DIEGO | SD | MANHOLE #13608 | ROOTS | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  |  |  | SAN DIEGO, CITY OF | 930923 | 0930AM | 930923 | 1030AM | 1200 | GAL | 28TH BTWN. HARBOR DR./MAIN ST. | SAN DIEGO | SD | 12" VC MAIN | GREASE | FLD. CTRL. CHAN./SAN D
| 930927 | ?????? | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 930923 | 1530PM | 930923 | 1730PM |  | 120 | GAL |  | 3911 CLEVELAND | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE | NO | NONE |  | SOAKED IN CANYON UNIV./VERMNT. | Y | N |  | RODDED GREASE AT 270 ' IN MAIN. |  | SAN DIEGO, CITY OF | 930923 | 0930AM | 930923 | 1000AM | 20 | GAL | MANHOLE AT 28TH ST. | SAN DIEGO | SD | MANHOLE | GREASE | ?????????????????????? | WASHED THE STREET.
| 930927 | 9822AM | DAVID BEST | 6195258686 | SAN DIEGO, CITY OF | 930924 | 1230PM | 930924 | 1430PM |  | 3000 | GAL |  | SKYLINE & VALENCIA PARKWAY | SAN DIEGO | SD | 8" VC SEWER MAIN | DEBRIS STOPPAGE | NO | NONE |  | STORM DRAIN,BONITA/CERVANTES | Y | N |  | MACHINE RODDED AND DEODORIZED AROUND MANHOLE & |  | SAN DIEGO, CITY OF | 930923 | 1000PM | 930929 | 1300PM | 9000 | GAL | W/SIDE 163 S/O ROBINSON AVE. | SAN DIEGO | SD | MANHOLE #13608 | ROOTS | STORM DRAIN/PACIFIC OC
| 930930 | ?????? | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 930926 | 0930AM | 930926 | 1030AM |  | 60 | GAL |  | BELLINGHAM & CHEROKEE | SAN DIEGO | SD | 8" VC | DEBRIS | NO | NONE |  | STORM DRAIN | Y |  |  | FLOWED INTO STORM DRAIN WHERE IT SETTLED. |  | SAN DIEGO, CITY OF | 930923 | 1530PM | 930923 | 1730PM | 120 | GAL | 3911 CLEVELAND | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE | NONE | RODDED GREASE AT 270 ' IN MAIN.
| 930928 | 1845PM | CHULA VISTA PD | 6196915151 | CHULA VISTA, CITY OF | 930928 | 1845PM | 930928 | 2050PM |  | 100 | GAL |  | MELROSE & TELEGRAPH CYN. RD. | CHULA VISTA | SD | MANHOLE | GRASS AND PAPER | NO | NONE |  | STORM DRAIN & OPEN DRN. CHAN. | N | N |  | WASH DOWN AREA INFECTED AND CATCH BASIN. |  | SAN DIEGO, CITY OF | 930924 | 1230PM | 930924 | 1430PM | 3000 | GAL | SKYLINE & VALENCIA PARKWAY | SAN DIEGO | SD | 8" VC SEWER MAIN | DEBRIS STOPPAGE | NONE | MACHINE RODDED AND DEODORIZED AROUND MANHOLE &
| 931001 | 1320PM | WILLIAM HAMPTON | 6195258687 | SAN DIEGO, CITY OF | 930930 | 2230PM | 931001 | 0100AM |  | 300 | GAL |  | 3274 FOX RUN WAY WEST | SAN DIEGO | SD | 8" PVC SEWER MAIN | ROOTS | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | RODDED 367' SECTION OF MANHOLES REMOVING ROOTS |  | SAN DIEGO, CITY OF | 930926 | 0930AM | 930926 | 1030AM | 60 | GAL | BELLINGHAM & CHEROKEE | SAN DIEGO | SD | 8" VC | DEBRIS | NONE | FLOWED INTO STORM DRAIN WHERE IT SETTLED.
| 930930 | 0700am | BOB SCRIBNER | 6192673228 | SAN DIEGO, COUNTY OF | 93/09/30 | 0600AM | 930930 | 0800AM |  | 500 | GAL |  | SWEETWATER RD. & PRAY ST. | BONITA | SD | 590-260-03908 | 8" AUGER FOUND IN LINE OBSTRUCTING MANHOLE | NO | NONE |  | GOLF COURSE GREEN | Y | N |  | WASTEWATER WAS CHLORINATED AND ABSORBED INTO G |  | CHULA VISTA, CITY OF | 930928 | 1845PM | 930928 | 2050PM | 100 | GAL | MELROSE & TELEGRAPH CYN. RD. | CHULA VISTA | SD | MANHOLE | GRASS AND PAPER | NONE | WASH DOWN AREA INFECTED AND CATCH BASIN.
| 931002 | 1037AM | L. HERNANDEZ | 6195258682 | SAN DIEGO, CITY OF | 931001 | 1045AM | 931001 | 1130AM |  | 450 | GAL |  | CORNISH & LADERA | SAN DIEGO | SD | PRIVATE 8" SEWER | GRAVITY MAIN BREAK DUE TO BLOCKAGE | NO | NONE |  | PRIVATE MAIN | Y | N |  | PRIVATE MAIN IS PROPERTY OF PT. LOMA NAZARENE |  | SAN DIEGO, CITY OF | 930930 | 2230PM | 931001 | 0100AM | 300 | GAL | 3274 FOX RUN WAY WEST | SAN DIEGO | SD | 8" PVC SEWER MAIN | ROOTS | STORM DRAIN/PACIFIC OC | RODDED 367' SECTION OF MANHOLES REMOVING ROOTS
| 931004 | 1545PM | MARK A. STOFFER | 6197254886 | USMC, CAMP PENDLETON | 931002 | 1520PM | 931002 | 1520PM |  | 100 | GAL |  | 11 AREA - CHRISMAN | CAMP PENDLETON | SD | HOUSING 208 | BLOCKED LINE | NO | NONE |  | SIDE OF HILL | Y | N |  | JET RODDED LINE & LIMED AREA. |  | SAN DIEGO, COUNTY OF | 93/09/30 | 0600AM | 930930 | 0800AM | 500 | GAL | SWEETWATER RD. & PRAY ST. | BONITA | SD | 590-260-03908 | 8" AUGER FOUND IN LINE OBSTRUCTING MANHOLE | NONE | WASTEWATER WAS CHLORINATED AND ABSORBED INTO G
| 931004 | 0130AM | RONALD ROBY-HAMPTON | 6195258685 | SAN DIEGO, CITY OF | 931003 | 1100AM | 931004 | 0800AM |  | 1260 | GAL |  | 11738 CARMEL MOUNTAIN ROAD | SAN DIEGO | SD | 8" POLYVINYL SEWER MAIN | ROEL CONSTRUCTION CO. CAUSED MUD AND ROCK T | Y | STORM DRAIN TO PACIFIC |  |  | Y | N |  | CITY HAVE NOT TAKEN OVER THE OWNERSHIP OF THIS |  | SAN DIEGO, CITY OF | 931001 | 1045AM | 931001 | 1130AM | 450 | GAL | CORNISH & LADERA | SAN DIEGO | SD | PRIVATE 8" SEWER | GRAVITY MAIN BREAK DUE TO BLOCKAGE | NONE | PRIVATE MAIN IS PROPERTY OF PT. LOMA NAZARENE
| 931004 | 1230PM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 931003 | 1000AM | 931003 | 1200PM |  | 350 | GAL |  | 700 CAPISTRANO DRIVE | OCEANSIDE | SD | SEWER MAIN MANHOLE | RAGS, ROOTS, TREE BARK & GLOVES CAUSED REST | Y | SAN LUIS REY RIV./PACI |  |  | Y | N |  | NO OBSERVABLE SOLIDS ESCAPED. DOMESTIC WASTEWA |  | USMC, CAMP PENDLETON | 931002 | 1520PM | 931002 | 1520PM | 100 | GAL | 11 AREA - CHRISMAN | CAMP PENDLETON | SD | HOUSING 208 | BLOCKED LINE | NONE | JET RODDED LINE & LIMED AREA.
| 931004 | 0130AM | RONALD D. ROBY | 6195258682 | SAN DIEGO, CITY OF | 931003 | 0700AM | 931003 | 0800AM |  | 7860 | GAL |  | 15500 PAYMOGO DRIVE | SAN DIEGO | SD | PUMP STATION 62 | POWER FAILURE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | SDG&E WAS WORKING IN AREA & CAUSED SPILL. CITY |  | SAN DIEGO, CITY OF | 931003 | 1100AM | 931004 | 0800AM | 1260 | GAL | 11738 CARMEL MOUNTAIN ROAD | SAN DIEGO | SD | 8" POLYVINYL SEWER MAIN | ROEL CONSTRUCTION CO. CAUSED MUD AND ROCK T | STORM DRAIN TO PACIFIC | CITY HAVE NOT TAKEN OVER THE OWNERSHIP OF THIS
| 931005 | 2400PM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931005 | 1700PM | 931005 | 1730PM |  | 150 | GAL |  | DUNHAVEN & MILTON | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN |  | STORM INTERCEPTOR TO SEWER | Y | Y |  | RODDED 160 FEET FROM MANHOLE #18876 TO MH#1887 |  | OCEANSIDE, CITY OF | 931003 | 1000AM | 931003 | 1200PM | 350 | GAL | 700 CAPISTRANO DRIVE | OCEANSIDE | SD | SEWER MAIN MANHOLE | RAGS, ROOTS, TREE BARK & GLOVES CAUSED REST | SAN LUIS REY RIV./PACI | NO OBSERVABLE SOLIDS ESCAPED. DOMESTIC WASTEWA
| 931007 | 0700AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931006 | 1800PM | 931006 | 1900PM |  | 30 | GAL |  | 3004 WARDLOW AVE. | SAN DIEGO | SD | 8" PVC SEWER MAIN | GREASE | Y | GUTTER ON WARDLOW TO P |  |  | Y | N |  | DEODORIZED. |  | SAN DIEGO, CITY OF | 931003 | 0700AM | 931003 | 0800AM | 7860 | GAL | 15500 PAYMOGO DRIVE | SAN DIEGO | SD | PUMP STATION 62 | POWER FAILURE | STORM DRAIN/PACIFIC OC | SDG&E WAS WORKING IN AREA & CAUSED SPILL. CITY
| 931007 | 0715AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931006 | 1800PM | 931006 | 1900PM |  | 30 | GAL |  | 7850 VISTA HILL AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | RODDED MAIN 290'; CLEARED STOPPAGE ABOUT 215'; |  | SAN DIEGO, CITY OF | 931005 | 1700PM | 931005 | 1730PM | 150 | GAL | DUNHAVEN & MILTON | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN | RODDED 160 FEET FROM MANHOLE #18876 TO MH#1887
| 931007 | 0730AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 931006 | 0927AM | 931006 | 0130AM |  | 2400 | GAL |  | 4138 VAN DYKE AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | NO | NONE |  | VACUMED UP AT ALLY | Y | N |  | OVERFLOW DIDN'T REACH SURFACE WATER. IT PUDDLE |  | SAN DIEGO, CITY OF | 931006 | 1800PM | 931006 | 1900PM | 30 | GAL | 3004 WARDLOW AVE. | SAN DIEGO | SD | 8" PVC SEWER MAIN | GREASE | GUTTER ON WARDLOW TO P | DEODORIZED.
| 931007 | 1100AM | DISTRICT OFFICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 931007 | 1100AM | 931007 | 1115AM |  | 60 | GAL |  | 1418 S. MISSION RD. | FALLBROOK | SD | 6" CLEANOUT | UNKNOWN | NO | NONE |  | DRIVEWAY & ROAD | N | N |  | AT 1108AM, OPENED CLEANOUT. WASHED DOWN WITH 1 |  | SAN DIEGO, CITY OF | 931006 | 1800PM | 931006 | 1900PM | 30 | GAL | 7850 VISTA HILL AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN/PACIFIC OC | RODDED MAIN 290'; CLEARED STOPPAGE ABOUT 215';
| 931008 | 0800AM | I. JENKINS | 6195258682 | SAN DIEGO, CITY OF | 931007 | 0830AM | 931007 | 1100AM |  | 150 | GAL |  | 2137 PACIFIC HIGHWAY | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | OVERFLOW WAS FROM CUSTOMER'S CLEANOUT LOCATION |  | SAN DIEGO, CITY OF | 931006 | 0927AM | 931006 | 0130AM | 2400 | GAL | 4138 VAN DYKE AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | NONE | OVERFLOW DIDN'T REACH SURFACE WATER. IT PUDDLE
| 931008 | 0110AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931007 | 1730PM | 931007 | 1930PM |  | 120 | GAL |  | INTERSECTION OF HOITT & K STS. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | NO | NONE |  | ENDED AT 29TH & L ON CURB. | Y | N |  | RODED MAIN; DEODORIZED AND SWEPT. |  | FALLBROOK SANITARY DISTRICT | 931007 | 1100AM | 931007 | 1115AM | 60 | GAL | 1418 S. MISSION RD. | FALLBROOK | SD | 6" CLEANOUT | UNKNOWN | NONE | AT 1108AM, OPENED CLEANOUT. WASHED DOWN WITH 1
| 931008 | 1520PM | MIKE BEDARD | 6195277456 | SAN DIEGO, CITY OF | 931008 | 0930AM | 931008 | 1100AM |  | 1600 | GAL |  | 898 SUNSET CLIFFS BLVD. | SAN DIEGO | SD | SPS 35 | BUBBLER FAILURE | Y | PACIFIC OCEAN |  |  | Y | Y |  | SIX SIGNS POSTED. 3 SOUTH OF SPILL PT. AND 3 |  | SAN DIEGO, CITY OF | 931007 | 0830AM | 931007 | 1100AM | 150 | GAL | 2137 PACIFIC HIGHWAY | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN/PACIFIC OC | OVERFLOW WAS FROM CUSTOMER'S CLEANOUT LOCATION
| 931010 | 0953AM | RONALD D. ROBY | 6195258686 | SAN DIEGO, CITY OF | 931008 | 1730PM | 931008 | 1830PM |  | 60 | GAL |  | 25TH & G ST. | SAN DIEGO | SD | 6" CP | ROCKS\ | NO | NONE |  | SWEPT BACK INTO MANHOLE | Y |  |  | FLOW WAS SWEPT FACK INTO MANHOLE BY CREW. |  | SAN DIEGO, CITY OF | 931007 | 1730PM | 931007 | 1930PM | 120 | GAL | INTERSECTION OF HOITT & K STS. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | NONE | RODED MAIN; DEODORIZED AND SWEPT.
| 931010 | 0900AM | MIKE DIETRICH | 6197535018 | ENCINITAS, CITY OF | 931008 | 1000AM | 931010 | 01200P |  | 250000 | GAL |  | 2695 MANCHESTER AVE. | CARDIFF BY SEA | SD | MANHOLE #9 MAP PG. 261-01 | ROCKS & ROOTS IN THE LINE, PRESUMABLY DUE T | NO | NONE |  | REACH SAND/DIRT FLOOD CHANNEL | Y | N |  | WAS NOT POSTED. WASTE CONTAINED WITHIN GATED |  | SAN DIEGO, CITY OF | 931008 | 0930AM | 931008 | 1100AM | 1600 | GAL | 898 SUNSET CLIFFS BLVD. | SAN DIEGO | SD | SPS 35 | BUBBLER FAILURE | PACIFIC OCEAN | SIX SIGNS POSTED. 3 SOUTH OF SPILL PT. AND 3
| 931011 | 0800AM | D. BEST | 6195258686 | SAN DIEGO, CITY OF | 931009 | 1930PM | 931009 | 2200PM |  | 750 | GAL |  | 4027 EL CAJON BLVD. | SAN DIEGO | SD | 6" VC MAIN | GREASE BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | MACHINE RODDED AND CLEANED AROUND MANHOLE. |  | SAN DIEGO, CITY OF | 931008 | 1730PM | 931008 | 1830PM | 60 | GAL | 25TH & G ST. | SAN DIEGO | SD | 6" CP | ROCKS\ | NONE | FLOW WAS SWEPT FACK INTO MANHOLE BY CREW.
| 931010 | 1045AM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931009 | 1830PM | 931009 | 2000PM |  | 90 | GAL |  | 5060 UNIVERSITY AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | INTO DIRT 5000 UNIVER. |  |  | Y |  |  | FLOW WENT INTO DIRT LOT AND SOAKED INTO GROUND |  | ENCINITAS, CITY OF | 931008 | 1000AM | 931010 | 01200P | 250000 | GAL | 2695 MANCHESTER AVE. | CARDIFF BY SEA | SD | MANHOLE #9 MAP PG. 261-01 | ROCKS & ROOTS IN THE LINE, PRESUMABLY DUE T | NONE | WAS NOT POSTED. WASTE CONTAINED WITHIN GATED
| 931010 | 0945AM | RONALD D. ROBY | 6195258686 | SAN DIEGO, CITY OF | 931009 | 0830AM | 931009 | 1000AM |  | 90 | GAL |  | 1815 FROUDE ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | CREW INVESTIGATED AND FOUND NO SIGNS OF SEWAGE |  | SAN DIEGO, CITY OF | 931009 | 1930PM | 931009 | 2200PM | 750 | GAL | 4027 EL CAJON BLVD. | SAN DIEGO | SD | 6" VC MAIN | GREASE BLOCKAGE | STORM DRAIN/PACIFIC OC | MACHINE RODDED AND CLEANED AROUND MANHOLE.
| 931011 | 0700AM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931010 | 1700PM | 931011 | 0200AM |  | 540 | GAL |  | 4436 CAM DE LA PLAZA | SAN DIEGO | SD | 8" PVC SEWER MAIN | BLOCKAGE CAUSED BY VANDALISM | NO | NONE |  | COLLECTED & RETURNED TO SEWER. | Y | N |  | FLOWED ONTO PARKING LOT WHERE IT WAS VACUMMED |  | SAN DIEGO, CITY OF | 931009 | 1830PM | 931009 | 2000PM | 90 | GAL | 5060 UNIVERSITY AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | INTO DIRT 5000 UNIVER. | FLOW WENT INTO DIRT LOT AND SOAKED INTO GROUND
| 931011 | 0700AM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931010 | 2000PM | 931011 | 0200AM |  | 720 | GAL |  | 9845 DESERTVIEW DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN TO SEWER |  |  | Y | N |  | FLOW WENT TO INTERCEPTOR WHERE IT RETURNED TO |  | SAN DIEGO, CITY OF | 931009 | 0830AM | 931009 | 1000AM | 90 | GAL | 1815 FROUDE ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN/PACIFIC OC | CREW INVESTIGATED AND FOUND NO SIGNS OF SEWAGE
| 931011 | 0800AM | D. BEST | 6125258686 | SAN DIEGO, CITY OF | 931010 | 2355PM | 931011 | 0439AM |  | 1440 | GAL |  | 40TH & ORANGE AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | DIRT ALLEY/PACIFIC OCE |  |  | Y | N |  | MACHINE RODDED; CLEANED AROUND CLEANOUT; AND D |  | SAN DIEGO, CITY OF | 931010 | 1700PM | 931011 | 0200AM | 540 | GAL | 4436 CAM DE LA PLAZA | SAN DIEGO | SD | 8" PVC SEWER MAIN | BLOCKAGE CAUSED BY VANDALISM | NONE | FLOWED ONTO PARKING LOT WHERE IT WAS VACUMMED
| 931012 | 1400PM | JAY ELSTON | 7143661553 | SAN CLEMENT, CITY OF | 931011 | 1200PM | 0 | 1210PM |  | 0 |  |  | SAN MATEO BASIN/SANDWASH | CAMP PENDLETON | SD | RECLAMATION WATER LINE | WATER DEPT. EMPLOYEE EXERCISING VALVES ACCI | NO | NONE |  |  | Y | N |  |  |  | SAN DIEGO, CITY OF | 931010 | 2000PM | 931011 | 0200AM | 720 | GAL | 9845 DESERTVIEW DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN TO SEWER | FLOW WENT TO INTERCEPTOR WHERE IT RETURNED TO
| 931011 | 1715PM | WILLIAM HAMPTON | 6195258687 | SAN DIEGO, CITY OF | 931011 | 0949AM | 931011 | 1230AM |  | 2040 | GAL |  | 941 BUSH STREET | SAN DIEGO | SD | 6" CONCRETE PIPE | DEBRIS BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | MACHINE RODDED RELIEVING STOPPAGE. DEODORIZED |  | SAN DIEGO, CITY OF | 931010 | 2355PM | 931011 | 0439AM | 1440 | GAL | 40TH & ORANGE AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | DIRT ALLEY/PACIFIC OCE | MACHINE RODDED; CLEANED AROUND CLEANOUT; AND D
| 931011 | 1735PM | WILLIAM HAMPTON | 6195258687 | SAN DIEGO, CITY OF | 931011 | 0835AM | 931011 | 1135AM |  | 3600 | GAL |  | 4293 JACKDAW STREET | SAN DIEGO | SD | 6" CONCRETE MAIN | ROOT BLOCKAGE | Y | CANYON/PACIFIC OCEAN |  |  | Y | N |  | MACHINE RODDED RELIEVING STOPPAGE. DEODORIZED |  | SAN CLEMENT, CITY OF | 931011 | 1200PM | 0 | 1210PM | 0 |  | SAN MATEO BASIN/SANDWASH | CAMP PENDLETON | SD | RECLAMATION WATER LINE | WATER DEPT. EMPLOYEE EXERCISING VALVES ACCI | NONE
| 931011 | 1545PM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 931011 | 0700AM | 931011 | 0930AM |  | 3000 | GAL |  | 2475 GRAND AVE./LEE ST. PLACE | SAN DIEGO | SD | 12" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN/INTERCEPTO |  |  | Y | N |  | SEWAGE WAS PUMPED BACK INTO SEWER SYSTEM AT IN |  | SAN DIEGO, CITY OF | 931011 | 0949AM | 931011 | 1230AM | 2040 | GAL | 941 BUSH STREET | SAN DIEGO | SD | 6" CONCRETE PIPE | DEBRIS BLOCKAGE | STORM DRAIN/PACIFIC OC | MACHINE RODDED RELIEVING STOPPAGE. DEODORIZED
| 931013 | 1250AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931012 | 1711PM | 931012 | 1811PM |  | 600 | GAL |  | 4010 THORN ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | DEBRIS BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | RODDED, AND ZEPPED AREA AROUND MANHOLE. |  | SAN DIEGO, CITY OF | 931011 | 0835AM | 931011 | 1135AM | 3600 | GAL | 4293 JACKDAW STREET | SAN DIEGO | SD | 6" CONCRETE MAIN | ROOT BLOCKAGE | CANYON/PACIFIC OCEAN | MACHINE RODDED RELIEVING STOPPAGE. DEODORIZED
| 931014 | 0535AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931013 | 1715PM | 931013 | 2050PM |  | 648 | GAL |  | 6944 EL CAJON BLVD. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | RODDED. RELIEVED STOPPAGE ABOUT 559' INTO SECT |  | SAN DIEGO, CITY OF | 931011 | 0700AM | 931011 | 0930AM | 3000 | GAL | 2475 GRAND AVE./LEE ST. PLACE | SAN DIEGO | SD | 12" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN/INTERCEPTO | SEWAGE WAS PUMPED BACK INTO SEWER SYSTEM AT IN
| 931015 | 0214AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931014 | 1844PM | 931015 | 0700AM |  | 369 | GAL |  | 1010 SAN YSIDRO BLVD. | SAN DIEGO | SD | CLEANOUT IN TRAILER PARK | SURCHARGE CONDITONS IN 36" SEWER MAIN ON DA | Y | DRAINAGE CHANNEL/PACIF |  |  | Y | N |  | 10-88(MEET) CONSUMER-INVESTIGATE. FOLLOW OVERF |  | SAN DIEGO, CITY OF | 931012 | 1711PM | 931012 | 1811PM | 600 | GAL | 4010 THORN ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | DEBRIS BLOCKAGE | STORM DRAIN/PACIFIC OC | RODDED, AND ZEPPED AREA AROUND MANHOLE.
| 931015 | 0247AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931014 | 1952PM | 931014 | 2015PM |  | 12 | GAL |  | 6315 CELIA VISTA DR. | SAN DIEGO | SD | 6" VC SEWER MAIN | UNKNOWN REASON FOR OVERFLOW SINCE IT STOPPE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | RODDED AND CLEARED MAIN BLOCKAGE. |  | SAN DIEGO, CITY OF | 931013 | 1715PM | 931013 | 2050PM | 648 | GAL | 6944 EL CAJON BLVD. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN/PACIFIC OC | RODDED. RELIEVED STOPPAGE ABOUT 559' INTO SECT
| 931018 | 1400PM | JOHN VAUGHT | 6197414854 | ESCONDIDO, CITY OF | 931015 | 1600PM | 931015 | 1130PM |  | 800 | GAL |  | 625 - 635 10TH AVE. | ESCONDIDO | SD | SEWER ATLAS PG. AS PRIVATE CO. | EXCESSIVE GREASE IN MAIN LINE CAUSED A PART | NO | NONE |  | SOAKED INTO GROUND. | Y | N |  | AREA WAS CLANED AND DISINFECTED. NO SURFACE W |  | SAN DIEGO, CITY OF | 931014 | 1844PM | 931015 | 0700AM | 369 | GAL | 1010 SAN YSIDRO BLVD. | SAN DIEGO | SD | CLEANOUT IN TRAILER PARK | SURCHARGE CONDITONS IN 36" SEWER MAIN ON DA | DRAINAGE CHANNEL/PACIF | 10-88(MEET) CONSUMER-INVESTIGATE. FOLLOW OVERF
| 931019 | 1510PM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 931015 | 1200PM | 931015 | 1330PM |  | 1500 | GAL |  | 1905 COMANCHE STREET | OCEANSIDE | SD | SEWER MAIN MANHOLE | RAGS, STICKS & GREASE BLOCKED SEWER MAIN AT | Y | NEIGHBOR SWAMP/LOMA AL |  |  | Y | N |  | NO SOLIDS DISCHARGED. DOMESTIC WASTEWATER FLOW |  | SAN DIEGO, CITY OF | 931014 | 1952PM | 931014 | 2015PM | 12 | GAL | 6315 CELIA VISTA DR. | SAN DIEGO | SD | 6" VC SEWER MAIN | UNKNOWN REASON FOR OVERFLOW SINCE IT STOPPE | STORM DRAIN/PACIFIC OC | RODDED AND CLEARED MAIN BLOCKAGE.
| 931016 | 1515PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 931016 | 1500PM | 931016 | 1550PM |  | 30 | GAL |  | 1090 VIA UNIDOS | FALLBROOK | SD | 4' CLEANOUT | LITTLE ROOTS AND A LOT OF PAPER | NO | NONE |  | ABOUT 6' AROUND CLEANOUT BOX | N | N |  | AT 1530PM, OPENED CLEANOUT. COMPLETED AT 1605 |  | ESCONDIDO, CITY OF | 931015 | 1600PM | 931015 | 1130PM | 800 | GAL | 625 - 635 10TH AVE. | ESCONDIDO | SD | SEWER ATLAS PG. AS PRIVATE CO. | EXCESSIVE GREASE IN MAIN LINE CAUSED A PART | NONE | AREA WAS CLANED AND DISINFECTED. NO SURFACE W
| 931017 | 1945PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931017 | 1030AM | 931017 | 1200PM |  | 900 | GAL |  | MISSION BLVD. & PACIFIC BEACH | SAN DIEGO | SD | PUMP STATION 17 | POWER OUTAGE PUMPS TRIPPED BRAKER. | Y | STRM DRAIN/MISSION BAY |  |  | Y | Y |  | POSTED 5 SIGNS BEHIND CATIMARAN MOTEL. VACTORE |  | OCEANSIDE, CITY OF | 931015 | 1200PM | 931015 | 1330PM | 1500 | GAL | 1905 COMANCHE STREET | OCEANSIDE | SD | SEWER MAIN MANHOLE | RAGS, STICKS & GREASE BLOCKED SEWER MAIN AT | NEIGHBOR SWAMP/LOMA AL | NO SOLIDS DISCHARGED. DOMESTIC WASTEWATER FLOW
| 931017 | 2200PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931017 | 0830AM | 931017 | 0930AM |  | 180 | GAL |  | 3910 THORN ST. | SAN DIEGO | SD | 8" CI SEWER MAIN | GRAVITY MAIN BREAK WHERE CI AND PVC COME TO | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | FLOW SOAKED INTO GROUND IN CANYON WEST OF I-5 |  | FALLBROOK SANITARY DISTRICT | 931016 | 1500PM | 931016 | 1550PM | 30 | GAL | 1090 VIA UNIDOS | FALLBROOK | SD | 4' CLEANOUT | LITTLE ROOTS AND A LOT OF PAPER | NONE | AT 1530PM, OPENED CLEANOUT. COMPLETED AT 1605
| 931019 | 1200PM | STEVE FRANCIS | 7145822330 | SANTA MARGARITA WATER DIST. | 931018 | 1230PM | 931018 | 1300PM |  | 2000 | GAL |  | ANTONIO PARKWAY | SANTA MARGARITA | OC | PLANO LIFT STATION | PROBES IN SURGE TANK MALFUNCTIONED INDUCING | Y | TIJERAS CREEK |  |  | Y | N |  | RECEIVING AREA WAS RY & IN A REMOTE AREA. SPIL |  | SAN DIEGO, CITY OF | 931017 | 1030AM | 931017 | 1200PM | 900 | GAL | MISSION BLVD. & PACIFIC BEACH | SAN DIEGO | SD | PUMP STATION 17 | POWER OUTAGE PUMPS TRIPPED BRAKER. | STRM DRAIN/MISSION BAY | POSTED 5 SIGNS BEHIND CATIMARAN MOTEL. VACTORE
| 931019 | 0900AM | I. JENKINS | 6195258682 | SAN DIEGO, CITY OF | 931018 | 0800AM | 931018 | 1000AM |  | 120 | GAL |  | 3743 FRONT ST.- AT PLAYGROUND | SAN DIEGO | SD | 6" CP MAIN | HEAVY ROOTS CAUSED BLOCKAGE IN MAIN. | NO | NONE |  | PLAYGROUND, THEN CLEANED UP. | Y | N |  | SETTLED IN PLAYGROUND WHICH WAS CLEANED UP & A |  | SAN DIEGO, CITY OF | 931017 | 0830AM | 931017 | 0930AM | 180 | GAL | 3910 THORN ST. | SAN DIEGO | SD | 8" CI SEWER MAIN | GRAVITY MAIN BREAK WHERE CI AND PVC COME TO | STORM DRAIN/PACIFIC OC | FLOW SOAKED INTO GROUND IN CANYON WEST OF I-5
| 931021 | 1400PM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931020 | 1730PM | 931020 | 1800PM |  | 600 | GAL |  | 43RD & WIGHTMAN | SAN DIEGO | SD | 8" CP SEWER MAIN | GREASE | Y | 43RD & MYRTLE/PACIFIC |  |  | Y | N |  | RODDED MAIN. DEODORIZED. |  | SANTA MARGARITA WATER DIST. | 931018 | 1230PM | 931018 | 1300PM | 2000 | GAL | ANTONIO PARKWAY | SANTA MARGARITA | OC | PLANO LIFT STATION | PROBES IN SURGE TANK MALFUNCTIONED INDUCING | TIJERAS CREEK | RECEIVING AREA WAS RY & IN A REMOTE AREA. SPIL
| 931021 | 1448PM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931020 | 1448PM | 931021 | 1130AM |  | 1224 | GAL |  | GILMAN DR. & LA JOLLA VILLAGE | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOTS, ROCKS, & DEBRIS IN PRIVATE SEWER MAI | Y | STORM DRAIN/PACIFIC OC |  |  | ? | N |  | RELIEVED STOPPAGE AT 1130AM. UNIVERSITY MAINT |  | SAN DIEGO, CITY OF | 931018 | 0800AM | 931018 | 1000AM | 120 | GAL | 3743 FRONT ST.- AT PLAYGROUND | SAN DIEGO | SD | 6" CP MAIN | HEAVY ROOTS CAUSED BLOCKAGE IN MAIN. | NONE | SETTLED IN PLAYGROUND WHICH WAS CLEANED UP & A
| 931020 | 1430PM | JOHN VAUGHT | 6197414954 | ESCONDIDO, CITY OF | 931020 | 1000AM | 931020 | 1030AM |  | 1500 | GAL |  | 1890 IRIS WAY | ESCONDIDO | SD | SEWER ATLAS PAGE 74, MH#7 | ROCKS, BROKEN PIPE, ASPHALT CHUNKS, ALL COM | Y | ESCONDIDO CREEK/SAN EL |  |  | Y | Y | 05 | TREATED AREA WITH DISINFECTANT & WASHED DOWN W |  | SAN DIEGO, CITY OF | 931020 | 1730PM | 931020 | 1800PM | 600 | GAL | 43RD & WIGHTMAN | SAN DIEGO | SD | 8" CP SEWER MAIN | GREASE | 43RD & MYRTLE/PACIFIC | RODDED MAIN. DEODORIZED.
| 931022 | 0800AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 931021 | 1022AM | 931021 | 1352PM |  | 840 | GAL |  | 3529 BOUNDARY ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | NO | NONE |  | PUMPED BACK INTO SEWER SYSTEM. | Y | N |  | VACTORED UP PUDDLES IN ALLEY. OTHER OVERFLOW |  | SAN DIEGO, CITY OF | 931020 | 1448PM | 931021 | 1130AM | 1224 | GAL | GILMAN DR. & LA JOLLA VILLAGE | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOTS, ROCKS, & DEBRIS IN PRIVATE SEWER MAI | STORM DRAIN/PACIFIC OC | RELIEVED STOPPAGE AT 1130AM. UNIVERSITY MAINT
| 931022 | 0106AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931021 | 2200PM | 931021 | 2300PM |  | 120 | GAL |  | 2805 MORENA BLVD. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | DID NOT ENTER STORM DR |  |  | Y | N |  | RODDED MAIN AND DEODORIZED. |  | ESCONDIDO, CITY OF | 931020 | 1000AM | 931020 | 1030AM | 1500 | GAL | 1890 IRIS WAY | ESCONDIDO | SD | SEWER ATLAS PAGE 74, MH#7 | ROCKS, BROKEN PIPE, ASPHALT CHUNKS, ALL COM | ESCONDIDO CREEK/SAN EL | TREATED AREA WITH DISINFECTANT & WASHED DOWN W
| 931022 | 1530PM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 931022 | 1055AM | 931022 | 1255PM |  | 1200 | GAL |  | 5480 UNIVERSITY AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | DRY CRK. BED/PACIFIC O |  |  | Y | N |  | DEODORIZED CREEK BED EAST OF 54TH ST., SOUTH O |  | SAN DIEGO, CITY OF | 931021 | 1022AM | 931021 | 1352PM | 840 | GAL | 3529 BOUNDARY ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | NONE | VACTORED UP PUDDLES IN ALLEY. OTHER OVERFLOW
| 931025 | 0830AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 931022 | 0713AM | 931022 | 0800AM |  | 2 | GAL |  | 858 SUNNYSIDE AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOTS BLOCKAGE | Y | CANYON/PACIFIC OCEAN |  |  | Y | N |  | OVERFLOW SOAKED INTO GROUND. DEODORIZED AREA. |  | SAN DIEGO, CITY OF | 931021 | 2200PM | 931021 | 2300PM | 120 | GAL | 2805 MORENA BLVD. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | DID NOT ENTER STORM DR | RODDED MAIN AND DEODORIZED.
| 931024 | 0830PM | RONAL D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931023 | 1000AM | 931023 | 2100PM |  | 3300 | GAL |  | 12760 RANCHO PENASQUITOS | SAN DIEGO | SD | 12" VC SEWER MAIN | GREASE BLOCKAGE | Y | PENASQUITOS CREEK/PACI |  |  | Y | Y |  | FLOW WENT INTO STORM DRAIN TO CREEK WATER. |  | SAN DIEGO, CITY OF | 931022 | 1055AM | 931022 | 1255PM | 1200 | GAL | 5480 UNIVERSITY AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | DRY CRK. BED/PACIFIC O | DEODORIZED CREEK BED EAST OF 54TH ST., SOUTH O
| 931025 | 1000AM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 931023 | 1600PM | 931023 | 2015PM |  | 8000 | GAL |  | 1664 OCEANSIDE BLVD. | OCEANSIDE | SD | SEWAGE PUMP STATION | PUMP STATON QUIT RUNNING, CAUSING WET WELL | Y | LOMA ALTA CREEK/BUCCAN |  |  | Y | Y |  | NO SOLIDS LOST. WASTEWATER FLOWED TO CHANNEL T |  | SAN DIEGO, CITY OF | 931022 | 0713AM | 931022 | 0800AM | 2 | GAL | 858 SUNNYSIDE AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOTS BLOCKAGE | CANYON/PACIFIC OCEAN | OVERFLOW SOAKED INTO GROUND. DEODORIZED AREA.
| 931024 | 2030PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931023 | 0800AM | 931023 | 0900AM |  | 60 | GAL |  | 3208 CANON ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | Y | SAN DIEGO BAY/PACIFIC |  |  | Y | Y |  | POSTED SIGN AT FOOT OF CANON AT ANCHORAGE ST. |  | SAN DIEGO, CITY OF | 931023 | 1000AM | 931023 | 2100PM | 3300 | GAL | 12760 RANCHO PENASQUITOS | SAN DIEGO | SD | 12" VC SEWER MAIN | GREASE BLOCKAGE | PENASQUITOS CREEK/PACI | FLOW WENT INTO STORM DRAIN TO CREEK WATER.
| 931024 | 0830PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931024 | 0915AM | 931024 | 1014AM |  | 300 | GAL |  | 12760 RANCHO PENASQUITOS BLVD. | SAN DIEGO | SD | 12" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | Y |  | CONTINUED WORK FROM LAST NIGHT TO REMOVE BLOCK |  | OCEANSIDE, CITY OF | 931023 | 1600PM | 931023 | 2015PM | 8000 | GAL | 1664 OCEANSIDE BLVD. | OCEANSIDE | SD | SEWAGE PUMP STATION | PUMP STATON QUIT RUNNING, CAUSING WET WELL | LOMA ALTA CREEK/BUCCAN | NO SOLIDS LOST. WASTEWATER FLOWED TO CHANNEL T
| 931024 | 0830PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931024 | 1200PM | 931024 | 1430PM |  | 750 | GAL |  | BEAVER LAKE DR. & LAKE CT. | SAN DIEGO | SD | 8" VC SEWER MAIN | DEBRIS BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | B |  | FLOWED INTO STORM DRAIN AND SOAKED TO GROUND.. |  | SAN DIEGO, CITY OF | 931023 | 0800AM | 931023 | 0900AM | 60 | GAL | 3208 CANON ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | SAN DIEGO BAY/PACIFIC | POSTED SIGN AT FOOT OF CANON AT ANCHORAGE ST.
| 931024 | 0900PM | RONALD ROBY | 6195258685 | SAN DIEGO, CITY OF | 931024 | 1445PM | 931024 | 1645PM |  | 240 | GAL |  | 4058 CHEROKEE AVE. | SAN DIEGO | SD | 8" PVC SEWER MAIN | GREASE BLOCKAGE | Y | CANYON/PACIFIC OCEAN |  |  | Y | N |  | WASHED FLOW INTO STORMDRAIN WHERE IT FLOWED TO |  | SAN DIEGO, CITY OF | 931024 | 0915AM | 931024 | 1014AM | 300 | GAL | 12760 RANCHO PENASQUITOS BLVD. | SAN DIEGO | SD | 12" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN/PACIFIC OC | CONTINUED WORK FROM LAST NIGHT TO REMOVE BLOCK
| 930126 | 1722PM | JOEL HOLT | 6197288319 | FALLBROOK SANITARY DISTRCIT | 931025 | 1400PM | 931025 | 1900PM |  | 662000 | GAL |  | CARPENTER RD. & BENET | OCEANSIDE | SD | OUTFALL LINE ALONG CARPENTER | AN AIR & VAC BLOW-OFF MAY HAVE BEWEN HIT BY | Y | SAN LUIS REY RIVER |  |  | Y |  |  | TERTIARY TREATED WATER WAS DIVERTED TO PLANT F |  | SAN DIEGO, CITY OF | 931024 | 1200PM | 931024 | 1430PM | 750 | GAL | BEAVER LAKE DR. & LAKE CT. | SAN DIEGO | SD | 8" VC SEWER MAIN | DEBRIS BLOCKAGE | STORM DRAIN/PACIFIC OC | FLOWED INTO STORM DRAIN AND SOAKED TO GROUND..
| 931025 | 1520PM | WILLIAM F. GRAHAM | 6195277456 | SAN DIEGO, CITY OF | 931025 | 1225PM | 931024 | 1313PM |  | 9600 | GAL |  | 15500 PAYMOGO ST. | SAN DIEGO | SD | SEWER PUMP STATION #62 | SDG/E P0OWER OUTAGE FOR MAINTENANCE--NOT SC | Y | STORM DRAIN/PACIFIC OC |  |  | Y | Y |  | SDG/E FAILED TO NOTIFY WATER UTILITIES OF SCHE |  | SAN DIEGO, CITY OF | 931024 | 1445PM | 931024 | 1645PM | 240 | GAL | 4058 CHEROKEE AVE. | SAN DIEGO | SD | 8" PVC SEWER MAIN | GREASE BLOCKAGE | CANYON/PACIFIC OCEAN | WASHED FLOW INTO STORMDRAIN WHERE IT FLOWED TO
| 931025 | 2220PM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931025 | 1100AM | 931025 | 1200AM |  | 120 | GAL |  | 2622 SPRIG PL. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | RODDED BY MACHINE. |  | FALLBROOK SANITARY DISTRCIT | 931025 | 1400PM | 931025 | 1900PM | 662000 | GAL | CARPENTER RD. & BENET | OCEANSIDE | SD | OUTFALL LINE ALONG CARPENTER | AN AIR & VAC BLOW-OFF MAY HAVE BEWEN HIT BY | SAN LUIS REY RIVER | TERTIARY TREATED WATER WAS DIVERTED TO PLANT F
| 931025 | 1438PM | WILLIAM HAMPTON | 6195258687 | SAN DIEGO, CITY OF | 931025 | 1057AM | 931025 | 1430PM |  | 2100 | GAL |  | 3454 CASTLE GLEN DRIVE | SAN DIEGO | SD | 10" VC SEWER MAIN | HEAVY DEBRIS AND MUD BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | AREA WAS DEODORIZED AND STOPPAGE WAS RELIEVED. |  | SAN DIEGO, CITY OF | 931025 | 1225PM | 931024 | 1313PM | 9600 | GAL | 15500 PAYMOGO ST. | SAN DIEGO | SD | SEWER PUMP STATION #62 | SDG/E P0OWER OUTAGE FOR MAINTENANCE--NOT SC | STORM DRAIN/PACIFIC OC | SDG/E FAILED TO NOTIFY WATER UTILITIES OF SCHE
| 931026 | 0100AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931025 | 1730PM | 931025 | 1830PM |  | 60 | GAL |  | 6320 POTOMAC | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | RODDED MAIN AND CLEANED UP SPILL. |  | SAN DIEGO, CITY OF | 931025 | 1100AM | 931025 | 1200AM | 120 | GAL | 2622 SPRIG PL. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN/PACIFIC OC | RODDED BY MACHINE.
| 931026 | 0930AM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 931025 | 0855AM | 931025 | 0930AM |  | 3640 | GAL |  | 300 BLOCK OF GARRISON | OCEANSIDE | SD | SEWER MAIN MANHOLD | CITY MAIN WAS CLOGGED WITH GREASE AND PAPER | Y | GARRISON CREEK/LOMA AL |  |  | Y | Y | 02 | NO SOLIDS ESCAPED. PUBLIC HAS ACCESS TO BEACH |  | SAN DIEGO, CITY OF | 931025 | 1057AM | 931025 | 1430PM | 2100 | GAL | 3454 CASTLE GLEN DRIVE | SAN DIEGO | SD | 10" VC SEWER MAIN | HEAVY DEBRIS AND MUD BLOCKAGE | STORM DRAIN/PACIFIC OC | AREA WAS DEODORIZED AND STOPPAGE WAS RELIEVED.
| 931027 | 1243AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931026 | 1630PM | 931026 | 1900PM |  | 750 | GAL |  | 4100 35TH ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | RODDED MAIN. DEODORIZED. |  | SAN DIEGO, CITY OF | 931025 | 1730PM | 931025 | 1830PM | 60 | GAL | 6320 POTOMAC | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN/PACIFIC OC | RODDED MAIN AND CLEANED UP SPILL.
| 931026 | 1600PM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 931026 | 0900AM | 931026 | 1000AM |  | 600 | GAL |  | 7329 COUNTRY CLUB DR. DRIVEWAY | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | CURB TO CANYON TO PACI |  |  | Y | N |  | SEWAGE STAYED IN CANYON AND DRIED IN DIRT. |  | OCEANSIDE, CITY OF | 931025 | 0855AM | 931025 | 0930AM | 3640 | GAL | 300 BLOCK OF GARRISON | OCEANSIDE | SD | SEWER MAIN MANHOLD | CITY MAIN WAS CLOGGED WITH GREASE AND PAPER | GARRISON CREEK/LOMA AL | NO SOLIDS ESCAPED. PUBLIC HAS ACCESS TO BEACH
| 931027 | 0255AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931026 | 1439PM | 931026 | 1700PM |  | 141 | GAL |  | 7301 HIGH ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | GOLF COURSE GROUNDS/PA |  |  | Y | N |  | RODDED MAIN. |  | SAN DIEGO, CITY OF | 931026 | 1630PM | 931026 | 1900PM | 750 | GAL | 4100 35TH ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN/PACIFIC OC | RODDED MAIN. DEODORIZED.
| 931026 | 1435PM | M. STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 931026 | 1215PM | 931026 | 1345PM |  | 450 | GAL |  | 1600 PUTERBOUGH | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOTS AND GREASE BLOCKAGE | Y | STORM DRAIN/S.D. BAY/P |  |  | Y | N |  | RODDED MAIN TO RELIEVE STOP. |  | SAN DIEGO, CITY OF | 931026 | 0900AM | 931026 | 1000AM | 600 | GAL | 7329 COUNTRY CLUB DR. DRIVEWAY | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | CURB TO CANYON TO PACI | SEWAGE STAYED IN CANYON AND DRIED IN DIRT.
| 931027 | 1330PM | BEN DUNCAN | 6197385051 | WILD ANIMAL PARK | 931027 | 1330PM | 931027 | 1400PM |  | 500 | GAL |  | 15500 SAN PASQUAL VALLEY RD. | ESCONDIDO | SD | AERATION TANK | LIMB BLOCKAGE DUE TO HIGH WINDS. ABOUT 500 | NO | NONE |  | PLANT GROUNDS CONTAINMENT | Y | N |  | THE SPILLED SLUDGE WAS CONTAINED ON SITE. |  | SAN DIEGO, CITY OF | 931026 | 1439PM | 931026 | 1700PM | 141 | GAL | 7301 HIGH ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | GOLF COURSE GROUNDS/PA | RODDED MAIN.
| 931028 | 0310AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931027 | 1659PM | 931027 | 1735PM |  | 3600 | GAL |  | 2334 CARMEL VALLEY RD. | SAN DIEGO | SD | 18" VC SEWER MAIN | POSSIBLE PUMP STA. MALFUNCTIONED AT P.S. #6 | Y | PENASQUITOS LAG./PACIF |  |  | Y | Y | ?? | OVERFLOW HAD PAST BY TIME WORK CREW ARRIVED AN |  | SAN DIEGO, CITY OF | 931026 | 1215PM | 931026 | 1345PM | 450 | GAL | 1600 PUTERBOUGH | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOTS AND GREASE BLOCKAGE | STORM DRAIN/S.D. BAY/P | RODDED MAIN TO RELIEVE STOP.
| 931027 | 1030AM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 931027 | 0720AM | 931027 | 0810AM |  | 2240 | GAL |  | 324 GARRISON ST. | OCEANSIDE | SD | PRIVATE CLEANOUT | BUILDUP OF GREASE IN PRIVATE PROPERTY LATER | Y | GARRISON CREEK/LOMA AL |  |  | Y | Y | 02 | SEWAGE FLOWED INTO GARRISON CREEK TO LOMA ALTA |  | WILD ANIMAL PARK | 931027 | 1330PM | 931027 | 1400PM | 500 | GAL | 15500 SAN PASQUAL VALLEY RD. | ESCONDIDO | SD | AERATION TANK | LIMB BLOCKAGE DUE TO HIGH WINDS. ABOUT 500 | NONE | THE SPILLED SLUDGE WAS CONTAINED ON SITE.
| 931027 | 1430PM | JOEL HOLT | 6197288319 | FALLBROOK SANITARY DISTRICT | 931027 | 0100AM | 931027 | 0530AM |  | 500 | GAL |  | 431 SO. MAIN ST. | FALLBROOK | SD | BELT PRESS | BELT PRESS OVERFLOWED DUE TO OPERATOR ERROR | Y | FALLBROOK CREEK |  |  | Y | ? | ?? | ABOUT 95% OF OVERFLOW WAS CONTAINED BY A FLOOR |  | SAN DIEGO, CITY OF | 931027 | 1659PM | 931027 | 1735PM | 3600 | GAL | 2334 CARMEL VALLEY RD. | SAN DIEGO | SD | 18" VC SEWER MAIN | POSSIBLE PUMP STA. MALFUNCTIONED AT P.S. #6 | PENASQUITOS LAG./PACIF | OVERFLOW HAD PAST BY TIME WORK CREW ARRIVED AN
| 931027 | 2100PM | GRAHAM WRIGHT | ?????????? | LAGUNA BEACH, CITY OF | 931027 | 1500PM | 931027 | 1600PM |  | 200 | GAL |  | LAGUNA BEACH | LAGUNA BEACH | OR | IRVINE CONE PUMP STATION #17 | POWER OUTAGE DUE TO FIRE | NO | NONE |  | SOAKED INTO SAND | Y |  |  | WE COULD NOT GET GENERATOR TO SITE DUE TO FIRE |  | OCEANSIDE, CITY OF | 931027 | 0720AM | 931027 | 0810AM | 2240 | GAL | 324 GARRISON ST. | OCEANSIDE | SD | PRIVATE CLEANOUT | BUILDUP OF GREASE IN PRIVATE PROPERTY LATER | GARRISON CREEK/LOMA AL | SEWAGE FLOWED INTO GARRISON CREEK TO LOMA ALTA
| 931029 | 1600PM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 931029 | 0715AM | 931029 | 0930AM |  | 495 | GAL |  | MT. ACKNORTH & BOYD | SAN DIEGO | SD | 8" VC | GREASE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | SEWAGE STAYED IN STORM DRAIN. |  | FALLBROOK SANITARY DISTRICT | 931027 | 0100AM | 931027 | 0530AM | 500 | GAL | 431 SO. MAIN ST. | FALLBROOK | SD | BELT PRESS | BELT PRESS OVERFLOWED DUE TO OPERATOR ERROR | FALLBROOK CREEK | ABOUT 95% OF OVERFLOW WAS CONTAINED BY A FLOOR
| 931030 | 1335PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931030 | 1025AM | 931030 | 1200PM |  | 290 | GAL |  | 2145 FROUDE ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | ROOTS BLOCKAGE | NO | NONE |  | VACUUMED PUDDLE SENT TO SEWER. | Y |  |  | SPILL PUDDLED AT INTERSECT. OF EBERS & MUIR ST |  | LAGUNA BEACH, CITY OF | 931027 | 1500PM | 931027 | 1600PM | 200 | GAL | LAGUNA BEACH | LAGUNA BEACH | OR | IRVINE CONE PUMP STATION #17 | POWER OUTAGE DUE TO FIRE | NONE | WE COULD NOT GET GENERATOR TO SITE DUE TO FIRE
| 931030 | 1230PM | RONALD D. ROBY | 6195158685 | SAN DIEGO, CITY OF | 931030 | 0945AM | 931030 | 1045AM |  | 120 | GAL |  | 3032 K ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | NO | NONE |  | OVERFLOW RETURNED TO SEWER. | Y | N |  | FLOW WAS SWEPT & WASHED BACK INTO MANHOLE. |  | SAN DIEGO, CITY OF | 931029 | 0715AM | 931029 | 0930AM | 495 | GAL | MT. ACKNORTH & BOYD | SAN DIEGO | SD | 8" VC | GREASE | STORM DRAIN/PACIFIC OC | SEWAGE STAYED IN STORM DRAIN.
| 931030 | 1030AM | BOB MANRY | 9096764101 | RANCHO CALIFORNIA WATER DIST. | 931030 | 1030AM | 931030 | 1230PM |  | 1200 | GAL |  | JEFFERSON & MANDRA | MURRIETA | SD | RAW SEWAGE MANHOLE | ASPHALT & GREASE CHUNKS BLOCKING LINE | Y | STORM DRAIN CHANNEL |  |  | Y | ? | ?? | ASPHALT & GREASE WERE REMOVED FROM SEWER MANHO |  | SAN DIEGO, CITY OF | 931030 | 1025AM | 931030 | 1200PM | 290 | GAL | 2145 FROUDE ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | ROOTS BLOCKAGE | NONE | SPILL PUDDLED AT INTERSECT. OF EBERS & MUIR ST
| 931030 | 1030AM | BOB MANRY | 9096764101 | RANCHO CALIFORNIA WATER DIST. | 931030 | 1030AM | 931030 | 1230PM |  | 1200 | GAL |  | JEFFERSON & MANDRA | MURRIETA | RI | RAW SEWAGE MANHOLE | ASPHALT & GREASE CHUNKS BLOCKING LINE | Y | STORM DRAIN |  |  | Y |  |  | BLOCKAGE WAS REMOVED FROM THE MANHOLE. |  | SAN DIEGO, CITY OF | 931030 | 0945AM | 931030 | 1045AM | 120 | GAL | 3032 K ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | NONE | FLOW WAS SWEPT & WASHED BACK INTO MANHOLE.
| 931031 | 1530PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931031 | 1304PM | 931031 | 1404PM |  | 60 | GAL |  | 4727 UNIVERSITY AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | DEBRIS BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y |  |  | FLOWED INTO STORM DRAIN WHERE IT SETTLED. |  | RANCHO CALIFORNIA WATER DIST. | 931030 | 1030AM | 931030 | 1230PM | 1200 | GAL | JEFFERSON & MANDRA | MURRIETA | SD | RAW SEWAGE MANHOLE | ASPHALT & GREASE CHUNKS BLOCKING LINE | STORM DRAIN CHANNEL | ASPHALT & GREASE WERE REMOVED FROM SEWER MANHO
| 930131 | 1330PM | BRENT BRADY | 6297281180 | FALLBROOK SANITARY DIST. | 931031 | 0130AM | 931031 | 0650AM |  | 10000 | GAL |  | FALLBROOK SANITARY PLANT | FALLBROOK | SD | LIFT STATION #5 | LIFT STATION'S CONTROL FLOATS HELD DOWN BY | Y | FALLBROOK/SANTA MARGAR |  |  | Y | N |  | AFFECTED AREA IS A RESTRICTED LOCATION ON NAVA |  | RANCHO CALIFORNIA WATER DIST. | 931030 | 1030AM | 931030 | 1230PM | 1200 | GAL | JEFFERSON & MANDRA | MURRIETA | RI | RAW SEWAGE MANHOLE | ASPHALT & GREASE CHUNKS BLOCKING LINE | STORM DRAIN | BLOCKAGE WAS REMOVED FROM THE MANHOLE.
| 931101 | 1100AM | JOHN VAUGHT | 6197414864 | ESCONDIDO, CITY OF | 931031 | 1201PM | 931031 | 0700PM |  | 840 | GAL |  | 660 N. QUINCE ST. | ESCONDIDO | SD | PRIVATE 4" CLEEANOUT | CITY MAINLINE WAS SURCHARGED CAUSING WATER | Y | ESCONDIDO CRK./SAN ELI |  |  | Y | Y | 03 | OVERFLOW AREA WAS ISOLATED. MOST OF THE WATER |  | SAN DIEGO, CITY OF | 931031 | 1304PM | 931031 | 1404PM | 60 | GAL | 4727 UNIVERSITY AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | DEBRIS BLOCKAGE | STORM DRAIN/PACIFIC OC | FLOWED INTO STORM DRAIN WHERE IT SETTLED.
| 931101 | 0930AM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 931031 | 1000AM | 931031 | 1130AM |  | 450 | GAL |  | 48TH & ORANGE | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | SEWAGE CONTAINED IN ALLEY BY STORM DRAIN AND S |  | FALLBROOK SANITARY DIST. | 931031 | 0130AM | 931031 | 0650AM | 10000 | GAL | FALLBROOK SANITARY PLANT | FALLBROOK | SD | LIFT STATION #5 | LIFT STATION'S CONTROL FLOATS HELD DOWN BY | FALLBROOK/SANTA MARGAR | AFFECTED AREA IS A RESTRICTED LOCATION ON NAVA
| 931031 | 1300PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANTIARY DISTRICT | 931031 | 1300PM | 931031 | 1330PM |  | 20 | GAL |  | 1610 E HILLCREST | FALLBROOK | SD | CLEANOUT | SANITARY NAPKINS | NO | NONE |  | AROUND CLEANOUT IN OWNER'S YD. | N |  |  | AT 1320PM, OPENED CLEANOUT. COMPLETED AT 1400 |  | ESCONDIDO, CITY OF | 931031 | 1201PM | 931031 | 0700PM | 840 | GAL | 660 N. QUINCE ST. | ESCONDIDO | SD | PRIVATE 4" CLEEANOUT | CITY MAINLINE WAS SURCHARGED CAUSING WATER | ESCONDIDO CRK./SAN ELI | OVERFLOW AREA WAS ISOLATED. MOST OF THE WATER
| 931101 | 1600PM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 931101 | 0849AM | 931101 | 1123AM |  | 770 | GAL |  | 5926 LA JOLLA CORONO | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOTS BLOCKAGE | Y | STORM DRAIN/CYN./PACIF |  |  | Y | N |  | SEWAGE CONTAINED IN CANYON. |  | SAN DIEGO, CITY OF | 931031 | 1000AM | 931031 | 1130AM | 450 | GAL | 48TH & ORANGE | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN/PACIFIC OC | SEWAGE CONTAINED IN ALLEY BY STORM DRAIN AND S
| 931103 | ?????? | GARY WORTHY | 6199664854 | OCEANSIDE, CITY OF | 931102 | 1400PM | 0 | ?????? |  | 0 |  |  | 485 VANDERGRIFT BLVD. | OCEANSIDE | SD | PRIVATE SEWER LINE - UNKNOWN | UNKNOWN. CITY CREW INVESTIGATING CAUSE. | ?? | NONE? | [5 empty] | COLLECTION CREW INVESTIGATING TO FIND RESPONSI |  | FALLBROOK SANTIARY DISTRICT | 931031 | 1300PM | 931031 | 1330PM | 20 | GAL | 1610 E HILLCREST | FALLBROOK | SD | CLEANOUT | SANITARY NAPKINS | NONE | AT 1320PM, OPENED CLEANOUT. COMPLETED AT 1400
| 931102 | 2016PM | LUPE RODRIGUEZ | ?????????? | OCEANSIDE, CITY OF | 931102 | 1610PM | 931102 | ?????? |  | 25 | GAL |  | 510 OCEANSIDE BLVD. | OCEANSIDE | SD | ?? | ?? | ?? | NONE? |  |  | ? | ? | ?? |  |  | SAN DIEGO, CITY OF | 931101 | 0849AM | 931101 | 1123AM | 770 | GAL | 5926 LA JOLLA CORONO | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOTS BLOCKAGE | STORM DRAIN/CYN./PACIF | SEWAGE CONTAINED IN CANYON.
| 931103 | 0855AM | DAVID BEST | 6195258686 | SAN DIEGO, CITY OF | 931102 | 0916AM | 931102 | 1230PM |  | 19400 | GAL |  | 3901 LANDIS ST. (CANYON) | SAN DIEGO | SD | 12" VC SEWER MAIN | VANDALISM: ROCKS & DEBRIS BLOCKAGE | Y | CANYON/PACIFIC OCEAN |  |  | Y | N |  | DEODORIZED AREA. CLEARED ROCKS AND DEBRIS FRO |  | OCEANSIDE, CITY OF | 931102 | 1400PM | 0 | ?????? | 0 |  | 485 VANDERGRIFT BLVD. | OCEANSIDE | SD | PRIVATE SEWER LINE - UNKNOWN | UNKNOWN. CITY CREW INVESTIGATING CAUSE. | NONE? | COLLECTION CREW INVESTIGATING TO FIND RESPONSI
| 931103 | 0400AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931102 | 1041AM | 931102 | 2040PM |  | 6000 | GAL |  | 919 S. 45TH STREET | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N | N | RODDED MAIN AND DEODORIZED. |  | OCEANSIDE, CITY OF | 931102 | 1610PM | 931102 | ?????? | 25 | GAL | 510 OCEANSIDE BLVD. | OCEANSIDE | SD | ?? | ?? | NONE?
| 931103 | 1255AM | M. A.WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931102 | 1407PM | 931102 | 1637PM |  | 150 | GAL |  | 2770 C STREET | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | Y | CANYON GROUND/PACIFIC |  |  | Y | N | N | RODDED MAIN. REMOVED DEBRIS FROM MANHOLE. DEOD |  | SAN DIEGO, CITY OF | 931102 | 0916AM | 931102 | 1230PM | 19400 | GAL | 3901 LANDIS ST. (CANYON) | SAN DIEGO | SD | 12" VC SEWER MAIN | VANDALISM: ROCKS & DEBRIS BLOCKAGE | CANYON/PACIFIC OCEAN | DEODORIZED AREA. CLEARED ROCKS AND DEBRIS FRO
| 931102 | 1430PM | JOHN EIFLING | 6192218768 | SAN DIEGO, CITY OF | 931102 | 0515AM | 931102 | 0516AM |  | 100 | GAL |  | 1902 GATCHELL ROAD | SAN DIEGO | SD | THROTTLING VALVE VENT LINE | WHILE CONTRACTOR INSTALLING CHECK VALVE ON | Y | PACIFIC OCEAN |  |  | Y | N |  |  |  | SAN DIEGO, CITY OF | 931102 | 1041AM | 931102 | 2040PM | 6000 | GAL | 919 S. 45TH STREET | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE | STORM DRAIN/PACIFIC OC | RODDED MAIN AND DEODORIZED.
| 931103 | 0749AM | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 931102 | 0952AM | 931102 | 1100AM |  | 2040 | GAL |  | ALLEY BEHIND 401 IDAHO ST. | SAN DIEGO | SD | 6" VC | GREASE | Y | STORM DRAIN/PACIFIC OC |  |  | Y |  |  |  |  | SAN DIEGO, CITY OF | 931102 | 1407PM | 931102 | 1637PM | 150 | GAL | 2770 C STREET | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | CANYON GROUND/PACIFIC | RODDED MAIN. REMOVED DEBRIS FROM MANHOLE. DEOD
| 931104 | 0815AM | DAVID BEST | 6195258686 | SAN DIEGO, CITY OF | 931103 | 1134AM | 931103 | 1230PM |  | 260 | GAL |  | 6104 NEWCASTLE PLACE | SAN DIEGO | SD | 8" VC SEWER MAIN | DEBRIS IN MAIN CAUSED BLOCKAGE. | Y | STORM DRAIN/CYN./PACIF |  |  | Y | N |  | DEODORIZED SPILL AREA. |  | SAN DIEGO, CITY OF | 931102 | 0515AM | 931102 | 0516AM | 100 | GAL | 1902 GATCHELL ROAD | SAN DIEGO | SD | THROTTLING VALVE VENT LINE | WHILE CONTRACTOR INSTALLING CHECK VALVE ON | PACIFIC OCEAN
| 931103 | 1100PM | RON WILSON | 6194261656 | KENTUCKY FRIED CHICKEN | 931103 | 0738AM | 931103 | 1345PM |  | 1000 | GAL |  | 461 THIRD AVE. | CHULA VISTA | SD | BUSINESS CLEANOUT,FRONT & SIDE | BUSINESS DUMPED GREASE IN LATERAL. FACILITY | Y | STORM DRAIN CHANNEL |  |  | Y |  |  | GREASE SPILLED ONTO PARK. LOT & SIDEWLK. COLLE |  | SAN DIEGO, CITY OF | 931102 | 0952AM | 931102 | 1100AM | 2040 | GAL | ALLEY BEHIND 401 IDAHO ST. | SAN DIEGO | SD | 6" VC | GREASE | STORM DRAIN/PACIFIC OC
| 931105 | 0245AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931104 | 2130PM | 931104 | 2300PM |  | 840 | GAL |  | 4150 MENLO AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | B |  | RODDED MAIN. |  | SAN DIEGO, CITY OF | 931103 | 1134AM | 931103 | 1230PM | 260 | GAL | 6104 NEWCASTLE PLACE | SAN DIEGO | SD | 8" VC SEWER MAIN | DEBRIS IN MAIN CAUSED BLOCKAGE. | STORM DRAIN/CYN./PACIF | DEODORIZED SPILL AREA.
| 931105 | 1545PM | DAVID BEST | 6195258686 | SAN DIEGO, CITY OF | 931104 | 0800AM | 931105 | 1300PM |  | 8700 | GAL |  | 3040 QUICE ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOTS IN MAIN | Y | CANYON/PACIFIC OCEAN |  |  | Y | N |  | OVERFLOW STOPPED & STARTED INTERMITTENTLY UNKN |  | KENTUCKY FRIED CHICKEN | 931103 | 0738AM | 931103 | 1345PM | 1000 | GAL | 461 THIRD AVE. | CHULA VISTA | SD | BUSINESS CLEANOUT,FRONT & SIDE | BUSINESS DUMPED GREASE IN LATERAL. FACILITY | STORM DRAIN CHANNEL | GREASE SPILLED ONTO PARK. LOT & SIDEWLK. COLLE
| 931105 | 1000AM | DAVID BEST | 6195258686 | SAN DIEGO, CITY OF | 931104 | 0835AM | 931104 | 1030AM |  | 2300 | GAL |  | 4553 MISSION GORGE PLACE | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | SAN DIEGO RIV./PACIFIC |  |  | Y | N |  | MACHINE RODDED 8" VC MAIN. COUNTY HEALTH ADVI |  | SAN DIEGO, CITY OF | 931104 | 2130PM | 931104 | 2300PM | 840 | GAL | 4150 MENLO AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN/PACIFIC OC | RODDED MAIN.
| 931110 | 1409PM | RANDY PECOR | 6195277659 | SAN DIEGO, CITY OF | 931105 | 1630PM | 0 |  |  | 0 | GAL |  | 7304 COUNTRY CLUB DR. | LA JOLLA | SD | 8" VC SEWER MAIN | BROKEN MAIN DISCOVERED DURING TV INSPECTION | NO | NONE |  | RETURNING TO SEWER SYSTEM | Y | N |  | REPAIRS ARE PLANNED, BUT SEWER IS IN EASEMENT |  | SAN DIEGO, CITY OF | 931104 | 0800AM | 931105 | 1300PM | 8700 | GAL | 3040 QUICE ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOTS IN MAIN | CANYON/PACIFIC OCEAN | OVERFLOW STOPPED & STARTED INTERMITTENTLY UNKN
| 931105 | 0950AM | RENZO MARIN | 7148371660 | EL TORO WATER DISTRICT | 931105 | 1430PM | 931105 | 1830PM |  | 720 | GAL |  | LAKE FOREST/AVENIDA CARLOTTA | LAGUNA HILLS | OR | LU-492 MH-1 | GREASE & OTHER KITCHEN REFUSE FLOWED TO & B | Y | SAN DIEGO CRK. |  |  | Y |  |  | SWEPT SOLIDS. FLUSHED AREA WITH 1200 GALS. OF |  | SAN DIEGO, CITY OF | 931104 | 0835AM | 931104 | 1030AM | 2300 | GAL | 4553 MISSION GORGE PLACE | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | SAN DIEGO RIV./PACIFIC | MACHINE RODDED 8" VC MAIN. COUNTY HEALTH ADVI
| 931107 | 1030AM | MGR.,1105 OLD STAGE | 6197288319 | FALLBROOK SANITARY DISTRCIT | 931107 | 1030AM | 931107 | 1220PM |  | 100 | GAL |  | 1105 OLD STAGE | FALLBROOK | SD | 24" MANHOLE | STICKS, GREASE AND 3-FOOT PIECE OF PIPE | NO | NONE |  | PARKING LOT & VINE STREET | N | N |  | AT 1050AM, OPENED MANHOLE AND WASHED DOWN THE |  | SAN DIEGO, CITY OF | 931105 | 1630PM | 0 |  | 0 | GAL | 7304 COUNTRY CLUB DR. | LA JOLLA | SD | 8" VC SEWER MAIN | BROKEN MAIN DISCOVERED DURING TV INSPECTION | NONE | REPAIRS ARE PLANNED, BUT SEWER IS IN EASEMENT
| 931109 | 1230AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931108 | 1530PM | 931108 | 1730PM |  | 60 | GAL |  | 3904 DIVISION ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | Y | OSBORN/DIVISION STS./P |  |  | Y | N |  | RODDED MAIN. |  | EL TORO WATER DISTRICT | 931105 | 1430PM | 931105 | 1830PM | 720 | GAL | LAKE FOREST/AVENIDA CARLOTTA | LAGUNA HILLS | OR | LU-492 MH-1 | GREASE & OTHER KITCHEN REFUSE FLOWED TO & B | SAN DIEGO CRK. | SWEPT SOLIDS. FLUSHED AREA WITH 1200 GALS. OF
| 931109 | 1642PM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 931109 | 0900AM | 931109 | 1000AM |  | 60 | GAL |  | BEHIND 1155 COAST BLVD. | SAN DIEGO | SD | PRIVATE 4" CLEANOUT LATERAL | SPILL OCCURRED FROM BLOCKED LATERAL ON LA J | Y | STORM DRAIN/PACIFIC OC |  |  | Y | Y | 02 | LIFEGUARD POSTED LA JOLLA COVE LATERAL. CITY |  | FALLBROOK SANITARY DISTRCIT | 931107 | 1030AM | 931107 | 1220PM | 100 | GAL | 1105 OLD STAGE | FALLBROOK | SD | 24" MANHOLE | STICKS, GREASE AND 3-FOOT PIECE OF PIPE | NONE | AT 1050AM, OPENED MANHOLE AND WASHED DOWN THE
| 931110 | 0235AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931109 | 1317PM | 931109 | 1417PM |  | 90 | GAL |  | 5244 WIGHTMAN ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE | Y | WIGHTMAN/52ND STS./PAC |  |  | Y | N |  | RODDED MAIN AND DEODORIZED. |  | SAN DIEGO, CITY OF | 931108 | 1530PM | 931108 | 1730PM | 60 | GAL | 3904 DIVISION ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | OSBORN/DIVISION STS./P | RODDED MAIN.
| 931109 | 1611PM | M. A. WHELAN | 6195258682 | SAN DIEGO, CITY OF | 931109 | 1050AM | 931109 | 1300PM |  | 1300 | GAL |  | 3876 ALABAMA PL. & GUY ST. | SAN DIEGO | SD | 8" CP SEWER MAIN | GREASE | Y | CANYON/SAN DIEGO BAY/P |  |  | Y | N |  | RODDED 126' SECTION IN CANYON IN ABOVE LOCATIO |  | SAN DIEGO, CITY OF | 931109 | 0900AM | 931109 | 1000AM | 60 | GAL | BEHIND 1155 COAST BLVD. | SAN DIEGO | SD | PRIVATE 4" CLEANOUT LATERAL | SPILL OCCURRED FROM BLOCKED LATERAL ON LA J | STORM DRAIN/PACIFIC OC | LIFEGUARD POSTED LA JOLLA COVE LATERAL. CITY
| 931111 | 0632AM | M. A. WHELAN | 6915258687 | SAN DIEGO, CITY OF | 931110 | 1634PM | 931110 | 1804PM |  | 900 | GAL |  | SAN FELIPE ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | RODDED MAIN. DEODORIZED. |  | SAN DIEGO, CITY OF | 931109 | 1317PM | 931109 | 1417PM | 90 | GAL | 5244 WIGHTMAN ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE | WIGHTMAN/52ND STS./PAC | RODDED MAIN AND DEODORIZED.
| 931112 | 0830AM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 931111 | 1236PM | 931112 | 1000AM |  | 600 | GAL |  | 4476 HORTENSIA ST. IN CANYON | SAN DIEGO | SD | 8" VC | ROOTS | Y | CANYON/PACIFIC OCEAN |  |  | Y | N |  | SEWAGE CONTAINED IN CANYON. |  | SAN DIEGO, CITY OF | 931109 | 1050AM | 931109 | 1300PM | 1300 | GAL | 3876 ALABAMA PL. & GUY ST. | SAN DIEGO | SD | 8" CP SEWER MAIN | GREASE | CANYON/SAN DIEGO BAY/P | RODDED 126' SECTION IN CANYON IN ABOVE LOCATIO
| 931112 | 0810AM | MARK STOFFER | 6197253564 | USMC - CAMP PENDLETON | 931111 | 1110AM | 931111 | 1350PM |  | 12000 | GAL |  | BASILONE- 51 AREA | CAMP PENDLETON | SD | LIFT STATION #51053 | CONTROL PANEL PROBLEM | NO | NONE |  | DITCH TO FIELD ON PROPERTY | Y | N |  | CALLED IN REPAIR SHOPS. FIXED CONTROLS. |  | SAN DIEGO, CITY OF | 931110 | 1634PM | 931110 | 1804PM | 900 | GAL | SAN FELIPE ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN/PACIFIC OC | RODDED MAIN. DEODORIZED.
| 931112 | 1430PM | DISTRICT OFFICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 931112 | 1415PM | 931112 | 1830PM |  | 5 | GAL |  | 208 W. AVAIATION | FALLBROOK | SD | TOILET | GREASE IN MAIN LINE | NO | NONE |  | BATHROOM & 3" INSIDE OFFICE | N | N |  | UNPLUGGED THE MAIN LINE. |  | SAN DIEGO, CITY OF | 931111 | 1236PM | 931112 | 1000AM | 600 | GAL | 4476 HORTENSIA ST. IN CANYON | SAN DIEGO | SD | 8" VC | ROOTS | CANYON/PACIFIC OCEAN | SEWAGE CONTAINED IN CANYON.
| 931114 | 0730AM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931113 | 1028AM | 931113 | 1130PM |  | 310 | GAL |  | 1120 28TH ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | DEBRIS BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | FLOWED INTO STORM DRAIN WHERE IT SETTLED. |  | USMC - CAMP PENDLETON | 931111 | 1110AM | 931111 | 1350PM | 12000 | GAL | BASILONE- 51 AREA | CAMP PENDLETON | SD | LIFT STATION #51053 | CONTROL PANEL PROBLEM | NONE | CALLED IN REPAIR SHOPS. FIXED CONTROLS.
| 931114 | 0730AM | RONALD D. ROBY619 52 | 6195258685 | SAN DIEGO, CITY OF | 931113 | 0909AM | 931113 | 1045AM |  | 480 | GAL |  | 2920 ALTA VIEW DR. | SAN DIEGO | SD | 18" VC SEWER MAIN | GREASE BLOCKAGE | Y | RANCHO DE LA ENCINO CR |  |  | Y | N |  | FLOWED INTO STORM DRAIN TO CREEK NORTH OF SOUT |  | FALLBROOK SANITARY DISTRICT | 931112 | 1415PM | 931112 | 1830PM | 5 | GAL | 208 W. AVAIATION | FALLBROOK | SD | TOILET | GREASE IN MAIN LINE | NONE | UNPLUGGED THE MAIN LINE.
| 931115 | 0930AM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 931113 | 1700PM | 931113 | 2200PM |  | 75000 | GAL |  | 3950 NORTH RIVER RD. | OCEANSIDE | SD | NORTH VALLEY SEWAGE PUMP STA. | PUMP STATION FAILURE CAUSED WET WELL OVERFL | Y | PILGRIM CRK./SAN LUIS |  |  | Y | Y | 02 | DOMESTIC WASTEWATER ULTIMATELY REACHED HARBOR |  | SAN DIEGO, CITY OF | 931113 | 1028AM | 931113 | 1130PM | 310 | GAL | 1120 28TH ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | DEBRIS BLOCKAGE | STORM DRAIN/PACIFIC OC | FLOWED INTO STORM DRAIN WHERE IT SETTLED.
| 931115 | 0830AM | MARK A. STOFFER | 6197254806 | USMC - CAMP PENDLETON | 931114 | 1430PM | 931114 | 2000PM |  | 150 | GAL |  | 249 JAMUL | CAMP PENDLETON | SD | MANHOLE | LINE BLOCKAGE | NO | NONE |  | AREA BY MANHOLE | Y | N |  | CLEANED OUT MAIN LINE. LIME THE AREA. |  | SAN DIEGO, CITY OF | 931113 | 0909AM | 931113 | 1045AM | 480 | GAL | 2920 ALTA VIEW DR. | SAN DIEGO | SD | 18" VC SEWER MAIN | GREASE BLOCKAGE | RANCHO DE LA ENCINO CR | FLOWED INTO STORM DRAIN TO CREEK NORTH OF SOUT
| 931114 | 1000PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931114 | 1313PM | 931114 | 1500PM |  | 107 | GAL |  | 2565 FAIRMONT AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | FLOWED INTO STORMDRAIN AND SETTLED. |  | OCEANSIDE, CITY OF | 931113 | 1700PM | 931113 | 2200PM | 75000 | GAL | 3950 NORTH RIVER RD. | OCEANSIDE | SD | NORTH VALLEY SEWAGE PUMP STA. | PUMP STATION FAILURE CAUSED WET WELL OVERFL | PILGRIM CRK./SAN LUIS | DOMESTIC WASTEWATER ULTIMATELY REACHED HARBOR
| 931116 | 0253AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931115 | 2139PM | 931115 | 2239PM |  | 120 | GAL |  | HOWARD AVE. & PARK BLVD. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | MACHINE RODDED TO CLEAR GREASE AND 7-31 FROM C |  | USMC - CAMP PENDLETON | 931114 | 1430PM | 931114 | 2000PM | 150 | GAL | 249 JAMUL | CAMP PENDLETON | SD | MANHOLE | LINE BLOCKAGE | NONE | CLEANED OUT MAIN LINE. LIME THE AREA.
| 931116 | 0800AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 931115 | 0934AM | 931115 | 1230PM |  | 176 | GAL |  | 471 SO. EUCLID AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | MACHINE RODDED. DEODORIZED AROUND MANHOLE AND |  | SAN DIEGO, CITY OF | 931114 | 1313PM | 931114 | 1500PM | 107 | GAL | 2565 FAIRMONT AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN/PACIFIC OC | FLOWED INTO STORMDRAIN AND SETTLED.
| 931116 | 0730AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 931115 | 0730AM | 931115 | 1000AM |  | 835 | GAL |  | 661 UNIVERSITY AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | DEBRIS BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | MACHINE RODDED. DEODORIZEDAROUND MANHOLE AND |  | SAN DIEGO, CITY OF | 931115 | 2139PM | 931115 | 2239PM | 120 | GAL | HOWARD AVE. & PARK BLVD. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN/PACIFIC OC | MACHINE RODDED TO CLEAR GREASE AND 7-31 FROM C
| 931115 | 0830AM | MIKE WILSON | 6196431902 | ALISO WATER MGMT. AGENCY | 931115 | 0830AM | 931115 | 0845AM |  | 50 | GAL |  | 29201 LA PAZ ROAD | LAGUNA NIGUEL | OR | SET SLUDGE LINE | LINE BREAK | Y | SULFUR CRK./LAGUNA NIG |  |  | Y |  |  |  |  | SAN DIEGO, CITY OF | 931115 | 0934AM | 931115 | 1230PM | 176 | GAL | 471 SO. EUCLID AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN/PACIFIC OC | MACHINE RODDED. DEODORIZED AROUND MANHOLE AND
| 931116 | 0830AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 931115 | 0630AM | 931115 | 1000AM |  | 21000 | GAL |  | 41 ST./REDWOOD ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROCK BLOCKAGE | Y | CANYON/PACIFIC OCEAN |  |  | Y | N |  | DEODORIZED AREA. CLEANED OUT MANHOLE. |  | SAN DIEGO, CITY OF | 931115 | 0730AM | 931115 | 1000AM | 835 | GAL | 661 UNIVERSITY AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | DEBRIS BLOCKAGE | STORM DRAIN/PACIFIC OC | MACHINE RODDED. DEODORIZEDAROUND MANHOLE AND
| 931116 | 0950AM | ALAN WILLIAMS | 6195227380 | CORONADO SHORES | 931115 | 1900PM | 931116 | 1000AM |  | 2200 | GAL |  | 1820 AVENIDA DEL MUNDO | CORONADO | SD | 24" MANHOLE | GREASE BLOCKAGE | Y | GLORIETTA BAY/PACIFIC |  |  | Y | Y | 01 |  |  | ALISO WATER MGMT. AGENCY | 931115 | 0830AM | 931115 | 0845AM | 50 | GAL | 29201 LA PAZ ROAD | LAGUNA NIGUEL | OR | SET SLUDGE LINE | LINE BREAK | SULFUR CRK./LAGUNA NIG
| 931117 | 0354AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931116 | 1430PM | 931116 | 1630PM |  | 600 | GAL |  | 4229 POLK AVE. | SAN DIEGO | SD | 8" PVC SEWER MAIN | GREASE BLOCKAGE | NO | NONE |  | VACTORED UP & SENT TO SEWER. | Y | N |  | MACHINE RODDED; COLLECTED AND RETURNED TO SEWE |  | SAN DIEGO, CITY OF | 931115 | 0630AM | 931115 | 1000AM | 21000 | GAL | 41 ST./REDWOOD ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROCK BLOCKAGE | CANYON/PACIFIC OCEAN | DEODORIZED AREA. CLEANED OUT MANHOLE.
| 931117 | 0343AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931116 | 1200AM | 931116 | 1430PM |  | 360 | GAL |  | 5763 LA JOLLA BLVD. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | NO | NONE |  | VACTORED STANDING WATER. | Y | N |  | OVERFLOW POOL AT CORNER OF CAMINO DELA COSTA W |  | CORONADO SHORES | 931115 | 1900PM | 931116 | 1000AM | 2200 | GAL | 1820 AVENIDA DEL MUNDO | CORONADO | SD | 24" MANHOLE | GREASE BLOCKAGE | GLORIETTA BAY/PACIFIC
| 931117 | 0900AM | JIM McCLURLEY | 6195258687 | SAN DIEGO, CITY OF | 931116 | 0744AM | 931116 | 0944AM |  | 2400 | GAL |  | 4474 CALLE DE VIDA | SAN DIEGO | SD | 8" VC SEWER LINE | ROOT BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | AREA WAS FLUSHED, VACTORED, & DEODORIZED; AND |  | SAN DIEGO, CITY OF | 931116 | 1430PM | 931116 | 1630PM | 600 | GAL | 4229 POLK AVE. | SAN DIEGO | SD | 8" PVC SEWER MAIN | GREASE BLOCKAGE | NONE | MACHINE RODDED; COLLECTED AND RETURNED TO SEWE
| 931118 | 0800AM | JIM McCLURY | 6195258687 | SAN DIEGO, CITY OF | 931117 | 1400PM | 931117 | 1500PM |  | 300 | GAL |  | I-15 SO. BOUND, N/O FRIARS RD. | SAN DIEGO | SD | 8" VC SEWER LINE | ROOT BLOCKAGE | Y | STORM CHANNEL/PACIFIC |  |  | Y | N |  | MACHINE RODDED MAIN; DEODORIZED AREA. MANHOLE |  | SAN DIEGO, CITY OF | 931116 | 1200AM | 931116 | 1430PM | 360 | GAL | 5763 LA JOLLA BLVD. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | NONE | OVERFLOW POOL AT CORNER OF CAMINO DELA COSTA W
| 931118 | 1430PM | HERNANDEZ LUIS | 6195258682 | SAN DIEGO, CITY OF | 931118 | 1029AM | 931118 | 1229PM |  | 1800 | GAL |  | 1120 28TH ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | DEBRIS BLOCKAGE | Y | CANYON/PACIFIC OCEAN |  |  | Y | Y |  | RODDED 152' SECTION. |  | SAN DIEGO, CITY OF | 931116 | 0744AM | 931116 | 0944AM | 2400 | GAL | 4474 CALLE DE VIDA | SAN DIEGO | SD | 8" VC SEWER LINE | ROOT BLOCKAGE | STORM DRAIN/PACIFIC OC | AREA WAS FLUSHED, VACTORED, & DEODORIZED; AND
| 931118 | 1400PM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 931118 | 1007AM | 931118 | 1107AM |  | 300 | GAL |  | 1133 SO. 41ST. ST. | SAN DIEGO | SD | 8" CP SEWER MAIN | ROOT BLOCKAGE | Y | CREEK BED/PACIFIC OCEA |  |  | Y | N |  | WASHED DOWN AND DEODORIZED AREA. |  | SAN DIEGO, CITY OF | 931117 | 1400PM | 931117 | 1500PM | 300 | GAL | I-15 SO. BOUND, N/O FRIARS RD. | SAN DIEGO | SD | 8" VC SEWER LINE | ROOT BLOCKAGE | STORM CHANNEL/PACIFIC | MACHINE RODDED MAIN; DEODORIZED AREA. MANHOLE
| 931119 | 0117AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931118 | 1504PM | 931118 | 1604PM |  | 300 | GAL |  | 2446 "L" ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | RODDED MAIN. DEODORIZED. |  | SAN DIEGO, CITY OF | 931118 | 1029AM | 931118 | 1229PM | 1800 | GAL | 1120 28TH ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | DEBRIS BLOCKAGE | CANYON/PACIFIC OCEAN | RODDED 152' SECTION.
| 931119 | 0830AM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 931118 | 0845AM | 931118 | 1000AM |  | 2000 | GAL |  | 1516 KELLEY STREET | OCEANSIDE | SD | SEWER MANHOLE | SAND, GREASE & GRIT CAUSED BLOCKAGE IN MAIN | NO | NONE |  | FLOWED ON GUTTER & POOLED. | Y |  |  | DOMESTIC WASTEWATER FLOWED OUT OF "PICK HOLES" |  | SAN DIEGO, CITY OF | 931118 | 1007AM | 931118 | 1107AM | 300 | GAL | 1133 SO. 41ST. ST. | SAN DIEGO | SD | 8" CP SEWER MAIN | ROOT BLOCKAGE | CREEK BED/PACIFIC OCEA | WASHED DOWN AND DEODORIZED AREA.
| 931119 | 1252AM | M. A. WHELAN | 6195258686 | SAN DIEGO, CITY OF | 931118 | 1007AM | 931118 | 1330PM |  | 406 | GAL |  | 1442 UNIVERSITY AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | FLUSHED. WASHED DOWN, DEODORIZED AREA. |  | SAN DIEGO, CITY OF | 931118 | 1504PM | 931118 | 1604PM | 300 | GAL | 2446 "L" ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN/PACIFIC OC | RODDED MAIN. DEODORIZED.
| 931120 | 0935AM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931119 | 1403PM | 931119 | 1400PM |  | 123 | GAL |  | WINDER & LYNWOOD ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | FLOW WENT INTO STORM DRAIN AND SETTLED. |  | OCEANSIDE, CITY OF | 931118 | 0845AM | 931118 | 1000AM | 2000 | GAL | 1516 KELLEY STREET | OCEANSIDE | SD | SEWER MANHOLE | SAND, GREASE & GRIT CAUSED BLOCKAGE IN MAIN | NONE | DOMESTIC WASTEWATER FLOWED OUT OF "PICK HOLES"
| 931119 | 1000PM | ANSWERING SERVICE | 6297288319 | FALLBROOK SANITARY DISTRICT | 931119 | 2200PM | 931120 | 0800AM |  | 50 | GAL |  | 1315 VIA FELIZ | FALLBROOK | SD | MAIN LINE | ROOTS, GREASE | NO | NONE |  | IN HOUSE & AROUND CLEANOUT | N | N |  | CLEARED STOPPAGE. CLEANOUT IS HIGHER THAN THE |  | SAN DIEGO, CITY OF | 931118 | 1007AM | 931118 | 1330PM | 406 | GAL | 1442 UNIVERSITY AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN/PACIFIC OC | FLUSHED. WASHED DOWN, DEODORIZED AREA.
| 931121 | 0830am | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931120 | 1726PM | 931120 | 1905PM |  | 2475 | GAL |  | 4298 TEMECULA ST. AT FAMOS BL. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | FAMOSA SLOUGH/PACIFIC |  |  | Y | Y | 04 | FLOWED TO STORM DRAIN TO SLOUGH. POSTED 4 SIG |  | SAN DIEGO, CITY OF | 931119 | 1403PM | 931119 | 1400PM | 123 | GAL | WINDER & LYNWOOD ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN/PACIFIC OC | FLOW WENT INTO STORM DRAIN AND SETTLED.
| 931121 | 0830AM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931120 | 1923PM | 931120 | 2046PM |  | 83 | GAL |  | 4728 BOUNDARY ST. | SAN DIEGO | SD | 6" VC | ROOT BLOCKAGE | NO | NONE |  | BACK INTO SEWER | Y | N |  | SENT VACTOR BALL NEXT DAY TO VACTOR PUDDLE IN |  | FALLBROOK SANITARY DISTRICT | 931119 | 2200PM | 931120 | 0800AM | 50 | GAL | 1315 VIA FELIZ | FALLBROOK | SD | MAIN LINE | ROOTS, GREASE | NONE | CLEARED STOPPAGE. CLEANOUT IS HIGHER THAN THE
| 931120 | 0900AM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 931120 | 0900AM | 931120 | 1130AM |  | 50 | GAL |  | 711 WEST ELDER ST. | FALLBROOK | SD | CLEANOUT | ROOTS | NO | NONE |  | AROUND CLEANOUT | N | N |  | OPENED CLEANOUT. POSSIBLE DIG-UP AFTER IT HAP |  | SAN DIEGO, CITY OF | 931120 | 1726PM | 931120 | 1905PM | 2475 | GAL | 4298 TEMECULA ST. AT FAMOS BL. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | FAMOSA SLOUGH/PACIFIC | FLOWED TO STORM DRAIN TO SLOUGH. POSTED 4 SIG
| 931121 | 1545PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 931121 | 1745PM | 931121 | 1845PM |  | 30 | GAL |  | 1581 S. MISSION RD. | FALLBROOK | SD | CLEANOUT | GREASE | NO | NONE |  | AROUND CLEANOUT | N | N |  | ARRIVED AT 1815PM. OPENED CLEANOUT. COMPLETE |  | SAN DIEGO, CITY OF | 931120 | 1923PM | 931120 | 2046PM | 83 | GAL | 4728 BOUNDARY ST. | SAN DIEGO | SD | 6" VC | ROOT BLOCKAGE | NONE | SENT VACTOR BALL NEXT DAY TO VACTOR PUDDLE IN
| 931121 | 2000PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931121 | 0930AM | 931121 | 1300PM |  | 1050 | GAL |  | 3693 ALBATROSS | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | Y | CANYON/PACIFIC OCEAN |  |  | Y | N |  | OVERFLOW WAS IN CANYON BEHIND ADDRESS. FLOW D |  | FALLBROOK SANITARY DISTRICT | 931120 | 0900AM | 931120 | 1130AM | 50 | GAL | 711 WEST ELDER ST. | FALLBROOK | SD | CLEANOUT | ROOTS | NONE | OPENED CLEANOUT. POSSIBLE DIG-UP AFTER IT HAP
| 931121 | 0930AM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 931121 | 0930AM | 931121 | 1215PM |  | 15 | GAL |  | 330 E. CLEMMENS | FALLBROOK | SD | CLEANOUT | ROOTS AND PAPER | NO | NONE |  | AROUND CLEANOUT | N |  |  | ARRIVED AT 1000AM. OPENED CLEANOUT. COMPLETE |  | FALLBROOK SANITARY DISTRICT | 931121 | 1745PM | 931121 | 1845PM | 30 | GAL | 1581 S. MISSION RD. | FALLBROOK | SD | CLEANOUT | GREASE | NONE | ARRIVED AT 1815PM. OPENED CLEANOUT. COMPLETE
| 931123 | 1211AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931122 | 1447PM | 931122 | 1700PM |  | 665 | GAL |  | 3503 INDIANA STREET | SAN DIEGO | SD | 6" VC SEWER MAIN | ROOT BLOCKAGE | Y | CANYON/PACIFIC OCEAN |  |  | Y | N |  | RODDED. |  | SAN DIEGO, CITY OF | 931121 | 0930AM | 931121 | 1300PM | 1050 | GAL | 3693 ALBATROSS | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | CANYON/PACIFIC OCEAN | OVERFLOW WAS IN CANYON BEHIND ADDRESS. FLOW D
| 931123 | 0800AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 931122 | 0805AM | 931122 | 0900AM |  | 550 | GAL |  | 411 GLORIA ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | DIRT GROUND/PACIFIC OC |  |  | Y | N |  | MACHINE RODDED TO REMOVE STOPPAGE. DEODORIZED |  | FALLBROOK SANITARY DISTRICT | 931121 | 0930AM | 931121 | 1215PM | 15 | GAL | 330 E. CLEMMENS | FALLBROOK | SD | CLEANOUT | ROOTS AND PAPER | NONE | ARRIVED AT 1000AM. OPENED CLEANOUT. COMPLETE
| 931124 | ?????? | JIM McCURLEY | 6195258687 | SAN DIEGO, CITY OF | 931122 | 1316PM | 931122 | 1446PM |  | 90 | GAL |  | 18736 AVENIDA CORDILLERA | SAN DIEGO | SD | 8" PVC SEWER LINE | ROCK BLOCKAGE | NO | NONE |  | INTO GROUND AT 18667 ROBLEDA | Y | N |  | MANHOLE #4461 WILL BE CLEANED OUT AND STRAPPED |  | SAN DIEGO, CITY OF | 931122 | 1447PM | 931122 | 1700PM | 665 | GAL | 3503 INDIANA STREET | SAN DIEGO | SD | 6" VC SEWER MAIN | ROOT BLOCKAGE | CANYON/PACIFIC OCEAN | RODDED.
| 921122 | 2325PM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931122 | 1203PM | 931122 | 1430PM |  | 735 | GAL |  | 1120 28TH ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | VANDALISM CAUSED DEBRIS | YN | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | RODDED AND CLEARED AFFECTED SECTIONS OF SEWER |  | SAN DIEGO, CITY OF | 931122 | 0805AM | 931122 | 0900AM | 550 | GAL | 411 GLORIA ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | DIRT GROUND/PACIFIC OC | MACHINE RODDED TO REMOVE STOPPAGE. DEODORIZED
| 931124 | 2424AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931123 | 1548PM | 931123 | 2148PM |  | 1800 | GAL |  | HWY. 163 N/BOUND UNDER 1-5 HWY | SAN DIEGO | SD | 8" VC | ROOT BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | RODDED MAIN. |  | SAN DIEGO, CITY OF | 931122 | 1316PM | 931122 | 1446PM | 90 | GAL | 18736 AVENIDA CORDILLERA | SAN DIEGO | SD | 8" PVC SEWER LINE | ROCK BLOCKAGE | NONE | MANHOLE #4461 WILL BE CLEANED OUT AND STRAPPED
| 931124 | 0800AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 931123 | 0934AM | 931123 | 1030AM |  | 560 | GAL |  | 54TH/LAUREL ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | MACHINE RODDED MAIN. DEODORIZED AREA. |  | SAN DIEGO, CITY OF | 931122 | 1203PM | 931122 | 1430PM | 735 | GAL | 1120 28TH ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | VANDALISM CAUSED DEBRIS | STORM DRAIN/PACIFIC OC | RODDED AND CLEARED AFFECTED SECTIONS OF SEWER
| 931123 | 1530PM | SCOTT WIKE | 6197254806 | USMC - CAMP PENDLETON | 931123 | 1500PM | 931123 | 1510PM |  | 50 | GAL |  | BUILDING 1655 | CAMP PENDLETON | SD | MANHOLE | MAIN LINE BLOCKAGE | N | NONE |  | FIELD | Y | N |  | CLEANED LINE AND LIMED THE AREA. |  | SAN DIEGO, CITY OF | 931123 | 1548PM | 931123 | 2148PM | 1800 | GAL | HWY. 163 N/BOUND UNDER 1-5 HWY | SAN DIEGO | SD | 8" VC | ROOT BLOCKAGE | STORM DRAIN/PACIFIC OC | RODDED MAIN.
| 931123 | 0720AM | CLINT BASE | 6197281178 | RAINBOW MUNICIPAL WATER DIST. | 931123 | 0655AM | 931123 | 0720AM |  | 2500 | GAL |  | OLD RIVER RD. & GOPHER CYN. | BONSAL | SD | LIFT STATION #2 | ELECTIRCAL RELAY SWITCH FAILURE. | NO | NONE |  | CONTAINED 50 FEET TO THE WEST. | Y | N |  | AREA WAS CLEANED AND RINSED BY DISTRICT PERSON |  | SAN DIEGO, CITY OF | 931123 | 0934AM | 931123 | 1030AM | 560 | GAL | 54TH/LAUREL ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN/PACIFIC OC | MACHINE RODDED MAIN. DEODORIZED AREA.
| 931123 | 0752AM | MICHAEL FILECCIA | 6192218728 | SAN DIEGO, CITY OF | 931123 | 0730AM | 931123 | 0730AM |  | 3000 | GAL |  | FIESTA ISLAND HIDDEN ANCHORAGE | SAN DIEGO | SD | N/A | CONTRACTOR "SUNCOAST PIPELINE, INC." BROKE | Y | MISSION BAY |  |  | Y | Y |  | RESPONSE BY PT. LOMA SERVICES TEAM CONTAINED 1 |  | USMC - CAMP PENDLETON | 931123 | 1500PM | 931123 | 1510PM | 50 | GAL | BUILDING 1655 | CAMP PENDLETON | SD | MANHOLE | MAIN LINE BLOCKAGE | NONE | CLEANED LINE AND LIMED THE AREA.
| 931124 | 1400PM | E. SEMO | 6195258685 | SAN DIEGO, CITY OF | 931124 | 0930AM | 931124 | 1100AM |  | 450 | GAL |  | INTERSTATE 163 & FRIARS RD. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | ALONG FREEWAY/PACIFIC |  |  | Y | N |  | OVERFLOW SOAKED INTO THICK ICE PLANTS ALONG FR |  | RAINBOW MUNICIPAL WATER DIST. | 931123 | 0655AM | 931123 | 0720AM | 2500 | GAL | OLD RIVER RD. & GOPHER CYN. | BONSAL | SD | LIFT STATION #2 | ELECTIRCAL RELAY SWITCH FAILURE. | NONE | AREA WAS CLEANED AND RINSED BY DISTRICT PERSON
| 931124 | 1545PM | DOUGLAS BRANCO | 6195258687 | SAN DIEGO, CITY OF | 931124 | 1256PM | 931124 | 1456PM |  | 600 | GAL |  | 2535 "K" ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | RODDED MAIN. |  | SAN DIEGO, CITY OF | 931123 | 0730AM | 931123 | 0730AM | 3000 | GAL | FIESTA ISLAND HIDDEN ANCHORAGE | SAN DIEGO | SD | N/A | CONTRACTOR "SUNCOAST PIPELINE, INC." BROKE | MISSION BAY | RESPONSE BY PT. LOMA SERVICES TEAM CONTAINED 1
| 931124 | 2105PM | DOUGLAS BRANCO | 6195258687 | SAN DIEGO, CITY OF | 931124 | 1557PM | 931124 | 1757PM |  | 60 | GAL |  | 4356 ARCADIA DR. | SAN DIEGO | SD | 6" VC SEWER MAIN | ROOT BLOCKAGE | Y | CANYON/PACIFIC OCEAN |  |  | Y | N |  | RODDED MAIN. |  | SAN DIEGO, CITY OF | 931124 | 0930AM | 931124 | 1100AM | 450 | GAL | INTERSTATE 163 & FRIARS RD. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | ALONG FREEWAY/PACIFIC | OVERFLOW SOAKED INTO THICK ICE PLANTS ALONG FR
| 931124 | 1445PM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 931124 | 0930AM | 931124 | 1200AM |  | 720 | GAL |  | 31TH/QUINCE STS. | SAN DIEGO | SD | 8" VC SEWER MAIN | VANDALISM OF SEWER MANHOLES CAUSED BLOCKAGE | Y | CREEK BED/PACIFIC OCEA |  |  | Y | N |  | REMOVED DEBRIS & CLEARED BLOCKAGE. MANHOLE WI |  | SAN DIEGO, CITY OF | 931124 | 1256PM | 931124 | 1456PM | 600 | GAL | 2535 "K" ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN/PACIFIC OC | RODDED MAIN.
| 931124 | 1130AM | STEVE FRANCIS | 7145822330 | SANTA MARGARITA WATER DIST. | 931124 | 0718AM | 931124 | 0728AM |  | 10000 | GAL |  | ANTONIO PARKWAY | SANTA MARGARITA | OR | PLANO LIFT STATION | EQUIPMENT FAILURE | Y | TIJERES CRK./TRABUCO C |  |  | Y | N |  | CRK. WAS NOT POSTED. TOO REMOTE. DISINFECTED |  | SAN DIEGO, CITY OF | 931124 | 1557PM | 931124 | 1757PM | 60 | GAL | 4356 ARCADIA DR. | SAN DIEGO | SD | 6" VC SEWER MAIN | ROOT BLOCKAGE | CANYON/PACIFIC OCEAN | RODDED MAIN.
| 931127 | 1030AM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931126 | 1312PM | 931126 | 1600PM |  | 1680 | GAL |  | 4729 CASTANA ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | STREET CURB/PACIFIC OC |  |  | Y | N |  | FLOWED ONTO DIRT LOT ACROSS FROM ADDRESS & SOA |  | SAN DIEGO, CITY OF | 931124 | 0930AM | 931124 | 1200AM | 720 | GAL | 31TH/QUINCE STS. | SAN DIEGO | SD | 8" VC SEWER MAIN | VANDALISM OF SEWER MANHOLES CAUSED BLOCKAGE | CREEK BED/PACIFIC OCEA | REMOVED DEBRIS & CLEARED BLOCKAGE. MANHOLE WI
| 931126 | 1310PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 931126 | 1310PM | 931126 | 1425PM |  | 50 | GAL |  | 1105 OLD STAGE | FALLBROOK | SD | MANHOLE | ROOTS | NO | NONE |  | ALONG ROAD | N | N |  | ARRIVED AT 1400PM. OPENED MANHOLE. COMPLETED |  | SANTA MARGARITA WATER DIST. | 931124 | 0718AM | 931124 | 0728AM | 10000 | GAL | ANTONIO PARKWAY | SANTA MARGARITA | OR | PLANO LIFT STATION | EQUIPMENT FAILURE | TIJERES CRK./TRABUCO C | CRK. WAS NOT POSTED. TOO REMOTE. DISINFECTED
| 931128 | 1030AM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931127 | 1043AM | 931127 | 1243PM |  | 240 | GAL |  | 5867 BASA DR. | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | FLOWED DOWN CANYON & INTO STORM DRAIN. |  | SAN DIEGO, CITY OF | 931126 | 1312PM | 931126 | 1600PM | 1680 | GAL | 4729 CASTANA ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | STREET CURB/PACIFIC OC | FLOWED ONTO DIRT LOT ACROSS FROM ADDRESS & SOA
| 931128 | 1030AM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931127 | 1058AM | 931127 | 1400PM |  | 910 | GAL |  | 1436 LEAF TERRACE | SAN DIEGO | SD | 12" VC SEWER MAIN | ROCK BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | FLOWED INTO STORM DRAIN CULVERT & DRIED UP. |  | FALLBROOK SANITARY DISTRICT | 931126 | 1310PM | 931126 | 1425PM | 50 | GAL | 1105 OLD STAGE | FALLBROOK | SD | MANHOLE | ROOTS | NONE | ARRIVED AT 1400PM. OPENED MANHOLE. COMPLETED
| 931128 | 0815AM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 931128 | 0815AM | 931128 | 0915AM |  | 10 | GAL |  | 217 S. ORANGE STREET | FALLBROOK | SD | CLEANOUT & MAINLINE | ROOTS | NO | NONE |  | AROUND CLEANOUT & DRIVEWAY | N | N |  | ARRIVED AT 0945M. OPENED CLEANOUT. COMPLETED A |  | SAN DIEGO, CITY OF | 931127 | 1043AM | 931127 | 1243PM | 240 | GAL | 5867 BASA DR. | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN/PACIFIC OC | FLOWED DOWN CANYON & INTO STORM DRAIN.
| 931030 | 0800AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 931129 | 0710AM | 931129 | 1000AM |  | 1700 | GAL |  | 5200 UNIVERSITY AVE. | SAN DIEGO | SD | 10" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | MACHINE RODDED TO RELIEVE STOPPAGE. DEODORIZE |  | SAN DIEGO, CITY OF | 931127 | 1058AM | 931127 | 1400PM | 910 | GAL | 1436 LEAF TERRACE | SAN DIEGO | SD | 12" VC SEWER MAIN | ROCK BLOCKAGE | STORM DRAIN/PACIFIC OC | FLOWED INTO STORM DRAIN CULVERT & DRIED UP.
| 931129 | 1650 P | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 931129 | 1056AM | 931129 | 1256PM |  | 900 | GAL |  | 163 UNDER I-5 NEAR BARRIERS | SAN DIEGO | SD | 8" VC SEWER MAIN | VANDALISM | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | RODDED MAIN. |  | FALLBROOK SANITARY DISTRICT | 931128 | 0815AM | 931128 | 0915AM | 10 | GAL | 217 S. ORANGE STREET | FALLBROOK | SD | CLEANOUT & MAINLINE | ROOTS | NONE | ARRIVED AT 0945M. OPENED CLEANOUT. COMPLETED A
| 931201 | 0830AM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 931129 | 1717PM | 931120 | 0930AM |  | 19460 | GAL |  | SAN CLEMENTE PK./GENESEE AVE. | SAN DIEGO | SD | 12" PVC SEWER MAIN | ROOT BLOCKAGE | Y | CANYON/PACIFIC OCEAN |  |  | Y | Y | 02 | POSTED 2 SIGNS AT WALKING PATH. SEWAGE DID NO |  | SAN DIEGO, CITY OF | 931129 | 0710AM | 931129 | 1000AM | 1700 | GAL | 5200 UNIVERSITY AVE. | SAN DIEGO | SD | 10" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN/PACIFIC OC | MACHINE RODDED TO RELIEVE STOPPAGE. DEODORIZE
| 931130 | 2400PM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931130 | 1619PM | 931130 | 1719PM |  | 30 | GAL |  | 4136 WALLACE ST. | SAN DIEGO | SD | 8" CP SEWER MAIN | GREASE BLOCKAGE | Y | SOAKED IN GROUND/PACIF |  |  | Y | N |  | RODDED MAIN. |  | SAN DIEGO, CITY OF | 931129 | 1056AM | 931129 | 1256PM | 900 | GAL | 163 UNDER I-5 NEAR BARRIERS | SAN DIEGO | SD | 8" VC SEWER MAIN | VANDALISM | STORM DRAIN/PACIFIC OC | RODDED MAIN.
| 931130 | 2348PM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931130 | 1831PM | 931130 | 1931PM |  | 300 | GAL |  | 5225 UNIVERSITY AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN/PACIFIC OC |  |  | Y | N |  | RODDED MAIN. |  | SAN DIEGO, CITY OF | 931129 | 1717PM | 931120 | 0930AM | 19460 | GAL | SAN CLEMENTE PK./GENESEE AVE. | SAN DIEGO | SD | 12" PVC SEWER MAIN | ROOT BLOCKAGE | CANYON/PACIFIC OCEAN | POSTED 2 SIGNS AT WALKING PATH. SEWAGE DID NO
| 931202 | 0259AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931201 | 1348PM | 931201 | 1648PM |  | 2700 | GAL |  | 66TH & BROOKLIN ST | SAN DIEGO | SD | 8" VC SEWER MAIN | ROCKS & ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N |  | RODDED MAIN. REMOVED ROCKS FROM MH. |  | SAN DIEGO, CITY OF | 931130 | 1619PM | 931130 | 1719PM | 30 | GAL | 4136 WALLACE ST. | SAN DIEGO | SD | 8" CP SEWER MAIN | GREASE BLOCKAGE | SOAKED IN GROUND/PACIF | RODDED MAIN.
| 931201 | 1215AM | JOGN VAUGHT | 6197414854 | ESCONDIDO, CITY OF | 931201 | 0620AM | 931201 | 0730AM |  | 1750 | GAL |  | 1104 SO. TULIP | ESCONDIDO | SD | SEWER AHAS PG.#12 MH#15 | GREASE & PAPER | Y | ESCONDIDO GREEK, SD LA |  |  | Y | Y | 10 | AREA WAS WASHED DOWN & CONTAINED, THEN VACUUME |  | SAN DIEGO, CITY OF | 931130 | 1831PM | 931130 | 1931PM | 300 | GAL | 5225 UNIVERSITY AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN/PACIFIC OC | RODDED MAIN.
| 931202 | 0341PM | MARK STROLNAN | 6195058680 | SAN DIEGO, CITY OF | 931202 | 1158AM | 931202 | 1258PM |  | 180 | GAL |  | 3933 BEYER BLVD | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y |  |  | FLUSHED MAIN |  | SAN DIEGO, CITY OF | 931201 | 1348PM | 931201 | 1648PM | 2700 | GAL | 66TH & BROOKLIN ST | SAN DIEGO | SD | 8" VC SEWER MAIN | ROCKS & ROOT BLOCKAGE | STORM DRAIN, PACIFIC O | RODDED MAIN. REMOVED ROCKS FROM MH.
| 931202 | 1150AM | ALAN WILLIAMS | 6195227380 | CORONADO, CITY OF | 931202 | 1025AM | 931202 | 1130AM |  | 400 | GAL |  | 1100 BLK THIRD ST SR 75 | CORONADO | SD | MH 24" | GREASE BLOCKAGE | Y | SAN DIEGO BAY, PACIFIC |  |  | Y | Y | 03 | AFFECTED PUBLIC AREA,WHICH HAVE BEEN SANITIZED |  | ESCONDIDO, CITY OF | 931201 | 0620AM | 931201 | 0730AM | 1750 | GAL | 1104 SO. TULIP | ESCONDIDO | SD | SEWER AHAS PG.#12 MH#15 | GREASE & PAPER | ESCONDIDO GREEK, SD LA | AREA WAS WASHED DOWN & CONTAINED, THEN VACUUME
| 931203 | 0530AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931202 | 1450PM | 931202 | 1650PM |  | 600 | GAL |  | INTERSECTION 31ST & "A" ST | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y |  |  | RODDED MAIN |  | SAN DIEGO, CITY OF | 931202 | 1158AM | 931202 | 1258PM | 180 | GAL | 3933 BEYER BLVD | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | FLUSHED MAIN
| 931203 | 1330PM | ED CALHOUN | 6199668763 | OCEANSIDE, CITY OF | 931203 | 0730AM | 931203 | 1105AM |  | 50 | GAL |  | 3160 CAMINO CREST | OCEANSIDE | SD | MANHOLE | ROOTS | Y | BUENA VISTA LAGOON |  |  | Y |  |  | NO REMARKS |  | CORONADO, CITY OF | 931202 | 1025AM | 931202 | 1130AM | 400 | GAL | 1100 BLK THIRD ST SR 75 | CORONADO | SD | MH 24" | GREASE BLOCKAGE | SAN DIEGO BAY, PACIFIC | AFFECTED PUBLIC AREA,WHICH HAVE BEEN SANITIZED
| 931204 | 0120PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931203 | 0956PM | 931204 | 1256AM |  | 900 | GAL |  | 3931 CLAIRMONT MESA BLVD | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORN DRAIN, PACIFIC O |  |  | Y | N |  | FLOWED INTO STORM DRAIN IN FRONT OF PACITE ST. |  | SAN DIEGO, CITY OF | 931202 | 1450PM | 931202 | 1650PM | 600 | GAL | INTERSECTION 31ST & "A" ST | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | RODDED MAIN
| 931205 | 0955PM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 931204 | 1443PM | 931205 | 0143PM |  | 6300 | GAL |  | 2618 VANCOUVER AVE. | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | Y | CANYON AROUND MH#11717 |  |  | Y | N |  | 6000 GALS FLOWED BACK INTO SYSTEM @ MH#11717, |  | OCEANSIDE, CITY OF | 931203 | 0730AM | 931203 | 1105AM | 50 | GAL | 3160 CAMINO CREST | OCEANSIDE | SD | MANHOLE | ROOTS | BUENA VISTA LAGOON | NO REMARKS
| 931204 | 1010PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931204 | 0125PM | 931204 | 0425PM |  | 900 | GAL |  | FRIARS DR BYWN SANTO & I-15 | SAN DIEGO | SD | 8" PVC SEWER MAIN | ROCK BLOCKAGE | Y | STORM DRAIN, SD RIVER/ |  |  | Y | Y | 10 | FLOWED INTO STORM DRAIN @ I-15 AND FRIARS RD., |  | SAN DIEGO, CITY OF | 931203 | 0956PM | 931204 | 1256AM | 900 | GAL | 3931 CLAIRMONT MESA BLVD | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORN DRAIN, PACIFIC O | FLOWED INTO STORM DRAIN IN FRONT OF PACITE ST.
| 931205 | 0800AM | RONALD D. ROBY | 6195258586 | SAN DIEGO, CITY OF | 931204 | 0927AM | 931204 | 1200PM |  | 3825 | GAL |  | 41ST & NORDICA ST | SAN DIEGO | SD | 15" VC SEWER MAIN | ROCK BLOCKAGE | Y | STORM CULVERT, PACIFIC |  |  | Y | N |  | FLOW WENT TO STORM CULVERT AND REMAINED THERE |  | SAN DIEGO, CITY OF | 931204 | 1443PM | 931205 | 0143PM | 6300 | GAL | 2618 VANCOUVER AVE. | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | CANYON AROUND MH#11717 | 6000 GALS FLOWED BACK INTO SYSTEM @ MH#11717,
| 931204 | 1010PM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 931204 | 1119AM | 931204 | 0419PM |  | 1500 | GAL |  | 12913 POLVERA ST | SAN DIEGO | SD | 8" PVC SEWER MAIN | ROOT BLOCKAGE | Y | STREET TO STORM DRAIN, |  |  | Y | N |  | APPROX 200 GAL SOAKED INTO CREEK BED AND 1300 |  | SAN DIEGO, CITY OF | 931204 | 0125PM | 931204 | 0425PM | 900 | GAL | FRIARS DR BYWN SANTO & I-15 | SAN DIEGO | SD | 8" PVC SEWER MAIN | ROCK BLOCKAGE | STORM DRAIN, SD RIVER/ | FLOWED INTO STORM DRAIN @ I-15 AND FRIARS RD.,
| 931205 | 0955PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931204 | 0530PM | 931205 | 0900AM |  | 1860 | GAL |  | 1261 RHODA DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N |  | FLOW SETTLED IN STORM DRAIN. TRACKED FLOW UNTI |  | SAN DIEGO, CITY OF | 931204 | 0927AM | 931204 | 1200PM | 3825 | GAL | 41ST & NORDICA ST | SAN DIEGO | SD | 15" VC SEWER MAIN | ROCK BLOCKAGE | STORM CULVERT, PACIFIC | FLOW WENT TO STORM CULVERT AND REMAINED THERE
| 931206 | ? | MARK A.STOFFER | 6197254806 | CAMP PENDLETON | 931205 | 0715AM | 931205 | 0800AM |  | 200 | GAL |  | SAN ONOFRE BEACH | CAMP PENDLETON | SD | LIFT STATION 51849 | BROKEN FORCED MAIN | NO | NONE |  | AREA BY LIFT STATION | Y | N |  | REPAIRED FORCED MAIN-PUMPER. REPAIR WAS MADE T |  | SAN DIEGO, CITY OF | 931204 | 1119AM | 931204 | 0419PM | 1500 | GAL | 12913 POLVERA ST | SAN DIEGO | SD | 8" PVC SEWER MAIN | ROOT BLOCKAGE | STREET TO STORM DRAIN, | APPROX 200 GAL SOAKED INTO CREEK BED AND 1300
| 931205 | 0955PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931205 | 1100AM | 931205 | 0130PM |  | 300 | GAL |  | 54TH & ADAMS AVE. | SAN DIEGO | SD | 6" CP SEWER MAIN | ROCK BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N |  | FLOW DRIED IN CANYON. |  | SAN DIEGO, CITY OF | 931204 | 0530PM | 931205 | 0900AM | 1860 | GAL | 1261 RHODA DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, PACIFIC O | FLOW SETTLED IN STORM DRAIN. TRACKED FLOW UNTI
| 931205 | 0955PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931205 | 0218PM | 931205 | 0518PM |  | 180 | GAL |  | 28TH & WEBSTER | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N |  | FLOWED INTO STORM DRAIN WHERE IT SETTLED. |  | CAMP PENDLETON | 931205 | 0715AM | 931205 | 0800AM | 200 | GAL | SAN ONOFRE BEACH | CAMP PENDLETON | SD | LIFT STATION 51849 | BROKEN FORCED MAIN | NONE | REPAIRED FORCED MAIN-PUMPER. REPAIR WAS MADE T
| 931207 | 0300PM | ORV SALISBURY | 6197440480 | VALLECITOS WATER DISTRICT | 931205 | 0800PM | 931205 | 0900PM |  | 200 | GAL |  | CENTER DR. | SAN MARCOS | SD | S4G-Q2-MH4 | PARTIAL BLOCKAGE IN LOCAL 8" SEWER LINE CAU | NO | NONE |  | PARKING LOT & STORMDRAIN @ 25' | Y | N |  | CLEANED THE PARKING LOT AND FLUSHED THE STORM |  | SAN DIEGO, CITY OF | 931205 | 1100AM | 931205 | 0130PM | 300 | GAL | 54TH & ADAMS AVE. | SAN DIEGO | SD | 6" CP SEWER MAIN | ROCK BLOCKAGE | CANYON, PACIFIC OCEAN | FLOW DRIED IN CANYON.
| 931208 | 0700PM | BRIAN BERTSCH | 7148580277 | TRABUCO CANYON WATER DISTRICT | 931205 | ? | 931207 | 0430PM |  | 292000 | ? |  | VIA ALEGRE & CAMINO DEL CIELO | TRABUCO CANYON | OR | MH12G-21 | LANDSCAPE POLES, STICKS, ROCKS AND ONE TOY | NO | NONE |  | STORM DRAIN. | Y | Y | 30 | SPRAYED AFFECTED AREA WITH CHLORINE SOLUTION. |  | SAN DIEGO, CITY OF | 931205 | 0218PM | 931205 | 0518PM | 180 | GAL | 28TH & WEBSTER | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | FLOWED INTO STORM DRAIN WHERE IT SETTLED.
| 931206 | 1138PM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931206 | 1127AM | 931206 | 1227PM |  | 60 | GAL |  | 2950 CURIE ST | SAN DIEGO | SD | 8" VC SEWER MAIN | DEBRIS BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N |  | PROBED WITH A FORK. |  | VALLECITOS WATER DISTRICT | 931205 | 0800PM | 931205 | 0900PM | 200 | GAL | CENTER DR. | SAN MARCOS | SD | S4G-Q2-MH4 | PARTIAL BLOCKAGE IN LOCAL 8" SEWER LINE CAU | NONE | CLEANED THE PARKING LOT AND FLUSHED THE STORM
| 931208 | 1558PM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931208 | 1019AM | 931208 | 1319PM |  | 900 | GAL |  | 2964 B ST | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N |  | RODDED MAIN. |  | TRABUCO CANYON WATER DISTRICT | 931205 | ? | 931207 | 0430PM | 292000 | ? | VIA ALEGRE & CAMINO DEL CIELO | TRABUCO CANYON | OR | MH12G-21 | LANDSCAPE POLES, STICKS, ROCKS AND ONE TOY | NONE | SPRAYED AFFECTED AREA WITH CHLORINE SOLUTION.
| 931209 | 0106AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931208 | 1418PM | 931208 | 1548PM |  | 270 | GAL |  | 47TH & DWIGHT ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N |  | RODDED MAIN. |  | SAN DIEGO, CITY OF | 931206 | 1127AM | 931206 | 1227PM | 60 | GAL | 2950 CURIE ST | SAN DIEGO | SD | 8" VC SEWER MAIN | DEBRIS BLOCKAGE | STORM DRAIN, PACIFIC O | PROBED WITH A FORK.
| 931211 | 0840AM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931210 | 0911AM | 931210 | 1000AM |  | 98 | GAL |  | 2411 BERYL ST | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | UNDER ICE PLANT BY MH, |  |  | Y | N |  | FLOW STAYED AROUND ICE PLANT AT MANHOLE AND SO |  | SAN DIEGO, CITY OF | 931208 | 1019AM | 931208 | 1319PM | 900 | GAL | 2964 B ST | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | RODDED MAIN.
| 931223 | 0900AM | MIKE BENARD | 6195277456 | SAN DIEGO, CITY OF | 931210 | 0100PM | 931210 | 0105PM |  | 93 | GAL |  | 102 FERN GLEN AVE | SAN DIEGO | SD | 8" VC PIPE | THE SEWAGE NEAR BEACHLINEOF A OLD SEPTIC TA | Y | PACIFIC OCEAN |  |  | Y | N |  | WHAT WAS INITIALLY THOUGHT TO BE SEWAGE,IT TUR |  | SAN DIEGO, CITY OF | 931208 | 1418PM | 931208 | 1548PM | 270 | GAL | 47TH & DWIGHT ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | RODDED MAIN.
| 931210 | 1710PM | ABEL HERNANDEZ | 6195334691 | SAN DIEGO, CITY OF | 931210 | ? | 931210 | ? |  | 200 | GAL |  | HEADWORKS OF AQUA 2 PLANT | SAN DIEGO | SD | SCREENING UNIT | SOLIDS PLUGGED UP THE LINE @ THE SCREENING | NO | NONE |  | ON SITE OF THE AQUA 2 PLANT. | ? | N |  | AQUA 2 PLANT WILL BE FULLY DECOMMISSIONED BY 1 |  | SAN DIEGO, CITY OF | 931210 | 0911AM | 931210 | 1000AM | 98 | GAL | 2411 BERYL ST | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | UNDER ICE PLANT BY MH, | FLOW STAYED AROUND ICE PLANT AT MANHOLE AND SO
| 931211 | 0840PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931211 | 0109PM | 931211 | 0209PM |  | 60 | GAL |  | 226 PLAYA DEL NORTE | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | Y | ? | FLOW WENT DOWN STREET AND THEN TO PACIFIC OCEA |  | SAN DIEGO, CITY OF | 931210 | 0100PM | 931210 | 0105PM | 93 | GAL | 102 FERN GLEN AVE | SAN DIEGO | SD | 8" VC PIPE | THE SEWAGE NEAR BEACHLINEOF A OLD SEPTIC TA | PACIFIC OCEAN | WHAT WAS INITIALLY THOUGHT TO BE SEWAGE,IT TUR
| 931211 | 0815PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931211 | 1100AM | 931211 | 1200PM |  | 6840 | GAL |  | 31ST & QUINCE ST | SAN DIEGO | SD | 8" VC SEWER MAIN | VANDALISM OF SEWER CAUSED BLOCKAGE AND OVER | Y | CANYON, PACIFIC OCEAN |  |  | Y | N |  | FLOW WENT THROUGH 2 CANYONS AND SETTLED. IT RA |  | SAN DIEGO, CITY OF | 931210 | ? | 931210 | ? | 200 | GAL | HEADWORKS OF AQUA 2 PLANT | SAN DIEGO | SD | SCREENING UNIT | SOLIDS PLUGGED UP THE LINE @ THE SCREENING | NONE | AQUA 2 PLANT WILL BE FULLY DECOMMISSIONED BY 1
| 931211 | 1000AM | MARK RAUL | 6194754805 | SAN DIEGO, CITY OF | 931211 | 0940AM | 931211 | 1100AM |  | 600 | GAL |  | 4421 FELICITA AVE | SPRING VALLEY | SD | 3" CLEANOUT CAP | GREASE AND DEBRIS. | NO | NONE |  | YARD AND HOUSE | N | N |  | LINE TO BE TV TO SEE WHAT ACTION IS NEEDED TO |  | SAN DIEGO, CITY OF | 931211 | 0109PM | 931211 | 0209PM | 60 | GAL | 226 PLAYA DEL NORTE | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, PACIFIC O | FLOW WENT DOWN STREET AND THEN TO PACIFIC OCEA
| 931212 | 0510PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931212 | 0939AM | 931212 | 1121AM |  | 3060 | GAL |  | 5331 WESRKNOLL DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | Y | 03 | WASHED ST. W/ 2500 GAL FLOW WENT TO TOURMALINE |  | SAN DIEGO, CITY OF | 931211 | 1100AM | 931211 | 1200PM | 6840 | GAL | 31ST & QUINCE ST | SAN DIEGO | SD | 8" VC SEWER MAIN | VANDALISM OF SEWER CAUSED BLOCKAGE AND OVER | CANYON, PACIFIC OCEAN | FLOW WENT THROUGH 2 CANYONS AND SETTLED. IT RA
| 931212 | 0720PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931212 | 0730AM | 931212 | 0930AM |  | 120 | GAL |  | 2500 RIDGEVIEW DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N |  | FLOWED INTO STORM DRAIN AND SETTLED. |  | SAN DIEGO, CITY OF | 931211 | 0940AM | 931211 | 1100AM | 600 | GAL | 4421 FELICITA AVE | SPRING VALLEY | SD | 3" CLEANOUT CAP | GREASE AND DEBRIS. | NONE | LINE TO BE TV TO SEE WHAT ACTION IS NEEDED TO
| 931213 | 0915AM | MARK A. STOFFER | 6197254806 | CAMP PENDLETON MARINE BASE | 931212 | 2150PM | 931212 | 2230PM |  | 200 | GAL |  | CHOSIN & WONSAN | CAMP PENDLETON | SD | MAN HOLE DELUZ HOUSING | MAIN LINE STOPPAGE 303 CHOSIN | NO | NONE |  | AREA BY MANHOLE | Y | N |  | UNPLUGGED LINE AND CLEANED AREA. |  | SAN DIEGO, CITY OF | 931212 | 0939AM | 931212 | 1121AM | 3060 | GAL | 5331 WESRKNOLL DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, PACIFIC O | WASHED ST. W/ 2500 GAL FLOW WENT TO TOURMALINE
| 931212 | 0230PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 931212 | 0230PM | 931212 | 0355PM |  | 10 | GAL |  | 356 DOUGHERTY | FALLBROOK | SD | 4" CLEANOUT | POSSIBLE COLLAPSED PIPE. | NO | NONE |  | 4" AROUND CLEANOUT. | N | N |  | MH B-165 WAS OPENED @ 3:15PM. IT SHOULD BE OPE |  | SAN DIEGO, CITY OF | 931212 | 0730AM | 931212 | 0930AM | 120 | GAL | 2500 RIDGEVIEW DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, PACIFIC O | FLOWED INTO STORM DRAIN AND SETTLED.
| 931214 | 0835AM | JACK J. WILLIAMS | 6195258682 | SAN DIEGO, CITY OF | 931213 | 1157AM | 931213 | 1245PM |  | 48 | GAL |  | 4TH & ELM ST | SAN DIEGO | SD | 4" VC SEWER MAIN | GREASE BLOCKAGE | Y | ST. @ 4TH & ELM, PACIF |  |  | Y | N | NA | MACHINE RODDED MAIN |  | CAMP PENDLETON MARINE BASE | 931212 | 2150PM | 931212 | 2230PM | 200 | GAL | CHOSIN & WONSAN | CAMP PENDLETON | SD | MAN HOLE DELUZ HOUSING | MAIN LINE STOPPAGE 303 CHOSIN | NONE | UNPLUGGED LINE AND CLEANED AREA.
| 931214 | 1230AM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931213 | 1004PM | 931213 | 1104PM |  | 300 | GAL |  | 3832 FAIRMONT AVE | SAN DIEGO | SD | 8" PVC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | FLOW WENT TO STORM DRAIN AY CORNER OF 43RD AND |  | FALLBROOK SANITARY DISTRICT | 931212 | 0230PM | 931212 | 0355PM | 10 | GAL | 356 DOUGHERTY | FALLBROOK | SD | 4" CLEANOUT | POSSIBLE COLLAPSED PIPE. | NONE | MH B-165 WAS OPENED @ 3:15PM. IT SHOULD BE OPE
| 931214 | 1230AM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 931213 | 0600PM | 931213 | 0700PM |  | 300 | GAL |  | 4765 TROJAN AVE | SAN DIEGO | SD | 10" CONCRETE SEWER MAIN | COLLAPSED SEWER MAIN=GRAVITY MAIN BREAK | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | FLOW WENT TO SRORM DRAIN AT 4288*48TH ST AND S |  | SAN DIEGO, CITY OF | 931213 | 1157AM | 931213 | 1245PM | 48 | GAL | 4TH & ELM ST | SAN DIEGO | SD | 4" VC SEWER MAIN | GREASE BLOCKAGE | ST. @ 4TH & ELM, PACIF | MACHINE RODDED MAIN
| 931215 | 1500PM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 931213 | 1600PM | 931213 | 1700PM |  | 100 | GAL |  | 3746 CAMEO DR | OCEANSIDE | SD | SEWER MAN HOLE | GREASE CAUSED BLOCKAGE IN MAIN LINE; CONTEN | NO | NONE |  | STORM DRAIN | Y | N | NA | DOMESTIC WASTEWATER FLOWED OUT OF "PICK HOLES" |  | SAN DIEGO, CITY OF | 931213 | 1004PM | 931213 | 1104PM | 300 | GAL | 3832 FAIRMONT AVE | SAN DIEGO | SD | 8" PVC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | FLOW WENT TO STORM DRAIN AY CORNER OF 43RD AND
| 931214 | 0315PM | LUCKY BISHOP IV | 6197414854 | ESCONDIDO, CITY OF | 931213 | 1230PM | 931213 | 0230PM |  | 1200 | GAL |  | ESCONDIDO COUNTRY CLUB | ESCONDIDO | SD | SEWER ATLAS PAGE#410 MH#21 | GREASE IN MAIN SEWER LINE | NO | NONE |  | GROUND ABSORPTION | Y | ? |  | WASHED DOWN THE AREA WITH POTABLE WATER. |  | SAN DIEGO, CITY OF | 931213 | 0600PM | 931213 | 0700PM | 300 | GAL | 4765 TROJAN AVE | SAN DIEGO | SD | 10" CONCRETE SEWER MAIN | COLLAPSED SEWER MAIN=GRAVITY MAIN BREAK | STORM DRAIN, PACIFIC O | FLOW WENT TO SRORM DRAIN AT 4288*48TH ST AND S
| 931213 | 0835PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 931213 | 0800PM | 931213 | 1055PM |  | 25 | GAL |  | 935 & 937 S. WISCONSIN | FALLBROOK | SD | 4" CLEANOUT (ON PROPERTY) | ROOTS IN FSD'S 6" CLEANOUT | NO | NONE |  | ABOUT 120'DOWN CEMENT DRIVEWAY | N | N | NA | OPENED JUST INSIDE 6" CLEANOUT. NEED TO GET RO |  | OCEANSIDE, CITY OF | 931213 | 1600PM | 931213 | 1700PM | 100 | GAL | 3746 CAMEO DR | OCEANSIDE | SD | SEWER MAN HOLE | GREASE CAUSED BLOCKAGE IN MAIN LINE; CONTEN | NONE | DOMESTIC WASTEWATER FLOWED OUT OF "PICK HOLES"
| 931214 | 1600PM | JIM McCURLEY | 6195258687 | SAN DIEGO, CITY OF | 931214 | 1330PM | 931214 | 1430PM |  | 60 | GAL |  | ALLEY WEST OF 40TH N/O BOSTON | SAN DIEGO | SD | 6" CP SEWER LINE | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | MACHINE RODDED MAIN TO RELIEVE HEAVY GREASE BL |  | ESCONDIDO, CITY OF | 931213 | 1230PM | 931213 | 0230PM | 1200 | GAL | ESCONDIDO COUNTRY CLUB | ESCONDIDO | SD | SEWER ATLAS PAGE#410 MH#21 | GREASE IN MAIN SEWER LINE | NONE | WASHED DOWN THE AREA WITH POTABLE WATER.
| 931216 | 1300PM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 931215 | 1430PM | 931215 | 1600PM |  | 3000 | GAL |  | 3875 MISSION AVE,BACK EASEMENT | OCEANSIDE | SD | SEWER MAN HOLE | GREASE AND DEBRIS BLOCKED MAIN LINE; CONTEN | NO | NONE |  | WASTEWATER SOAKED INTO SOIL | Y | N | NA | DOMESTIC WASTEWATER FLOWED OUT OF MANHOLE LID, |  | FALLBROOK SANITARY DISTRICT | 931213 | 0800PM | 931213 | 1055PM | 25 | GAL | 935 & 937 S. WISCONSIN | FALLBROOK | SD | 4" CLEANOUT (ON PROPERTY) | ROOTS IN FSD'S 6" CLEANOUT | NONE | OPENED JUST INSIDE 6" CLEANOUT. NEED TO GET RO
| 931216 | 0838AM | JACK J. WILLIAMS | 6195258682 | SAN DIEGO, CITY OF | 931215 | 0104AM | 931215 | 1004AM |  | 3000 | GAL |  | 1089 SUNSET CLIFFS BLVD | SAN DIEGO | SD | 8' CP SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | Y | 02 | MACHINE RODDED MAIN |  | SAN DIEGO, CITY OF | 931214 | 1330PM | 931214 | 1430PM | 60 | GAL | ALLEY WEST OF 40TH N/O BOSTON | SAN DIEGO | SD | 6" CP SEWER LINE | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | MACHINE RODDED MAIN TO RELIEVE HEAVY GREASE BL
| 931220 | 0900AM | JOHN VAUGHT | 6197414854 | ESCONDIDO, CITY OF | 931217 | 1530PM | 931217 | 1730PM |  | 2400 | GAL |  | 2100 S. ESCONDIDO BLVD. | ESCONDIDO | SD | PRIVATE 3" CLEANOUT | PUMP FAILURE AT LIFT STATION#3. CAUSED A OV | Y | SOUTH ESC. CREEK, LAKE |  |  | Y | Y | 04 | CLEANED AND RAKED CONTAMINATED DIRT AREA, THEN |  | OCEANSIDE, CITY OF | 931215 | 1430PM | 931215 | 1600PM | 3000 | GAL | 3875 MISSION AVE,BACK EASEMENT | OCEANSIDE | SD | SEWER MAN HOLE | GREASE AND DEBRIS BLOCKED MAIN LINE; CONTEN | NONE | DOMESTIC WASTEWATER FLOWED OUT OF MANHOLE LID,
| 931219 | 1000AM | RICHARD ANDREWS | 6197553294 | DEL MAR, CITY OF | 931219 | 0615AM | 931219 | 0745AM |  | 1350 | GAL |  | 615 STRATFORD COURT | DEL MAR | SD | SEWER MAIN 6" | LINE OBSTRUCTION | Y | PACIFIC OCEAN |  |  | N | N | NA | OF THE 1350 GAL OF SEWAGE OVERFLOW MOST DISSIP |  | SAN DIEGO, CITY OF | 931215 | 0104AM | 931215 | 1004AM | 3000 | GAL | 1089 SUNSET CLIFFS BLVD | SAN DIEGO | SD | 8' CP SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | MACHINE RODDED MAIN
| 931219 | 0752AM | TELEMETERING ALARM | ? | FALLBROOK SANITARY DISTRICT | 931219 | 0752AM | 931219 | 0830AM |  | 200 | GAL |  | E. SHADY LN & DOURGHTY | FALLBROOK | SD | SHADY LN, LIFT STATION | DUMP LOCK AND SUBSEQUENT CIRCUIT OVERLOAD. | NO | NONE |  | DUG OUT RETAINING AREA | Y | N | NA | NONE |  | ESCONDIDO, CITY OF | 931217 | 1530PM | 931217 | 1730PM | 2400 | GAL | 2100 S. ESCONDIDO BLVD. | ESCONDIDO | SD | PRIVATE 3" CLEANOUT | PUMP FAILURE AT LIFT STATION#3. CAUSED A OV | SOUTH ESC. CREEK, LAKE | CLEANED AND RAKED CONTAMINATED DIRT AREA, THEN
| 931220 | 1600PM | D A BRANCO | 6195258687 | SAN DIEGO, CITY OF | 931220 | 1135AM | 931220 | 1325PM |  | 1500 | GAL |  | KORINK AVE/MERYON ST | SAN DIEGO | SD | 8" VC SEWER MAIN | DEBRIS BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | RODDED MAIN |  | DEL MAR, CITY OF | 931219 | 0615AM | 931219 | 0745AM | 1350 | GAL | 615 STRATFORD COURT | DEL MAR | SD | SEWER MAIN 6" | LINE OBSTRUCTION | PACIFIC OCEAN | OF THE 1350 GAL OF SEWAGE OVERFLOW MOST DISSIP
| 931220 | 0600PM | POLICE DEPARTMENT | 6197414722 | ESCONDIDO, CITY OF | 931220 | 0530PM | 931220 | 0710PM |  | 455 | GAL |  | 950 MARTIN ST | ESCONDIDO | SD | SEWER ATLAS PG.21, CLEANOUT | GREASE AND PAPER | NO | NONE |  | CONTAINED IN BACKYARD. | Y | ? |  | TREATED AFFECTED AREA. CONTAINED IN BACKYARD. |  | FALLBROOK SANITARY DISTRICT | 931219 | 0752AM | 931219 | 0830AM | 200 | GAL | E. SHADY LN & DOURGHTY | FALLBROOK | SD | SHADY LN, LIFT STATION | DUMP LOCK AND SUBSEQUENT CIRCUIT OVERLOAD. | NONE | NONE
| 931222 | 1248AM | D. A. BRANCO | 6195258687 | SAN DIEGO, CITY OF | 931221 | 1653PM | 931221 | 2353PM |  | 4200 | GAL |  | MURRAY PARK DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | SAN DIEGO RIVER, PACIF |  |  | Y | Y | ? | RODDED MAIN-SEWAGE DID NOT REACH LAKE MURRAY R |  | SAN DIEGO, CITY OF | 931220 | 1135AM | 931220 | 1325PM | 1500 | GAL | KORINK AVE/MERYON ST | SAN DIEGO | SD | 8" VC SEWER MAIN | DEBRIS BLOCKAGE | STORM DRAIN, PACIFIC O | RODDED MAIN
| 931221 | 1935PM | DOUGLAS BRANCO | 6195258687 | SAN DIEGO, CITY OF | 931221 | 1206PM | 931221 | 1656PM |  | 4350 | GAL |  | 4230 MONTALVO ST | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | FAMOSA SLOUGH, PACIFIC |  |  | Y | Y | ? | FLUSHED MAIN |  | ESCONDIDO, CITY OF | 931220 | 0530PM | 931220 | 0710PM | 455 | GAL | 950 MARTIN ST | ESCONDIDO | SD | SEWER ATLAS PG.21, CLEANOUT | GREASE AND PAPER | NONE | TREATED AFFECTED AREA. CONTAINED IN BACKYARD.
| 931223 | 0245AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931222 | 1552PM | 931222 | 1652PM |  | 30 | GAL |  | 738 ROSECRANS | SAN DIEGO | SD | 6" VC SEWER MAIN | ROOT BLOCKAGE | Y | SOAKED INTO GROUND, OC |  |  | Y | N | NA | HAND RODDED 10' TO RELIEVE HEAVY ROOT STOP. |  | SAN DIEGO, CITY OF | 931221 | 1653PM | 931221 | 2353PM | 4200 | GAL | MURRAY PARK DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | SAN DIEGO RIVER, PACIF | RODDED MAIN-SEWAGE DID NOT REACH LAKE MURRAY R
| 931223 | 2107PM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 931223 | 1532PM | 931223 | 1932PM |  | 2400 | GAL |  | 232 54TH ST | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | FLUSHED MAIN |  | SAN DIEGO, CITY OF | 931221 | 1206PM | 931221 | 1656PM | 4350 | GAL | 4230 MONTALVO ST | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | FAMOSA SLOUGH, PACIFIC | FLUSHED MAIN
| 931223 | 1630PM | JACK SWERLEIN | 6195388187 | SAN DIEGO, CITY OF | 931223 | 1030AM | 931223 | 1430PM |  | 67000 | GAL |  | 1403 HIGHLAND VALLEY ROAD | SAN DIEGO | SD | ? | BREAK IN UNDERGROUNG LINE-CAUSE OF BREAK NO | Y | SYCAMORE CREEK |  |  | N | N | NA | NONE |  | SAN DIEGO, CITY OF | 931222 | 1552PM | 931222 | 1652PM | 30 | GAL | 738 ROSECRANS | SAN DIEGO | SD | 6" VC SEWER MAIN | ROOT BLOCKAGE | SOAKED INTO GROUND, OC | HAND RODDED 10' TO RELIEVE HEAVY ROOT STOP.
| 931227 | ? | MARK A. SROFFER | 6197254806 | CAMP PENDLETON MARINE BASE | 931224 | 0200AM | 931224 | 0330AM |  | 2000 | GAL |  | VANDERGRIFT | CAMP PENDLETON | SD | WASTEWATER PLANT#13-2083 | SLUDGE BED GATE BOARDS LEAKING THRU | NO | NONE |  | FIELD AND HEAVY BRUSH | Y | N | NA | RESET BOARDS-CLEANED AND LINED AREA |  | SAN DIEGO, CITY OF | 931223 | 1532PM | 931223 | 1932PM | 2400 | GAL | 232 54TH ST | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | FLUSHED MAIN
| 931227 | 1015AM | LUCKY BISHOP IV | 6197414854 | ESCONDIDO, CITY OF | 931224 | 0130PM | 931224 | 0215PM |  | 2125 | GAL |  | 30*IRIS CROSS ST. FOREST GLEN. | ESCONDIDO | SD | ESCON. SEWER ATLAS PG#151,MH30 | ROOTS AND GREASE | Y | REIDY CANYON CREEK,SAN |  |  | Y | Y | 10 | AREA WASHED AND DISINFECTED. |  | SAN DIEGO, CITY OF | 931223 | 1030AM | 931223 | 1430PM | 67000 | GAL | 1403 HIGHLAND VALLEY ROAD | SAN DIEGO | SD | ? | BREAK IN UNDERGROUNG LINE-CAUSE OF BREAK NO | SYCAMORE CREEK | NONE
| 931227 | 1030PM | LUCKY BISHOP IV | 6197414854 | ESCONDIDO, CITY OF | 931224 | 1130AM | 931224 | 0115PM |  | 1575 | GAL |  | ALLEY B/W 5TH & 6TH ST * MAPLE | ESCONDIDO | SD | ESCON. SEWER ATLAS PG#2,MH#19A | GREASE AND ROOTS | Y | ESCON. CREEK,SAN ELIJO |  |  | Y | Y | 10 | AREA WAS WASHED DOWN AND VACUUMED UP THEN DISI |  | CAMP PENDLETON MARINE BASE | 931224 | 0200AM | 931224 | 0330AM | 2000 | GAL | VANDERGRIFT | CAMP PENDLETON | SD | WASTEWATER PLANT#13-2083 | SLUDGE BED GATE BOARDS LEAKING THRU | NONE | RESET BOARDS-CLEANED AND LINED AREA
| 931225 | 2100PM | JIM McCURLEY | 6195258687 | SAN DIEGO, CITY OF | 931225 | 1327PM | 931225 | 1627PM |  | 900 | GAL |  | 5715 HUGHES ST. | SAN DIEGO | SD | SEWER LINE 8" VC | DEBRIS BLOCKAGE | Y | PACIFIC OCEAN |  |  | Y | N | NA | AREA WAS DEODORIZED. |  | ESCONDIDO, CITY OF | 931224 | 0130PM | 931224 | 0215PM | 2125 | GAL | 30*IRIS CROSS ST. FOREST GLEN. | ESCONDIDO | SD | ESCON. SEWER ATLAS PG#151,MH30 | ROOTS AND GREASE | REIDY CANYON CREEK,SAN | AREA WASHED AND DISINFECTED.
| 931225 | 2100PM | JIM McCURLEY | 6195258687 | SAN DIEGO, CITY OF | 931225 | 1155AM | 931225 | 1455PM |  | 2700 | GAL |  | 1631 BAYVIEW HTS. DR. | SAN DIEGO | SD | SEWER LINE 8" VC | GREASE BLOCKAGE | Y | PACIFIC OCEAN |  |  | Y | N | NA | AREA WAS DEODORIZED. |  | ESCONDIDO, CITY OF | 931224 | 1130AM | 931224 | 0115PM | 1575 | GAL | ALLEY B/W 5TH & 6TH ST * MAPLE | ESCONDIDO | SD | ESCON. SEWER ATLAS PG#2,MH#19A | GREASE AND ROOTS | ESCON. CREEK,SAN ELIJO | AREA WAS WASHED DOWN AND VACUUMED UP THEN DISI
| 931225 | 1630PM | JIM McCURLEY | 6195258687 | SAN DIEGO, CITY OF | 931225 | 1148AM | 931225 | 1400PM |  | 132 | GAL |  | 400 GLORIA ST. | SAN DIEGO | SD | SEWER LINE 6" VC | GREASE BLOCKAGE | Y | SOME SETTLED IN SOIL, |  |  | Y | N | NA | AREA WAS CLEANED AND DEODORIZED. |  | SAN DIEGO, CITY OF | 931225 | 1327PM | 931225 | 1627PM | 900 | GAL | 5715 HUGHES ST. | SAN DIEGO | SD | SEWER LINE 8" VC | DEBRIS BLOCKAGE | PACIFIC OCEAN | AREA WAS DEODORIZED.
| 931227 | 1000AM | LUCKY BISHOP IV | 6197414854 | ESCONDIDO, CITY OF | 931225 | 0600AM | 931225 | 0425PM |  | 1890 | GAL |  | 1400 HAMILTON*EUCALYPTUS AVE. | ESCONDIDO | SD | FORCE MAIN PLAN#1649,ESC. P.31 | CRACKED PRESSURIZED FORCE MAIN 6" PIPE. | Y | FELICITA CREEK, LAKE H |  |  | Y | Y | 03 | SEWER ENTERED STORM DRAIN WITHIN 50'OF CRACKED |  | SAN DIEGO, CITY OF | 931225 | 1155AM | 931225 | 1455PM | 2700 | GAL | 1631 BAYVIEW HTS. DR. | SAN DIEGO | SD | SEWER LINE 8" VC | GREASE BLOCKAGE | PACIFIC OCEAN | AREA WAS DEODORIZED.
| 931227 | 0900AM | ORV SALISBURY | 6197440460 | VALLECITOS WATER DISTRICT | 931226 | 0310PM | 931226 | 0600PM |  | 5000 | GAL |  | VIA BRISA DEL LAGO | SAN MARCOS | SD | S38-Q6-MH5,THOMAS-P20-F2 | GRAVITY SEWER LINE BLOCKAGE JUST OUTSIDE TH | Y | LAKE SAN MARCOS |  |  | Y | Y | 07 | THERE IS NO BODY CONTACT IN THIS LAKE, THE BLO |  | SAN DIEGO, CITY OF | 931225 | 1148AM | 931225 | 1400PM | 132 | GAL | 400 GLORIA ST. | SAN DIEGO | SD | SEWER LINE 6" VC | GREASE BLOCKAGE | SOME SETTLED IN SOIL, | AREA WAS CLEANED AND DEODORIZED.
| 931228 | 0900AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 931227 | 1319PM | 931227 | 2030PM |  | 10775 | GAL |  | 40TH ST EL CAJON BLVD. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | RODDED MAIN BY MACHIN. VACTORED UP STANDING WA |  | ESCONDIDO, CITY OF | 931225 | 0600AM | 931225 | 0425PM | 1890 | GAL | 1400 HAMILTON*EUCALYPTUS AVE. | ESCONDIDO | SD | FORCE MAIN PLAN#1649,ESC. P.31 | CRACKED PRESSURIZED FORCE MAIN 6" PIPE. | FELICITA CREEK, LAKE H | SEWER ENTERED STORM DRAIN WITHIN 50'OF CRACKED
| 931227 | 1730PM | JIM McCURLEY | 6195258687 | SAN DIEGO, CITY OF | 931227 | 1026AM | 931227 | 1600PM |  | 167 | GAL |  | 45TH AND MARKET | SAN DIEGO | SD | SEWER LINE 6" | GRAVITY MAIN BREAK | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | AREA WAS WASHED DOWN AND DEODORIZED. REPAIR CR |  | VALLECITOS WATER DISTRICT | 931226 | 0310PM | 931226 | 0600PM | 5000 | GAL | VIA BRISA DEL LAGO | SAN MARCOS | SD | S38-Q6-MH5,THOMAS-P20-F2 | GRAVITY SEWER LINE BLOCKAGE JUST OUTSIDE TH | LAKE SAN MARCOS | THERE IS NO BODY CONTACT IN THIS LAKE, THE BLO
| 931229 | 0800AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 931228 | 1056AM | 931228 | 1256PM |  | 6000 | GAL |  | 4484 ORANGE AVE. | SAN DIEGO | SD | 8" PVC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | MACHINED RODDED MAIN AND DEODORIZED AREA. |  | SAN DIEGO, CITY OF | 931227 | 1319PM | 931227 | 2030PM | 10775 | GAL | 40TH ST EL CAJON BLVD. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | RODDED MAIN BY MACHIN. VACTORED UP STANDING WA
| 931230 | 1045AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 931229 | 1701PM | 931229 | 1830PM |  | 1335 | GAL |  | 3128 JUNIPER ST | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | Y | PACIFIC OCEAN |  |  | Y | Y | ? | RODDED MAIN DEODORIZED STREET AND ALLEY. |  | SAN DIEGO, CITY OF | 931227 | 1026AM | 931227 | 1600PM | 167 | GAL | 45TH AND MARKET | SAN DIEGO | SD | SEWER LINE 6" | GRAVITY MAIN BREAK | STORM DRAIN, PACIFIC O | AREA WAS WASHED DOWN AND DEODORIZED. REPAIR CR
| 931230 | 0745AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 931229 | 0906AM | 931229 | 1130AM |  | 7200 | GAL |  | 400 SO. 38TH ST | SAN DIEGO | SD | 6" CP | ROOTS BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | RODDED MAIN BY MACHINE. |  | SAN DIEGO, CITY OF | 931228 | 1056AM | 931228 | 1256PM | 6000 | GAL | 4484 ORANGE AVE. | SAN DIEGO | SD | 8" PVC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | MACHINED RODDED MAIN AND DEODORIZED AREA.
| 931230 | 0740AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 931229 | 1051AM | 931229 | 1300PM |  | 645 | GAL |  | 2435 JEFFERSON ST | SAN DIEGO | SD | 6" VO SEWER MAIN | DEBRIS BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | RODDED BY MACHINE AND DISINFECTED AREA. |  | SAN DIEGO, CITY OF | 931229 | 1701PM | 931229 | 1830PM | 1335 | GAL | 3128 JUNIPER ST | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | PACIFIC OCEAN | RODDED MAIN DEODORIZED STREET AND ALLEY.
| 931229 | 1630PM | JIM McCURLEY | 6195258687 | SAN DIEGO, CITY OF | 931229 | 1121AM | 931229 | 1251PM |  | 900 | GAL |  | 54TH AND HANIMAN DR. | SAN DIEGO | SD | SEWER LINE 8" VC | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | FLUSHED 203'SECTION, RELIEVED STOP, WASHED DOW |  | SAN DIEGO, CITY OF | 931229 | 0906AM | 931229 | 1130AM | 7200 | GAL | 400 SO. 38TH ST | SAN DIEGO | SD | 6" CP | ROOTS BLOCKAGE | STORM DRAIN, PACIFIC O | RODDED MAIN BY MACHINE.
| 931229 | 1630PM | JIM McCURLEY | 6195258687 | SAN DIEGO, CITY OF | 931229 | 1101AM | 931229 | 1201PM |  | 180 | GAL |  | 6160 MISSION GORGE | SAN DIEGO | SD | SEWER LINE 8" VC | GREASE BLOCKAGE | Y | PACIFIC OCEAN |  |  | Y | N | NA | MACHINE RODDED, RELIEVED STOP, AND DEODORIZED |  | SAN DIEGO, CITY OF | 931229 | 1051AM | 931229 | 1300PM | 645 | GAL | 2435 JEFFERSON ST | SAN DIEGO | SD | 6" VO SEWER MAIN | DEBRIS BLOCKAGE | STORM DRAIN, PACIFIC O | RODDED BY MACHINE AND DISINFECTED AREA.
| 931230 | 1500PM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 931230 | 1020AM | 931230 | 1100AM |  | 40 | GAL |  | 6302 CELIA VISTA DR. | SAN DIEGO | SD | 6" VC SEWER MAIN | ROCK BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | OVERFLOW HAD STOPPED WHEN CREW ARRIVED. RODDED |  | SAN DIEGO, CITY OF | 931229 | 1121AM | 931229 | 1251PM | 900 | GAL | 54TH AND HANIMAN DR. | SAN DIEGO | SD | SEWER LINE 8" VC | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | FLUSHED 203'SECTION, RELIEVED STOP, WASHED DOW
| 931230 | 0245PM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 931230 | 1002AM | 931230 | 1130AM |  | 440 | GAL |  | 5011 WARING RD. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | RODDED MAIN BY MACHINE. |  | SAN DIEGO, CITY OF | 931229 | 1101AM | 931229 | 1201PM | 180 | GAL | 6160 MISSION GORGE | SAN DIEGO | SD | SEWER LINE 8" VC | GREASE BLOCKAGE | PACIFIC OCEAN | MACHINE RODDED, RELIEVED STOP, AND DEODORIZED
| 940103 | 0730AM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 931231 | 1012AM | 931231 | 1100AM |  | 480 | GAL |  | 42ND & DELTA ALLEY NORTH | SAN DIEGO | SD | 6" CP MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | OVERFLOW CONTAINED IN CANYON. OVERFLOW UNABLE |  | SAN DIEGO, CITY OF | 931230 | 1020AM | 931230 | 1100AM | 40 | GAL | 6302 CELIA VISTA DR. | SAN DIEGO | SD | 6" VC SEWER MAIN | ROCK BLOCKAGE | STORM DRAIN, PACIFIC O | OVERFLOW HAD STOPPED WHEN CREW ARRIVED. RODDED
| 940103 | 1300PM | SENIOR, JAY | 6195258682 | SAN DIEGO, CITY OF | 940101 | 1953PM | 940101 | 2400PM |  | 2470 | GAL |  | 5056 WIGHTMAN ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | DISSINFECTED AREA |  | SAN DIEGO, CITY OF | 931230 | 1002AM | 931230 | 1130AM | 440 | GAL | 5011 WARING RD. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | RODDED MAIN BY MACHINE.
| 940103 |  |  |  | SANTA MARGARITA WATER DIST. | 940101 | 1535PM | 940101 | 1710PM |  | 100 | GAL |  | SANTA MARGARITA PARKWAY | MISSION VIEGO | OR | MH#771.22 | GREASE BLOCKAGE | NO | NONE |  | ? | Y | N | NA | SPILL CONTAINED, SOLIDS VACTORED UP, AFFECTED |  | SAN DIEGO, CITY OF | 931231 | 1012AM | 931231 | 1100AM | 480 | GAL | 42ND & DELTA ALLEY NORTH | SAN DIEGO | SD | 6" CP MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | OVERFLOW CONTAINED IN CANYON. OVERFLOW UNABLE
| 940102 | 0240PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DIST. | 940102 | 0200PM | 940102 | 0305PM |  | 3 | GAL |  | 1197 SENWOOD | FALLBROOK | SD | 4" CLEANOUT | ROOTS IN LATERAL | NO | NONE |  | SOAKED INTO GROUND BY CLEANOUT | N | N | NA | OPENED 8' NORTH CLEANOUT, HAD ROOTS, BUT NO TR |  | SAN DIEGO, CITY OF | 940101 | 1953PM | 940101 | 2400PM | 2470 | GAL | 5056 WIGHTMAN ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, PACIFIC O | DISSINFECTED AREA
| 940104 | 1100AM | RODERICK W. STEELE | 6197414854 | ESCONDIDO, CITY OF | 940103 | 0700PM | 910103 | 0830PM |  | 15750 | GAL |  | 1062 LINCOLN | ESCONDIDO | SD | SEWER ATLAS PG.21 MH#5 | GREASE BLOCKAGE | Y | ESCONDIDO CREEK, SD LA |  |  | Y | Y | 05 | AREA WAS WASHED DOWM AND CONTAINED, THEN AREA |  | SANTA MARGARITA WATER DIST. | 940101 | 1535PM | 940101 | 1710PM | 100 | GAL | SANTA MARGARITA PARKWAY | MISSION VIEGO | OR | MH#771.22 | GREASE BLOCKAGE | NONE | SPILL CONTAINED, SOLIDS VACTORED UP, AFFECTED
| 940104 | 0900AM | CUSTOMER |  | PADRE DAM MUNICIPAL WATER DIST | 940104 | 0830AM | 940104 | 1100AM |  | 10 | GPM |  | SOUTH OF 8212 MESA RD. | SANTEE | SD | SEWER LINE MH FROM 6" MAIN | ROCKS IN 6" MAIN LINE | NO | NONE |  | ROAD AREA AROUND MANHOLE | N | N | NA | AREA WAS CLEANED AND TREATED WITH CHLORINE. |  | FALLBROOK SANITARY DIST. | 940102 | 0200PM | 940102 | 0305PM | 3 | GAL | 1197 SENWOOD | FALLBROOK | SD | 4" CLEANOUT | ROOTS IN LATERAL | NONE | OPENED 8' NORTH CLEANOUT, HAD ROOTS, BUT NO TR
| 940106 | 0715AM | LUCKY BISHOP IV | 6197414654 | ESCONDIDO, CITY OF | 940104 | 0245PM | 940104 | 0315PM |  | 150 | GAL |  | 121 FELICITA AVE. | ESCONDIDO | SD | SEWER ATLAS PG. 28 MH#73 | PAPER IN SEWER MAIN LINE POSSIBLY X-MAS WRA | NO | NONE |  | VACUUMED INTO VACTOR TRUCK | Y | N | NA | WASHEDDOWN STREET AND THEN VACUUMED. |  | ESCONDIDO, CITY OF | 940103 | 0700PM | 910103 | 0830PM | 15750 | GAL | 1062 LINCOLN | ESCONDIDO | SD | SEWER ATLAS PG.21 MH#5 | GREASE BLOCKAGE | ESCONDIDO CREEK, SD LA | AREA WAS WASHED DOWM AND CONTAINED, THEN AREA
| 940106 | 0800AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 940105 | 1358PM | 940105 | 1630PM |  | 152 | GAL |  | 3017 30TH ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM CHANNEL, PACIFIC |  |  | Y | N | NA | MACHINE AND HAND RODDED MAIN TO RELIEVE STOP. |  | PADRE DAM MUNICIPAL WATER DIST | 940104 | 0830AM | 940104 | 1100AM | 10 | GPM | SOUTH OF 8212 MESA RD. | SANTEE | SD | SEWER LINE MH FROM 6" MAIN | ROCKS IN 6" MAIN LINE | NONE | AREA WAS CLEANED AND TREATED WITH CHLORINE.
| 940106 | 0745AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 940105 | 1350PM | 940105 | 1450PM |  | 600 | GAL |  | 49TH / FEDERAL BLVD | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | RODDED MAIN BY MACHINE AND DEODORIZED AREA OVE |  | ESCONDIDO, CITY OF | 940104 | 0245PM | 940104 | 0315PM | 150 | GAL | 121 FELICITA AVE. | ESCONDIDO | SD | SEWER ATLAS PG. 28 MH#73 | PAPER IN SEWER MAIN LINE POSSIBLY X-MAS WRA | NONE | WASHEDDOWN STREET AND THEN VACUUMED.
| 940113 | 1500 | F PADUA | 6195277443 | SAN DIEGO, CITY OF | 940106 | 1415PM | 940113 | 1300PM |  | 10 | GAL |  | 3838 FRANKLING AVE. | SAN DIEGO | SD | 4" SEWER LATERAL | BROKEN SEWER LATERAL BENEATH ST. | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | PROBLEM WAS ORIGINALLY REPORTED AS A METER LEA |  | SAN DIEGO, CITY OF | 940105 | 1358PM | 940105 | 1630PM | 152 | GAL | 3017 30TH ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | ROOT BLOCKAGE | STORM CHANNEL, PACIFIC | MACHINE AND HAND RODDED MAIN TO RELIEVE STOP.
| 940106 | 1445PM | GARRY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 940106 | 0200AM | 940106 | 0925AM |  | 2000 | GAL |  | 3222 MORNINGSIDE DR. | OCEANSIDE | SD | SEWER MAN HOLE | GREASE BLOCKAGE | Y | UNNAMED CHANNEL,BUENA |  |  | Y | N | NA | DOMESTIC WASTEWATER FLOWED OUT OF "PICK HOLES" |  | SAN DIEGO, CITY OF | 940105 | 1350PM | 940105 | 1450PM | 600 | GAL | 49TH / FEDERAL BLVD | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, PACIFIC O | RODDED MAIN BY MACHINE AND DEODORIZED AREA OVE
| 940107 | 1800PM | JIM McCURLEY | 6195258687 | SAN DIEGO, CITY OF | 940106 | 1453PM | 940107 | 1100AM |  | 1217 | GAL |  | 4374 ARCADIA DR. | SAN DIEGO | SD | SEWER LINE 6" CP | ROOT BLOCKAGE | Y | MH#15013, PACIFIC OCEA |  |  | Y | N | NA | MACHINE AND HAND RODDED 6" CP MAIN TO RELIEVE |  | SAN DIEGO, CITY OF | 940106 | 1415PM | 940113 | 1300PM | 10 | GAL | 3838 FRANKLING AVE. | SAN DIEGO | SD | 4" SEWER LATERAL | BROKEN SEWER LATERAL BENEATH ST. | STORM DRAIN, PACIFIC O | PROBLEM WAS ORIGINALLY REPORTED AS A METER LEA
| 940107 | 1415PM | LEO HARRIS | 6195258685 | SAN DIEGO, CITY OF | 940107 | 0930AM | 940107 | 1100AM |  | 90 | GAL |  | 3883 INGRAHM ST. | SAN DIEGO | SD | 8" VC | ROOTS IN 98FT SECT | Y | DRAIN SYSTEM, MISSION |  |  | Y | N | NA | DEODORIZED AREA. |  | OCEANSIDE, CITY OF | 940106 | 0200AM | 940106 | 0925AM | 2000 | GAL | 3222 MORNINGSIDE DR. | OCEANSIDE | SD | SEWER MAN HOLE | GREASE BLOCKAGE | UNNAMED CHANNEL,BUENA | DOMESTIC WASTEWATER FLOWED OUT OF "PICK HOLES"
| 940108 | 1143AM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 940108 | 1130AM | 940108 | 1220PM |  | 2 | GAL |  | 500 DEBBYST. | FALLBROOK | SD | 4" CLEANOUT | POSSIBLE ROOTS | NO | NONE |  | AROUND CLEANOUT BOX | N | N | NA | OPENED 10'WEST OF CLEANOUT, COMPLETED AT 1230P |  | SAN DIEGO, CITY OF | 940106 | 1453PM | 940107 | 1100AM | 1217 | GAL | 4374 ARCADIA DR. | SAN DIEGO | SD | SEWER LINE 6" CP | ROOT BLOCKAGE | MH#15013, PACIFIC OCEA | MACHINE AND HAND RODDED 6" CP MAIN TO RELIEVE
| 940109 | 0830PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 940109 | 0214PM | 940109 | 0614PM |  | 1200 | GAL |  | 3578 GILLETE ST. | SAN DIEGO | SD | 6" PV | DEBRIS BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | NA | FLOW WENT INTO CANYON DIRT AND DRIED. |  | SAN DIEGO, CITY OF | 940107 | 0930AM | 940107 | 1100AM | 90 | GAL | 3883 INGRAHM ST. | SAN DIEGO | SD | 8" VC | ROOTS IN 98FT SECT | DRAIN SYSTEM, MISSION | DEODORIZED AREA.
| 940109 | 0520PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 940109 | 1133AM | 940109 | 0400PM |  | 534 | GAL |  | 35TH ST. & MONROE AVE. | SAN DIEGO | SD | 6" CP SEWER MAIN | DEBRIS BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | FLOWED INTO STORM DRAIN AT MEADE AND BANCROFT. |  | FALLBROOK SANITARY DISTRICT | 940108 | 1130AM | 940108 | 1220PM | 2 | GAL | 500 DEBBYST. | FALLBROOK | SD | 4" CLEANOUT | POSSIBLE ROOTS | NONE | OPENED 10'WEST OF CLEANOUT, COMPLETED AT 1230P
| 940110 | 0800AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 940109 | 1800PM | 940109 | 2330PM |  | 1605 | GAL |  | 1927 FLORIDA ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | Y | SOAKED INTO CREEK, PAC |  |  | Y | N | NA | MACINE RODDED AND DEODORIZED CLEANOUT AND CREE |  | SAN DIEGO, CITY OF | 940109 | 0214PM | 940109 | 0614PM | 1200 | GAL | 3578 GILLETE ST. | SAN DIEGO | SD | 6" PV | DEBRIS BLOCKAGE | CANYON, PACIFIC OCEAN | FLOW WENT INTO CANYON DIRT AND DRIED.
| 940111 | 1230PM | CITY OF CHULA VISTA | 6196915027 | PRIVATE LATERAL | 940110 | ? | 940110 | 1130PM |  | 500 | GAL |  | 570 MARINA PARKWAY | CHULA VISTA | SD | CLEANOUT | GREASE BLOCKAGE | Y | CHULA VISTA HARBOR |  |  | Y | ? |  | CALLED KATHY STONE ON 940111 AT 230PM. |  | SAN DIEGO, CITY OF | 940109 | 1133AM | 940109 | 0400PM | 534 | GAL | 35TH ST. & MONROE AVE. | SAN DIEGO | SD | 6" CP SEWER MAIN | DEBRIS BLOCKAGE | STORM DRAIN, PACIFIC O | FLOWED INTO STORM DRAIN AT MEADE AND BANCROFT.
| 940111 | 1515PM | LEO HARRIS | 6195258685 | SAN DIEGO, CITY OF | 940110 | 2019PM | 940111 | 1130AM |  | 4555 | GAL |  | 4251 ROBBINS ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | NA | DEODORIZED AREA. |  | SAN DIEGO, CITY OF | 940109 | 1800PM | 940109 | 2330PM | 1605 | GAL | 1927 FLORIDA ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | SOAKED INTO CREEK, PAC | MACINE RODDED AND DEODORIZED CLEANOUT AND CREE
| 940111 | 0830PM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 940110 | 0832AM | 940110 | 1050AM |  | 138 | GAL |  | 4300 FALCON ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | BROKEN 4" PIPE, STUCK INSIDE MAIN. | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | MACHINE RODDED TO REMOVE OBSTRUCTION CAUSED BY |  | PRIVATE LATERAL | 940110 | ? | 940110 | 1130PM | 500 | GAL | 570 MARINA PARKWAY | CHULA VISTA | SD | CLEANOUT | GREASE BLOCKAGE | CHULA VISTA HARBOR | CALLED KATHY STONE ON 940111 AT 230PM.
| 940111 | 0930AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 940110 | 1120AM | 940110 | 1830PM |  | 2150 | GAL |  | 10460 CLAIREMONT MESA BLVD. | SAN DIEGO | SD | 18" VC SEWER MAIN | GREASE BLOCKAGE | Y | CREEK IN CANYON, PACIF |  |  | Y | N | NA | HAND RODDED/CLEAN DEBRIS FROM MANHOLE. |  | SAN DIEGO, CITY OF | 940110 | 2019PM | 940111 | 1130AM | 4555 | GAL | 4251 ROBBINS ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | CANYON, PACIFIC OCEAN | DEODORIZED AREA.
| 0 | ? | ? | ? | SANTA MARGARITA WATER DISTRICT | 940110 | 0730AM | 940110 | 0930AM |  | 2400 | GAL |  | OSO VIEJO & LA PAZ | MISSION VIEJO | OR | MANHOLE | CONSTRUCTION DEDRIS. | Y | STORM DRAIN, OSO CREEK |  |  | Y | ? |  | SOLIDS AND WATER WERE VACTURED. WASHDOWN WATER |  | SAN DIEGO, CITY OF | 940110 | 0832AM | 940110 | 1050AM | 138 | GAL | 4300 FALCON ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | BROKEN 4" PIPE, STUCK INSIDE MAIN. | STORM DRAIN, PACIFIC O | MACHINE RODDED TO REMOVE OBSTRUCTION CAUSED BY
| 940110 | 0400PM | DISTRICT OFFICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 940110 | 0345PM | 940110 | 04300P |  | 25 | GAL |  | 562 AMMUNITION RD. | SAN DIEGO | SD | 6" CLEANOUT | GREASE IN LATERAL | NO | NONE |  | SOAKED AROUND CLEANOUT | N | N | NA | OPENED 30'NORTH CLEANOUT. TOLD MANAGER THAT TE |  | SAN DIEGO, CITY OF | 940110 | 1120AM | 940110 | 1830PM | 2150 | GAL | 10460 CLAIREMONT MESA BLVD. | SAN DIEGO | SD | 18" VC SEWER MAIN | GREASE BLOCKAGE | CREEK IN CANYON, PACIF | HAND RODDED/CLEAN DEBRIS FROM MANHOLE.
| 940111 | 1535PM | LEONARD MOORE | 6195258687 | SAN DIEGO, CITY OF | 940111 | 0721AM | 940111 | 0900AM |  | 495 | GAL |  | 6035 FOLSOM DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOTBOUND | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | RODDED BY MACHINE. |  | SANTA MARGARITA WATER DISTRICT | 940110 | 0730AM | 940110 | 0930AM | 2400 | GAL | OSO VIEJO & LA PAZ | MISSION VIEJO | OR | MANHOLE | CONSTRUCTION DEDRIS. | STORM DRAIN, OSO CREEK | SOLIDS AND WATER WERE VACTURED. WASHDOWN WATER
| 940111 | 1515PM | LEO HARIS | 6195258685 | SAN DIEGO, CITY OF | 940111 | 2030PM | 940111 | 1130AM |  | 4500 | GAL |  | 4251 ROBBIN ST. | SAN DIEGO | SD | 8" VC 130' SECT | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | DEODORIZED AREA. |  | FALLBROOK SANITARY DISTRICT | 940110 | 0345PM | 940110 | 04300P | 25 | GAL | 562 AMMUNITION RD. | SAN DIEGO | SD | 6" CLEANOUT | GREASE IN LATERAL | NONE | OPENED 30'NORTH CLEANOUT. TOLD MANAGER THAT TE
| 940113 | 0321AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 940112 | 1437PM | 940112 | 1637PM |  | 600 | GAL |  | ALTA VIEW & PARIS | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | RODDED MAIN TO CLEAR BLOCKAGE. |  | SAN DIEGO, CITY OF | 940111 | 0721AM | 940111 | 0900AM | 495 | GAL | 6035 FOLSOM DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOTBOUND | STORM DRAIN, PACIFIC O | RODDED BY MACHINE.
| 940114 | 1000AM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 940112 | 2130PM | 940114 | 1000AM |  | 300 | GAL |  | ALLEY BEHIND 414 GRANT ST. | OCEANSIDE | SD | SEWER CLEANOUT | HOLE BUSTED IN TOP OF "CLEAN-OUT" CAP. | NO | NONE |  | STORM DRAIN | Y | N | NA | FECES AND WASTEWATER RESIDUE REMAINED ON PRIVA |  | SAN DIEGO, CITY OF | 940111 | 2030PM | 940111 | 1130AM | 4500 | GAL | 4251 ROBBIN ST. | SAN DIEGO | SD | 8" VC 130' SECT | ROOT BLOCKAGE | STORM DRAIN, PACIFIC O | DEODORIZED AREA.
| 940114 | 1130AM | SENIOR JAY | 6195258682 | SAN DIEGO, CITY OF | 940113 | 1359PM | 940114 | 0859AM |  | 57000 | GAL |  | 1200 PAXTON DR. | SAN DIEGO | SD | 12" VC SEWER MAIN | VANDALISM OF SEWER MANHOLE. | Y | CONTROL CHANNEL, OTAY |  |  | Y | Y | 50 | OVER FLOW STOPPED AT CERRISA ST. SOUTH OF CANT |  | SAN DIEGO, CITY OF | 940112 | 1437PM | 940112 | 1637PM | 600 | GAL | ALTA VIEW & PARIS | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | RODDED MAIN TO CLEAR BLOCKAGE.
| 940113 | 1545PM | SENIOR JAY | 6195258682 | SAN DIEGO, CITY OF | 940113 | 0849AM | 940113 | 1030AM |  | 524 | GAL |  | 6102 LA PINTURA DR. | SAN DIEGO | SD | 8" VC MAIN CLEAN OUT | ROOT BLOCKAGE | Y | SOAKED INTO GROUND, PA |  |  | Y | N | NA | NONE |  | OCEANSIDE, CITY OF | 940112 | 2130PM | 940114 | 1000AM | 300 | GAL | ALLEY BEHIND 414 GRANT ST. | OCEANSIDE | SD | SEWER CLEANOUT | HOLE BUSTED IN TOP OF "CLEAN-OUT" CAP. | NONE | FECES AND WASTEWATER RESIDUE REMAINED ON PRIVA
| 940117 | 1300PM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 940114 | 1030AM | 940114 | 1045AM |  | 80 | GAL |  | 100 BLK OF COLLEGE BLVD. | OCEANSIDE | SD | END OF SEVERED SEWER MAIN. | CRACKS IN SEWER MAIN & LEAKS AROUND "PLUG". | Y | SAN LUIS REY RIVER |  |  | Y | N | NA | DOMESTIC WASTEWATER FLOWED INTO THE SAND OF TH |  | SAN DIEGO, CITY OF | 940113 | 1359PM | 940114 | 0859AM | 57000 | GAL | 1200 PAXTON DR. | SAN DIEGO | SD | 12" VC SEWER MAIN | VANDALISM OF SEWER MANHOLE. | CONTROL CHANNEL, OTAY | OVER FLOW STOPPED AT CERRISA ST. SOUTH OF CANT
| 940114 | 1510PM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 940114 | 1019AM | 940114 | 1200PM |  | 303 | GAL |  | 4473 MENLO AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | SOAKED INTO GROUND, PA |  |  | Y | N | NA | MACHINE RODDED; DEODORIZED. |  | SAN DIEGO, CITY OF | 940113 | 0849AM | 940113 | 1030AM | 524 | GAL | 6102 LA PINTURA DR. | SAN DIEGO | SD | 8" VC MAIN CLEAN OUT | ROOT BLOCKAGE | SOAKED INTO GROUND, PA | NONE
| 940115 | 1345PM | SENIOR JAY | 6195258682 | SAN DIEGO, CITY OF | 940115 | 1032AM | 940115 | 1132AM |  | 300 | GAL |  | 2656 F ST. | SAN DIEGO | SD | 6" VC | GREASE BLOCKAGE | Y | STORM DRAIN, SD BAY |  |  | Y | N | NA | NONE |  | OCEANSIDE, CITY OF | 940114 | 1030AM | 940114 | 1045AM | 80 | GAL | 100 BLK OF COLLEGE BLVD. | OCEANSIDE | SD | END OF SEVERED SEWER MAIN. | CRACKS IN SEWER MAIN & LEAKS AROUND "PLUG". | SAN LUIS REY RIVER | DOMESTIC WASTEWATER FLOWED INTO THE SAND OF TH
| 940115 | 1100AM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 940115 | 1100AM | 940115 | 0100PM |  | 50 | GAL |  | 309 MORRO RD. | FALLBROOK | SD | CLEANOUT/MAIN LINE | GREASE BLOCKAGE | NO | NONE |  | ? | N | N | NA | OPENED AO FT INTO MAIN LINE. FLUSHED/RODDED FR |  | SAN DIEGO, CITY OF | 940114 | 1019AM | 940114 | 1200PM | 303 | GAL | 4473 MENLO AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | SOAKED INTO GROUND, PA | MACHINE RODDED; DEODORIZED.
| 940115 | 1315PM | RODERICK STEELE | 6197414854 | ESCONDIDO, CITY OF | 940115 | 1000AM | 940115 | 1210PM |  | 26000 | GAL |  | 850 N. JUNIPER | ESCONDIDO | SD | SEWER ATLAS PG20 MH50-51-53-54 | GREASE AND OTHER DEBRIS. | Y | ESCOND. CREEK, SAN ELI |  |  | Y | Y | 05 | AREA WAS WASHEDDOWN THEN TREATED WITH DISENFEC |  | SAN DIEGO, CITY OF | 940115 | 1032AM | 940115 | 1132AM | 300 | GAL | 2656 F ST. | SAN DIEGO | SD | 6" VC | GREASE BLOCKAGE | STORM DRAIN, SD BAY | NONE
| 940116 | 1045PM | RONALD S. ROBY | 6195258685 | SAN DIEGO, CITY OF | 940116 | 1206PM | 940116 | 0306PM |  | 180 | GAL |  | 430542ND ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | SETTLED IN STORM DRAINAT 42ND & EL CAJON BLVD. |  | FALLBROOK SANITARY DISTRICT | 940115 | 1100AM | 940115 | 0100PM | 50 | GAL | 309 MORRO RD. | FALLBROOK | SD | CLEANOUT/MAIN LINE | GREASE BLOCKAGE | NONE | OPENED AO FT INTO MAIN LINE. FLUSHED/RODDED FR
| 940116 | 1045PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 940116 | 0941AM | 940116 | 1141AM |  | 240 | GAL |  | 6463 QUILLAN ST. | SAN DIEGO | SD | 10" VC SEWER MAIN | ROOTS BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | NA | FLOW SOAKED INTO GROUND IN CANYON AROUND MANHO |  | ESCONDIDO, CITY OF | 940115 | 1000AM | 940115 | 1210PM | 26000 | GAL | 850 N. JUNIPER | ESCONDIDO | SD | SEWER ATLAS PG20 MH50-51-53-54 | GREASE AND OTHER DEBRIS. | ESCOND. CREEK, SAN ELI | AREA WAS WASHEDDOWN THEN TREATED WITH DISENFEC
| 940116 | 0330PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 940116 | 1023AM | 940116 | 1253PM |  | 4500 | GAL |  | 3055 ERIE ST. | SAN DIEGO | SD | 8" VC MAIN BREAK | VANDELISM OF SEWER MAIN IN CANYON CAUSED MA | Y | STORM CHANNEL, MISSION |  |  | Y | Y | 05 | 8"VC BROKE AND OVERFLOW WENT TO MISSION BAY. |  | SAN DIEGO, CITY OF | 940116 | 1206PM | 940116 | 0306PM | 180 | GAL | 430542ND ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | SETTLED IN STORM DRAINAT 42ND & EL CAJON BLVD.
| 940116 | 0330PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 940116 | 1001AM | 940116 | 1046AM |  | 225 | GAL |  | ELDER ST. & THERMAL ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | FLOWED INTO STORM DRAIN AND SETTLED. |  | SAN DIEGO, CITY OF | 940116 | 0941AM | 940116 | 1141AM | 240 | GAL | 6463 QUILLAN ST. | SAN DIEGO | SD | 10" VC SEWER MAIN | ROOTS BLOCKAGE | CANYON, PACIFIC OCEAN | FLOW SOAKED INTO GROUND IN CANYON AROUND MANHO
| 940117 | 1145AM | MICHAEL DUNBAR | 7144994555 | SOUTH COAST WATER DISTRICT | 940117 | 1120AM | 940117 | 1135AM |  | 1000 | GAL |  | ALISO CREEK | LAGUNA BEACH | OR | ? | AT THE COASTAL TREATMENT PLANT THE SHAFT ON | Y | ALISO CREEK, PACIFIC O |  |  | Y | Y | ? | NONE |  | SAN DIEGO, CITY OF | 940116 | 1023AM | 940116 | 1253PM | 4500 | GAL | 3055 ERIE ST. | SAN DIEGO | SD | 8" VC MAIN BREAK | VANDELISM OF SEWER MAIN IN CANYON CAUSED MA | STORM CHANNEL, MISSION | 8"VC BROKE AND OVERFLOW WENT TO MISSION BAY.
| 940118 | 0748AM | MARK STROBMAN | 6195258682 | SAN DIEGO, CITY OF | 940117 | 2056PM | 940117 | 2256PM |  | 60 | GAL |  | 1800 INTERNATIONAL RD. | SAN DIEGO | SD | 8" PVC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | NONE |  | SAN DIEGO, CITY OF | 940116 | 1001AM | 940116 | 1046AM | 225 | GAL | ELDER ST. & THERMAL ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | FLOWED INTO STORM DRAIN AND SETTLED.
| 940117 | 1545PM | ROBERT WADE | 6197891330 | RAMONA MUNICIPAL WATER DIST. | 940117 | 1130AM | 940117 | 1330PM |  | 200 | GAL |  | DAVIS CUP LANE | RAMONA | SD | MANHOLE #2 | MAIN LINE BLOCKAGE | NO | NONE |  | CUB AND ST. DRAIN, OPEN AREA | Y | N | NA | BLOCKAGE WAS CLEAREDAND FLOWAREAWASHED DOWN AN |  | SOUTH COAST WATER DISTRICT | 940117 | 1120AM | 940117 | 1135AM | 1000 | GAL | ALISO CREEK | LAGUNA BEACH | OR | ? | AT THE COASTAL TREATMENT PLANT THE SHAFT ON | ALISO CREEK, PACIFIC O | NONE
| 940118 | 1100AM | GARRY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 940117 | 0910AM | 940117 | 0950AM |  | 650 | GAL |  | 1300 BUENA ST. | OCEANSIDE | SD | I-5 SYPHON OVERFLOW | RAGS & PAPER CLOGGED SEWER MAIN. | Y | SAN LUIS REY RIVER |  |  | Y | N | NA | WASTEWATER FLOWED INTO A DITCH AND FROM THERE |  | SAN DIEGO, CITY OF | 940117 | 2056PM | 940117 | 2256PM | 60 | GAL | 1800 INTERNATIONAL RD. | SAN DIEGO | SD | 8" PVC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | NONE
| 940119 | 1145AM | MARK A. STOFFER | 6197254806 | CAMP PENDLETON | 940118 | 2100PM | 940117 | 2400PM |  | 500 | GAL |  | BASILONG | CAMP PENDLETON | SD | 51053 DISCHARGE LINE 52 AREA | BROKEN DISCHARGE LINE | NO | NONE |  | BRUSH AREA | Y | N | NA | SECUREDSTATION BYPASS TO 51050 STOOD BY WITH P |  | RAMONA MUNICIPAL WATER DIST. | 940117 | 1130AM | 940117 | 1330PM | 200 | GAL | DAVIS CUP LANE | RAMONA | SD | MANHOLE #2 | MAIN LINE BLOCKAGE | NONE | BLOCKAGE WAS CLEAREDAND FLOWAREAWASHED DOWN AN
| 940118 | 1500PM | MARK STROBMAN | 6195258682 | SAN DIEGO, CITY OF | 940118 | 1030AM | 940118 | 1300PM |  | 143 | GAL |  | CLOVE AND OLIPHANT | SAN DIEGO | SD | 6CP SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRIAIN, PACIFIC |  |  | Y | N | NA | NONE |  | OCEANSIDE, CITY OF | 940117 | 0910AM | 940117 | 0950AM | 650 | GAL | 1300 BUENA ST. | OCEANSIDE | SD | I-5 SYPHON OVERFLOW | RAGS & PAPER CLOGGED SEWER MAIN. | SAN LUIS REY RIVER | WASTEWATER FLOWED INTO A DITCH AND FROM THERE
| 940118 | 1510PM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 940118 | 0926AM | 940118 | 1100AM |  | 94 | GAL |  | 6042 BROOKLING AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | MACHINE RODDED TO RELIEVE STOP. |  | CAMP PENDLETON | 940118 | 2100PM | 940117 | 2400PM | 500 | GAL | BASILONG | CAMP PENDLETON | SD | 51053 DISCHARGE LINE 52 AREA | BROKEN DISCHARGE LINE | NONE | SECUREDSTATION BYPASS TO 51050 STOOD BY WITH P
| 940119 | 1200PM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 940119 | 0317AM | 940119 | 0353AM |  | 2992 | GAL |  | 100 BLK OF COLLEGE BLVD. | OCEANSIDE | SD | END OF SEVERED SEWER MAIN. | DRAINAGE OF CONTENTS OF 200 FT OF 24" SEWER | Y | SAN LUIS REY RIVER |  |  | Y | N | NA | DOMESTIC WASTEWATER WAS PONDED IN THE SAND OF |  | SAN DIEGO, CITY OF | 940118 | 1030AM | 940118 | 1300PM | 143 | GAL | CLOVE AND OLIPHANT | SAN DIEGO | SD | 6CP SEWER MAIN | ROOT BLOCKAGE | STORM DRIAIN, PACIFIC | NONE
| 940121 | 0100AM | M. A. WHELAN | 6195258685 | SAN DIEGO, CITY OF | 940120 | 0743AM | 940120 | 1028AM |  | 165 | GAL |  | 2768 HIDDEN VALLEY RD. | SAN DIEGO | SD | 8" VC SEWER | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | MACHINE RODDED 157'8"VC SEC. RELIEVE STOP. MAI |  | SAN DIEGO, CITY OF | 940118 | 0926AM | 940118 | 1100AM | 94 | GAL | 6042 BROOKLING AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | MACHINE RODDED TO RELIEVE STOP.
| 940121 | 0008AM | M. A. WHELAN | 6195258685 | SAN DIEGO, CITY OF | 940120 | 1014AM | 940120 | 1200AM |  | 212 | GAL |  | 7859 IVANHOE | SAN DIEGO | SD | 6" VC SEWER MAIN | ROOT BLOCKAGE | Y | PACIFIC OCEAN |  |  | Y | N | NA | ROD 285' SECTION OF6" VC MAIN ON IVANHOE. RELI |  | OCEANSIDE, CITY OF | 940119 | 0317AM | 940119 | 0353AM | 2992 | GAL | 100 BLK OF COLLEGE BLVD. | OCEANSIDE | SD | END OF SEVERED SEWER MAIN. | DRAINAGE OF CONTENTS OF 200 FT OF 24" SEWER | SAN LUIS REY RIVER | DOMESTIC WASTEWATER WAS PONDED IN THE SAND OF
| 940121 | 0400AM | M.A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 940120 | 2001PM | 940120 | 2045PM |  | 220 | GAL |  | 3866 41 ST. | SAN DIEGO' | SD | 8" CP SEWER MAIN | GREASE BLOCKAGE | Y | PACIFIC OCEAN |  |  | Y | N | NA | RODDED MAIN AND DEODORIZED. |  | SAN DIEGO, CITY OF | 940120 | 0743AM | 940120 | 1028AM | 165 | GAL | 2768 HIDDEN VALLEY RD. | SAN DIEGO | SD | 8" VC SEWER | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | MACHINE RODDED 157'8"VC SEC. RELIEVE STOP. MAI
| 940121 |  | MARK A STOFFER | 6197254806 | CAMP PENDLETON | 940120 | 1430PM | 940120 | 1500PM |  | 50 | GAL |  | 14 AREA | CAMP PENDLETON | SD | 14008 BARRACKS | LINE BLOCKAGE | NO | NONE |  | GRASS BY MANHOLE | Y | N | NA | PUMPER TRUCK PUMPED OUT AND STOOD BY WHILE PIP |  | SAN DIEGO, CITY OF | 940120 | 1014AM | 940120 | 1200AM | 212 | GAL | 7859 IVANHOE | SAN DIEGO | SD | 6" VC SEWER MAIN | ROOT BLOCKAGE | PACIFIC OCEAN | ROD 285' SECTION OF6" VC MAIN ON IVANHOE. RELI
| 940112 | 0830PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 940121 | 1303PM | 940121 | 1428PM |  | 8.7 | GAL |  | 1ST AND REDWOOD | SAN DIEGO | SD | 6" CP | ROOT BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | NA | 8.7 GAL SOAKED INTO GROUND AROUND MANHOLE. |  | SAN DIEGO, CITY OF | 940120 | 2001PM | 940120 | 2045PM | 220 | GAL | 3866 41 ST. | SAN DIEGO' | SD | 8" CP SEWER MAIN | GREASE BLOCKAGE | PACIFIC OCEAN | RODDED MAIN AND DEODORIZED.
| 940125 | 1100AM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 940122 | 0840AM | 940122 | 1100AM |  | 500 | GAL |  | 3765 CAMEO DR. | OCEANSIDE | SD | SEWER MANHOLE | GREASE BLOCKAGE | NO | NONE |  | STORM DRAIN | Y | N | NA | DOMESTIC WASTEWATER FLOWED OUT OF "PICK HOLES" |  | CAMP PENDLETON | 940120 | 1430PM | 940120 | 1500PM | 50 | GAL | 14 AREA | CAMP PENDLETON | SD | 14008 BARRACKS | LINE BLOCKAGE | NONE | PUMPER TRUCK PUMPED OUT AND STOOD BY WHILE PIP
| 940124 | 1400PM | MARK A STOFFER | 6197254806 | CAMP PENDLETON | 940123 | 1650PM | 940123 | 2310PM |  | 160 | GAL |  | ENEDY & CHRISMAN CIRCLE | CAMP PENDLETON | SD | MAN HOLE | MAIN LINE BLOCKAGE | NO | NONE |  | SUROUNDING VEGETATION | Y | N | NA | UNPLUGED LINE, CLEANED AND LIMED AREA. |  | SAN DIEGO, CITY OF | 940121 | 1303PM | 940121 | 1428PM | 8.7 | GAL | 1ST AND REDWOOD | SAN DIEGO | SD | 6" CP | ROOT BLOCKAGE | CANYON, PACIFIC OCEAN | 8.7 GAL SOAKED INTO GROUND AROUND MANHOLE.
| 940124 | 0930AM | LINDA JONES | 7144994555 | SOUTH COAST WATER DISTRICT | 940123 | 0945AM | 940124 | 0930AM |  | 4000 | GAL |  | LAGUNITA BEACH | LAGUNA BEACH | OR | MANHOLE | GREASE DETERGENT BLOCKED MANHOLE | Y | PACIFIC OCEAN |  |  | Y | Y | ? | HYDROFLUSHED THE LINE WITH POTABLE WATER AND R |  | OCEANSIDE, CITY OF | 940122 | 0840AM | 940122 | 1100AM | 500 | GAL | 3765 CAMEO DR. | OCEANSIDE | SD | SEWER MANHOLE | GREASE BLOCKAGE | NONE | DOMESTIC WASTEWATER FLOWED OUT OF "PICK HOLES"
| 940123 | 1000PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 940123 | 0852PM | 940123 | 0922PM |  | 150 | GAL |  | 2404 LORING ST. | SAN DIEGO | SD | 8" VC | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | FLOWED INTO STORM DRAIN AND SETTLED. |  | CAMP PENDLETON | 940123 | 1650PM | 940123 | 2310PM | 160 | GAL | ENEDY & CHRISMAN CIRCLE | CAMP PENDLETON | SD | MAN HOLE | MAIN LINE BLOCKAGE | NONE | UNPLUGED LINE, CLEANED AND LIMED AREA.
| 940131 | 1300PM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 940124 | 0900AM | 940124 | 1130AM |  | 1000 | GAL |  | COLLEGE BLVD AND MARVIN ST. | OCEANSIDE | SD | SEWER MANHOLE | ROOTS AND GREASE CAUSED BLOCKAGE | NO | NONE |  | STORM DRAIN. | Y | N | NA | DOMESTIC WASTEWATER FLOWED OUT OF "PICK HOLES" |  | SOUTH COAST WATER DISTRICT | 940123 | 0945AM | 940124 | 0930AM | 4000 | GAL | LAGUNITA BEACH | LAGUNA BEACH | OR | MANHOLE | GREASE DETERGENT BLOCKED MANHOLE | PACIFIC OCEAN | HYDROFLUSHED THE LINE WITH POTABLE WATER AND R
| 940125 | 0814AM | JIM Mc CURLEY | 6195258687 | SAN DIEGO, CITY OF | 940124 | 1627PM | 940124 | 1827PM |  | 60 | GAL |  | 372 69TH ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | AROUND CLEANOUT, PACIF |  |  | Y | N | NA | FLUSHED MAIN. |  | SAN DIEGO, CITY OF | 940123 | 0852PM | 940123 | 0922PM | 150 | GAL | 2404 LORING ST. | SAN DIEGO | SD | 8" VC | ROOT BLOCKAGE | STORM DRAIN, PACIFIC O | FLOWED INTO STORM DRAIN AND SETTLED.
| 940124 | 1300PM | BOB MANRY | 9096764101 | RANCHO CALIF. WATER DISTRICT | 940124 | 0930AM | 940124 | 1015AM |  | 64256 | GAL |  | CLINTON KEITH ROAD | MURRIETA | SD | T.E. RESERVOIR | DRAIN TERTIARY RESERVOIY FOR BEAR CREEK GOL | N0 | NONE |  | DRY SLAUGHTERHOUSE CREEK | Y | N | NA | THIS WAS TERTIARY TREATED WATER. DID NOT REQUI |  | OCEANSIDE, CITY OF | 940124 | 0900AM | 940124 | 1130AM | 1000 | GAL | COLLEGE BLVD AND MARVIN ST. | OCEANSIDE | SD | SEWER MANHOLE | ROOTS AND GREASE CAUSED BLOCKAGE | NONE | DOMESTIC WASTEWATER FLOWED OUT OF "PICK HOLES"
| 940125 | 0945AM | HAROLD BAILEY | 6194488600 | PADRE DAM MUNICIPAL WATER DIST | 940125 | 0300AM | 940125 | 0700AM |  | 70000 | GAL |  | FANITA PARKWAY EXTENSION | SANTEE | SD | 24" FORCE MAIN | PIPELINE FAILURE | Y | SYCAMORE CANYON, SD RI |  |  | Y | Y | ? | AFFECTED OVERFLOW AREA TREATED WITH SODIUM HYP |  | SAN DIEGO, CITY OF | 940124 | 1627PM | 940124 | 1827PM | 60 | GAL | 372 69TH ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | AROUND CLEANOUT, PACIF | FLUSHED MAIN.
| 940127 | 0021AM | M. A. WHELAN | 6195258682 | SAN DIEGO, CITY OF | 940126 | 0733AM | 940126 | 0838AM |  | 19.5 | GAL |  | 3941 9TH AVE | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | Y | SOAKED INTO GROUND, PA |  |  | Y | N | NA | RODDED 180' SECT EASEMENT 9TH AVE. NORTH OF UN |  | RANCHO CALIF. WATER DISTRICT | 940124 | 0930AM | 940124 | 1015AM | 64256 | GAL | CLINTON KEITH ROAD | MURRIETA | SD | T.E. RESERVOIR | DRAIN TERTIARY RESERVOIY FOR BEAR CREEK GOL | NONE | THIS WAS TERTIARY TREATED WATER. DID NOT REQUI
| 940127 | 0825AM | MARK A STOFFER | 6197254806 | CAMP PENDLETON | 940126 | 1900PM | 940126 | 1915PM |  | 15 | GAL |  | 312 CHERRY | CAMP PENDLETON | SD | 312 CHERYWIRE MOUNTAIN HOUSING | PLUGGED LINE | NO | AREA BY MANHOLE |  |  | Y | N | NA | PIPE SHOP CLEARED LINE-CLEANED AND LIMED AREA. |  | PADRE DAM MUNICIPAL WATER DIST | 940125 | 0300AM | 940125 | 0700AM | 70000 | GAL | FANITA PARKWAY EXTENSION | SANTEE | SD | 24" FORCE MAIN | PIPELINE FAILURE | SYCAMORE CANYON, SD RI | AFFECTED OVERFLOW AREA TREATED WITH SODIUM HYP
| 940127 | 0132AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 940126 | 1608PM | 940126 | 1908PM |  | 900 | GAL |  | 550 STORK ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | RODDED MAIN. |  | SAN DIEGO, CITY OF | 940126 | 0733AM | 940126 | 0838AM | 19.5 | GAL | 3941 9TH AVE | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | SOAKED INTO GROUND, PA | RODDED 180' SECT EASEMENT 9TH AVE. NORTH OF UN
| 940126 | 1554PM | JIM McCURLEY | 6195258687 | SAN DIEGO, CITY OF | 940126 | 0840AM | 940126 | 1110AM |  | 7500 | GAL |  | 9200 MIRA MESA BLVD | SAN DIEGO | SD | SEWER LINE 10" VC | DEBRIS BLOCKAGE CAUSED BY PRIVATE CONTRACTO | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | JET RODDED MAIN, RELIEVED GREASE AND DEBRIS BL |  | CAMP PENDLETON | 940126 | 1900PM | 940126 | 1915PM | 15 | GAL | 312 CHERRY | CAMP PENDLETON | SD | 312 CHERYWIRE MOUNTAIN HOUSING | PLUGGED LINE | AREA BY MANHOLE | PIPE SHOP CLEARED LINE-CLEANED AND LIMED AREA.
| 940127 | 0052AM | M. A. WHELAN | 6195258685 | SAN DIEGO, CITY OF | 940126 | 1415PM | 940126 | 1715PM |  | 180 | GAL |  | N.EL CAMINO REAL/VIA DE LA VAL | SAN DIEGO | SD | 8" VC SEWER MAIN | RAGS AND PAPER TOWELS IN MAIN CAUSED BLOCKA | Y | SOAKED INTO FIELD, PAC |  |  | Y | N | NA | ROD 360'- SET TRAFFIC CONTROL DURING RUSH HOUR |  | SAN DIEGO, CITY OF | 940126 | 1608PM | 940126 | 1908PM | 900 | GAL | 550 STORK ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | RODDED MAIN.
| 940128 | 0520PM | RONALD D ROBY | 6195258685 | SAN DIEGO, CITY OF | 940128 | 0859AM | 940128 | 1340PM |  | 341 | GAL |  | 1834 RIDGE VIEWDR. | SAN DIEGO | SD | 8" VC | ROOT BLOCKAGE | Y | CANYON, PACIFIC OCEAM |  |  | Y | N | NA | FLOWED SOUTH FROM MANHOLE AND SOAKED INTO DIRT |  | SAN DIEGO, CITY OF | 940126 | 0840AM | 940126 | 1110AM | 7500 | GAL | 9200 MIRA MESA BLVD | SAN DIEGO | SD | SEWER LINE 10" VC | DEBRIS BLOCKAGE CAUSED BY PRIVATE CONTRACTO | STORM DRAIN, PACIFIC O | JET RODDED MAIN, RELIEVED GREASE AND DEBRIS BL
| 940129 | 0945PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 940129 | 1227PM | 940129 | 0257PM |  | 2250 | GAL |  | 8950 CARLEY CIRCLE | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | NA | FLOW DRIED IN CANYON BEHIND ADDRESS. |  | SAN DIEGO, CITY OF | 940126 | 1415PM | 940126 | 1715PM | 180 | GAL | N.EL CAMINO REAL/VIA DE LA VAL | SAN DIEGO | SD | 8" VC SEWER MAIN | RAGS AND PAPER TOWELS IN MAIN CAUSED BLOCKA | SOAKED INTO FIELD, PAC | ROD 360'- SET TRAFFIC CONTROL DURING RUSH HOUR
| 940131 | 0915AM | LUCKY BISHOP IV | 6197414854 | ESCONDIDO, CITY OF | 940129 | 1100AM | 940129 | 0110PM |  | 520 | GAL |  | GRAND AVE./CROSS ST./FERNWOOD | ESCONDIDO | SD | SEWER ATLAS PG#46 MH#30 | GREASE BLOCKAGE | NO | NONE |  | ALONG CURB & GUTTER | ? | N | NA | AREA WAS VACUUMED, WASHED AND DISINFECTED. |  | SAN DIEGO, CITY OF | 940128 | 0859AM | 940128 | 1340PM | 341 | GAL | 1834 RIDGE VIEWDR. | SAN DIEGO | SD | 8" VC | ROOT BLOCKAGE | CANYON, PACIFIC OCEAM | FLOWED SOUTH FROM MANHOLE AND SOAKED INTO DIRT
| 940129 | 0945PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 940129 | 0738AM | 940129 | 1038AM |  | 180 | GAL |  | 1834 RIDGEVIEW DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | NA | FLOWED INTO CANYON WHERE IT SOAKED INTO GROUND |  | SAN DIEGO, CITY OF | 940129 | 1227PM | 940129 | 0257PM | 2250 | GAL | 8950 CARLEY CIRCLE | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | CANYON, PACIFIC OCEAN | FLOW DRIED IN CANYON BEHIND ADDRESS.
| 940129 | 0945PM | RONALD D.ROBY | 6195258685 | SAN DIEGO, CITY OF | 940129 | 1156AM | 940129 | 1241PM |  | 45 | GAL |  | 6070 WANDA ST | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STREET, PACIFIC OCEAN |  |  | Y | N | NA | DRIED IN STREET. |  | ESCONDIDO, CITY OF | 940129 | 1100AM | 940129 | 0110PM | 520 | GAL | GRAND AVE./CROSS ST./FERNWOOD | ESCONDIDO | SD | SEWER ATLAS PG#46 MH#30 | GREASE BLOCKAGE | NONE | AREA WAS VACUUMED, WASHED AND DISINFECTED.
| 940129 | 0945PM | RONALD D ROBY | 6195258685 | SAN DIEGO, CITY OF | 940129 | 1219PM | 940129 | 1340PM |  | 750 | GAL |  | 4120 POLK AVE. | SAN DIEGO | SD | 8" CP SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | APX. 70 GAL WERE SWEPT BACK INTO SEWER MANHOLE |  | SAN DIEGO, CITY OF | 940129 | 0738AM | 940129 | 1038AM | 180 | GAL | 1834 RIDGEVIEW DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | CANYON, PACIFIC OCEAN | FLOWED INTO CANYON WHERE IT SOAKED INTO GROUND
| 940130 | 0830PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 940130 | 0131PM | 940130 | 0401PM |  | 150 | GAL |  | RIVERDALE & SHERIDAN | SAN DIEGO | SD | 8:VC SEWER MAIN | DEBRIS BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | FLOWED INTO STORM DRAIN AND SOAKED INTO DIRT I |  | SAN DIEGO, CITY OF | 940129 | 1156AM | 940129 | 1241PM | 45 | GAL | 6070 WANDA ST | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STREET, PACIFIC OCEAN | DRIED IN STREET.
| 940130 | 1013AM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 940130 | 1000AM | 940130 | 1030AM |  | 3 | GAL |  | 1025 E. FALLBROOK ST. | FALLBROOK | SD | 4" CLEANOUT | POSSIBLE ROOTS | NO | NONE |  | ON CEMENT DRIVEWAY | N | N | NA | OPENED5' TO 15' FROM CLEANOUT. NEEDS TO BE DUG |  | SAN DIEGO, CITY OF | 940129 | 1219PM | 940129 | 1340PM | 750 | GAL | 4120 POLK AVE. | SAN DIEGO | SD | 8" CP SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | APX. 70 GAL WERE SWEPT BACK INTO SEWER MANHOLE
| 940130 | 0215PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 940130 | 0215PM | 940130 | 0225PM |  | 1 | GAL |  | 1025 E. FALLBROOK ST. | FALLBROOK | SD | 4" CLEANOUT | POSSIBLE ROOTS | NO | NONE |  | JUST OUT OF CLEANOUT | N | N | NA | OPENED 10'FROM CLEANOUT. SHOULD BE DUG-UP. |  | SAN DIEGO, CITY OF | 940130 | 0131PM | 940130 | 0401PM | 150 | GAL | RIVERDALE & SHERIDAN | SAN DIEGO | SD | 8:VC SEWER MAIN | DEBRIS BLOCKAGE | STORM DRAIN, PACIFIC O | FLOWED INTO STORM DRAIN AND SOAKED INTO DIRT I
| 940131 | 2350PM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 940131 | 1550PM | 940131 | 1650PM |  | 60 | GAL |  | 3040 MISION BLVD | SAN DIEGO | SD | 8" PVC SEWER MAIN | GREASE BLOCKAGE | Y | MISSION BAY, PACIFIC O |  |  | Y | N | NA | RODDED MAIN. |  | FALLBROOK SANITARY DISTRICT | 940130 | 1000AM | 940130 | 1030AM | 3 | GAL | 1025 E. FALLBROOK ST. | FALLBROOK | SD | 4" CLEANOUT | POSSIBLE ROOTS | NONE | OPENED5' TO 15' FROM CLEANOUT. NEEDS TO BE DUG
| 940131 | 1520PM | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 940131 | 0826AM | 940131 | 0900AM |  | 3.4 | GAL |  | 815 OSTEGO DR. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | Y | AROUND MANHOLE, PACIFI |  |  | Y | N | NA | SEWAGE SOAKED INTO GROUND AROUND MANHOLE. |  | FALLBROOK SANITARY DISTRICT | 940130 | 0215PM | 940130 | 0225PM | 1 | GAL | 1025 E. FALLBROOK ST. | FALLBROOK | SD | 4" CLEANOUT | POSSIBLE ROOTS | NONE | OPENED 10'FROM CLEANOUT. SHOULD BE DUG-UP.
| 940201 | 0730AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 940131 | 1300PM | 940131 | 1342PM |  | 705 | GAL |  | 7238 KEIGLEY ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | NA | OPERATOR FOUND OVERFLOW WHILE WORKING IN AREA/ |  | SAN DIEGO, CITY OF | 940131 | 1550PM | 940131 | 1650PM | 60 | GAL | 3040 MISION BLVD | SAN DIEGO | SD | 8" PVC SEWER MAIN | GREASE BLOCKAGE | MISSION BAY, PACIFIC O | RODDED MAIN.
| 940131 | 1530PM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 940131 | 0953AM | 940131 | 1045AM |  | 260 | GAL |  | 6300 CLAREMORE LN. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | MACHINE RODDED AND DEODORIZED MAIN. |  | SAN DIEGO, CITY OF | 940131 | 0826AM | 940131 | 0900AM | 3.4 | GAL | 815 OSTEGO DR. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | AROUND MANHOLE, PACIFI | SEWAGE SOAKED INTO GROUND AROUND MANHOLE.
| 940201 | 1200AM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 940131 | 0830AM | 940131 | 0930AM |  | 50 | GAL |  | BEHIND 1046 MISSION AVE. | OCEANSIDE | SD | LATERAL CLEANOUT | PRIVATE PROPERTY BLOCKAGE | NO | NONE |  | UNDERGROUND STORM DRAIN. | Y | N | NA | DOMESTIC WASTEWATER FLOWED OUT OF "OFFICE DEPO |  | SAN DIEGO, CITY OF | 940131 | 1300PM | 940131 | 1342PM | 705 | GAL | 7238 KEIGLEY ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | CANYON, PACIFIC OCEAN | OPERATOR FOUND OVERFLOW WHILE WORKING IN AREA/
| 940201 | 0710AM | MRS. TERRY NOWLEN | 6194635551 | SAN DIEGO, COUNTY OF | 94/02/01 | 0710AM | 940201 | 0145AM |  | 1500 | GAL |  | ESMT IN SCHOOL YARD SWEETWATER | SPRING VALLEY | SD | 8" V.C.P. | STICKS AND DEBRIS IN MAIN LINE | NO | NONE |  | IN SCHOOL YARD FIELD AREA | Y | Y | 03 | NONE |  | SAN DIEGO, CITY OF | 940131 | 0953AM | 940131 | 1045AM | 260 | GAL | 6300 CLAREMORE LN. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, PACIFIC O | MACHINE RODDED AND DEODORIZED MAIN.
| 940202 | 1920PM | THOMAS POWEL | 6197253567 | CAMP PENDLETON USMC | 940201 | 1920PM | 940201 | 2015PM |  | 25 | GAL |  | BLDG 1656 | CAMP PENDLETON | SD | BLDG 1656 | PLUGGED LINE | NO | NONE |  | AREA NEAR CLEAN OUT | Y | N | NA | UNPLUGGED CLEAN OUT AND LIMED AREA |  | OCEANSIDE, CITY OF | 940131 | 0830AM | 940131 | 0930AM | 50 | GAL | BEHIND 1046 MISSION AVE. | OCEANSIDE | SD | LATERAL CLEANOUT | PRIVATE PROPERTY BLOCKAGE | NONE | DOMESTIC WASTEWATER FLOWED OUT OF "OFFICE DEPO
| 940201 | 1240PM | TOM POWELL | 6197253567 | CAMP PENDLETON USMC | 940201 | 0800AM | 940201 | 1240PM |  | 200 | GAL |  | 234 WONJU | CAMP PENDLETON | SD | 234 WONJU DE LUZ HOUSING | PLUGGED LINE | NO | NONE |  | BACK LAWN | Y | N | NA | BASE HOUSING UNPLUGGED LINE, AND LIMED AREA. |  | SAN DIEGO, COUNTY OF | 94/02/01 | 0710AM | 940201 | 0145AM | 1500 | GAL | ESMT IN SCHOOL YARD SWEETWATER | SPRING VALLEY | SD | 8" V.C.P. | STICKS AND DEBRIS IN MAIN LINE | NONE | NONE
| 940203 | 0559AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 940202 | 1500PM | 940202 | 1630PM |  | 270 | GAL |  | ALDINE DR. & MONROE AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | GRAVITY MAIN BREAK CAUSED BY WATER MAIN BRE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | THE CREW REPAIRED THE SEWER MAIN AT THE LOCATO |  | CAMP PENDLETON USMC | 940201 | 1920PM | 940201 | 2015PM | 25 | GAL | BLDG 1656 | CAMP PENDLETON | SD | BLDG 1656 | PLUGGED LINE | NONE | UNPLUGGED CLEAN OUT AND LIMED AREA
| 940204 | 1045AM | DOUGLAS L. BROWN | 6196702271 | OTAY WATER DISTICT | 940203 | 0730AM | 940203 | 0731AM |  | 1500 | GAL |  | TREATMENT PLANT | SPRIN VALLEY | SD | FILTER STRUCTURE | OPERATOR LEFT FILTER UNATTENDED WHILE PERFO | NO | NONE |  | NONE | Y | N | NA | FILTER WAS BEING BACKWASHED WITH POTABLE WATER |  | CAMP PENDLETON USMC | 940201 | 0800AM | 940201 | 1240PM | 200 | GAL | 234 WONJU | CAMP PENDLETON | SD | 234 WONJU DE LUZ HOUSING | PLUGGED LINE | NONE | BASE HOUSING UNPLUGGED LINE, AND LIMED AREA.
| 940203 | 0330PM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 940203 | 1158AM | 940203 | 1228PM |  | 60 | GAL |  | 7229 COUNTRY CLUB DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE\ | Y | DIRT CURB, PACIFIC OCE |  |  | Y | N | NA | SEWER DRIED IN DIRT AREA |  | SAN DIEGO, CITY OF | 940202 | 1500PM | 940202 | 1630PM | 270 | GAL | ALDINE DR. & MONROE AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | GRAVITY MAIN BREAK CAUSED BY WATER MAIN BRE | STORM DRAIN, PACIFIC O | THE CREW REPAIRED THE SEWER MAIN AT THE LOCATO
| 940204 | 0608AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 940203 | 1700PM | 940203 | 1830PM |  | 45 | GAL |  | 4255 RANDOLPH ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | RODDED MAIN |  | OTAY WATER DISTICT | 940203 | 0730AM | 940203 | 0731AM | 1500 | GAL | TREATMENT PLANT | SPRIN VALLEY | SD | FILTER STRUCTURE | OPERATOR LEFT FILTER UNATTENDED WHILE PERFO | NONE | FILTER WAS BEING BACKWASHED WITH POTABLE WATER
| 940205 | 1250AM | RONALD D ROBY | 6195258685 | SAN DIEGO, CITY OF | 940204 | 0413PM | 940204 | 0513PM |  | 300 | GAL |  | 225 REDWOOD ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | RAGS AND DEBRIS CAUSED BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | NA | FLOW WENT INTO CANYON AT 2ND & QUINCE ST. AND |  | SAN DIEGO, CITY OF | 940203 | 1158AM | 940203 | 1228PM | 60 | GAL | 7229 COUNTRY CLUB DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE\ | DIRT CURB, PACIFIC OCE | SEWER DRIED IN DIRT AREA
| 940205 | 0845AM | RONALD D ROBY | 6195258685 | SAN DIEGO, CITY OF | 940205 | 1212AM | 940205 | 0212AM |  | 120 | GAL |  | 4315 53RD ST | SAN DIEGO | SD | 6" VC SEWER MAIN | PLUMER SNAKE IN CITY MAIN CAUSED BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | COUNTY HEALTH FOUND PLUMER'S SCREW IN MAIN FLO |  | SAN DIEGO, CITY OF | 940203 | 1700PM | 940203 | 1830PM | 45 | GAL | 4255 RANDOLPH ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, PACIFIC O | RODDED MAIN
| 940205 | 0540PM | RONALD D ROBY | 6195258685 | SAN DIEGO, CITY OF | 940205 | 0916AM | 940205 | 1230PM |  | 970 | GAL |  | 4840 COLLEGE AVE. | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | NA | FLOWED 100' FROM MANHOLE#8460 AND SOAKED INTO |  | SAN DIEGO, CITY OF | 940204 | 0413PM | 940204 | 0513PM | 300 | GAL | 225 REDWOOD ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | RAGS AND DEBRIS CAUSED BLOCKAGE | CANYON, PACIFIC OCEAN | FLOW WENT INTO CANYON AT 2ND & QUINCE ST. AND
| 940205 | 0940PM | RONALD D ROBY | 6195258685 | SAN DIEGO, CITY OF | 940205 | 0855AM | 940205 | 1200PM |  | 555 | GAL |  | 4200 41ST ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | NO | NONE |  | SWEPT BACK INTO MANHOLE | Y | N | NA | FLOW WAS SWEPT BACK INTO MANHOLE AND ALLEY WAS |  | SAN DIEGO, CITY OF | 940205 | 1212AM | 940205 | 0212AM | 120 | GAL | 4315 53RD ST | SAN DIEGO | SD | 6" VC SEWER MAIN | PLUMER SNAKE IN CITY MAIN CAUSED BLOCKAGE | STORM DRAIN, PACIFIC O | COUNTY HEALTH FOUND PLUMER'S SCREW IN MAIN FLO
| 940205 | 0940PM | RONALD D ROBY | 6195258685 | SAN DIEGO, CITY OF | 940205 | 0632PM | 940205 | 0800PM |  | 176 | GAL |  | REDWOOD & BANCROFT ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | NO | NONE |  | SWEPT BACK INTO MANHOLE | Y | N | NA | FLOW PUDDLED AT INTERSECTION AND WAS SWEPT BAC |  | SAN DIEGO, CITY OF | 940205 | 0916AM | 940205 | 1230PM | 970 | GAL | 4840 COLLEGE AVE. | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | CANYON, PACIFIC OCEAN | FLOWED 100' FROM MANHOLE#8460 AND SOAKED INTO
| 940205 | 0940PM | RONALD D ROBY | 6195258685 | SAN DIEGO, CITY OF | 940205 | 0921AM | 940205 | 1121AM |  | 600 | GAL |  | 9903 WALDGROVE PL | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | NA | FLOWED INTO POMERADO CANYON AND DRIED |  | SAN DIEGO, CITY OF | 940205 | 0855AM | 940205 | 1200PM | 555 | GAL | 4200 41ST ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | NONE | FLOW WAS SWEPT BACK INTO MANHOLE AND ALLEY WAS
| 940208 | 0930AM | LUCKY BISHOP IV | 6197414854 | ESCONDIDO, CITY OF | 940205 | 1055AM | 940205 | 1145AM |  | 3750 | GAL |  | EMISSON AVE. XST JUNIPER ST. | ESCONDIDO | SD | SEWER ATLAS PG#20 MANHOLE#50 | GREASE BLOCKAGE | Y | ESC. CREEK, SAN ELIJO |  |  | Y | Y | 05 | AREA WAS WASHED DOWN AND TREATED WITH DISINFEC |  | SAN DIEGO, CITY OF | 940205 | 0632PM | 940205 | 0800PM | 176 | GAL | REDWOOD & BANCROFT ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | NONE | FLOW PUDDLED AT INTERSECTION AND WAS SWEPT BAC
| 940205 | 0920AM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 940205 | ? | 940205 | 1025AM |  | 100 | GAL |  | 610 GOLDEN RD. | FALLBROOK | SD | 4" CLEANOUT | ROOTS AND SANITATY NAPKINS | NO | NONE |  | AROUND CLEANOUT & DOWN 100' | N | N | NA | ROOTS IN MAIN LINE, NEEDED TO BE DUG UP OR ROO |  | SAN DIEGO, CITY OF | 940205 | 0921AM | 940205 | 1121AM | 600 | GAL | 9903 WALDGROVE PL | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | CANYON, PACIFIC OCEAN | FLOWED INTO POMERADO CANYON AND DRIED
| 940206 | 0140PM | RONALD D ROBY | 6195258685 | SAN DIEGO, CITY OF | 940206 | 0843AM | 940206 | 0945AM |  | 310 | GAL |  | 7336 FAIRWAY RD. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | FLOWED INTO STORM DRAIN AND DRIED |  | ESCONDIDO, CITY OF | 940205 | 1055AM | 940205 | 1145AM | 3750 | GAL | EMISSON AVE. XST JUNIPER ST. | ESCONDIDO | SD | SEWER ATLAS PG#20 MANHOLE#50 | GREASE BLOCKAGE | ESC. CREEK, SAN ELIJO | AREA WAS WASHED DOWN AND TREATED WITH DISINFEC
| 940206 | 0940PM | RONALD D ROBY | 6195258685 | SAN DIEGO, CITY OF | 940206 | 1004AM | 940206 | 1330PM |  | 206 | GAL |  | 1727 MANZANA WAY | SAN DIEGO | SD | 8" VC SEWER MAIN | DEBRIS BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | FLOWED INTO STROM DRAIN AND SOAKED INTO GROUND |  | FALLBROOK SANITARY DISTRICT | 940205 | ? | 940205 | 1025AM | 100 | GAL | 610 GOLDEN RD. | FALLBROOK | SD | 4" CLEANOUT | ROOTS AND SANITATY NAPKINS | NONE | ROOTS IN MAIN LINE, NEEDED TO BE DUG UP OR ROO
| 940206 | 0140PM | RONALD D ROBY | 6195258685 | SAN DIEGO, CITY OF | 940206 | 0954AM | 940206 | 1130AM |  | 1440 | GAL |  | EUCLID & GUYMON ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | FLOWED INTO STORM DRAIN THEN TO CREEKBED AND D |  | SAN DIEGO, CITY OF | 940206 | 0843AM | 940206 | 0945AM | 310 | GAL | 7336 FAIRWAY RD. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | FLOWED INTO STORM DRAIN AND DRIED
| 940207 | 1730PM | R. H. PARKER | 6195258685 | TLC CONTRACTOR FOR P/S#17 | 940207 | 1301PM | 940207 | 1530PM |  | 149 | GAL |  | 3999 MISSIONBLVD | SAN DIEGO | SD | CLEAN OUT BY LOADING DOCK | CONTRACTOR HAD PUMP SETTINGD TOO HIGH | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | NO SIGN'S NEEDED TO POSTED |  | SAN DIEGO, CITY OF | 940206 | 1004AM | 940206 | 1330PM | 206 | GAL | 1727 MANZANA WAY | SAN DIEGO | SD | 8" VC SEWER MAIN | DEBRIS BLOCKAGE | STORM DRAIN, PACIFIC O | FLOWED INTO STROM DRAIN AND SOAKED INTO GROUND
| 940207 | 2257PM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 940207 | 1646PM | 940207 | ? |  | 0 | GAL |  | OCEAN BEACH PIER FOOT | SAN DIEGO | SD | PUMP STATION-PRIVATE | PUMPS BURNED OUT AT PRIVATE PARK DEPT. PUMP | Y | PACIFIC OCEAN |  |  | Y | N | NA | CALLED TO SHUT OFF WATER TO PIER AT THE METER |  | SAN DIEGO, CITY OF | 940206 | 0954AM | 940206 | 1130AM | 1440 | GAL | EUCLID & GUYMON ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, PACIFIC O | FLOWED INTO STORM DRAIN THEN TO CREEKBED AND D
| 940208 | 0845AM | BOB WADE | 6197891330 | RAMONA MWD | 940208 | 1230AM | 940208 | 0830AM |  | 240000 | GAL |  | 260 SAWDAY | RAMONA | 37 | AERATION TANK | BLOCKED LINE FROM AERATION TANK TO SECONDAR | NO | NONE |  | OPEN FIELD NEAR STP | Y | ? | ? | THE DISCHARGER IN THE PROCESS JETTING OUT BLOC |  | TLC CONTRACTOR FOR P/S#17 | 940207 | 1301PM | 940207 | 1530PM | 149 | GAL | 3999 MISSIONBLVD | SAN DIEGO | SD | CLEAN OUT BY LOADING DOCK | CONTRACTOR HAD PUMP SETTINGD TOO HIGH | STORM DRAIN, PACIFIC O | NO SIGN'S NEEDED TO POSTED
| 940208 | 1520PM | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 940208 | 0900AM | 940208 | 1028AM |  | 340 | GAL |  | CLEVELAND & VERMONT | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | NONE |  | SAN DIEGO, CITY OF | 940207 | 1646PM | 940207 | ? | 0 | GAL | OCEAN BEACH PIER FOOT | SAN DIEGO | SD | PUMP STATION-PRIVATE | PUMPS BURNED OUT AT PRIVATE PARK DEPT. PUMP | PACIFIC OCEAN | CALLED TO SHUT OFF WATER TO PIER AT THE METER
| 940208 | 1110AM | JOHN THOMPSON | 6197444550 | VALLECITOS WATER DISTRICT | 940208 | 0830AM | 940208 | 0845AM |  | 500 | GAL |  | 2310 RANCHO SANTA FE RD. | SAN MARCOS | SD | MANHOLE ENTRANCE,RD TO PLANT | INFLUENT PUMP FAILURE | Y | SAN MARCOS CREEK |  |  | Y | N | NA | SWITCHING PLANT TO EMERGENCY STANDBY POWER TRI |  | RAMONA MWD | 940208 | 1230AM | 940208 | 0830AM | 240000 | GAL | 260 SAWDAY | RAMONA | 37 | AERATION TANK | BLOCKED LINE FROM AERATION TANK TO SECONDAR | NONE | THE DISCHARGER IN THE PROCESS JETTING OUT BLOC
| 940209 | 0400AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 940208 | 1716PM | 940208 | 1816PM |  | 30 | GAL |  | 3939 MARKET ST | SAN DIEGO | SD | 10" VC SEWER MAIN | ROCKS AND DEBRIS CAUSED BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | FLUSHED, VACTORED AND RODDED MAIN |  | SAN DIEGO, CITY OF | 940208 | 0900AM | 940208 | 1028AM | 340 | GAL | CLEVELAND & VERMONT | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | NONE
| 940209 | 1200PM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 940208 | 1753PM | 940208 | 1920PM |  | 125 | GAL |  | ASILADO & CALLE DEL PALO | OCEANSIDE | SD | MANHOLE OVER SEWER MAIN | BLOCKAGE FROM GREASE BUILD UP IN MAIN | NO | NONE |  | CONCRETE LINED STORMDRAIN CHNL | Y | N | NA | DOMESTIC WASTEWATER FLOWED OUT OF "PICK HOLES" |  | VALLECITOS WATER DISTRICT | 940208 | 0830AM | 940208 | 0845AM | 500 | GAL | 2310 RANCHO SANTA FE RD. | SAN MARCOS | SD | MANHOLE ENTRANCE,RD TO PLANT | INFLUENT PUMP FAILURE | SAN MARCOS CREEK | SWITCHING PLANT TO EMERGENCY STANDBY POWER TRI
| 940210 | 0830PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 940210 | 0830PM | 940210 | 0945PM |  | 5 | GAL |  | 611 VILLAGE VIEW | FALLBROOK | SD | CLEANOUT | ROOTS AND GREASE BLOCKAGE | NO | NONE |  | AROUND CLEANOUT | N | N | NA | OPENED 5' FROM CLEANOUT. WORK WAS COMPLETED AT |  | SAN DIEGO, CITY OF | 940208 | 1716PM | 940208 | 1816PM | 30 | GAL | 3939 MARKET ST | SAN DIEGO | SD | 10" VC SEWER MAIN | ROCKS AND DEBRIS CAUSED BLOCKAGE | STORM DRAIN, PACIFIC O | FLUSHED, VACTORED AND RODDED MAIN
| 940211 | 1520PM | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 940210 | 0900AM | 940211 | 1200PM |  | 1620 | GAL |  | 4472 HORTENSIA | SAN DIEGO | SD | 6 CP SEWER MAIN | ROOT BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | NA | NONE |  | OCEANSIDE, CITY OF | 940208 | 1753PM | 940208 | 1920PM | 125 | GAL | ASILADO & CALLE DEL PALO | OCEANSIDE | SD | MANHOLE OVER SEWER MAIN | BLOCKAGE FROM GREASE BUILD UP IN MAIN | NONE | DOMESTIC WASTEWATER FLOWED OUT OF "PICK HOLES"
| 940212 | 2200PM | RONALD D ROBY | 6195258685 | SAN DIEGO, CITY OF | 940212 | 0853AM | 940212 | 1000AM |  | 335 | GAL |  | 338 35TH ST | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | NO | NONE |  | PUDDLED IN BACK YARD-CLEAN UP | Y | N | NA | FLOW PUDDLED IN BACK YARD, WE CALLED CLAIMS FO |  | FALLBROOK SANITARY DISTRICT | 940210 | 0830PM | 940210 | 0945PM | 5 | GAL | 611 VILLAGE VIEW | FALLBROOK | SD | CLEANOUT | ROOTS AND GREASE BLOCKAGE | NONE | OPENED 5' FROM CLEANOUT. WORK WAS COMPLETED AT
| 940212 | 2200PM | RONALD D ROBY | 6195258685 | SAN DIEGO, CITY OF | 940212 | 1008AM | 940212 | 1200PM |  | 4480 | GAL |  | 3656 BIRCH ST | SAN DIEGO | SD | 8" CP SEWER MAIN | DEBRIS BLOCKAGE | Y | STORM DRAIN, SD BAY/PA |  |  | Y | Y | 03 | FLOW ENTERED CHOLLA CREEK AT MAIN ST AT NAVY B |  | SAN DIEGO, CITY OF | 940210 | 0900AM | 940211 | 1200PM | 1620 | GAL | 4472 HORTENSIA | SAN DIEGO | SD | 6 CP SEWER MAIN | ROOT BLOCKAGE | CANYON, PACIFIC OCEAN | NONE
| 940212 | 2200PM | RONALD D ROBY | 6195258685 | SAN DIEGO, CITY OF | 940212 | 1024AM | 940212 | 1230AM |  | 630 | GAL |  | BURLINGAME & SAN MARCOS AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | NA | FLOW STOPED IN CANYON AND SOAKED INTO THE GROU |  | SAN DIEGO, CITY OF | 940212 | 0853AM | 940212 | 1000AM | 335 | GAL | 338 35TH ST | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | NONE | FLOW PUDDLED IN BACK YARD, WE CALLED CLAIMS FO
| 940213 | 1330PM | G DONALD EVANS | 6195258685 | SAN DIEGO, CITY OF | 940213 | 0922AM | 940213 | 1022AM |  | 60 | GAL |  | 3284 NATIONAL AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | SEWAGE WENT INTO STORM DRAIN WHERE IT SOAKED I |  | SAN DIEGO, CITY OF | 940212 | 1008AM | 940212 | 1200PM | 4480 | GAL | 3656 BIRCH ST | SAN DIEGO | SD | 8" CP SEWER MAIN | DEBRIS BLOCKAGE | STORM DRAIN, SD BAY/PA | FLOW ENTERED CHOLLA CREEK AT MAIN ST AT NAVY B
| 940215 | 0730AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 940214 | 0752AM | 940214 | 1000AM |  | 640 | GAL |  | BURLINGAME & SAN MARCOS AVE. | SAN DIEGO | SD | 6" C.P. SEWER MAIN | ROOT BLOCKAGE | Y | SOKED INTO GROUND, PAC |  |  | Y | N | NA | THIS SECTION OF MAIN WAS NEAR SECTION THAT STO |  | SAN DIEGO, CITY OF | 940212 | 1024AM | 940212 | 1230AM | 630 | GAL | BURLINGAME & SAN MARCOS AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | CANYON, PACIFIC OCEAN | FLOW STOPED IN CANYON AND SOAKED INTO THE GROU
| 940215 | 0759AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 940214 | 2107PM | 940214 | 2215PM |  | 68 | GAL |  | 904 AGATE ST. | SAN DIEGO | SD | 8" PVC SEWER MAIN | DEBRIS BLOCKAGE | Y | GUTTER, PACIFIC OCEAN |  |  | Y | N | NA | RODDED SEWER MAIN TO 46', OPENED STOP AND RODD |  | SAN DIEGO, CITY OF | 940213 | 0922AM | 940213 | 1022AM | 60 | GAL | 3284 NATIONAL AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | SEWAGE WENT INTO STORM DRAIN WHERE IT SOAKED I
| 940224 | 0433PM | DAVE BLYDHE | 7148310203 | MOULTON NIGUEL WATER DISTRICT | 940214 | 0630AM | 940214 | 0715AM |  | 2250 | GAL |  | I-5 AT OSO CREEK | MISSION VIEJO | OR | 6" MAINLINE ON SITE | 6" LINE BREAK CALTRANS RECLAIMED WATER IRRI | Y | OSO CREEK, PACIFIC OCE |  |  | N | N | NA | WATER DISCHARGED WAS TITLE 22 ARTICLE 4 60313 |  | SAN DIEGO, CITY OF | 940214 | 0752AM | 940214 | 1000AM | 640 | GAL | BURLINGAME & SAN MARCOS AVE. | SAN DIEGO | SD | 6" C.P. SEWER MAIN | ROOT BLOCKAGE | SOKED INTO GROUND, PAC | THIS SECTION OF MAIN WAS NEAR SECTION THAT STO
| 940216 | 0300PM | LUCKY BISOP IV | 6197414654 | ESCONDIDO, CITY OF | 940215 | 0330PM | 940215 | 0500PM |  | 4000 | GAL |  | 1605 HAMILTON LN. | ESCONDIDO | SD | MH THAT HOUSES AIR-VAC FOR 6" | FAILURE OF AIR-VAC ON FORCE MAIN | Y | FELICITA CREEK, LAKE H |  |  | Y | Y | 03 | MAJORITY OF WASTEWATER WAS CAPTURED AND RETURN |  | SAN DIEGO, CITY OF | 940214 | 2107PM | 940214 | 2215PM | 68 | GAL | 904 AGATE ST. | SAN DIEGO | SD | 8" PVC SEWER MAIN | DEBRIS BLOCKAGE | GUTTER, PACIFIC OCEAN | RODDED SEWER MAIN TO 46', OPENED STOP AND RODD
| 940215 | 1215PM | PAUL KANONAS STOFFER | 6197254806 | CAMP PENDLETON USMC | 940215 | ? | 0 | ? |  | 250000 | GAL |  | LAKE ONEIL | CAMP PENDLETON | SD | LAKE ONEIL | TEMPORARY DIVERSION O PLANT#1 WWTP EFFLUENT | NO | NONE |  | LAKE ONEIL | Y | N | NA | LAKE ONEIL IS A NO SWIMMING NONBODY CONTACT LA |  | MOULTON NIGUEL WATER DISTRICT | 940214 | 0630AM | 940214 | 0715AM | 2250 | GAL | I-5 AT OSO CREEK | MISSION VIEJO | OR | 6" MAINLINE ON SITE | 6" LINE BREAK CALTRANS RECLAIMED WATER IRRI | OSO CREEK, PACIFIC OCE | WATER DISCHARGED WAS TITLE 22 ARTICLE 4 60313
| 940216 | 0831AM | JIM GRABLE | 6195388118 | SAN DIEGO, CITY OF | 940215 | 1147AM | 940215 | 2000PM |  | 506 | GAL |  | 4604 CHEROKEE AVE. | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | NA | MAIN CREW RODDED MAIN FROM MANHOLE AND ALSO CL |  | ESCONDIDO, CITY OF | 940215 | 0330PM | 940215 | 0500PM | 4000 | GAL | 1605 HAMILTON LN. | ESCONDIDO | SD | MH THAT HOUSES AIR-VAC FOR 6" | FAILURE OF AIR-VAC ON FORCE MAIN | FELICITA CREEK, LAKE H | MAJORITY OF WASTEWATER WAS CAPTURED AND RETURN
| 940216 | 0147AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 940215 | 1756PM | 940215 | 1925PM |  | 890 | GAL |  | 3771 SWIFT AVE. | SAN DIEGO | SD | 6" CP SEWER MAIN | DEBRIS AND PAPER BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | OPENED MH#46025 & SEWAGE RAN BACK INTO MAIN, R |  | CAMP PENDLETON USMC | 940215 | ? | 0 | ? | 250000 | GAL | LAKE ONEIL | CAMP PENDLETON | SD | LAKE ONEIL | TEMPORARY DIVERSION O PLANT#1 WWTP EFFLUENT | NONE | LAKE ONEIL IS A NO SWIMMING NONBODY CONTACT LA
| 940217 | 0900AM | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 940216 | 1420PM | 940216 | 1520OM |  | 120 | GAL |  | NEWTON AVE. & 16TH ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | NONE |  | SAN DIEGO, CITY OF | 940215 | 1147AM | 940215 | 2000PM | 506 | GAL | 4604 CHEROKEE AVE. | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | CANYON, PACIFIC OCEAN | MAIN CREW RODDED MAIN FROM MANHOLE AND ALSO CL
| 940217 | 0800AM | JAMES E. SMITH | 7146432006 | MOULTON NIGUEL WATER DISTRICT | 940216 | 1600PM | 940216 | 1730PM |  | 900 | GAL |  | CABOT RD. SOUTH OF RAPID FALLS | MISSION VIEJO | OR | MANHOLE | CHUNK OF ASPHALT LODGED IN 8" SEWER | NO | NONE |  | HOLDING BASIN E. OF CABOT RD. | Y | N | NA | COUNTY CONSTRUCTING STORM HOLDING BASIN E OF C |  | SAN DIEGO, CITY OF | 940215 | 1756PM | 940215 | 1925PM | 890 | GAL | 3771 SWIFT AVE. | SAN DIEGO | SD | 6" CP SEWER MAIN | DEBRIS AND PAPER BLOCKAGE | STORM DRAIN, PACIFIC O | OPENED MH#46025 & SEWAGE RAN BACK INTO MAIN, R
| 940217 | 1600PM | NANCY/DISTR. OFFICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 940217 | 1600PM | 940217 | 1645PM |  | 10 | GAL |  | 2355 S. STAGE COACH LANE | FALLBROOK | SD | CLEANOUT | ROOTS | NO | NONE |  | AROUND CLEANOUT | N | N | NA | RODDED LIN, BROUGHT BACK ROOTS |  | SAN DIEGO, CITY OF | 940216 | 1420PM | 940216 | 1520OM | 120 | GAL | NEWTON AVE. & 16TH ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | NONE
| 940217 | 1912PM | POLICE DEPARTMENT | 6196915151 | CHULA VISTA, CITY OF | 940217 | 1912PM | 940217 | 2015PM |  | 300 | GAL |  | MADRONA & ASH | CHULA VISTA | SD | MANHOLE (SEWER) | GREASE & PAPER | Y | PACIFIC OCEAN |  |  | Y | N | NA | WASHED DOWN AFFECTED AREA |  | MOULTON NIGUEL WATER DISTRICT | 940216 | 1600PM | 940216 | 1730PM | 900 | GAL | CABOT RD. SOUTH OF RAPID FALLS | MISSION VIEJO | OR | MANHOLE | CHUNK OF ASPHALT LODGED IN 8" SEWER | NONE | COUNTY CONSTRUCTING STORM HOLDING BASIN E OF C
| 940218 | 0516AM | M.A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 940217 | 2144PM | 940217 | 2244PM |  | 300 | GAL |  | 11009 NEGLEY AVENUE | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | RODDED MAIN |  | FALLBROOK SANITARY DISTRICT | 940217 | 1600PM | 940217 | 1645PM | 10 | GAL | 2355 S. STAGE COACH LANE | FALLBROOK | SD | CLEANOUT | ROOTS | NONE | RODDED LIN, BROUGHT BACK ROOTS
| 940219 | 2100PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 940219 | 1454PM | 940219 | 1622PM |  | 88 | GAL |  | 200 BLOCK SYCAMORE | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | NO | NONE |  | SWEPT BACK INTO MANHOLE | Y | N | NA | 88 GALS. SWEPT BACK INTO MANHOLE AND CLEANED U |  | CHULA VISTA, CITY OF | 940217 | 1912PM | 940217 | 2015PM | 300 | GAL | MADRONA & ASH | CHULA VISTA | SD | MANHOLE (SEWER) | GREASE & PAPER | PACIFIC OCEAN | WASHED DOWN AFFECTED AREA
| 940219 | 1415PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 940219 | 0857AM | 940219 | 1040AM |  | 5665 | GAL |  | 17048 GRANDEE WAY | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM CHANEL, PACIFIC |  |  | Y | N | NA | FLOW WENT INTO STORM CHANEL, THEN TO PACIFIC O |  | SAN DIEGO, CITY OF | 940217 | 2144PM | 940217 | 2244PM | 300 | GAL | 11009 NEGLEY AVENUE | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, PACIFIC O | RODDED MAIN
| 940222 | 0825AM | MARK A. STOFFER | 6197254806 | CAMP PENDLETON MARINE BASE | 940219 | 1230PM | 940219 | 1430PM |  | 500 | GAL |  | VALLECITO-FORESTER HILLS | CAMP PENDLETON | SD | 322 B (CLEANOUT BETW. HOMES) | PLUGGED LINE | NO | NONE |  | OPEN FIELD | Y | N | NA | CLEANED AREA & LIMED |  | SAN DIEGO, CITY OF | 940219 | 1454PM | 940219 | 1622PM | 88 | GAL | 200 BLOCK SYCAMORE | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | NONE | 88 GALS. SWEPT BACK INTO MANHOLE AND CLEANED U
| 940220 | 1600PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 940220 | 1600PM | 940220 | 1700PM |  | 20 | GAL |  | 301 NORTH PICO | FALLBROOK | SD | CLEANOUT | ROOTS | NO | NONE |  | ALONG THE ROAD | N | N | NA | NONE |  | SAN DIEGO, CITY OF | 940219 | 0857AM | 940219 | 1040AM | 5665 | GAL | 17048 GRANDEE WAY | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM CHANEL, PACIFIC | FLOW WENT INTO STORM CHANEL, THEN TO PACIFIC O
| 940220 |  | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 940220 | 1612PM | 940220 | 1730PM |  | 156 | GAL |  | 8672 WAHL STREET | SANTEE | SD | 8" PVC | ROOTS | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | FLOWED INTO STORM DRAIN AND MIXED WITH STORM W |  | CAMP PENDLETON MARINE BASE | 940219 | 1230PM | 940219 | 1430PM | 500 | GAL | VALLECITO-FORESTER HILLS | CAMP PENDLETON | SD | 322 B (CLEANOUT BETW. HOMES) | PLUGGED LINE | NONE | CLEANED AREA & LIMED
| 940221 | 1400PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 940221 | 1400PM | 940221 | 1430PM |  | 5 | GAL |  | 748 W. COLLEGE | FALLBROOK | SD | CLEANOUT | ROOTS | NO | NONE |  | IN CLEANOUT | N | N | NA | NONE |  | FALLBROOK SANITARY DISTRICT | 940220 | 1600PM | 940220 | 1700PM | 20 | GAL | 301 NORTH PICO | FALLBROOK | SD | CLEANOUT | ROOTS | NONE | NONE
| 940221 | 1800PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 940221 | 1800PM | 940221 | 1900PM |  | 50 | GAL |  | 713 SOUTH MAIN STREET | FALLBROOK | SD | CLEANOUT | GREASE | NO | NONE |  | ALONG SIDE OF ROAD | N | N | NA | NONE |  | SAN DIEGO, CITY OF | 940220 | 1612PM | 940220 | 1730PM | 156 | GAL | 8672 WAHL STREET | SANTEE | SD | 8" PVC | ROOTS | STORM DRAIN, PACIFIC O | FLOWED INTO STORM DRAIN AND MIXED WITH STORM W
| 940224 | 1400PM | MICHAEL FILECCIA | 6192218728 | SAN DIEGO, CITY OF | 940223 |  | 940223 |  |  | 50 | GAL |  | FIESTA ISLAND | SAN DIEGO | SD | MANHOLE NO. 7 ON DECANT LINE | CALCIUM CARBONATE BUILDUP ON PIPE INTERIOR | NO | NONE |  | GROUND AROUND MANHOLE | N | N | NA | DIRT EXCAVATED & PLACED IN SLUDGE STREAM TO TH |  | FALLBROOK SANITARY DISTRICT | 940221 | 1400PM | 940221 | 1430PM | 5 | GAL | 748 W. COLLEGE | FALLBROOK | SD | CLEANOUT | ROOTS | NONE | NONE
| 940224 | 0455AM | M.A. WHELAN | 6195258686 | SAN DIEGO, CITY OF | 940223 | 1109AM | 940223 | 1219PM |  | 210 | GAL |  | 3700 VAN DYKE AVENUE | SAN DIEGO | SD | 8" C.P. SEWER MAIN | GREASE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | MACHINE RODDED SEWER MAIN |  | FALLBROOK SANITARY DISTRICT | 940221 | 1800PM | 940221 | 1900PM | 50 | GAL | 713 SOUTH MAIN STREET | FALLBROOK | SD | CLEANOUT | GREASE | NONE | NONE
| 940224 | 0655AM | M.A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 940223 | 2030PM | 940223 | 2230PM |  | 240 | GAL |  | 53RD & NARANJA STREET | SAN DIEGO | SD | 8"VC SEWER MAIN | GREASE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | RODDED MAIN |  | SAN DIEGO, CITY OF | 940223 |  | 940223 |  | 50 | GAL | FIESTA ISLAND | SAN DIEGO | SD | MANHOLE NO. 7 ON DECANT LINE | CALCIUM CARBONATE BUILDUP ON PIPE INTERIOR | NONE | DIRT EXCAVATED & PLACED IN SLUDGE STREAM TO TH
| 940224 | 0515AM | M.A. WHELAN | 6195258686 | SAN DIEGO, CITY OF | 940223 | 0827AM | 940223 | 1130AM |  | 183 | GAL |  | 4604 CHEROKEE | SAN DIEGO | SD | 6" CP SEWER MAIN | GRAVITY MAIN BREAK | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | NA | UNABLE TO ROD MAIN, TURNED OVER TO MAIN CREW F |  | SAN DIEGO, CITY OF | 940223 | 1109AM | 940223 | 1219PM | 210 | GAL | 3700 VAN DYKE AVENUE | SAN DIEGO | SD | 8" C.P. SEWER MAIN | GREASE | STORM DRAIN, PACIFIC O | MACHINE RODDED SEWER MAIN
| 940224 | 1530PM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 940224 | 1027AM | 940224 | 1210PM |  | 51.5 | GAL |  | 717 SANTA CLARA PL. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | MISSION BAY, PACIFIC O |  |  | Y | Y | ? | .5 G/M WENT TO STORM DRAIN THEN TO MISSION BAY |  | SAN DIEGO, CITY OF | 940223 | 2030PM | 940223 | 2230PM | 240 | GAL | 53RD & NARANJA STREET | SAN DIEGO | SD | 8"VC SEWER MAIN | GREASE | STORM DRAIN, PACIFIC O | RODDED MAIN
| 940301 | 1430PM | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 940225 | 0800AM | 940301 | 1300PM |  | 630 | GAL |  | PRESIDENTS WAY BALBOA PARK | SAN DIEGO | SD | STORM DRAIN | WOMEN'S BATHROOM IN MUNICIPAL GYM IS CONNEC | Y | CANYON, SD BAY/PACIFIC |  |  | Y | Y | ? | BATHROOM IS CLOSED UNTIL REPAIRS ARE DONE. |  | SAN DIEGO, CITY OF | 940223 | 0827AM | 940223 | 1130AM | 183 | GAL | 4604 CHEROKEE | SAN DIEGO | SD | 6" CP SEWER MAIN | GRAVITY MAIN BREAK | CANYON, PACIFIC OCEAN | UNABLE TO ROD MAIN, TURNED OVER TO MAIN CREW F
| 940228 | 1045AM | JOHN VAUGHT | 6197414864 | ESCONDIDO, CITY OF | 940225 | 1200PM | 940225 | 0140PM |  | 700 | GAL |  | 100 BLOCK E. 6TH ST. | ESCONDIDO | SD | SEWER ATLAS PG.MH#45 | COMBINATION OF ROOTS, GREASE AND PAPER. | Y | ESC. CREEK, SAN ELIJO |  |  | Y | Y | 03 | OVERFLOW AREA WAS TREATED WITH DISINFECTANT. |  | SAN DIEGO, CITY OF | 940224 | 1027AM | 940224 | 1210PM | 51.5 | GAL | 717 SANTA CLARA PL. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | MISSION BAY, PACIFIC O | .5 G/M WENT TO STORM DRAIN THEN TO MISSION BAY
| 940225 | 1530PM | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 940225 | 0944AM | 940225 | 1115AM |  | 455 | GAL |  | 3710 CRESTWOOD PLO. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | NONE |  | SAN DIEGO, CITY OF | 940225 | 0800AM | 940301 | 1300PM | 630 | GAL | PRESIDENTS WAY BALBOA PARK | SAN DIEGO | SD | STORM DRAIN | WOMEN'S BATHROOM IN MUNICIPAL GYM IS CONNEC | CANYON, SD BAY/PACIFIC | BATHROOM IS CLOSED UNTIL REPAIRS ARE DONE.
| 940228 | 1125AM | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 940227 | 1634PM | 940228 | 1020AM |  | 3730 | GAL |  | 27TH & CORONADO AVE. | SAN DIEGO | SD | 12" VC SEWER MAIN | DEBRIS BLOCKAGE | Y | STORM DRAIN, OTAY RIVE |  |  | Y | Y | ? | STILL POSTED AND STILL FLOWING. |  | ESCONDIDO, CITY OF | 940225 | 1200PM | 940225 | 0140PM | 700 | GAL | 100 BLOCK E. 6TH ST. | ESCONDIDO | SD | SEWER ATLAS PG.MH#45 | COMBINATION OF ROOTS, GREASE AND PAPER. | ESC. CREEK, SAN ELIJO | OVERFLOW AREA WAS TREATED WITH DISINFECTANT.
| 940227 | 1030PM | RONALD D ROBY | 6195258685 | SAN DIEGO, CITY OF | 940227 | 0434PM | 940227 | ? |  | 12600 | GAL |  | 27TH & CORONADO AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | VANDALISM | Y | STORMCHANNEL, PACIFIC |  |  | N | N | NA | FLOW IS STILL FLOWING, WE COULD NOT GET TO MAI |  | SAN DIEGO, CITY OF | 940225 | 0944AM | 940225 | 1115AM | 455 | GAL | 3710 CRESTWOOD PLO. | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | NONE
| 940227 | 0825PM | RONALD D ROBY | 6195258685 | SAN DIEGO, CITY OF | 940227 | 1105PM | 940227 | 1435PM |  | 420 | GAL |  | 2435 FELTON ST. | SAN DIEGO | SD | 10" VCSEWER MAIN | ROOT BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | NA | FLOW SOAKED INTO GROUND IN CANYON. |  | SAN DIEGO, CITY OF | 940227 | 1634PM | 940228 | 1020AM | 3730 | GAL | 27TH & CORONADO AVE. | SAN DIEGO | SD | 12" VC SEWER MAIN | DEBRIS BLOCKAGE | STORM DRAIN, OTAY RIVE | STILL POSTED AND STILL FLOWING.
| 940227 | 0845PM | RONALD D ROBY | 6195258685 | SAN DIEGO, CITY OF | 940227 | 0532PM | 940227 | 0732PM |  | 240 | GAL |  | 580 69TH ST. | SAN DIEGO | SD | 6" VCSEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | FLOWED INTO STORMDRAIN AND SETTLED INTO GROUND |  | SAN DIEGO, CITY OF | 940227 | 0434PM | 940227 | ? | 12600 | GAL | 27TH & CORONADO AVE. | SAN DIEGO | SD | 8" VC SEWER MAIN | VANDALISM | STORMCHANNEL, PACIFIC | FLOW IS STILL FLOWING, WE COULD NOT GET TO MAI
| 940301 | 0700AM | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 940228 | 1011AM | 940228 | 1350PM |  | 10950 | GAL |  | 6104 NEWCASTLE | SAN DIEGO | SD | 8" VC | CITY PARK WORKERS DRAINING SWIMMING POOL CA | Y | STORM DRAIN, SD BAY/PA |  |  | Y | N | NA | OVERFLOW WAS CAUSED BY POOL MAINTENANCE WORKER |  | SAN DIEGO, CITY OF | 940227 | 1105PM | 940227 | 1435PM | 420 | GAL | 2435 FELTON ST. | SAN DIEGO | SD | 10" VCSEWER MAIN | ROOT BLOCKAGE | CANYON, PACIFIC OCEAN | FLOW SOAKED INTO GROUND IN CANYON.
| 940305 | 2130PM | G. DONALD EVANS | 6195258685 | SAN DIEGO, CITY OF | 940300 | 0540PM | 940308 | 0540PM |  | 302400 | GAL |  | 10687 PORTOBELLO DR. | SAN DIEGO | SD | 12" PVC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | Y | 05 | SEWAGE HAD BEEN OVERFLOWING FOR A WEEK BEFORE |  | SAN DIEGO, CITY OF | 940227 | 0532PM | 940227 | 0732PM | 240 | GAL | 580 69TH ST. | SAN DIEGO | SD | 6" VCSEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | FLOWED INTO STORMDRAIN AND SETTLED INTO GROUND
| 940301 | 1945PM | ROBERT CHAROS | 6197254806 | CAMP PENDLETON USMC | 940301 | 1945PM | 940301 | 2230PM |  | 200 | GAL |  | 51053 BASOLONE RD. | CAMP PENDLETON | SD | 51053 LIFT STATION | STATION 51050 UNABLE TO HANDLE FLOW IN AREA | NO | NONE |  | CURB AREA | Y | Y | .5 | CLEANED SPILL AREA AND SPREAD HYDRATED LIME ON |  | SAN DIEGO, CITY OF | 940228 | 1011AM | 940228 | 1350PM | 10950 | GAL | 6104 NEWCASTLE | SAN DIEGO | SD | 8" VC | CITY PARK WORKERS DRAINING SWIMMING POOL CA | STORM DRAIN, SD BAY/PA | OVERFLOW WAS CAUSED BY POOL MAINTENANCE WORKER
| 940302 | 4852PM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 940302 | 0634AM | 940302 | 0915AM |  | 700 | GAL |  | 6255 RADIO DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | NA | CLEARED MAIN OF ROOTS. |  | SAN DIEGO, CITY OF | 940300 | 0540PM | 940308 | 0540PM | 302400 | GAL | 10687 PORTOBELLO DR. | SAN DIEGO | SD | 12" PVC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, PACIFIC O | SEWAGE HAD BEEN OVERFLOWING FOR A WEEK BEFORE
| 940302 | 0400PM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 940302 | 0833AM | 940302 | 1030AM |  | 635 | GAL |  | 5540 KIOWA DR. | SAN DIEGO | SD | 8"VC SEWER MAIN | ROOT BLOCKAGE | Y | SOAKED IN GROUND, PACI |  |  | Y | N | NA | MACHINE RODDED MAIN DEODORIZED SPILL AREA. |  | CAMP PENDLETON USMC | 940301 | 1945PM | 940301 | 2230PM | 200 | GAL | 51053 BASOLONE RD. | CAMP PENDLETON | SD | 51053 LIFT STATION | STATION 51050 UNABLE TO HANDLE FLOW IN AREA | NONE | CLEANED SPILL AREA AND SPREAD HYDRATED LIME ON
| 940302 | 1600PM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 940302 | 0640AM | 940302 | 0930AM |  | 170 | GAL |  | 4169 VISTA GRANDE AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | ROOT BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | NA | MACHINE RODDED MAIN DEODORIZED AREA IN CANYON. |  | SAN DIEGO, CITY OF | 940302 | 0634AM | 940302 | 0915AM | 700 | GAL | 6255 RADIO DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | CANYON, PACIFIC OCEAN | CLEARED MAIN OF ROOTS.
| 940304 | 1430PM | GARY K. ORR | 6199664854 | OCEANSIDE WATER UTILITIES | 940303 | 1800PM | 940303 | 2230PM |  | 1000 | GAL |  | OLD RANCH RD. & HITCHING | OCEANSIDE | SD | MANHOLE OVER SEWER MAIN | BLOCKAGE FROM GREASE AND RAGS | Y | GUAJOME LAKE |  |  | Y | N |  | WASTEWATER FLOWED OUT OF MANHOLE TO GUTTER FOR |  | SAN DIEGO, CITY OF | 940302 | 0833AM | 940302 | 1030AM | 635 | GAL | 5540 KIOWA DR. | SAN DIEGO | SD | 8"VC SEWER MAIN | ROOT BLOCKAGE | SOAKED IN GROUND, PACI | MACHINE RODDED MAIN DEODORIZED SPILL AREA.
| 940303 | 1245PM | MARCIA STOFFER | 6197254806 | CAMP PENDLETON MARINE BASE | 940303 | 1045AM | 940303 | 1150AM |  | 25000 | GAL |  | STEWART MES AND MTICCA | CAMP PENDLETON | SD | FROCED MAIN FROM 31520 LIFT ST | SDG&E BACK HOE BROKE LINE | NO | NONE |  | RAVINE WITH HEAVY BRUSH | Y | N | NA | STANDING BY WITH PUMPERS TO PREVENT FURTHER SP |  | SAN DIEGO, CITY OF | 940302 | 0640AM | 940302 | 0930AM | 170 | GAL | 4169 VISTA GRANDE AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | ROOT BLOCKAGE | CANYON, PACIFIC OCEAN | MACHINE RODDED MAIN DEODORIZED AREA IN CANYON.
| 940303 | 1218PM | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 940303 | 1005AM | 940303 | 1135AM |  | 90 | GAL |  | 4451 MENTONE ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | ROOT BLOCKAGE | Y | FAMOSA SLOUGH, PACIFIC |  |  | Y | N | NA | RAN ALONG CURB LINE DID NOT REACH STRM DRAIN @ |  | OCEANSIDE WATER UTILITIES | 940303 | 1800PM | 940303 | 2230PM | 1000 | GAL | OLD RANCH RD. & HITCHING | OCEANSIDE | SD | MANHOLE OVER SEWER MAIN | BLOCKAGE FROM GREASE AND RAGS | GUAJOME LAKE | WASTEWATER FLOWED OUT OF MANHOLE TO GUTTER FOR
| 940304 | 1644PM | DISTRICT OFFICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 940304 | 1650PM | 940304 | 1735PM |  | 25 | GAL |  | 1214 S. ALTURAS | FALLBROOK | SD | 6 CLEANOUT | GRASE, PAPER TOWELS AND RAGS. | NO | NONE |  | ALONG DRIVEWAY FOR 60 FEET | N | N | NA | NONE |  | CAMP PENDLETON MARINE BASE | 940303 | 1045AM | 940303 | 1150AM | 25000 | GAL | STEWART MES AND MTICCA | CAMP PENDLETON | SD | FROCED MAIN FROM 31520 LIFT ST | SDG&E BACK HOE BROKE LINE | NONE | STANDING BY WITH PUMPERS TO PREVENT FURTHER SP
| 940304 | 2010PM | G. DONALD EVANS | 6195258685 | SAN DIEGO, CITY OF | 940304 | 0302AM | 940304 | 0432PM |  | 90 | GAL |  | 835 ORISKANY ST. | SAN DIEGO | SD | 8" VC MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | FLOWED INTO STORM DRAIN AND SOAKED INTO GROUND |  | SAN DIEGO, CITY OF | 940303 | 1005AM | 940303 | 1135AM | 90 | GAL | 4451 MENTONE ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | ROOT BLOCKAGE | FAMOSA SLOUGH, PACIFIC | RAN ALONG CURB LINE DID NOT REACH STRM DRAIN @
| 940308 | 0850AM | DAVE BLYTHE | 7148310203 | MOULTON NIGUEL WATER DISTRICT | 940304 | 1845PM | 940304 | 1905PM |  | 1000 | GAL |  | CHAPPAROSA PARK ROAD | LAGUNA NIGUEL | OR | 4" MAIN LINE ON SITE | 4" LINE BREAK, CITY OF LAGUNA NIGUEL'S ONSI | Y | SALT CREEK, PACIFIC OC |  |  | Y | N | NA | WATER DISCHARGED WAS TITLE 22 ARTICLE 4 60313 |  | FALLBROOK SANITARY DISTRICT | 940304 | 1650PM | 940304 | 1735PM | 25 | GAL | 1214 S. ALTURAS | FALLBROOK | SD | 6 CLEANOUT | GRASE, PAPER TOWELS AND RAGS. | NONE | NONE
| 940305 | 0130PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 940305 | 0130PM | 940305 | 0205PM |  | 15 | GAL |  | 1449 LOS CONEJOS | FALLBROOK | SD | 4" CLEANOUT | GREASE IN MAINLINE AND LATERAL | NO | NONE |  | ABOUT 3'AROUND CLEANOUT | N | N | NA | THE LINE HAD A LOT OF GREASE IN IT. |  | SAN DIEGO, CITY OF | 940304 | 0302AM | 940304 | 0432PM | 90 | GAL | 835 ORISKANY ST. | SAN DIEGO | SD | 8" VC MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | FLOWED INTO STORM DRAIN AND SOAKED INTO GROUND
| 940305 | 0317PM | JIM McCURLEY | 6195258687 | SAN DIEGO, CITY OF | 940305 | 0916AM | 940305 | 1128AM |  | 1320 | GAL |  | LA JOLLA SHORE, L.J.SHORE LANE | SAN DIEGO | SD | SEWER LINE 8" VC | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | Y | 05 | SIGNS WERE POSTED 100' APART, 0TARTING 100' NO |  | MOULTON NIGUEL WATER DISTRICT | 940304 | 1845PM | 940304 | 1905PM | 1000 | GAL | CHAPPAROSA PARK ROAD | LAGUNA NIGUEL | OR | 4" MAIN LINE ON SITE | 4" LINE BREAK, CITY OF LAGUNA NIGUEL'S ONSI | SALT CREEK, PACIFIC OC | WATER DISCHARGED WAS TITLE 22 ARTICLE 4 60313
| 940308 | 0236AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 940307 | 1703PM | 940307 | 2303PM |  | 360 | GAL |  | 10935 BARBADOS WAY | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | RODDED MAIN TO RELIEVE STOPPAGE. |  | FALLBROOK SANITARY DISTRICT | 940305 | 0130PM | 940305 | 0205PM | 15 | GAL | 1449 LOS CONEJOS | FALLBROOK | SD | 4" CLEANOUT | GREASE IN MAINLINE AND LATERAL | NONE | THE LINE HAD A LOT OF GREASE IN IT.
| 940309 | 1030AM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 940308 | 1500PM | 940308 | 1530PM |  | 500 | GAL |  | SAN LUIS REY RD./VIA DEL MONTE | OCEANSIDE | SD | MANHOLE LIDS OVER SEWER MAIN | GREASE AND RAGS BLOCKAGE | Y | STORM CONTROL CHANNEL |  |  | Y | N | NA | THE WASTEWATER FLOWED OUT OF "PICK HOLES" IN M |  | SAN DIEGO, CITY OF | 940305 | 0916AM | 940305 | 1128AM | 1320 | GAL | LA JOLLA SHORE, L.J.SHORE LANE | SAN DIEGO | SD | SEWER LINE 8" VC | ROOT BLOCKAGE | STORM DRAIN, PACIFIC O | SIGNS WERE POSTED 100' APART, 0TARTING 100' NO
| 940309 | 1615PM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 940309 | 1343PM | 940309 | 1445PM |  | 1240 | GAL |  | LINDA VISTA RD/VIA LOS CUMBRES | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | Y | ? | SIGNS POSTED. |  | SAN DIEGO, CITY OF | 940307 | 1703PM | 940307 | 2303PM | 360 | GAL | 10935 BARBADOS WAY | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | RODDED MAIN TO RELIEVE STOPPAGE.
| 940309 | 1515PM | SENIOR | 6195258686 | SAN DIEGO, CITY OF | 940309 | 0933AM | 940309 | 1007AM |  | 102 | GAL |  | 38TH AND BETA ST. | SAN DIEGO | SD | 8" VC MAIN | GREASE BLOCKAGE | Y | SOAKED IN CREEK, PACIF |  |  | Y | N | NA | MACHINE RODDED. |  | OCEANSIDE, CITY OF | 940308 | 1500PM | 940308 | 1530PM | 500 | GAL | SAN LUIS REY RD./VIA DEL MONTE | OCEANSIDE | SD | MANHOLE LIDS OVER SEWER MAIN | GREASE AND RAGS BLOCKAGE | STORM CONTROL CHANNEL | THE WASTEWATER FLOWED OUT OF "PICK HOLES" IN M
| 940311 | 0340PM | WILLIAM F. GRAHAM | 6195277456 | SAN DIEGO, CITY OF | 940311 | 1115AM | 940311 | 1130AM |  | 120 | GAL |  | 898 SUNSET CLIFFS BLVD. | SAN DIEGO | SD | PUMP STATION #35 | CONTROL FAILURE ON BUBBLER SYSTEM | Y | PACIFIC OCEAN |  |  | Y | Y | ? | POSTED 35 SIGNS SOUTH OF STATION AND 3 SIGNS N |  | SAN DIEGO, CITY OF | 940309 | 1343PM | 940309 | 1445PM | 1240 | GAL | LINDA VISTA RD/VIA LOS CUMBRES | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | SIGNS POSTED.
| 940312 | 0900PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 940312 | 1136AM | 940312 | 0336PM |  | 1200 | GAL |  | IMPERIAL AVE. AND MERLIN DR. | SAN DIEGO | SD | 8"VC SEWER MAIN | DEBRIS BLOCKAGE | Y | CREEK BED, PACIFIC OCE |  |  | Y | N | NA | FLOWED WENT TO CREEK BED AND SOAKED INTO GROUN |  | SAN DIEGO, CITY OF | 940309 | 0933AM | 940309 | 1007AM | 102 | GAL | 38TH AND BETA ST. | SAN DIEGO | SD | 8" VC MAIN | GREASE BLOCKAGE | SOAKED IN CREEK, PACIF | MACHINE RODDED.
| 940312 | 0900PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 940312 | 0827AM | 940312 | 1145PM |  | 9900 | GAL |  | 9255 CAMINO SANTA FE | SAN DIEGO | SD | 12" PVC SEWER MAIN | GREASE BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | NA | FLOW DRIED IN CANYON AT FINTON SAND Co. |  | SAN DIEGO, CITY OF | 940311 | 1115AM | 940311 | 1130AM | 120 | GAL | 898 SUNSET CLIFFS BLVD. | SAN DIEGO | SD | PUMP STATION #35 | CONTROL FAILURE ON BUBBLER SYSTEM | PACIFIC OCEAN | POSTED 35 SIGNS SOUTH OF STATION AND 3 SIGNS N
| 940314 | 0800AM | STEVE F. T. BRADLY | 7145822330 | SANTA MARGARITA WATER DISTRICT | 940313 | 2130PM | 940313 | 2230PM |  | 500 | GAL |  | VERDUGO | MISSION VIEJO | OR | MANHOLE | DEBRIS AND ROOTS | Y | STORM DRAIN, OSO CREEK |  |  | Y | N | NA | SPILL WAS CONTAINED UPON ARRIVAL, THEN AREA WA |  | SAN DIEGO, CITY OF | 940312 | 1136AM | 940312 | 0336PM | 1200 | GAL | IMPERIAL AVE. AND MERLIN DR. | SAN DIEGO | SD | 8"VC SEWER MAIN | DEBRIS BLOCKAGE | CREEK BED, PACIFIC OCE | FLOWED WENT TO CREEK BED AND SOAKED INTO GROUN
| 940313 | 1130AM | EDDIE TAYLOR | 6197288319 | FALLBROOK SANITARY DISTRICT | 940313 | 1130AM | 940313 | 1215PM |  | 10 | GAL |  | 316 KALMIA ST. | SAN DIEGO | SD | CLEANOUT | ROOT BLOCKAGE | NO | NONE |  | AROUND CLEANOUT IN YARD | N | N | NA | UPSTREAM MANHOLE 121. DOWNSTREAM MANHOLE 120. |  | SAN DIEGO, CITY OF | 940312 | 0827AM | 940312 | 1145PM | 9900 | GAL | 9255 CAMINO SANTA FE | SAN DIEGO | SD | 12" PVC SEWER MAIN | GREASE BLOCKAGE | CANYON, PACIFIC OCEAN | FLOW DRIED IN CANYON AT FINTON SAND Co.
| 940313 | 0100PM | EDDIE TAYLOR | 6197288319 | FALLBROOK SANITARY DISTRICT | 940313 | 0100PM | 940313 | 0130PM |  | 5 | GAL |  | 472 EAST KALMIA ST. | SAN DIEGO | SD | 4" CLEANOUT | ROOT BLOCKAGE | NO | NONE |  | AROUND CLEANOUT. | N | N | NA | UPSTREAM MANHOLE F-82. DOWNSTREAM MANHOLE F-81 |  | SANTA MARGARITA WATER DISTRICT | 940313 | 2130PM | 940313 | 2230PM | 500 | GAL | VERDUGO | MISSION VIEJO | OR | MANHOLE | DEBRIS AND ROOTS | STORM DRAIN, OSO CREEK | SPILL WAS CONTAINED UPON ARRIVAL, THEN AREA WA
| 940314 | 1025AM | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 940313 | 1847PM | 940314 | 1025AM |  | 4590 | GAL |  | 2815 HAWTHORN | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | Y | CREEK BED,SD BAY/PACIF |  |  | Y | N | NA | NONE |  | FALLBROOK SANITARY DISTRICT | 940313 | 1130AM | 940313 | 1215PM | 10 | GAL | 316 KALMIA ST. | SAN DIEGO | SD | CLEANOUT | ROOT BLOCKAGE | NONE | UPSTREAM MANHOLE 121. DOWNSTREAM MANHOLE 120.
| 940314 | 1554PM | JIM McCURLEY | 6195258687 | SAN DIEGO, CITY OF | 940314 | 0915AM | 940314 | 1124AM |  | 1320 | GAL |  | 8950 CARLEY CIRCLE | SAN DIEGO | SD | SEWER LINE 8" PVC | ROCK BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | MAIN WAS VACTER AND FLUSHED. THE AREA WAS DEO |  | FALLBROOK SANITARY DISTRICT | 940313 | 0100PM | 940313 | 0130PM | 5 | GAL | 472 EAST KALMIA ST. | SAN DIEGO | SD | 4" CLEANOUT | ROOT BLOCKAGE | NONE | UPSTREAM MANHOLE F-82. DOWNSTREAM MANHOLE F-81
| 940316 | 1445pm | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 940315 | 1227PM | 940316 | 1402PM |  | 7675 | GAL |  | 3606 8TH AVE. IN CANYON | SAN DIEGO | SD | 8 VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, SD BAY/PA |  |  | Y | N | NA | THE RODDING CREW WAS NOT NOTIFIED OF THE PROBL |  | SAN DIEGO, CITY OF | 940313 | 1847PM | 940314 | 1025AM | 4590 | GAL | 2815 HAWTHORN | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | CREEK BED,SD BAY/PACIF | NONE
| 940315 |  | JIM McCURLEY | 6195258687 | SAN DIEGO, CITY OF | 940315 | 1316PM | 940315 | 1436PM |  | 800 | GAL |  | FASHION VALLEY RD & HOTEL CIRC | SAN DIEGO | SD | SEWER LINE 10" VC | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | OVERFLOW DID NOT REACH THE RIVER. AREA WAS DEO |  | SAN DIEGO, CITY OF | 940314 | 0915AM | 940314 | 1124AM | 1320 | GAL | 8950 CARLEY CIRCLE | SAN DIEGO | SD | SEWER LINE 8" PVC | ROCK BLOCKAGE | STORM DRAIN, PACIFIC O | MAIN WAS VACTER AND FLUSHED. THE AREA WAS DEO
| 940315 | 1530PM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 94/03/15 | 0725AM | 940315 | 0900AM |  | 135 | GAL |  | 54TH AND MONTEZUMA RD. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | DRY CREEK, PACIFIC OCE |  |  | Y | N |  | MACHINE RODDED MAIN/DEODORIZED |  | SAN DIEGO, CITY OF | 940315 | 1227PM | 940316 | 1402PM | 7675 | GAL | 3606 8TH AVE. IN CANYON | SAN DIEGO | SD | 8 VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, SD BAY/PA | THE RODDING CREW WAS NOT NOTIFIED OF THE PROBL
| 940317 | 0128AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 94/03/16 | 1754PM | 940316 | 1854PM |  | 120 | GAL |  | 5205 LE BARRON RD. | SAN DIEGO | CA | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | INTO CANYON, PACIFIC O |  |  | Y | N | NA | HAND AND MACHINE RODDED MAIN TO RELIEVE STOPPA |  | SAN DIEGO, CITY OF | 940315 | 1316PM | 940315 | 1436PM | 800 | GAL | FASHION VALLEY RD & HOTEL CIRC | SAN DIEGO | SD | SEWER LINE 10" VC | GREASE BLOCKAGE | STORM DRAIN, PACIFIC O | OVERFLOW DID NOT REACH THE RIVER. AREA WAS DEO
| 940316 | 1430PM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 94/03/16 | 0622AM | 940316 | 1030AM |  | 74400 | GAL |  | 7500 MISSION GORGE RD. | SAN DIEGO | SD | 30" RCP SEWER MAIN | ROCK BLOCKAGE | Y | SAN DIEGO RIVER,DOG BE |  |  | Y | Y | ? | SHUT DOWN E. MISSION GORGE PUMP STATION IN ORD |  | SAN DIEGO, CITY OF | 94/03/15 | 0725AM | 940315 | 0900AM | 135 | GAL | 54TH AND MONTEZUMA RD. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | DRY CREEK, PACIFIC OCE | MACHINE RODDED MAIN/DEODORIZED
83 | 940318 | 1100AM | JAMES E. SMITH | 7146432006 | MOULTON NIGUEL WATER DISTRICT | 94/03/16 | 0630AM | 940316 | 0800AM |  | 300 | GAL |  | PARKING LOT AT TREATMENT PLANT | LAGUNA NIGUEL | OR | MANHOLE IN PARKING LOT | GREASE BUILD-UP IN A FLAT LINE AT 90 DEGREE | Y | STRM CHANNEL, SULPHUR |  |  | Y | N |  | MOST OF THE WATER WAS CONTAINED IN THE PARKING |  | SAN DIEGO, CITY OF | 94/03/16 | 1754PM | 940316 | 1854PM | 120 | GAL | 5205 LE BARRON RD. | SAN DIEGO | CA | 8" VC SEWER MAIN | ROOT BLOCKAGE | INTO CANYON, PACIFIC O | HAND AND MACHINE RODDED MAIN TO RELIEVE STOPPA
| 940321 | 0830AM | R.L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 94/03/20 | 1710PM | 940320 | 2330PM |  | 780 | GAL |  | 40TH AND ORANGE AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | VANDALISM | Y | GROUND, PACIFIC OCEAN |  |  | Y | N |  | CLEARED MANHOLE OF DEBRIS. DEODORIZED AND DIS |  | SAN DIEGO, CITY OF | 94/03/16 | 0622AM | 940316 | 1030AM | 74400 | GAL | 7500 MISSION GORGE RD. | SAN DIEGO | SD | 30" RCP SEWER MAIN | ROCK BLOCKAGE | SAN DIEGO RIVER,DOG BE | SHUT DOWN E. MISSION GORGE PUMP STATION IN ORD
| 940321 | 1400PM | LUCKY BISHOP II | 6197414854 | ESCONDIDO, CITY OF | 94/03/20 | 1345PM | 940320 | 1415PM |  | 1500 | GAL |  | SECOND AVE. & FIG ST. | ESCONDIDO | SD | SEWER, ATLAS PG.8 MH53 | GREASE AND ROOTS IN MAIN LINE | Y | ESCONDIDO CRK,SAN ELIJ |  |  | Y | Y | 10 | AREA WAS DISINFECTED, THEN WASHED DOWN | 83 | MOULTON NIGUEL WATER DISTRICT | 94/03/16 | 0630AM | 940316 | 0800AM | 300 | GAL | PARKING LOT AT TREATMENT PLANT | LAGUNA NIGUEL | OR | MANHOLE IN PARKING LOT | GREASE BUILD-UP IN A FLAT LINE AT 90 DEGREE | STRM CHANNEL, SULPHUR | MOST OF THE WATER WAS CONTAINED IN THE PARKING
| 940321 | 1007AM | E.C. CALHOUN | 6199664875 | OCEANSIDE, CITY OF | 94/03/21 | 0800AM | 940321 | 1000AM |  | 1000 | GAL |  | 4750 CALLE LAS POSITAS | OCEANSIDE | SD | PRIVATE LINE M/H | PROBABLE GREASE | Y | LIBBY LAKE |  |  | Y | Y |  |  |  | SAN DIEGO, CITY OF | 94/03/20 | 1710PM | 940320 | 2330PM | 780 | GAL | 40TH AND ORANGE AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | VANDALISM | GROUND, PACIFIC OCEAN | CLEARED MANHOLE OF DEBRIS. DEODORIZED AND DIS
| 940322 | 1535PM | MIKE BEDARD | 6195277425 | SAN DIEGO, CITY OF | 94/03/22 | 1115AM | 940322 | 1145AM |  | 90 | GAL |  | 18700 WEST BERNARDO DRIVE | SAN DIEGO | SD | SEWER PUMP STATION 77 | PORTABLE PUMP DISCHARGE HOSE RUPTURED WHILE | Y | LAKE HODGES, PACIFIC O |  |  | Y | N |  | 50 GAL FROM BLACK TOP INTO SEWER/VACTORED 20 G |  | ESCONDIDO, CITY OF | 94/03/20 | 1345PM | 940320 | 1415PM | 1500 | GAL | SECOND AVE. & FIG ST. | ESCONDIDO | SD | SEWER, ATLAS PG.8 MH53 | GREASE AND ROOTS IN MAIN LINE | ESCONDIDO CRK,SAN ELIJ | AREA WAS DISINFECTED, THEN WASHED DOWN
| 940323 | 0915AM | DISTRICT OFFICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 94/03/23 | 0915AM | 940323 | 0930AM |  | 5 | GAL |  | 316 W. KALMIA | FALLBROOK | SD | 4" CLEANOUT | ROOT BLOCKAGE | NO | NONE |  | BLACK TOP AREA | N | N |  | WASHED DOWN BLACK TOP AREA. PICKED UP ALL SOL |  | OCEANSIDE, CITY OF | 94/03/21 | 0800AM | 940321 | 1000AM | 1000 | GAL | 4750 CALLE LAS POSITAS | OCEANSIDE | SD | PRIVATE LINE M/H | PROBABLE GREASE | LIBBY LAKE
| 940324 | 2229PM | DOUGLAS BRANCO | 6195258687 | SAN DIEGO, CITY OF | 94/03/24 | 1819PM | 940324 | 1949PM |  | 450 | GAL |  | 2257 MONTCLAIR STREET | SAN DIEGO | SD | 8" SEWER LINE | ROOT BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N |  | ROD MAIN. OVERFLOW SOAKED INTO CANYON FLOOR. |  | SAN DIEGO, CITY OF | 94/03/22 | 1115AM | 940322 | 1145AM | 90 | GAL | 18700 WEST BERNARDO DRIVE | SAN DIEGO | SD | SEWER PUMP STATION 77 | PORTABLE PUMP DISCHARGE HOSE RUPTURED WHILE | LAKE HODGES, PACIFIC O | 50 GAL FROM BLACK TOP INTO SEWER/VACTORED 20 G
| 940324 | 1600PM | LEO HARRIS | 6195258682 | SAN DIEGO, CITY OF | 94/03/24 | 0803AM | 940324 | 1248PM |  | 570 | GAL |  | 1300 WEST UPAS STREET | SAN DIEGO | SD | SEWER LINE 6" CP | ROOT BLOCKAGE | Y | SOAKED INTO GRND,PACIF |  |  | Y | N |  | RODDED MAIN 285' SECTION S/O UPAS ST. ON HORTO |  | FALLBROOK SANITARY DISTRICT | 94/03/23 | 0915AM | 940323 | 0930AM | 5 | GAL | 316 W. KALMIA | FALLBROOK | SD | 4" CLEANOUT | ROOT BLOCKAGE | NONE | WASHED DOWN BLACK TOP AREA. PICKED UP ALL SOL
| 940407 | 0314AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 94/03/25 | 0720PM | 940406 | 0720PM |  | 112800 | GAL |  | 8061 HUMMINGBIRD LANE | SAN DIEGO | SD | 8" VC | SEWER MAIN WAS EXPOSED AND BROKEN BY RAIN S | Y | MURRAY CANYON, PACIFIC |  |  | Y | Y | ? | OVERFLOW FROM BROKEN SEWER MAIN WAS DISCOVERED |  | SAN DIEGO, CITY OF | 94/03/24 | 1819PM | 940324 | 1949PM | 450 | GAL | 2257 MONTCLAIR STREET | SAN DIEGO | SD | 8" SEWER LINE | ROOT BLOCKAGE | CANYON, PACIFIC OCEAN | ROD MAIN. OVERFLOW SOAKED INTO CANYON FLOOR.
| 940407 | 0314AM | RANDALL PECOR | 6195277659 | SAN DIEGO, CITY OF | 94/03/25 | 0720PM | 940406 | 0720PM |  | 112800 | GAL |  | 8061 HUMMINGBIRD LANE (CANYON) | SAN DIEGO | SD | 8" VC SEWER MAIN | SEWER MAIN WAS EXPOSED AND BROKEN BY RAIN S | Y | SAN DIEGO RIVER, PACIF |  |  | Y | Y | ? | BROKEN SEWER MAIN WAS DISCOVERED AND CORRECTED |  | SAN DIEGO, CITY OF | 94/03/24 | 0803AM | 940324 | 1248PM | 570 | GAL | 1300 WEST UPAS STREET | SAN DIEGO | SD | SEWER LINE 6" CP | ROOT BLOCKAGE | SOAKED INTO GRND,PACIF | RODDED MAIN 285' SECTION S/O UPAS ST. ON HORTO
| 940327 | 1930PM | R.H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 94/03/27 | 1541PM | 940327 | 1800PM |  | 695 | GAL |  | 2353 SHELTER ISLAND DRIVE | SAN DIEGO | SD | SEWER PUMP STATION 37 | BUBBLER FAILURE | Y | STORM DRAIN, PACIFIC O |  |  | Y | Y | 5 | SIGNS 3 EAST & 2 WEST OF OVERFLOW. BUBBLER RE |  | SAN DIEGO, CITY OF | 94/03/25 | 0720PM | 940406 | 0720PM | 112800 | GAL | 8061 HUMMINGBIRD LANE | SAN DIEGO | SD | 8" VC | SEWER MAIN WAS EXPOSED AND BROKEN BY RAIN S | MURRAY CANYON, PACIFIC | OVERFLOW FROM BROKEN SEWER MAIN WAS DISCOVERED
| 940329 | 0719AM | M.A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 94/03/28 | 2016PM | 940329 | 0041AM |  | 132 | GAL |  | 7146 DENNISON PL | SAN DIEGO | SD | 8" VC SEWER MAIN | UNKNOWN SUBSTANCE CAUSED BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N |  | OVERFLOW HAD STOPPED ON ARRIVAL OF CREW. CAUS |  | SAN DIEGO, CITY OF | 94/03/25 | 0720PM | 940406 | 0720PM | 112800 | GAL | 8061 HUMMINGBIRD LANE (CANYON) | SAN DIEGO | SD | 8" VC SEWER MAIN | SEWER MAIN WAS EXPOSED AND BROKEN BY RAIN S | SAN DIEGO RIVER, PACIF | BROKEN SEWER MAIN WAS DISCOVERED AND CORRECTED
| 940330 | 0339AM | M.A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 94/03/29 | 2115PM | 940329 | 2315PM |  | 120 | GAL |  | INTSECT'N OF THERMAL & EVERGRN | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N |  | RODDED MAIN FROM MH 1692 TO 1695. REMOVED LIG |  | SAN DIEGO, CITY OF | 94/03/27 | 1541PM | 940327 | 1800PM | 695 | GAL | 2353 SHELTER ISLAND DRIVE | SAN DIEGO | SD | SEWER PUMP STATION 37 | BUBBLER FAILURE | STORM DRAIN, PACIFIC O | SIGNS 3 EAST & 2 WEST OF OVERFLOW. BUBBLER RE
| 940329 | 1700PM | ADKINS | 6197258731 | CAMP PENDLETON | 94/03/29 | 1700PM | 940329 | 2140PM |  | 2000 | GAL |  | BETWEEN CHAPEL & GYM IN 33 AR. | CAMP PENDLETON | SD |  | LINE BLOCKAGE | N |  |  | DOWN EMBANKMENT INTO BRUSH | Y | N |  | SEWAGE CLEANED UP AND AREA COVERED WITH LIME. |  | SAN DIEGO, CITY OF | 94/03/28 | 2016PM | 940329 | 0041AM | 132 | GAL | 7146 DENNISON PL | SAN DIEGO | SD | 8" VC SEWER MAIN | UNKNOWN SUBSTANCE CAUSED BLOCKAGE | STORM DRAIN, PACIFIC O | OVERFLOW HAD STOPPED ON ARRIVAL OF CREW. CAUS
| 940331 | 0339AM | M.A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 94/03/30 | 1405PM | 940330 | 1935PM |  | 1650 | GAL |  | MONTEZUMA RD. E. OF FAIRMONT | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOTS | Y | CANYON, PACIFIC OCEAN |  |  | Y | N |  | RODDED MAIN FROM MH 18132 ON LUCILLE DR. TO MH |  | SAN DIEGO, CITY OF | 94/03/29 | 2115PM | 940329 | 2315PM | 120 | GAL | INTSECT'N OF THERMAL & EVERGRN | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE | STORM DRAIN, PACIFIC O | RODDED MAIN FROM MH 1692 TO 1695. REMOVED LIG
| 940331 |  | M.A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 94/03/30 | 2023PM | 940330 | 2123PM |  | 300 | GAL |  | LAKE MURRAY BLVD. & LYNNHAVEN | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOTS | Y | STORM DRAIN, PACIFIC O |  |  | Y | N |  | RODDED MAIN. |  | CAMP PENDLETON | 94/03/29 | 1700PM | 940329 | 2140PM | 2000 | GAL | BETWEEN CHAPEL & GYM IN 33 AR. | CAMP PENDLETON | SD |  | LINE BLOCKAGE |  | SEWAGE CLEANED UP AND AREA COVERED WITH LIME.
| 940404 | 0805AM | MIKE MARTINEZ | 6197259756 | CAMP PLENDLETON | 94/04/02 | 1600PM | 940402 | 1836PM |  | 75 | GAL |  | MARINE,BLDG 302,DE LUZ HOUSING | CAMP PENDLETON | SD | BLDG 302, DE LUZ HOUSING | DIAPER BLOCKAGE | NO | NONE |  | LAWN AREA | Y | N | NA | LIME WAS APPLIED TO AREA. |  | SAN DIEGO, CITY OF | 94/03/30 | 1405PM | 940330 | 1935PM | 1650 | GAL | MONTEZUMA RD. E. OF FAIRMONT | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOTS | CANYON, PACIFIC OCEAN | RODDED MAIN FROM MH 18132 ON LUCILLE DR. TO MH
| 940404 | 0805AM | MIKE MARTINEZ | 6197259756 | CAMP PENDLETON | 94/04/02 | 2200PM | 940403 | 0155AM |  | 5 | GAL |  | 108 CHOSIN, DE LUZ HOUSING | CAMP PLENDLETON | SD | 108 CHOSIN, DE LUZ HOUSING | ROOT BLOCKAGE | NO | NONE |  | LAWN AREA | Y | N | NA | THE AREA WAS DISINFECTED WITH LIME. |  | SAN DIEGO, CITY OF | 94/03/30 | 2023PM | 940330 | 2123PM | 300 | GAL | LAKE MURRAY BLVD. & LYNNHAVEN | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOTS | STORM DRAIN, PACIFIC O | RODDED MAIN.
| 940404 | 0700AM | ROBERT BRAUN | 6196602007 | SAN DIEGO, COUNTY OF | 94/04/03 | 1900PM | 940403 | 2230PM |  | 110 | GAL |  | EAST 3133 HIGHLAND BLVD. | SPRING VALLEY | SD | MANHOLE, 1" HOLE IN LID | POSSIBLE ROOTS OR BROKEN PIPE | NO | NONE |  | SOAKED AROUND MANHOLE | Y | N |  | AREA WAS CHLORINATED AND THEN WAS WASHED DOWN. |  | CAMP PLENDLETON | 94/04/02 | 1600PM | 940402 | 1836PM | 75 | GAL | MARINE,BLDG 302,DE LUZ HOUSING | CAMP PENDLETON | SD | BLDG 302, DE LUZ HOUSING | DIAPER BLOCKAGE | NONE | LIME WAS APPLIED TO AREA.
| 940494 | 0815AM | KENNY RODRIGUEZ | 6197281180 | FALLBROOK SANITARY DISTRICT | 94/04/03 | 0830AM | 940403 | 1015AM |  | 5500 | GAL |  | So. of MISSION ST 200 | FALLBROOK | SD | 10" PVC 900 PIPE FORCEMAIN | 10" SPLIT ALONG TOP OF PIPE. | Y | CREEK,S MISSION/OVERLA |  |  | Y | N | NA | FORCEMAIN PIPE HAS BEEN REPAIRED |  | CAMP PENDLETON | 94/04/02 | 2200PM | 940403 | 0155AM | 5 | GAL | 108 CHOSIN, DE LUZ HOUSING | CAMP PLENDLETON | SD | 108 CHOSIN, DE LUZ HOUSING | ROOT BLOCKAGE | NONE | THE AREA WAS DISINFECTED WITH LIME.
| 940405 | 1430PM | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 94/04/05 | 0800AM | 940405 | 1100AM |  | 360 | GAL |  | 2359 AIRLANE | SAN DIEGO | SD | 8" VC | GREASE BLOCKAGE | Y | PACIFIC OCEAN |  |  | Y | N | NA | NONE |  | SAN DIEGO, COUNTY OF | 94/04/03 | 1900PM | 940403 | 2230PM | 110 | GAL | EAST 3133 HIGHLAND BLVD. | SPRING VALLEY | SD | MANHOLE, 1" HOLE IN LID | POSSIBLE ROOTS OR BROKEN PIPE | NONE | AREA WAS CHLORINATED AND THEN WAS WASHED DOWN.
| 940406 | 0051AM | M.A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 94/04/05 | 1435PM | 940405 | 1535PM |  | 30 | GAL |  | 2521 G. ST. ALLEY E/O 25TH ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N |  | ROD 320' SECTION, MEDIUM ROOTS FOUND IN MAIN. |  | FALLBROOK SANITARY DISTRICT | 94/04/03 | 0830AM | 940403 | 1015AM | 5500 | GAL | So. of MISSION ST 200 | FALLBROOK | SD | 10" PVC 900 PIPE FORCEMAIN | 10" SPLIT ALONG TOP OF PIPE. | CREEK,S MISSION/OVERLA | FORCEMAIN PIPE HAS BEEN REPAIRED
| 940406 | 1010AM | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 94/04/06 | 1058AM | 940406 | 1300PM |  | 12.2 | GAL |  | 2359 AIRLANE IN DRIVEWAY | SAN DIEGO | SD | 8" VC | GREASE BLOCKAGE | Y | SAN DIEGO BAY, PACIFIC |  |  | Y | N | NA | AREA WAS DEODORIZED AND CLEAR UP. |  | SAN DIEGO, CITY OF | 94/04/05 | 0800AM | 940405 | 1100AM | 360 | GAL | 2359 AIRLANE | SAN DIEGO | SD | 8" VC | GREASE BLOCKAGE | PACIFIC OCEAN | NONE
| 940407 | 0845PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 94/04/07 | 0845PM | 940407 | 1115PM |  | 50 | GAL |  | 610 GOLDEN ROAD | FALLBROOK | SD | CLEANOUT (POSSIBLE MAINLINE) | PAPER BLOCKAGE | NO | NONE |  | DOWN ROAD | N | N | NA | OPENED 10' FROM CLEANOUT, UPSTREAM MH G-120, D |  | SAN DIEGO, CITY OF | 94/04/05 | 1435PM | 940405 | 1535PM | 30 | GAL | 2521 G. ST. ALLEY E/O 25TH ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, PACIFIC O | ROD 320' SECTION, MEDIUM ROOTS FOUND IN MAIN.
| 940410 | 2000PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 94/04/10 | 1152AM | 940410 | 1322PM |  | 90 | GAL |  | 60TH AND UNIVERSITY AVENUE | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N |  | FLOW WENT INTO STORM DRAIN AT 60TH & UNIVERSIT |  | SAN DIEGO, CITY OF | 94/04/06 | 1058AM | 940406 | 1300PM | 12.2 | GAL | 2359 AIRLANE IN DRIVEWAY | SAN DIEGO | SD | 8" VC | GREASE BLOCKAGE | SAN DIEGO BAY, PACIFIC | AREA WAS DEODORIZED AND CLEAR UP.
| 940410 | 2000PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 94/04/10 | 0857AM | 940410 | 1157AM |  | 180 | GAL |  | 5880 UNIVERSITY AVENUE | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N |  | FLOW WENT TO STORM DRAIN, THEN TO CANYON AND S |  | FALLBROOK SANITARY DISTRICT | 94/04/07 | 0845PM | 940407 | 1115PM | 50 | GAL | 610 GOLDEN ROAD | FALLBROOK | SD | CLEANOUT (POSSIBLE MAINLINE) | PAPER BLOCKAGE | NONE | OPENED 10' FROM CLEANOUT, UPSTREAM MH G-120, D
| 940410 | 2015PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 94/04/10 | 1603PM | 940410 | 1703PM |  | 300 | GAL |  | 4818 MT. ELBRUS DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N |  | FLOWED INTO CANYON ADJACENT TO ADDRESS, AND SO |  | SAN DIEGO, CITY OF | 94/04/10 | 1152AM | 940410 | 1322PM | 90 | GAL | 60TH AND UNIVERSITY AVENUE | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | CANYON, PACIFIC OCEAN | FLOW WENT INTO STORM DRAIN AT 60TH & UNIVERSIT
| 940410 | 2015PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 94/04/10 | 0954AM | 940410 | 1130AM |  | 960 | GAL |  | VIA ANDAR | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N |  | FLOW WENT TO CANYON AND SOAKED INTO GROUND |  | SAN DIEGO, CITY OF | 94/04/10 | 0857AM | 940410 | 1157AM | 180 | GAL | 5880 UNIVERSITY AVENUE | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, PACIFIC O | FLOW WENT TO STORM DRAIN, THEN TO CANYON AND S
| 940412 | 1520PM | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 94/04/12 | 1057AM | 940412 | 1300PM |  | 246 | GAL |  | CHATSWORTH AND LYTTON | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N |  | STORM DRAIN AT ROSECRANS AND LYTTON |  | SAN DIEGO, CITY OF | 94/04/10 | 1603PM | 940410 | 1703PM | 300 | GAL | 4818 MT. ELBRUS DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | CANYON, PACIFIC OCEAN | FLOWED INTO CANYON ADJACENT TO ADDRESS, AND SO
| 940414 | 0908AM | HELIX IRRIGATION | 6194645934 | LEMON GROVE, CITY OF | 94/04/14 | 0908AM | 940414 | 1115AM |  | 18000 | GAL |  | 1987 ENSENADA STREET | LEMON GROVE | SD | REAR EASEMENT | ROCKS, VANDALISM | NO | NONE |  | DRY DRAINAGE DITCH ADJ. TO MH | Y | N | NA | REMOVED ROCKS FROM 8" LINE. AREA CHLORINATED. |  | SAN DIEGO, CITY OF | 94/04/10 | 0954AM | 940410 | 1130AM | 960 | GAL | VIA ANDAR | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | CANYON, PACIFIC OCEAN | FLOW WENT TO CANYON AND SOAKED INTO GROUND
| 940415 | 1930PM | DON EVANS | 6195258685 | SAN DIEGO, CITY OF | 94/04/15 | 1008AM | 940415 | 1550PM |  | 96 | GAL |  | 4127 38TH STREET | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | NO | NONE |  | VACTORED AND RETURNED TO SEWER | Y | N | NA | ALL SEWAGE VACUMED UP, FLOW FROM CLEAN OUT |  | SAN DIEGO, CITY OF | 94/04/12 | 1057AM | 940412 | 1300PM | 246 | GAL | CHATSWORTH AND LYTTON | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, PACIFIC O | STORM DRAIN AT ROSECRANS AND LYTTON
| 940418 | 0400PM | CHUCK J. LOCKHART | 6197414835 | ESCONDIDO, CITY OF | 94/04/16 | 0130PM | 940416 | 0400PM |  | 20 | GAL |  | 1521 S. HALE | ESCONDIDO | SD | HALF INCH IRRIGATION | BROKEN IRRIGATION LINE | Y | ESCONDIDO, SAN ELIJO P |  |  | Y | N | NA | A DISCHARGE MAY NOT HAVE OCCURRED, WE ARE REPO |  | LEMON GROVE, CITY OF | 94/04/14 | 0908AM | 940414 | 1115AM | 18000 | GAL | 1987 ENSENADA STREET | LEMON GROVE | SD | REAR EASEMENT | ROCKS, VANDALISM | NONE | REMOVED ROCKS FROM 8" LINE. AREA CHLORINATED.
| 940417 | 0800PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 94/04/17 | 0800PM | 940417 | 0900PM |  | 15 | GAL |  | 425 PORTER ST. | FALLBROOK | SD | CLEANOUT | ROOT BLOCKAGE | NO | NONE |  | AROUND CLEANOUT | N | N | NA | OPEN 15' INTO MAINLINE, FLUSHED LINE, COMPLETE |  | SAN DIEGO, CITY OF | 94/04/15 | 1008AM | 940415 | 1550PM | 96 | GAL | 4127 38TH STREET | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | NONE | ALL SEWAGE VACUMED UP, FLOW FROM CLEAN OUT
| 940417 | 1130PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 94/04/17 | 0600AM | 940418 | 0720AM |  | 20 | GAL |  | 606 GOLDEN ROAD | FALLBROOK | SD | CLEANOUT | ROOTS OFFSET JOINT | NO | NONE |  | AROUND CLEANOUT | N | N | NA | OPENED 5' FROM CLEANOUT, UPSTREAM MH G-120 AND |  | ESCONDIDO, CITY OF | 94/04/16 | 0130PM | 940416 | 0400PM | 20 | GAL | 1521 S. HALE | ESCONDIDO | SD | HALF INCH IRRIGATION | BROKEN IRRIGATION LINE | ESCONDIDO, SAN ELIJO P | A DISCHARGE MAY NOT HAVE OCCURRED, WE ARE REPO
| 940419 | 1130AM | MIKE BEDARD | 6195277425 | SAN DIEGO, CITY OF | 94/04/18 | 0200PM | 940418 | 0315PM |  | 2625 | GAL |  | 988 LA JOLLA FARMS RD. | SAN DIEGO | SD | SEWER PUMP STATION #45 | PUMPS LEFT OFF | Y | CANYON, PACIFIC OCEAN |  |  | Y | Y | 02 | 10 SIGNS POSTED ON WEST SIDE OF THE STATION. S |  | FALLBROOK SANITARY DISTRICT | 94/04/17 | 0800PM | 940417 | 0900PM | 15 | GAL | 425 PORTER ST. | FALLBROOK | SD | CLEANOUT | ROOT BLOCKAGE | NONE | OPEN 15' INTO MAINLINE, FLUSHED LINE, COMPLETE
| 940419 | 0700PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 94/04/19 | 0645PM | 940419 | 0730PM |  | 20 | GAL |  | 462 AMMUNITION | FALLBROOK | SD | CLEANOUT | GREASE IN LINE. | NO | NONE |  | DOWN THE ROAD. | N | N | NA | OPEN 15' FROMM CLEANOUT UPSTREAM MH C-67 AND D |  | FALLBROOK SANITARY DISTRICT | 94/04/17 | 0600AM | 940418 | 0720AM | 20 | GAL | 606 GOLDEN ROAD | FALLBROOK | SD | CLEANOUT | ROOTS OFFSET JOINT | NONE | OPENED 5' FROM CLEANOUT, UPSTREAM MH G-120 AND
| 940420 | 1530PM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 94/04/20 | 0952AM | 940420 | 1300PM |  | 188 | GAL |  | 2915 CHAMOUNE AVE. | SAN DIEGO | SD | 8" VR SEWER MAIN | ROOT BLOCKAGE | f | wetlands will be impac | g an unnamed tribu | Marcos Creek. |  |  |  | unnamed tributary to San Marcos Creek |  | SAN DIEGO, CITY OF | 94/04/18 | 0200PM | 940418 | 0315PM | 2625 | GAL | 988 LA JOLLA FARMS RD. | SAN DIEGO | SD | SEWER PUMP STATION #45 | PUMPS LEFT OFF | CANYON, PACIFIC OCEAN | 10 SIGNS POSTED ON WEST SIDE OF THE STATION. S
| 940421 | 1545PM | JIM McCURLEY | 6195258687 | SAN DIEGO, CITY OF | 94/04/21 | 0914AM | 940421 | 1014AM |  | 30 | GAL |  | 18525 BERNARDO TRAILS DR. | SAN DIEGO | SD | SEWER LINE 8" PVC | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | 117' SECTION WAS MACHINE RODDED TO CLEAR A ROO |  | FALLBROOK SANITARY DISTRICT | 94/04/19 | 0645PM | 940419 | 0730PM | 20 | GAL | 462 AMMUNITION | FALLBROOK | SD | CLEANOUT | GREASE IN LINE. | NONE | OPEN 15' FROMM CLEANOUT UPSTREAM MH C-67 AND D
| 940422 | 0320PM | E. SWANSON | 6195257442 | SAN DIEGO, CITY OF | 94/04/21 | 0230PM | 940421 | 0330PM |  | 300 | GAL |  | CHOLLAS PKWY & BOYCE | SAN DIEGO | SD | 8" PVC SEWER MAIN | VANDALS BROKE PIPE, WHILE THE CREW MADE REP | Y | SAN DIEGO BAY/ PACIFIC |  |  | Y | N | NA | CREW REPAIRED SEWER MAIN BROKEN BY VANDALS. |  | SAN DIEGO, CITY OF | 94/04/20 | 0952AM | 940420 | 1300PM | 188 | GAL | 2915 CHAMOUNE AVE. | SAN DIEGO | SD | 8" VR SEWER MAIN | ROOT BLOCKAGE | wetlands will be impac | unnamed tributary to San Marcos Creek
| 0 | ? | RICHARD ANDREWS | 6197553294 | DEL MAR, CITY OF | 94/04/21 | 0614PM | 940421 | 0711PM |  | 1800 | GAL |  | NB ON RAMP/JIMMY DURANTE BLVD | DEL MAR | SD | SEWER MAIN | LINE OBSTRUCTION | NO | NONE |  | DRAINAGE DITCH | Y | N | NA | NONE |  | SAN DIEGO, CITY OF | 94/04/21 | 0914AM | 940421 | 1014AM | 30 | GAL | 18525 BERNARDO TRAILS DR. | SAN DIEGO | SD | SEWER LINE 8" PVC | ROOT BLOCKAGE | STORM DRAIN, PACIFIC O | 117' SECTION WAS MACHINE RODDED TO CLEAR A ROO
| 940422 | 0524AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 94/04/21 | 1502PM | 940421 | 1632PM |  | 45 | GAL |  | 4041 T ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | PACIFIC OCEAN |  |  | Y | N | NA | RODDED MAIN. DEODORIZED AREA AND CLEAN UP SCHO |  | SAN DIEGO, CITY OF | 94/04/21 | 0230PM | 940421 | 0330PM | 300 | GAL | CHOLLAS PKWY & BOYCE | SAN DIEGO | SD | 8" PVC SEWER MAIN | VANDALS BROKE PIPE, WHILE THE CREW MADE REP | SAN DIEGO BAY/ PACIFIC | CREW REPAIRED SEWER MAIN BROKEN BY VANDALS.
| 940423 | 0900PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 94/04/23 | 0147PM | 940423 | 0330PM |  | 515 | GAL |  | 302 BILLOW DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | ? | SWEPT BACK INTO MA | SWEPT BACK INTO MANHOLE | Y | N | NA | ALL FLOW WAS SWEPT BACK INTO MANHOLE. |  | DEL MAR, CITY OF | 94/04/21 | 0614PM | 940421 | 0711PM | 1800 | GAL | NB ON RAMP/JIMMY DURANTE BLVD | DEL MAR | SD | SEWER MAIN | LINE OBSTRUCTION | NONE | NONE
| 940424 | 0940PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 94/04/24 | 0710PM | 940424 | 0840PM |  | 450 | GAL |  | 47TH AND FRANKLIN | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC O |  |  | Y | N | NA | FLOW DRIED IN STORM DRAIN |  | SAN DIEGO, CITY OF | 94/04/21 | 1502PM | 940421 | 1632PM | 45 | GAL | 4041 T ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | PACIFIC OCEAN | RODDED MAIN. DEODORIZED AREA AND CLEAN UP SCHO
| 940426 | 1545PM | FRANK PADUN | 6195277443 | SAN DIEGO, CITY OF | 94/04/25 | 0930AM | 940425 | 1030AM |  | 120 | GAL |  | 3655 VAN DYKC AVE. | SAN DIEGO | SD | 4" SEWER LATERAL | WOMAN'S HIGH HEEL SHOE RETRIEVED FROM 4" SE | Y | ALLEY |  |  | Y | N | NA | ALLEY WAS VACTORED OF ALL RAW SEWAGE ON 940425 |  | SAN DIEGO, CITY OF | 94/04/23 | 0147PM | 940423 | 0330PM | 515 | GAL | 302 BILLOW DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | ? | ALL FLOW WAS SWEPT BACK INTO MANHOLE.
| 940426 | 0730AM | BILL SANCET | 6197253868 | CAMP PENDLETON | 94/04/25 | ? | 940425 | 1145AM |  | 70 | GAL |  | UNKNOWN | SAN DIEGO | SD | CLOSEST BLDG, 31334 | LIFT STATION PUMP MALFUNCTION | NO | NONE |  | AROUND MANHOLE IN STREET | Y | N | NA | NONE |  | SAN DIEGO, CITY OF | 94/04/24 | 0710PM | 940424 | 0840PM | 450 | GAL | 47TH AND FRANKLIN | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, PACIFIC O | FLOW DRIED IN STORM DRAIN
| 940425 | 1626PM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 94/04/25 | 0940AM | 940425 | 1000AM |  | 40 | GAL |  | 338 35TH ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | IN YARD, PACIFIC OCEAN |  |  | Y | N | NA | FLUSH, CLEAN UP, AND DEODORIZED AREA. |  | SAN DIEGO, CITY OF | 94/04/25 | 0930AM | 940425 | 1030AM | 120 | GAL | 3655 VAN DYKC AVE. | SAN DIEGO | SD | 4" SEWER LATERAL | WOMAN'S HIGH HEEL SHOE RETRIEVED FROM 4" SE | ALLEY | ALLEY WAS VACTORED OF ALL RAW SEWAGE ON 940425
| 940426 | 0545AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 94/04/25 | 1442PM | 940425 | 1612PM |  | 90 | GAL |  | 4165 MONROE AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | NO | NONE |  | CONTAINED IN ALLEY | Y | N | NA | RODDED MAIN AND DEODORIZED AREA. |  | CAMP PENDLETON | 94/04/25 | ? | 940425 | 1145AM | 70 | GAL | UNKNOWN | SAN DIEGO | SD | CLOSEST BLDG, 31334 | LIFT STATION PUMP MALFUNCTION | NONE | NONE
| 940427 | 1400PM | JOEL HOLT | 6197281180 | FALLBROOK SANITARY DISTRICT | 94/04/27 | 0920AM | 940427 | 1000AM |  | 3600 | GAL |  | 1425 S. ALTURAS | FALLBROOK | SD | STORM WATER CONTAINMENT | PIPE FAILURE | Y | FALLBROOK CREEK | LAKE O'NEILL, CAMP |  | Y |  |  | 3600 GALS. RECLAIMED WATER & 8 OR 10 GALS. FLO |  | SAN DIEGO, CITY OF | 94/04/25 | 0940AM | 940425 | 1000AM | 40 | GAL | 338 35TH ST. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | IN YARD, PACIFIC OCEAN | FLUSH, CLEAN UP, AND DEODORIZED AREA.
| 940428 | 1320PM | MICHAEL BASOM | 6195277442 | SAN DIEGO, CITY OF | 94/04/28 | 0900AM | 940428 | 1200PM |  | 540 | GAL |  | CHOLLAS PKY & BOYCE LN | SAN DIEGO | SD | 8" PVC GRAVITY MAIN | RAIN RUNOFF WASHED OUT SUPPORTS UNDER GRAVI | Y | CHOLLAS CREEK/SAN DIEG |  |  | Y | Y |  |  |  | SAN DIEGO, CITY OF | 94/04/25 | 1442PM | 940425 | 1612PM | 90 | GAL | 4165 MONROE AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | NONE | RODDED MAIN AND DEODORIZED AREA.
1 | 940501 | 1050PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 94/05/01 | 0423PM | 940501 | 0745PM | N | 202 | GAL | 0 | 2029 DEL MAR HTS. ROAD | SAN DEIGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | PACIFIC OCEAN |  |  | Y | N | N/A | UPON ARRIVAL TO SITE THE OVERFLOW HAD STOPPED. IT DRIED ON STREET. |  | FALLBROOK SANITARY DISTRICT | 94/04/27 | 0920AM | 940427 | 1000AM | 3600 | GAL | 1425 S. ALTURAS | FALLBROOK | SD | STORM WATER CONTAINMENT | PIPE FAILURE | FALLBROOK CREEK | 3600 GALS. RECLAIMED WATER & 8 OR 10 GALS. FLO
2 | 940502 | ?? | BILL RUTH | 6194287401 | INTERNATIONAL BOUNDARY & WATER | 94/05/01 | 0600AM | 940503 | 0600AM | N | 36000000 | GAL | 0 | TIJUANA RIVER VALLEY | SAN DIEGO | SD | 42" PRESSURE LINE | ?? | Y | TIJUANA RIVER, PACIFIC OCEAN |  |  | Y | Y | ? | ESTIMATED TIME OF REPAIR; 72 HOURS FROM THE TIME OF THE BREAK |  | SAN DIEGO, CITY OF | 94/04/28 | 0900AM | 940428 | 1200PM | 540 | GAL | CHOLLAS PKY & BOYCE LN | SAN DIEGO | SD | 8" PVC GRAVITY MAIN | RAIN RUNOFF WASHED OUT SUPPORTS UNDER GRAVI | CHOLLAS CREEK/SAN DIEG
3 | 940501 | 1220PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 94/05/01 | 0935AM | 940501 | 1035AM | N | 2400 | GAL | 0 | 15706 CAMINO CRISALIDA | SAN DIEGO | SD | 8" PVC MAIN | GREASE BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | N/A | FLOWED INTO CANYON WHERE IT WAS ABSORBED INTO GROUND | 1 | SAN DIEGO, CITY OF | 94/05/01 | 0423PM | 940501 | 0745PM | 202 | GAL | 2029 DEL MAR HTS. ROAD | SAN DEIGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | PACIFIC OCEAN | UPON ARRIVAL TO SITE THE OVERFLOW HAD STOPPED. IT DRIED ON STREET.
4 | 940502 | 0200PM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 94/05/02 | 0700AM | 940502 | 0900AM | N | 1200 | GAL | 0 | DEL MAR HTS. RD. & CAMINO DEL MAR | DEL MAR | SD | 8" VC OVERFLOW SYST. | GRAVITY MAIN BREAK | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | Y | 005 | SIGNS WERE POSTED ON THE BEACH AT ENTRY & 50' APART-MAIN REPAIRED BY CITY CREW. | 2 | INTERNATIONAL BOUNDARY & WATER | 94/05/01 | 0600AM | 940503 | 0600AM | 36000000 | GAL | TIJUANA RIVER VALLEY | SAN DIEGO | SD | 42" PRESSURE LINE | ?? | TIJUANA RIVER, PACIFIC OCEAN | ESTIMATED TIME OF REPAIR; 72 HOURS FROM THE TIME OF THE BREAK
5 | 940503 | 0745AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 94/05/02 | 1017AM | 940502 | 1130AM | N | 584 | GAL | 0 | UNIVERSITY AVE./WIGHTMAN ST. ALLEY | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | PACIFIC OCEAN |  |  | Y | N | N/A | OVERFLOW SOAKED INTO GROUN, AND DEODORIZED THE AREA | 3 | SAN DIEGO, CITY OF | 94/05/01 | 0935AM | 940501 | 1035AM | 2400 | GAL | 15706 CAMINO CRISALIDA | SAN DIEGO | SD | 8" PVC MAIN | GREASE BLOCKAGE | CANYON, PACIFIC OCEAN | FLOWED INTO CANYON WHERE IT WAS ABSORBED INTO GROUND
6 | 940503 | 1500PM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 94/05/02 | 1400PM | 940503 | 0300AM | Y | 1241000 | GAL | 0 | 3476 MISSION AVE., INT. WITH MESA BLVD & GARRISON | OCEANSIDE | SD | 42" GATE VALVE | CONTRACTOR BROKE A 42" GATE VALVE OFF SEWER MAIN. | Y | LOMA ALTA CREEK, BUENA VISTA CREEK | BUCCANEER BEACH, BUENA VISTA LAGOON |  | Y | Y | 002 | 1MG OF SEWAGE FLOWED INTO LOMA ALTA CREEK, 0.124 MG OF SEWAGE FLOWED INTO BUENA VISTA LAGOON. | 4 | SAN DIEGO, CITY OF | 94/05/02 | 0700AM | 940502 | 0900AM | 1200 | GAL | DEL MAR HTS. RD. & CAMINO DEL MAR | DEL MAR | SD | 8" VC OVERFLOW SYST. | GRAVITY MAIN BREAK | STORM DRAIN, PACIFIC OCEAN | SIGNS WERE POSTED ON THE BEACH AT ENTRY & 50' APART-MAIN REPAIRED BY CITY CREW.
7 | 940502 | 1045PM | JOHN VAUGHT | 6197414854 | ESCONDIDO, CITY OF | 94/05/02 | 0830AM | 940502 | 0915AM | N | 250 | GAL | 0 | 116 W. 13TH C/L MAPLE | ESCONDIDO | SD | SEWER ATLAS MH22 P11 | PLASTIC BAGS IN MAIN LINE CAUSED THE OBSTRUCTION | Y | STORM DRAIN |  |  | Y | N | N/A | WASTEWATER DID NOT REACH SURFACE WATERS. | 5 | SAN DIEGO, CITY OF | 94/05/02 | 1017AM | 940502 | 1130AM | 584 | GAL | UNIVERSITY AVE./WIGHTMAN ST. ALLEY | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | PACIFIC OCEAN | OVERFLOW SOAKED INTO GROUN, AND DEODORIZED THE AREA
8 | 940503 | 1030AM | ROBRT WADE | 6197891330 | RAMONA MUNICIPAL WATER DIST. | 94/05/03 | 0800AM | 940503 | 0810AM | N | 7000 | GAL | 0 | 22758 SAN VICENTE ROAD | RAMONA | SD | MH#1, PLANT HEADWORK | GREASE BLOCKAGE | NO | NONE |  | DISTRICT PROPERTY | Y | Y | 002 | LARGE AMOUNTS OF GREASE FLOWED INTO PLANT HEADWORKS CAUSING THE MANHOLE TO OVERFLOW. | 6 | OCEANSIDE, CITY OF | 94/05/02 | 1400PM | 940503 | 0300AM | 1241000 | GAL | 3476 MISSION AVE., INT. WITH MESA BLVD & GARRISON | OCEANSIDE | SD | 42" GATE VALVE | CONTRACTOR BROKE A 42" GATE VALVE OFF SEWER MAIN. | LOMA ALTA CREEK, BUENA VISTA CREEK | 1MG OF SEWAGE FLOWED INTO LOMA ALTA CREEK, 0.124 MG OF SEWAGE FLOWED INTO BUENA VISTA LAGOON.
9 | 940503 | 1305PM | BOB MANRY | 9096764101 | RANCHO CALIF. WATER DISTRICT | 94/05/03 | 0500AM | 940503 | 0700AM | N | 6000 | GAL | 0 | 38427 VIA ALISOL | MURRIETA | RIV | CHLORINE CONTACT BOX | FLOAT SWITCH TOO HIGH TO SHUT DOWN PUMPS. | NO | NONE |  | DRIED IN MURRITA CREEK | Y | N | N/A | CORRECTED FLOAT SWITCH PROBLEM. CHLORINATED FINAL EFFLUENT. | 7 | ESCONDIDO, CITY OF | 94/05/02 | 0830AM | 940502 | 0915AM | 250 | GAL | 116 W. 13TH C/L MAPLE | ESCONDIDO | SD | SEWER ATLAS MH22 P11 | PLASTIC BAGS IN MAIN LINE CAUSED THE OBSTRUCTION | STORM DRAIN | WASTEWATER DID NOT REACH SURFACE WATERS.
10 | 940505 | 0810AM | SANCET X3868 | X3868 | CAMP PENDLETON | 94/05/04 | 1215AM | 940504 | 1230AM | N | 1500 | GAL | 0 | 51849 BLDG ONOFRE BEACH ROAD | CAMP PENDLETON | SD | 51849 | BROKEN DISCHARGE LINE FROM LIFT STATION | NO | NONE |  | ROADWAY/SHOULDER | Y | N | N/A | LIMED AREA | 8 | RAMONA MUNICIPAL WATER DIST. | 94/05/03 | 0800AM | 940503 | 0810AM | 7000 | GAL | 22758 SAN VICENTE ROAD | RAMONA | SD | MH#1, PLANT HEADWORK | GREASE BLOCKAGE | NONE | LARGE AMOUNTS OF GREASE FLOWED INTO PLANT HEADWORKS CAUSING THE MANHOLE TO OVERFLOW.
11 | 940505 | 1300PM | ORV SALISBURY | 6197440460 | VALLECITOS WATER DISTRICT | 94/05/04 | 2000PM | 940505 | 0930AM | N | 20000 | GAL | 0 | MISSION RD./BENNET DR. IN AN EASMENT | SAN MARCOS | SD | S4G-Q1-MH9:P22-A1 | SEPTIC PUMPER DUMPING ILLEGAL LOAD CAUSED BLOCKAGE | Y | STORM DRAINS/DITCHES,SAN MARCOS CRK |  |  | Y | Y | 7 | ONCE THE OVERFLOW WAS LOCATED, BLOCKAGE WAS CLEARED WITHIN 1 HR. THE AREA WAS FLUSHED, DISINFECTED & POSTED. | 9 | RANCHO CALIF. WATER DISTRICT | 94/05/03 | 0500AM | 940503 | 0700AM | 6000 | GAL | 38427 VIA ALISOL | MURRIETA | RIV | CHLORINE CONTACT BOX | FLOAT SWITCH TOO HIGH TO SHUT DOWN PUMPS. | NONE | CORRECTED FLOAT SWITCH PROBLEM. CHLORINATED FINAL EFFLUENT.
12 | 940504 | 0833AM | B. SANCET | X3868 | CAMP PENDLETON | 94/05/04 | ?? | 940504 | 0020AM | N | 50 | GAL | 0 | WASH RACK AT 18TH STREET OFF G STREET | CAMP PENDLETON | SD | BUILDING 14137 | MISSING CAP OFF SEWER CLEAN OUT | NO | NONE |  | 100 YARDS FROM CLEAN OUT | Y | N | N/A | CAP WAS REPLACED, AREA DISINFECTED WITH LIME. | 10 | CAMP PENDLETON | 94/05/04 | 1215AM | 940504 | 1230AM | 1500 | GAL | 51849 BLDG ONOFRE BEACH ROAD | CAMP PENDLETON | SD | 51849 | BROKEN DISCHARGE LINE FROM LIFT STATION | NONE | LIMED AREA
13 | 940505 | 2354PM | M.A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 94/05/05 | 1651PM | 940505 | 1751PM | N | 300 | GAL | 0 | 3622 KEMPER COURT | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | RODDED MAIN, DEODORIZED. HEAVY ROOTS IN TWO MANHOLES AND IN MAIN. | 11 | VALLECITOS WATER DISTRICT | 94/05/04 | 2000PM | 940505 | 0930AM | 20000 | GAL | MISSION RD./BENNET DR. IN AN EASMENT | SAN MARCOS | SD | S4G-Q1-MH9:P22-A1 | SEPTIC PUMPER DUMPING ILLEGAL LOAD CAUSED BLOCKAGE | STORM DRAINS/DITCHES,SAN MARCOS CRK | ONCE THE OVERFLOW WAS LOCATED, BLOCKAGE WAS CLEARED WITHIN 1 HR. THE AREA WAS FLUSHED, DISINFECTED & POSTED.
14 | 940505 | 1454PM | B. SANCET | X3868 | CAMP PENDLETON | 94/05/05 | 1150AM | 940505 | 1200PM | N | 300 | GAL | 0 | SEWAGE PLANT #13, VAN JERGRIFT | CAMP PENDLETON | SD | BUILDING 2031 | VALVE FAILURE/DISCHARGE SIDE OF SECONDARY DIGESTER | NO | NONE |  | ON SITE AT SEWAGE PLANT #13 | Y | N | N/A |  | 12 | CAMP PENDLETON | 94/05/04 | ?? | 940504 | 0020AM | 50 | GAL | WASH RACK AT 18TH STREET OFF G STREET | CAMP PENDLETON | SD | BUILDING 14137 | MISSING CAP OFF SEWER CLEAN OUT | NONE | CAP WAS REPLACED, AREA DISINFECTED WITH LIME.
15 | 940509 | 0805AM | R.E. ANDREWS | 6197553294 | DEL MAR, CITY OF | 94/05/06 | 0245PM | 940506 | 0450PM | N | 150 | GAL | 0 | 138 COEAN FRONT | DEL MAR | SD | CLEANOUT/1800 BLOCK | MAIN @ 18TH ST. BLOCKED BY BROKEN MH RAIN GUARD | NO | NONE |  | SAND AND DIERT AT ROAD EDGE | Y | N | N/A | MINOR SPILL DISSIPATED AT ROAD EDGE | 13 | SAN DIEGO, CITY OF | 94/05/05 | 1651PM | 940505 | 1751PM | 300 | GAL | 3622 KEMPER COURT | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, PACIFIC OCEAN | RODDED MAIN, DEODORIZED. HEAVY ROOTS IN TWO MANHOLES AND IN MAIN.
16 | 940506 | 1010PM | G. DONALD EVANS | 6195258685 | SAN DIEGO, CITY OF | 94/05/06 | 0651PM | 940506 | 0851PM | N | 120 | GAL | 0 | 5861 DESERT VIEW DR. | SAN DIEGO | SD | 8" VC MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | FLOWED INTO STORM DRAIN WHERE IT DRIED | 14 | CAMP PENDLETON | 94/05/05 | 1150AM | 940505 | 1200PM | 300 | GAL | SEWAGE PLANT #13, VAN JERGRIFT | CAMP PENDLETON | SD | BUILDING 2031 | VALVE FAILURE/DISCHARGE SIDE OF SECONDARY DIGESTER | NONE
17 | 940506 | 1020PM | G. DONALD EVANS | 6192720916 | SAN DIEGO, CITY OF | 94/05/06 | 1453PM | 940506 | 1953PM | N | 300 | GAL | 0 | 7844 WHELAN DR. | SAN DIEGO | SD | 8" PVC MAIN | DEBRIS BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | N/A | FLOWED INTO CANYON WHERE IT SOAKED INTO THE GROUND | 15 | DEL MAR, CITY OF | 94/05/06 | 0245PM | 940506 | 0450PM | 150 | GAL | 138 COEAN FRONT | DEL MAR | SD | CLEANOUT/1800 BLOCK | MAIN @ 18TH ST. BLOCKED BY BROKEN MH RAIN GUARD | NONE | MINOR SPILL DISSIPATED AT ROAD EDGE
18 | 940509 | 1200PM | GARY K. ORR | 6199664854 | OCEANSIDE, CITY OF | 94/05/07 | 1000AM | 940507 | 1200PM | N | 2000 | GAL | 0 | FESTIVAL DR. & AVERY STREET | OCEANSIDE | SD | MH LID OVER 10" MAIN | GREASE & RAGS IN THE 10" SEWER LINE | Y | PILGRIM CREEK, SAN LUIS REY RIVER |  |  | Y | N | N/A | ALL FLOWS DOMESTIC WASTEWATER. PILGRIM CRK. IS FENCED & CONCRETE LINED FLOOD CONTROL CHANNEL/ PUBLIC CONTACT CONTROLLED | 16 | SAN DIEGO, CITY OF | 94/05/06 | 0651PM | 940506 | 0851PM | 120 | GAL | 5861 DESERT VIEW DR. | SAN DIEGO | SD | 8" VC MAIN | ROOT BLOCKAGE | STORM DRAIN, PACIFIC OCEAN | FLOWED INTO STORM DRAIN WHERE IT DRIED
19 | 940507 | 0900AM | LAGUNA BEACH POLICE | 7144973311 | LAGUNA BEACH, CITY OF | 94/05/07 | 0900AM | 940507 | 0945AM | Y | 2000 | GAL | 0 | 800 BLOCK PACIFIC COAST HIGHWAY | LAGUNA BEACH | OR | MANHOLE #21 | LARGE AMOUNT OF ROOTS @ MANHOLE # 21 | Y | FISHERMAN COVE BEACH, PACIFIC OCEAN |  |  | Y | Y | 3 |  | 17 | SAN DIEGO, CITY OF | 94/05/06 | 1453PM | 940506 | 1953PM | 300 | GAL | 7844 WHELAN DR. | SAN DIEGO | SD | 8" PVC MAIN | DEBRIS BLOCKAGE | CANYON, PACIFIC OCEAN | FLOWED INTO CANYON WHERE IT SOAKED INTO THE GROUND
20 | 940507 | 1300PM | LAGUNA BEACH POLICE | 7144973311 | LAGUNA BEACH, CITY OF | 94/05/07 | 1245PM | 940507 | 0130AM | N | 500 | GAL | 0 | CLIFF DR. & JASMINE ST. | LAGUNA BEACH | OR | HEISLER PARK RESTRM. | TREE ROOTS & SAND IN 15" VCP TRUNK SEWER | NO | NONE |  | GRASS AREA IN HEISLER PARK | Y | Y | 2 |  | 18 | OCEANSIDE, CITY OF | 94/05/07 | 1000AM | 940507 | 1200PM | 2000 | GAL | FESTIVAL DR. & AVERY STREET | OCEANSIDE | SD | MH LID OVER 10" MAIN | GREASE & RAGS IN THE 10" SEWER LINE | PILGRIM CREEK, SAN LUIS REY RIVER | ALL FLOWS DOMESTIC WASTEWATER. PILGRIM CRK. IS FENCED & CONCRETE LINED FLOOD CONTROL CHANNEL/ PUBLIC CONTACT CONTROLLED
21 | 940508 | 2030PM | LAGUNA BEACH POLICE | 7144973311 | LAGUNA BEACH, CITY OF | 94/05/08 | 2000PM | 940508 | 2100PM | N | 500 | GAL | 0 | 565 NYES PLACE | LAGUNA BEACH | OR | SEWER MANHOLE | LATERAL ROOT AT THE MANHOLE | Y | VICTORIA BEACH, PACIFIC OCEAN |  |  | Y | Y | 2 | CREW REMOVED ROOT TO OPEN THE LINE. HEALTH DEPARTMENT WOULD LIKE TO KEEP AREA CLOSED UNTIL 5/10/94. | 19 | LAGUNA BEACH, CITY OF | 94/05/07 | 0900AM | 940507 | 0945AM | 2000 | GAL | 800 BLOCK PACIFIC COAST HIGHWAY | LAGUNA BEACH | OR | MANHOLE #21 | LARGE AMOUNT OF ROOTS @ MANHOLE # 21 | FISHERMAN COVE BEACH, PACIFIC OCEAN
70 | 940508 | 0830PM | LAGUNA BEACH POLICE | 7144973311 | LAGUNA BEACH, CITY OF | 94/05/08 | 0800PM | 940508 | 0900PM | N | 500 | GAL | 0 | 565 MYES PL. | LAGUNA BEACH | ORG | SEWER MANHOLE | LATERAL ROOT AT THE MANHOLE. | Y | VICTORIA BEACH, PACIFIC OCEAN |  |  | Y | Y | 02 | HEALTH DEPT. WOULD LIKE TO KEEP THE AREA CLOSED UNTIL THE 10TH. | 20 | LAGUNA BEACH, CITY OF | 94/05/07 | 1245PM | 940507 | 0130AM | 500 | GAL | CLIFF DR. & JASMINE ST. | LAGUNA BEACH | OR | HEISLER PARK RESTRM. | TREE ROOTS & SAND IN 15" VCP TRUNK SEWER | NONE
22 | 940509 | 2338PM | D.A. BRANCO | 6195258687 | SAN DIEGO, CITY OF | 94/05/09 | 1918PM | 940509 | 2048PM | N | 900 | GAL | 0 | 4200 LANDIS ST. | SAN DIEGO | SD | " CP | MAIN BREAK | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | MAIN BREAK CREW DISPATCHED. | 21 | LAGUNA BEACH, CITY OF | 94/05/08 | 2000PM | 940508 | 2100PM | 500 | GAL | 565 NYES PLACE | LAGUNA BEACH | OR | SEWER MANHOLE | LATERAL ROOT AT THE MANHOLE | VICTORIA BEACH, PACIFIC OCEAN | CREW REMOVED ROOT TO OPEN THE LINE. HEALTH DEPARTMENT WOULD LIKE TO KEEP AREA CLOSED UNTIL 5/10/94.
23 | 940510 | 0800AM | R.L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 94/05/09 | 1007AM | 940509 | 1155AM | N | 1080 | GAL | 0 | 4514 55TH STREET/449 EL CAJON | SAN DIEGO | SD | 8" CP SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, CANYON, PACIFIC OCEAN |  |  | Y | N | N/A | RODDED MAIN BY MACHINE, WASHED DOWN AND DEODORIZED AREA. | 70 | LAGUNA BEACH, CITY OF | 94/05/08 | 0800PM | 940508 | 0900PM | 500 | GAL | 565 MYES PL. | LAGUNA BEACH | ORG | SEWER MANHOLE | LATERAL ROOT AT THE MANHOLE. | VICTORIA BEACH, PACIFIC OCEAN | HEALTH DEPT. WOULD LIKE TO KEEP THE AREA CLOSED UNTIL THE 10TH.
24 | 940511 | 1035AM | CHAROS | X3868 | CAMP PENDLETON | 94/05/09 | 1600PM | 940509 | 1740PM | N | 300 | GAL | 0 | BASILONE ROAD & STAGECOACH ROAD | CAMP PENDLETON | SD | N/A | BROKEN LINE FROM BLDG 24153 TO 33 AREA, SWGE. PT.8 | NO | NONE |  | PERCOLATED INTO GROUND E/O BASILONE | Y | N | N/A | AREA WAS DISINFECTED WITH LIME. | 22 | SAN DIEGO, CITY OF | 94/05/09 | 1918PM | 940509 | 2048PM | 900 | GAL | 4200 LANDIS ST. | SAN DIEGO | SD | " CP | MAIN BREAK | STORM DRAIN, PACIFIC OCEAN | MAIN BREAK CREW DISPATCHED.
25 | 940511 | 1035AM | SANCHEZ | X3868 | CAMP PENDLETON | 94/05/09 | 1900PM | 940509 | 2250PM | N | 200 | GAL | 0 | DELUZ HOUSING/CHOSIN CIRCLE & WONSAN DR. | CAMP PENDLETON | SD | ?? | BLOCKAGE IN LINE | NO | NONE |  | PERCOLATED INTO GROUND/SIDE OF ROAD | Y | N | N/A |  | 23 | SAN DIEGO, CITY OF | 94/05/09 | 1007AM | 940509 | 1155AM | 1080 | GAL | 4514 55TH STREET/449 EL CAJON | SAN DIEGO | SD | 8" CP SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, CANYON, PACIFIC OCEAN | RODDED MAIN BY MACHINE, WASHED DOWN AND DEODORIZED AREA.
26 | 940518 | 0837AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 94/05/10 | 1035AM | 940517 | 1930PM | N | 21230 | GAL | 0 | 3959 CLARK ST | SAN DIEGO | SD | 6" CP SEWER MAIN | GRAVITY MAIN BREAK | Y | PACIFIC OCEAN |  |  | Y | N | N/A | MAIN CREW MADE REPAIRS ON 6" MAIN. | 24 | CAMP PENDLETON | 94/05/09 | 1600PM | 940509 | 1740PM | 300 | GAL | BASILONE ROAD & STAGECOACH ROAD | CAMP PENDLETON | SD | N/A | BROKEN LINE FROM BLDG 24153 TO 33 AREA, SWGE. PT.8 | NONE | AREA WAS DISINFECTED WITH LIME.
27 | 940511 | 1450PM | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 94/05/11 | 1121AM | 940511 | 1430PM | N | 1134 | GAL | 0 | 12TH & C, CITY COLLEGE LAWN | SAN DIEGO | SD | 6" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, S.D. BAY/PACIFIC OCEAN |  |  | Y | N | N/A |  | 25 | CAMP PENDLETON | 94/05/09 | 1900PM | 940509 | 2250PM | 200 | GAL | DELUZ HOUSING/CHOSIN CIRCLE & WONSAN DR. | CAMP PENDLETON | SD | ?? | BLOCKAGE IN LINE | NONE
28 | 940511 | 1700PM | M.A. WHELAN | 6195258685 | SAN DIEGO, CITY OF | 94/05/11 | 1150AM | 940511 | 1300PM | N | 70 | GAL | 0 | INTERSECTION OF LA MANCHA & BAYONNE | SAN DIEGO | SD | 6" VC SEWER MAIN | ROOT BLOCKAGE | NO | NONE |  | VACTORED UP & RETURNED TO SEWER | Y | N | N/A | RELIEVED STOP & VACTORED SEWAGE AT CORNER, RETURNED TO SYSTEM. CLEANED & DEODORIZED AREA. | 26 | SAN DIEGO, CITY OF | 94/05/10 | 1035AM | 940517 | 1930PM | 21230 | GAL | 3959 CLARK ST | SAN DIEGO | SD | 6" CP SEWER MAIN | GRAVITY MAIN BREAK | PACIFIC OCEAN | MAIN CREW MADE REPAIRS ON 6" MAIN.
29 | 940511 | 1610PM | JIM MCCURLEY | 6195258687 | SAN DIEGO, CITY OF | 94/05/11 | 0716AM | 940511 | 0816AM | N | 300 | GAL | 0 | 10247 THANKSGIVING LANE | SAN DIEGO | SD | SEWER LINE, 8" PVC | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | MACHINE RODDED 8" PVC SEWER MAIN, RELIEVED STOP AND DEODORIZED AREA. | 27 | SAN DIEGO, CITY OF | 94/05/11 | 1121AM | 940511 | 1430PM | 1134 | GAL | 12TH & C, CITY COLLEGE LAWN | SAN DIEGO | SD | 6" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, S.D. BAY/PACIFIC OCEAN
30 | 940518 | 0913AM | R.L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 94/05/12 | 1323PM | 940514 | 1000AM | Y | 20970 | GAL | 0 | 400 BLOCK C STREET | SAN DIEGO | SD | 18" VC SEWER MAIN | CONSTRUCTION DAMAGE | NO | NONE |  | POOLED IN TRENCH | Y | N | N/A | SEWAGE DID NOT SURFACE OR COME OUT OF MAIN. SOME SEWAGE CAME FROM MAIN WHEN CREWS TRIED TO PLUG IT & SET UP PUMPS. | 28 | SAN DIEGO, CITY OF | 94/05/11 | 1150AM | 940511 | 1300PM | 70 | GAL | INTERSECTION OF LA MANCHA & BAYONNE | SAN DIEGO | SD | 6" VC SEWER MAIN | ROOT BLOCKAGE | NONE | RELIEVED STOP & VACTORED SEWAGE AT CORNER, RETURNED TO SYSTEM. CLEANED & DEODORIZED AREA.
31 | 940613 | 1010AM | R.L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 94/05/12 | 1048AM | 940512 | 1230PM | N | 102 | GAL | 0 | 3623 35TH ST. | SAN DIEGO | SD | 8" CP SEWER MAIN | ROOT BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | N/A | MACHINE RODDED, DEODORIZED AREA. | 29 | SAN DIEGO, CITY OF | 94/05/11 | 0716AM | 940511 | 0816AM | 300 | GAL | 10247 THANKSGIVING LANE | SAN DIEGO | SD | SEWER LINE, 8" PVC | ROOT BLOCKAGE | STORM DRAIN, PACIFIC OCEAN | MACHINE RODDED 8" PVC SEWER MAIN, RELIEVED STOP AND DEODORIZED AREA.
32 | 940513 | 1515PM | DENNIS MATTIUZZI | X4514 | CAMP PENDLETON | 94/05/13 | 0615AM | 940513 | 1000AM | N | 100 | GAL | 0 | BLDG. 62420 BARRACKS 62 AREA, 7TH ST. & SAN MATEO | CAMP PENDLETON | SD | BUILDING 62420 | PLUGGED SEWER LINE/ROOTS | NO | NONE |  | PERCOLATED INTO RAVINE ACROSS ST. | Y | N | N/A | AREA WAS DISINFECTED WITH LIME. | 30 | SAN DIEGO, CITY OF | 94/05/12 | 1323PM | 940514 | 1000AM | 20970 | GAL | 400 BLOCK C STREET | SAN DIEGO | SD | 18" VC SEWER MAIN | CONSTRUCTION DAMAGE | NONE | SEWAGE DID NOT SURFACE OR COME OUT OF MAIN. SOME SEWAGE CAME FROM MAIN WHEN CREWS TRIED TO PLUG IT & SET UP PUMPS.
33 | 940513 | 1533PM | JIM MCCURLEY | 6195258687 | SAN DIEGO, CITY OF | 94/05/13 | 1048AM | 940513 | 1200PM | N | 2160 | GAL | 0 | 11977 FAIRHOPE RD. | SAN DIEGO | SD | SEWER LINE 8" PVC | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | MACHINE RODDED MAIN, RELIEVED STOP AND DEODORIZED AREA. | 31 | SAN DIEGO, CITY OF | 94/05/12 | 1048AM | 940512 | 1230PM | 102 | GAL | 3623 35TH ST. | SAN DIEGO | SD | 8" CP SEWER MAIN | ROOT BLOCKAGE | CANYON, PACIFIC OCEAN | MACHINE RODDED, DEODORIZED AREA.
76 | 940614 | 0730AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 94/05/13 | 0751AM | 940513 | 0909AM | Y | 1560 | GAL | 0 | 5945 STREAMVIEW DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | POOLED IN CREEK BED, PACIFIC OCEAN |  |  | Y | Y | ? | MACHINE RODDED/DISSINFECTED POOL OF WATER & POSTED SIGNS UNTIL POOL DRIES UP. | 32 | CAMP PENDLETON | 94/05/13 | 0615AM | 940513 | 1000AM | 100 | GAL | BLDG. 62420 BARRACKS 62 AREA, 7TH ST. & SAN MATEO | CAMP PENDLETON | SD | BUILDING 62420 | PLUGGED SEWER LINE/ROOTS | NONE | AREA WAS DISINFECTED WITH LIME.
34 | 940515 | 1100AM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 94/05/14 | 1942PM | 940515 | 0115AM | N | 1665 | GAL | 0 | 5215 CHOLLAS PARKWAY | SAN DIEGO | SD | 8" PVC SEWER MAIN | MAIN BREAK CAUSED BY VANDALISM. | Y | CHOLLAS CREEK BED, PACIFIC OCEAN |  |  | Y | Y | ? | VANDALS SET FIRE TO 8" PVC SEWER MAIN EXTENDING ACROSS CREEK BED. | 33 | SAN DIEGO, CITY OF | 94/05/13 | 1048AM | 940513 | 1200PM | 2160 | GAL | 11977 FAIRHOPE RD. | SAN DIEGO | SD | SEWER LINE 8" PVC | GREASE BLOCKAGE | STORM DRAIN, PACIFIC OCEAN | MACHINE RODDED MAIN, RELIEVED STOP AND DEODORIZED AREA.
35 | 940515 | 1050AM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 94/05/14 | 0900AM | 940514 | 1000AM | Y | 360 | GAL | 0 | UNION ST. AND C ST. | SAN DIEGO | SD | 18" VC | CONTRACTOR DRILLED HOLE IN MAIN | NO | NONE |  | IN CONSTRUCTION SITE | Y | N | N/A | FLOW WAS CONTAINED IN SITE AND SOAKED INTO GROUND. | 76 | SAN DIEGO, CITY OF | 94/05/13 | 0751AM | 940513 | 0909AM | 1560 | GAL | 5945 STREAMVIEW DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | POOLED IN CREEK BED, PACIFIC OCEAN | MACHINE RODDED/DISSINFECTED POOL OF WATER & POSTED SIGNS UNTIL POOL DRIES UP.
36 | 940517 | 1105PM | D. A. BRANCO | 6195258687 | SAN DIEGO, CITY OF | 94/05/17 | 1739PM | 940517 | 2009PM | N | 750 | GAL | 0 | 2968 NUTMEG ST. | SAN DIEGO | SD | 8" VC | ROOT BLOCKAGE | Y | PACIFIC OCEAN |  |  | Y | N | N/A | RODDED MAIN | 34 | SAN DIEGO, CITY OF | 94/05/14 | 1942PM | 940515 | 0115AM | 1665 | GAL | 5215 CHOLLAS PARKWAY | SAN DIEGO | SD | 8" PVC SEWER MAIN | MAIN BREAK CAUSED BY VANDALISM. | CHOLLAS CREEK BED, PACIFIC OCEAN | VANDALS SET FIRE TO 8" PVC SEWER MAIN EXTENDING ACROSS CREEK BED.
37 | 940517 | 1700PM | MR. MILLER | 6194438437 | LAKESIDE SANITATION DISTRICT | 94/05/17 | 1700PM | 940517 | 1815PM | N | 2000 | GAL | 0 | 1459 OLDE HIGHWAY 80 | LAKESIDE | SD | 8" SEWER MAIN | GREASE | Y | LOS COCHES CREEK, PACIFIC OCEAN |  |  | Y | N | N/A | AREA WAS CHLORINATED. | 35 | SAN DIEGO, CITY OF | 94/05/14 | 0900AM | 940514 | 1000AM | 360 | GAL | UNION ST. AND C ST. | SAN DIEGO | SD | 18" VC | CONTRACTOR DRILLED HOLE IN MAIN | NONE | FLOW WAS CONTAINED IN SITE AND SOAKED INTO GROUND.
38 | 940518 | 0330PM | R.H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 94/05/18 | 0916AM | 940518 | 1000AM | N | 220 | GAL | 0 | 2045 VIA VALVERDE | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | SEWAGE DRIED IN STORM DRAIN. | 36 | SAN DIEGO, CITY OF | 94/05/17 | 1739PM | 940517 | 2009PM | 750 | GAL | 2968 NUTMEG ST. | SAN DIEGO | SD | 8" VC | ROOT BLOCKAGE | PACIFIC OCEAN | RODDED MAIN
39 | 940519 | 0745AM | R.L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 94/05/18 | 0753AM | 940518 | 0925AM | N | 460 | GAL | 0 | 8511 HARWELL DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | FLUSHED MAIN, WASHED DOWN AND DEODORIZED AREA. | 37 | LAKESIDE SANITATION DISTRICT | 94/05/17 | 1700PM | 940517 | 1815PM | 2000 | GAL | 1459 OLDE HIGHWAY 80 | LAKESIDE | SD | 8" SEWER MAIN | GREASE | LOS COCHES CREEK, PACIFIC OCEAN | AREA WAS CHLORINATED.
40 | 940519 | 1545PM | JOHN VAUGHT | 6197414854 | ESCONDIDO, CITY OF | 94/05/19 | 1235PM | 940519 | 1300PM | N | 200 | GAL | 0 | 1348 S. ORANGE ST. | ESCONDIDO | SD | SEWER ATLAS P.28/MH4 | COMBINATION OF GREASE AND PAPER TOWELS | NO | NONE |  | POOLED IN APRON AND GUTTER AREAS | Y | ? | N/A | AREA WAS WASHED DOWN AND CONTAINED. WATER WAS THEN VACUUMED AND RETURNED TO SYSTEM. | 38 | SAN DIEGO, CITY OF | 94/05/18 | 0916AM | 940518 | 1000AM | 220 | GAL | 2045 VIA VALVERDE | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, PACIFIC OCEAN | SEWAGE DRIED IN STORM DRAIN.
41 | 940520 | 0830AM | JAMES E. SMITH | 7146432006 | MOULTON NIGUEL WATER DISTRICT | 94/05/19 | 1030AM | 940519 | 1530PM | N | 4000 | GAL | 0 | LAGUNA NIGUEL REGIONAL PARK | LAGUN NIGUEL | OR | 24" FORCE MAIN | LEAK FROM LIFT STATION TO REGIONAL TREATMENT PLANT | Y | SULPHUR CREEK, PACIFIC OCEAN |  |  | Y | Y | ? | THE PIPE HAS BEEN SHUT DOWN AND REPAIR WILL BE INITITATED ON MONDAY MAY 23, 1994. | 39 | SAN DIEGO, CITY OF | 94/05/18 | 0753AM | 940518 | 0925AM | 460 | GAL | 8511 HARWELL DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, PACIFIC OCEAN | FLUSHED MAIN, WASHED DOWN AND DEODORIZED AREA.
42 | 950521 | 1200PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 94/05/20 | 1420PM | 940520 | 1520PM | N | 60 | GAL | 0 | 45TH & MARKET | SAN DIEGO | SD | 6" PVC | ROOTS | NO | NONE |  | DRIED AROUND MANHOLE | Y | N | N/A | DRIED AROUND MANHOLE IN STREET. | 40 | ESCONDIDO, CITY OF | 94/05/19 | 1235PM | 940519 | 1300PM | 200 | GAL | 1348 S. ORANGE ST. | ESCONDIDO | SD | SEWER ATLAS P.28/MH4 | COMBINATION OF GREASE AND PAPER TOWELS | NONE | AREA WAS WASHED DOWN AND CONTAINED. WATER WAS THEN VACUUMED AND RETURNED TO SYSTEM.
43 | 940523 | 0830AM | MIKE BEDARD | 6196726148 | SAN DIEGO, CITY OF | 94/05/22 | 1142AM | 940522 | 2030PM | N | 528 | GAL | 0 | 1831 TORRANCE | SAN DIEGO | SD | 6" VC MAIN | 6" VC MAIN BREAK | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | N/A | REPAIRED 6" VC MAIN. | 41 | MOULTON NIGUEL WATER DISTRICT | 94/05/19 | 1030AM | 940519 | 1530PM | 4000 | GAL | LAGUNA NIGUEL REGIONAL PARK | LAGUN NIGUEL | OR | 24" FORCE MAIN | LEAK FROM LIFT STATION TO REGIONAL TREATMENT PLANT | SULPHUR CREEK, PACIFIC OCEAN | THE PIPE HAS BEEN SHUT DOWN AND REPAIR WILL BE INITITATED ON MONDAY MAY 23, 1994.
44 | 940523 | 1430PM | V.T. BRADLEY | 7144935225 | SANTA MARGARITA WATER DISTRICT | 94/05/23 | 1235PM | 940523 | 1305PM | N | 29000 | GAL | 0 | LA PROMESA & ANTONIO | RCHO STA MGRITA | OR | GREASE TRAP CLEANOUT | BLOCKAGE AT VONS PAVILLION'S GREASE TRAP | Y | TIJERAS CREEK, PACIFIC OCEAN |  |  | Y | N | N/A | SPILL CAUSED BY PRIVATELY OWNED GREASE TRAP. INLET SIDE PLUGGED. | 42 | SAN DIEGO, CITY OF | 94/05/20 | 1420PM | 940520 | 1520PM | 60 | GAL | 45TH & MARKET | SAN DIEGO | SD | 6" PVC | ROOTS | NONE | DRIED AROUND MANHOLE IN STREET.
45 | 940524 | 0110AM | M.A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 94/05/23 | 1330PM | 940523 | 2130PM | N | 240 | GAL | 0 | 515 W. MAPLE ST. | SAN DIEGO | SD | 4" CI SEWER LATERAL | COLLAPSED 4" CI SEWER LATERAL, BROKEN BY CITY CREW | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | N/A | LOCATED BROKEN LATERAL IN CANYON, TURNED OVER TO STANDBY BACKUP TRUCK FOR REPAIR. FINISHED REPAIRS @ 2130. | 43 | SAN DIEGO, CITY OF | 94/05/22 | 1142AM | 940522 | 2030PM | 528 | GAL | 1831 TORRANCE | SAN DIEGO | SD | 6" VC MAIN | 6" VC MAIN BREAK | CANYON, PACIFIC OCEAN | REPAIRED 6" VC MAIN.
46 | 940525 | 0452AM | M.A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 94/05/24 | 2027PM | 940524 | 2127PM | N | 120 | GAL | 0 | 38TH STREET & WARD ROAD | SAN DIEGO | SD | 8" CP SEWER MAIN | GREASE BLOCKAGE | Y | CANYON, PACIFIC OCEAN |  |  | Y | N | N/A | LOCATED STOP, MACHINE RODDED MAIN. RELIEVED STOP. | 44 | SANTA MARGARITA WATER DISTRICT | 94/05/23 | 1235PM | 940523 | 1305PM | 29000 | GAL | LA PROMESA & ANTONIO | RCHO STA MGRITA | OR | GREASE TRAP CLEANOUT | BLOCKAGE AT VONS PAVILLION'S GREASE TRAP | TIJERAS CREEK, PACIFIC OCEAN | SPILL CAUSED BY PRIVATELY OWNED GREASE TRAP. INLET SIDE PLUGGED.
47 | 940525 | 0438AM | M.A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 94/05/24 | 1723PM | 940524 | 1823PM | N | 2400 | GAL | 0 | MATINAL ROAD & POBLADO ROAD | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | MACHINE RODDED MAIN. | 45 | SAN DIEGO, CITY OF | 94/05/23 | 1330PM | 940523 | 2130PM | 240 | GAL | 515 W. MAPLE ST. | SAN DIEGO | SD | 4" CI SEWER LATERAL | COLLAPSED 4" CI SEWER LATERAL, BROKEN BY CITY CREW | CANYON, PACIFIC OCEAN | LOCATED BROKEN LATERAL IN CANYON, TURNED OVER TO STANDBY BACKUP TRUCK FOR REPAIR. FINISHED REPAIRS @ 2130.
48 | 940526 | 0042AM | M.A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 94/05/25 | 1729PM | 940525 | 1830PM | N | 1525 | GAL | 0 | 42ND STREET BETWEEN DELTA STREET & GAMMA STREET | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | RODDED 286' OF 6" CP, RELIEVED STOP AT APPROX 80' MAIN 10-34. CLEANED UP DEBRIS AROUND OVERFLOW & SPRAYED WITH ZEP. | 46 | SAN DIEGO, CITY OF | 94/05/24 | 2027PM | 940524 | 2127PM | 120 | GAL | 38TH STREET & WARD ROAD | SAN DIEGO | SD | 8" CP SEWER MAIN | GREASE BLOCKAGE | CANYON, PACIFIC OCEAN | LOCATED STOP, MACHINE RODDED MAIN. RELIEVED STOP.
49 | 940525 | 1322PM | J.ROBERTSON/P.HUIZAR | 6197253868 | CAMP PENDLETON | 94/05/25 | 1015AM | 940525 | 1030AM | N | 15 | GAL | 0 | BUILDING H-49/OUT-PT. HOSPITAL, SANTA MARGARITA R | CAMP PENDLETON | SD | BUILDING H-49 | BROKEN SEWER LINE | NO | NONE |  | AT SITE | Y | N | N/A | LINE REPAIRED. | 47 | SAN DIEGO, CITY OF | 94/05/24 | 1723PM | 940524 | 1823PM | 2400 | GAL | MATINAL ROAD & POBLADO ROAD | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC OCEAN | MACHINE RODDED MAIN.
50 | 940530 | 0844PM | JIM McCURLEY | 6195258687 | SAN DIEGO, CITY OF | 94/05/30 | 1132AM | 940530 | 1330PM | N | 880 | GAL | 0 | 4478 47TH ST. | SAN DIEGO | SD | SEWER LINE 12" CP | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | RODDED MAIN BY MACHINE. | 48 | SAN DIEGO, CITY OF | 94/05/25 | 1729PM | 940525 | 1830PM | 1525 | GAL | 42ND STREET BETWEEN DELTA STREET & GAMMA STREET | SAN DIEGO | SD | 6" CP SEWER MAIN | GREASE | STORM DRAIN, PACIFIC OCEAN | RODDED 286' OF 6" CP, RELIEVED STOP AT APPROX 80' MAIN 10-34. CLEANED UP DEBRIS AROUND OVERFLOW & SPRAYED WITH ZEP.
51 | 940530 | 0843PM | JIM McCURLEY | 6195258687 | SAN DIEGO, CITY OF | 94/05/30 | 0900AM | 940530 | 1130AM | N | 8010 | GAL | 0 | 3504 36TH ST. | SAN DIEGO | SD | SEWER LINE 8" VC | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | RODDED BY MACHINE. | 49 | CAMP PENDLETON | 94/05/25 | 1015AM | 940525 | 1030AM | 15 | GAL | BUILDING H-49/OUT-PT. HOSPITAL, SANTA MARGARITA R | CAMP PENDLETON | SD | BUILDING H-49 | BROKEN SEWER LINE | NONE | LINE REPAIRED.
52 | 940530 | 0845PM | JIM McCURLEY | 6195258687 | SAN DIEGO, CITY OF | 94/05/30 | 1025AM | 940530 | 1517PM | N | 14480 | GAL | 0 | 4880 COLLEGE AVE. | SAN DIEGO | SD | SEWER LINE 8" VC | ROOT BLOCKAGE | Y | PACIFIC OCEAN |  |  | Y | N | N/A | RODDED MAIN BY MACHINE. | 50 | SAN DIEGO, CITY OF | 94/05/30 | 1132AM | 940530 | 1330PM | 880 | GAL | 4478 47TH ST. | SAN DIEGO | SD | SEWER LINE 12" CP | GREASE BLOCKAGE | STORM DRAIN, PACIFIC OCEAN | RODDED MAIN BY MACHINE.
53 | 940531 | 0430PM | R. PECOR | 6195277459 | SAN DIEGO, CITY OF | 94/05/30 | 0751PM | 940531 | 1030AM | N | 4395 | GAL | 0 | 5215 CHOLLAS PARKWAY | SAN DIEGO | SD | 6" PVC SEWER MAIN | SEWER MAIN BREAK CAUSED BY VANDALS. | Y | SAN DIEGO BAY, PACIFIC OCEAN |  |  | Y | Y | ? | SEWER MAIN WAS REPAIRED BY CREW. | 51 | SAN DIEGO, CITY OF | 94/05/30 | 0900AM | 940530 | 1130AM | 8010 | GAL | 3504 36TH ST. | SAN DIEGO | SD | SEWER LINE 8" VC | ROOT BLOCKAGE | STORM DRAIN, PACIFIC OCEAN | RODDED BY MACHINE.
54 | 940531 | 1745PM | D. A. BRANCO | 6195258687 | SAN DIEGO, CITY OF | 94/05/31 | 1630PM | 940531 | 1830PM | N | 120 | GAL | 0 | 4120 ESTRELLA | SAN DIEGO | SD | 6" VC | DEBRIS BLOCKAGE | Y | STORM DRAIN, PACIFIC OCEAN |  |  | N | N | N/A | RODDED MAIN. | 52 | SAN DIEGO, CITY OF | 94/05/30 | 1025AM | 940530 | 1517PM | 14480 | GAL | 4880 COLLEGE AVE. | SAN DIEGO | SD | SEWER LINE 8" VC | ROOT BLOCKAGE | PACIFIC OCEAN | RODDED MAIN BY MACHINE.
55 | 940531 | 2330PM | D.A. BRANCO | 6195258687 | SAN DIEGO, CITY OF | 94/05/31 | 1335PM | 940531 | 1805PM | N | 6750 | GAL | 0 | COPLEY DR. & HICKMAN FIELD DR. | SAN DIEGO | SD | SEWER PUMP STATION | PUMP STATION FAILURE/VALDALISM @ STATION 86 | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | PUMP CREWS OPENED INLET VALVES, SOMEONE CLOSED INLET VALVES AT PUMP STATION 86 CAUSING FAILURE. SOME VACTORED. | 53 | SAN DIEGO, CITY OF | 94/05/30 | 0751PM | 940531 | 1030AM | 4395 | GAL | 5215 CHOLLAS PARKWAY | SAN DIEGO | SD | 6" PVC SEWER MAIN | SEWER MAIN BREAK CAUSED BY VANDALS. | SAN DIEGO BAY, PACIFIC OCEAN | SEWER MAIN WAS REPAIRED BY CREW.
56 | 940603 | 1400PM | MIKE BEDARD | 6195277425 | SAN DIEGO, CITY OF | 94/06/02 | 1110AM | 940602 | 1116PM | N | 60 | GAL | 0 | 464 36TH STREET | SAN DIEGO | SD | COLLAPSED LATERAL | LATERAL COLLAPSED | NO | NONE |  | ALLEY/STREET | N | N | N/A | SEWAGE FLOWED IN ALLEY/STREET AND WAS VACTORED, AREA WAS THEN CLEANED. | 54 | SAN DIEGO, CITY OF | 94/05/31 | 1630PM | 940531 | 1830PM | 120 | GAL | 4120 ESTRELLA | SAN DIEGO | SD | 6" VC | DEBRIS BLOCKAGE | STORM DRAIN, PACIFIC OCEAN | RODDED MAIN.
57 | 940602 | 1145AM | ARTURO MAPULA | 6195277456 | SAN DIEGO, CITY OF | 94/06/02 | 1100AM | 940602 | 1330PM | N | 45 | GAL | 0 | 15500 PAYMOGO ST. | SAN DIEGO | SD | LINK W/0F MH #42865 | PARTIAL STOP ON GRAVITY MAIN TO SEWER PUMP STATION | Y | LUSARDI CREEK, PACIFIC OCEAN |  |  | Y | Y | 2 | 1 SIGN POSTED AT OVERFLOW SITE. SEWAGE WAS ABSORBED INTO GROUND. | 55 | SAN DIEGO, CITY OF | 94/05/31 | 1335PM | 940531 | 1805PM | 6750 | GAL | COPLEY DR. & HICKMAN FIELD DR. | SAN DIEGO | SD | SEWER PUMP STATION | PUMP STATION FAILURE/VALDALISM @ STATION 86 | STORM DRAIN, PACIFIC OCEAN | PUMP CREWS OPENED INLET VALVES, SOMEONE CLOSED INLET VALVES AT PUMP STATION 86 CAUSING FAILURE. SOME VACTORED.
58 | 940604 | 2130PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 94/06/03 | 1513PM | 940604 | 1913PM | N | 1680 | GAL | 0 | 4TH & MARKET STREET | SAN DIEGO | SD | 6" CP | GREASE | Y | STREET GUTTER, PACIFIC OCEAN |  |  | Y | N | N/A | FLOWED SOUTH ON 4TH AVE. THEN INTO STORM DRAIN AND SOAKED INTO DIRT. INVESTIGATED 10 MI. OF S.D. BAY, NO SIGN OF FLOW. | 56 | SAN DIEGO, CITY OF | 94/06/02 | 1110AM | 940602 | 1116PM | 60 | GAL | 464 36TH STREET | SAN DIEGO | SD | COLLAPSED LATERAL | LATERAL COLLAPSED | NONE | SEWAGE FLOWED IN ALLEY/STREET AND WAS VACTORED, AREA WAS THEN CLEANED.
59 | 940604 | 1000AM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 94/06/03 | 0926AM | 940603 | 1900PM | Y | 574 | GAL | 0 | CURLEW & PENNSYLVANIA | SAN DIEGO | SD | 6" CP | GRAVITY MAIN BREAK | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | FLOWED INTO STORM DRAIN AT BROOKES AND SOAKED INTO GROUND. MAIN WAS DUG UP AND REPAIRED. | 57 | SAN DIEGO, CITY OF | 94/06/02 | 1100AM | 940602 | 1330PM | 45 | GAL | 15500 PAYMOGO ST. | SAN DIEGO | SD | LINK W/0F MH #42865 | PARTIAL STOP ON GRAVITY MAIN TO SEWER PUMP STATION | LUSARDI CREEK, PACIFIC OCEAN | 1 SIGN POSTED AT OVERFLOW SITE. SEWAGE WAS ABSORBED INTO GROUND.
60 | 940606 | 0800AM | MIKE BARDIN | 6197530155 | LEUCADIA COUNTY WATER DISTRICT | 94/06/03 | 1815PM | 940603 | 2145PM | N | 200 | GAL | 0 | 579 LA COSTA AVENUE | ENCINITAS | SD | PRIVATE CLEAN OUT | UNKNOWN, TELEVISION INSPECTION SHOWED NO PROBLEMS. | NO | NONE |  | DIRT AREA IN BACK YARD | Y | N | N/A | DISINFECTED AREA IN BACKYARD AND CLEANED DEBRIS FROM AREA. | 58 | SAN DIEGO, CITY OF | 94/06/03 | 1513PM | 940604 | 1913PM | 1680 | GAL | 4TH & MARKET STREET | SAN DIEGO | SD | 6" CP | GREASE | STREET GUTTER, PACIFIC OCEAN | FLOWED SOUTH ON 4TH AVE. THEN INTO STORM DRAIN AND SOAKED INTO DIRT. INVESTIGATED 10 MI. OF S.D. BAY, NO SIGN OF FLOW.
61 | 940603 | 1530PM | MIKE BEDARD | 6195277425 | SAN DIEGO, CITY OF | 94/06/03 | 1000AM | 940604 | 1730PM | N | 103466 | GAL | 0 | 15500 PAYMOGA | SAN DIEGO | SD | 10" PVC FORCE MAIN | FORCE MAIN PIPE PULLED FROM MECHANICAL JOINT | Y | LUSARDI CREEK, PACIFIC OCEAN |  |  | Y | Y | ? | FORCE MAIN WAS REPAIRED. | 59 | SAN DIEGO, CITY OF | 94/06/03 | 0926AM | 940603 | 1900PM | 574 | GAL | CURLEW & PENNSYLVANIA | SAN DIEGO | SD | 6" CP | GRAVITY MAIN BREAK | STORM DRAIN, PACIFIC OCEAN | FLOWED INTO STORM DRAIN AT BROOKES AND SOAKED INTO GROUND. MAIN WAS DUG UP AND REPAIRED.
62 | 940608 | ? | HOA TRAN | 6196943974 | SAN DIEGO, COUNTY OF | 94/06/04 | 1640PM | 940604 | ? | Y | 100 | GAL | 0 | 3401 TURF LANE | SPRING VALLEY | SD | MANHOLE | RAGS, GREASE, ROCKS & BROKEN ASPHALT | NO | NONE |  | CONTAINED AND CHLORINATED | Y | N | N/A | CONTAINED AND CHLORINATED. | 60 | LEUCADIA COUNTY WATER DISTRICT | 94/06/03 | 1815PM | 940603 | 2145PM | 200 | GAL | 579 LA COSTA AVENUE | ENCINITAS | SD | PRIVATE CLEAN OUT | UNKNOWN, TELEVISION INSPECTION SHOWED NO PROBLEMS. | NONE | DISINFECTED AREA IN BACKYARD AND CLEANED DEBRIS FROM AREA.
63 | 940606 | 1415PM | DEBORAH WOODS | 6197553294 | DEL MAR, CITY OF | 94/06/05 | 2045PM | 940605 | 2235PM | N | 1650 | GAL | 0 | 15TH STREET/STRATFORD CT. | DEL MAR | SD | SEWER LINE | GREASE & CLOTH RAGS OBSTRUCTING SEWER MAIN | Y | PACIFIC OCEAN |  |  | Y | Y | 1 | SEWAGE FLOW DID NOT REACH WATER, AS IT DISSIPATED INTO THE SAND & HIGH TIDE WAS OVER. WASH WATER RUNOFF REACHED OCEAN. | 61 | SAN DIEGO, CITY OF | 94/06/03 | 1000AM | 940604 | 1730PM | 103466 | GAL | 15500 PAYMOGA | SAN DIEGO | SD | 10" PVC FORCE MAIN | FORCE MAIN PIPE PULLED FROM MECHANICAL JOINT | LUSARDI CREEK, PACIFIC OCEAN | FORCE MAIN WAS REPAIRED.
64 | 940608 | 0100AM | D.A. BRANCO | 6195258687 | SAN DIEGO, CITY OF | 94/06/07 | 1056AM | 940607 | 1956PM | N | 16200 | GAL | 0 | CONESTOGA DR. & CONESTOGA WAY | SAN DIEGO | SD | 12" VC SEWER MAIN | ROOT BLOCKAGE | Y | SAN DIEGO RIVER, PACIFIC OCEAN |  |  | Y | Y | ? | ROD MAIN, 13 SIGNS POSTED AT DOG BEACH IN OCEAN BEACH. | 62 | SAN DIEGO, COUNTY OF | 94/06/04 | 1640PM | 940604 | ? | 100 | GAL | 3401 TURF LANE | SPRING VALLEY | SD | MANHOLE | RAGS, GREASE, ROCKS & BROKEN ASPHALT | NONE | CONTAINED AND CHLORINATED.
65 | 940607 | 1800PM | ANSWERING SERVICE | 6197288319 | FALLBROOK SANITARY DISTRICT | 94/06/07 | 1800PM | 940607 | 2030PM | N | 50 | GAL | 0 | 1102 MORRO ROAD | FALLBROOK | SD | CLEANOUT | ROOT BLOCKAGE | NO | NONE |  | PROPERTY NEXT DOOR | N | N | N/A | OPENED 5' FROM CLEANOUT. UPSTREAM MH G-115. DOWNSTREAM MH G-112. FLUSHED MAINLINE. COMPLETED AT 2030 PM. | 63 | DEL MAR, CITY OF | 94/06/05 | 2045PM | 940605 | 2235PM | 1650 | GAL | 15TH STREET/STRATFORD CT. | DEL MAR | SD | SEWER LINE | GREASE & CLOTH RAGS OBSTRUCTING SEWER MAIN | PACIFIC OCEAN | SEWAGE FLOW DID NOT REACH WATER, AS IT DISSIPATED INTO THE SAND & HIGH TIDE WAS OVER. WASH WATER RUNOFF REACHED OCEAN.
66 | 940607 | 1223PM | MARK STROHMAN | 6195258680 | SAN DIEGO, CITY OF | 94/06/07 | 1005AM | 940607 | 1127AM | N | 164 | GAL | 0 | 1800 HARBOR ISLAND DR. | SAN DIEGO | SD | 10" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | Y | 1 | NONE | 64 | SAN DIEGO, CITY OF | 94/06/07 | 1056AM | 940607 | 1956PM | 16200 | GAL | CONESTOGA DR. & CONESTOGA WAY | SAN DIEGO | SD | 12" VC SEWER MAIN | ROOT BLOCKAGE | SAN DIEGO RIVER, PACIFIC OCEAN | ROD MAIN, 13 SIGNS POSTED AT DOG BEACH IN OCEAN BEACH.
67 | 940608 | 0215AM | D.A. BRANCO | 6195258687 | SAN DIEGO, CITY OF | 94/06/07 | 2018PM | 940607 | 2338PM | N | 200 | GAL | 0 | 5514 LONE STAR ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | RODDED MAIN. | 65 | FALLBROOK SANITARY DISTRICT | 94/06/07 | 1800PM | 940607 | 2030PM | 50 | GAL | 1102 MORRO ROAD | FALLBROOK | SD | CLEANOUT | ROOT BLOCKAGE | NONE | OPENED 5' FROM CLEANOUT. UPSTREAM MH G-115. DOWNSTREAM MH G-112. FLUSHED MAINLINE. COMPLETED AT 2030 PM.
68 | 940608 | 0200AM | D.A. BRANCO | 6195258687 | SAN DIEGO, CITY OF | 94/06/07 | 2004PM | 940607 | 2134PM | N | 23 | GAL | 0 | 8938 STIMSON CT. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | OVERFLOW SOAKED INTO DEBRIS OF STORM DRAIN. ROD TO RELIEVE SEWER STOP. | 66 | SAN DIEGO, CITY OF | 94/06/07 | 1005AM | 940607 | 1127AM | 164 | GAL | 1800 HARBOR ISLAND DR. | SAN DIEGO | SD | 10" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC OCEAN | NONE
69 | 940610 | 1150am | RENZP MARIN | 7148371660 | EL TORO WATER DISTRICT | 94/06/08 | 1100PM | 940609 | 1015AM | N | 30000 | GAL | 0 | BLDG.#900-RHONDA SEVILLA | ORANGE | ORG | FORCE MAIN SIPHON | SIPHON BLOCKAGE. STICKS AND GREASE BUILD UP. | Y | ALISO CREEK |  |  | Y | ? | N/A | USED HYDROCLEANER TO BREAK BLOCKAGE. WASHED DOWN WITH 2000 GALLONS OF WATER. | 67 | SAN DIEGO, CITY OF | 94/06/07 | 2018PM | 940607 | 2338PM | 200 | GAL | 5514 LONE STAR ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | ROOT BLOCKAGE | STORM DRAIN, PACIFIC OCEAN | RODDED MAIN.
71 | 940609 | 0812AM | BILL SANCET | 6197253868 | MARINE CORPS BASE | 94/06/08 | 1725PM | 940608 | 1810PM | N | 700 | GAL | 0 | BLDG. 41300, SEWAGE LIFT STATION | CAMP PENDLETON | SD | BLDG 41300, LIFT ST. | MALFUNCTION PUMP IN LIFT STATION, NO POWER. | NO | NONE |  |  | Y | N | N/A | THE AREA WAS DISINFECTED AND LIMED. | 68 | SAN DIEGO, CITY OF | 94/06/07 | 2004PM | 940607 | 2134PM | 23 | GAL | 8938 STIMSON CT. | SAN DIEGO | SD | 8" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC OCEAN | OVERFLOW SOAKED INTO DEBRIS OF STORM DRAIN. ROD TO RELIEVE SEWER STOP.
112 | 940610 | 1600PM | BERNARD POWELL | 6195277442 | SAN DIEGO, CITY OF | 94/06/10 | 1400PM | 940613 | 2300PM | Y | 1800 | GAL | 0 | 1400 K ST. | SAN DIEGO | SD | 33" VC SEWER MAIN | DAMAGE BY CONTRACTOR | NO | NONE |  | SEWER TRENCH AND RETURNED TO SEWER | Y | N | N/A | ALL SEWAGE WAS RETURNED TO SYSTEM AND SEWER MAIN WAS REPAIRED. | 69 | EL TORO WATER DISTRICT | 94/06/08 | 1100PM | 940609 | 1015AM | 30000 | GAL | BLDG.#900-RHONDA SEVILLA | ORANGE | ORG | FORCE MAIN SIPHON | SIPHON BLOCKAGE. STICKS AND GREASE BUILD UP. | ALISO CREEK | USED HYDROCLEANER TO BREAK BLOCKAGE. WASHED DOWN WITH 2000 GALLONS OF WATER.
72 | 940611 | 0804PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 94/06/11 | 1010AM | 940611 | 1210PM | N | 240 | GAL | 0 | 4444 PARK BLVD. | SAN DIEGO | SD | 6" CP SEWER MAIN | BEBRIS BLOCKAGE | NO | NONE |  | SWEPT BACK INTO MANHOLE | Y | N | N/A | ALL FLOW WAS SWEPT BACK INTO MANHOLE#15384-THEN THE PAVEMENT WAS WASHED. | 71 | MARINE CORPS BASE | 94/06/08 | 1725PM | 940608 | 1810PM | 700 | GAL | BLDG. 41300, SEWAGE LIFT STATION | CAMP PENDLETON | SD | BLDG 41300, LIFT ST. | MALFUNCTION PUMP IN LIFT STATION, NO POWER. | NONE | THE AREA WAS DISINFECTED AND LIMED.
73 | 940611 | 0130PM | MITCH PIERSON | 6197288319 | FALLBROOK SANITARY DISTRICT | 94/06/11 | 0130PM | 940611 | 0230PM | N | 0 | GAL | 0 | 1425 S. ALTURAS | FALLBROOK | SD | MANHOLE | BREASE BLOCKAGE | NO | NONE |  | IN MANHOLE | N | N | N/A | WORK WAS COMPETED AT 2:30PM. | 112 | SAN DIEGO, CITY OF | 94/06/10 | 1400PM | 940613 | 2300PM | 1800 | GAL | 1400 K ST. | SAN DIEGO | SD | 33" VC SEWER MAIN | DAMAGE BY CONTRACTOR | NONE | ALL SEWAGE WAS RETURNED TO SYSTEM AND SEWER MAIN WAS REPAIRED.
74 | 940612 | 0630PM | RONALD D. ROBY | 6195258685 | SAN DIEGO, CITY OF | 94/06/12 | 0908AM | 940612 | 1008AM | N | 60 | GAL | 0 | 3276 ROSECRANS ST. | SAN DIEGO | SD | 8" CI SEWER MAIN | ROOT BLOCKAGE | Y | PACIFIC OCEAN |  |  | Y | N | N/A | FLOW OF 60 GAL DRIED IN STREET. | 72 | SAN DIEGO, CITY OF | 94/06/11 | 1010AM | 940611 | 1210PM | 240 | GAL | 4444 PARK BLVD. | SAN DIEGO | SD | 6" CP SEWER MAIN | BEBRIS BLOCKAGE | NONE | ALL FLOW WAS SWEPT BACK INTO MANHOLE#15384-THEN THE PAVEMENT WAS WASHED.
75 | 940613 | 0740AM | JOHN ROBERTSON | 6197253868 | CAMP PENDLETON | 94/06/12 | 2345PM | 940613 | 0220AM | N | 100 | GAL | 0 | CAMP PENDLETON | CAMP PENDLETON | SD | BLDG 21713 E CLUB | PLUGGED LINE | NO | NONE |  | MANHOLE AT BLDG. 21713 | Y | N | N/A | AREA WAS LIMED. | 73 | FALLBROOK SANITARY DISTRICT | 94/06/11 | 0130PM | 940611 | 0230PM | 0 | GAL | 1425 S. ALTURAS | FALLBROOK | SD | MANHOLE | BREASE BLOCKAGE | NONE | WORK WAS COMPETED AT 2:30PM.
77 | 940613 | 0820AM | STEVE FRANCIS | 7145822330 | TRABUCO CANYON WATER DISTRICT | 94/06/13 | 0700AM | 940613 | 0845AM | N | 10000 | GAL | 0 | LOS ALISO RANCHO SANTA MARGARITA ROAD | MISSION VIEJO | ORG | EL TORO FORCE MAIN | CORROSION | Y | STORM DRAIN, RIVER BED, OCEAN |  |  | Y | Y | .25 | CONTAINED IN 45 MINUTES. | 74 | SAN DIEGO, CITY OF | 94/06/12 | 0908AM | 940612 | 1008AM | 60 | GAL | 3276 ROSECRANS ST. | SAN DIEGO | SD | 8" CI SEWER MAIN | ROOT BLOCKAGE | PACIFIC OCEAN | FLOW OF 60 GAL DRIED IN STREET.
78 | 940613 | 0600PM | EDDIE TAYLOR | 6197288319 | FALLBROOK SANITARY DISTRICT | 94/06/13 | 0600PM | 940613 | 0800PM | N | 20 | GAL | 0 | LA SOLONA | FALLBROOK | SD | MANHOLE | ROOT BLOCKAGE | NO | NONE |  | DOWN THE ROAD | N | N | N/A | ROOTS WERE CLEARED AT AROUND 8:00PM FROM LINE. | 75 | CAMP PENDLETON | 94/06/12 | 2345PM | 940613 | 0220AM | 100 | GAL | CAMP PENDLETON | CAMP PENDLETON | SD | BLDG 21713 E CLUB | PLUGGED LINE | NONE | AREA WAS LIMED.
79 | 940615 | 0032AM | M. A. WHELAN | 6195258687 | PROPERTY OWNER | 94/06/13 | 0840AM | 940616 | 0700AM | Y | 21055 | GAL | 0 | 2065 SAN DIEGO AVE. | SAN DIEGO | SD | 4" SEWER LATERAL | UNKNOWN PROBLEM | Y | PACIFIC OCEAN |  |  | Y | N | N/A | RODDED MAIN 3 TIMES. PROBLEM IS RESPONSIBILITY OF PROPERTY OWNER NOT CITY. TURN TO COUNTY HEALTH FOR ENFORCEMENT. | 77 | TRABUCO CANYON WATER DISTRICT | 94/06/13 | 0700AM | 940613 | 0845AM | 10000 | GAL | LOS ALISO RANCHO SANTA MARGARITA ROAD | MISSION VIEJO | ORG | EL TORO FORCE MAIN | CORROSION | STORM DRAIN, RIVER BED, OCEAN | CONTAINED IN 45 MINUTES.
80 | 940614 | 0330PM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 94/06/14 | 1100AM | 940614 | 1200PM | N | 60 | GAL | 0 | MESA COLLEGE DR. & LINDA VISTA RD. | SAN DIEGO | SD | 8" PVC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | CLEANED BEBRIS ON STREET. | 78 | FALLBROOK SANITARY DISTRICT | 94/06/13 | 0600PM | 940613 | 0800PM | 20 | GAL | LA SOLONA | FALLBROOK | SD | MANHOLE | ROOT BLOCKAGE | NONE | ROOTS WERE CLEARED AT AROUND 8:00PM FROM LINE.
81 | 940614 | 0130PM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 94/06/14 | 0753AM | 940614 | 0930AM | N | 194 | GAL | 0 | 2585 JUDSON ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | DEBRIS BLOCKAGE | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | DEODORIZED AREA AND WASHED DOWN STREET. | 79 | PROPERTY OWNER | 94/06/13 | 0840AM | 940616 | 0700AM | 21055 | GAL | 2065 SAN DIEGO AVE. | SAN DIEGO | SD | 4" SEWER LATERAL | UNKNOWN PROBLEM | PACIFIC OCEAN | RODDED MAIN 3 TIMES. PROBLEM IS RESPONSIBILITY OF PROPERTY OWNER NOT CITY. TURN TO COUNTY HEALTH FOR ENFORCEMENT.
90 | 940627 | 1215PM | WILLIAM F. GRAHAM | 6195277456 | SAN DIEGO, CITY OF | 94/06/15 | ? | 940622 | 1100AM | Y | 168 | GAL | 0 | 12101 LAKE DR. | ESCONDIDO | CA | AIR VALVE VAULT | BROKEN AIR VALVE LEAKING THROUGH DISCHARGE | Y | PACIFIC OCEAN |  |  | Y | N | N/A | THE AIR VALVE LEAKED THROUGH THE DISCHARGE, VACTOR ALL REMAINING FLOW AND DUMP SEWER SYSTEM. | 80 | SAN DIEGO, CITY OF | 94/06/14 | 1100AM | 940614 | 1200PM | 60 | GAL | MESA COLLEGE DR. & LINDA VISTA RD. | SAN DIEGO | SD | 8" PVC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC OCEAN | CLEANED BEBRIS ON STREET.
91 | 940616 | 1055AM | TOM BRADNEY | 7144935225 | SANTA MARGARITA WATER DIST. | 94/06/15 | 1805PM | 940615 | 2000PM | N | 2400 | GAL | 0 | OSO PARKWAY | MISSION VIEJO | ORG | MAIN HOLE | CONSTRUCTION DEBRIS | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | SPILL WAS CHLORINATED AND FLUSHED WITH WATER. | 81 | SAN DIEGO, CITY OF | 94/06/14 | 0753AM | 940614 | 0930AM | 194 | GAL | 2585 JUDSON ST. | SAN DIEGO | SD | 8" VC SEWER MAIN | DEBRIS BLOCKAGE | STORM DRAIN, PACIFIC OCEAN | DEODORIZED AREA AND WASHED DOWN STREET.
82 | 940617 | 0644AM | M. A. WHELAN | 6195258687 | SAN DIEGO, CITY OF | 94/06/16 | 1511PM | 940616 | 1741PM | N | 750 | GAL | 0 | 2816 LINCOLN AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | FLUSHED MAIN TO RELIEVE STOP AND SPRAYED AREA WITH ZEP, WASHED DOWM ALLEY AND GUTTERS. | 90 | SAN DIEGO, CITY OF | 94/06/15 | ? | 940622 | 1100AM | 168 | GAL | 12101 LAKE DR. | ESCONDIDO | CA | AIR VALVE VAULT | BROKEN AIR VALVE LEAKING THROUGH DISCHARGE | PACIFIC OCEAN | THE AIR VALVE LEAKED THROUGH THE DISCHARGE, VACTOR ALL REMAINING FLOW AND DUMP SEWER SYSTEM.
84 | 940617 | 1615PM | R. L. WILLIAMS | 6195258686 | SAN DIEGO, CITY OF | 94/06/17 | 0716AM | 940617 | 0840AM | N | 178 | GAL | 0 | 5211 ALCORN PL. | SAN DIEGO | SD | 8" INCH SEWER MAIN | HAEVY ROOTS | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | RODDED MAIN BY MAICHINE / OVERFLOW DISSIPATED IN STORM DRAIN. | 91 | SANTA MARGARITA WATER DIST. | 94/06/15 | 1805PM | 940615 | 2000PM | 2400 | GAL | OSO PARKWAY | MISSION VIEJO | ORG | MAIN HOLE | CONSTRUCTION DEBRIS | STORM DRAIN, PACIFIC OCEAN | SPILL WAS CHLORINATED AND FLUSHED WITH WATER.
85 | 940621 | 0128AM | M. A. WHELAN | 6195258686 | SAN DIEGO, CITY OF | 94/06/20 | 1824PM | 940620 | 1904PM | N | 38 | GAL | 0 | 12179 BAJADA RD. | SAN DIEGO | SD | 8" VC SEWER MAIN | PUMP STATION 77 FLOODED OUT. | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | STOPPED PUMPING CONTRACTOR FROM DUMPING SEWAGE FROM PUMP STATION 77 INTO ABOVE AFFECTED AREA. | 82 | SAN DIEGO, CITY OF | 94/06/16 | 1511PM | 940616 | 1741PM | 750 | GAL | 2816 LINCOLN AVE. | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | STORM DRAIN, PACIFIC OCEAN | FLUSHED MAIN TO RELIEVE STOP AND SPRAYED AREA WITH ZEP, WASHED DOWM ALLEY AND GUTTERS.
86 | 940620 | 1030AM | LINDA JONES | 7144994555 | SOUTH COAST WATER DISTRICT | 94/06/20 | 1200AM | 940620 | 1000AM | N | 16000 | GAL | 0 | ALISO WOODS CANYON PARK | LAGUNA NIGUEL | ORG | ? | BREAK IN SLUDGE FORCE MAIN | Y | PACIFIC OCEAN |  |  | Y | Y | 003 | NONE | 84 | SAN DIEGO, CITY OF | 94/06/17 | 0716AM | 940617 | 0840AM | 178 | GAL | 5211 ALCORN PL. | SAN DIEGO | SD | 8" INCH SEWER MAIN | HAEVY ROOTS | STORM DRAIN, PACIFIC OCEAN | RODDED MAIN BY MAICHINE / OVERFLOW DISSIPATED IN STORM DRAIN.
87 | 940622 | 0506AM | M. A. WHELAN | 6195258686 | SAN DIEGO, CITY OF | 94/06/21 | 0756AM | 940621 | 1220PM | N | 264 | GAL | 0 | 2791 TREAT ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | DEBRIS BLOCKAGE | Y | PACIFIC OCEAN |  |  | Y | N | N/A | RODDED 230' SECT. BETWEEN M/H 7881 AND 7876 AND EARED DEBRIS. | 85 | SAN DIEGO, CITY OF | 94/06/20 | 1824PM | 940620 | 1904PM | 38 | GAL | 12179 BAJADA RD. | SAN DIEGO | SD | 8" VC SEWER MAIN | PUMP STATION 77 FLOODED OUT. | STORM DRAIN, PACIFIC OCEAN | STOPPED PUMPING CONTRACTOR FROM DUMPING SEWAGE FROM PUMP STATION 77 INTO ABOVE AFFECTED AREA.
88 | 940622 | 0529AM | M. A. WHELAN | 6195258686 | SAN DIEGO, CITY OF | 94/06/21 | 1924PM | 940621 | 2124PM | Y | 2400 | GAL | 0 | CAMINO LINDO & CAMINITO NOGUERA | SAN DIEGO | SD | 12" PVC SEWER MAIN | ROOT BLOCKAGE | NO | NONE |  | ROSE CREEK STORM DRAIN | Y | N | N/A | RELIEVE STOPPAGE WITH FORK AND EXTENSION BAR. HEAVY ROOTS IN MH#31940. | 86 | SOUTH COAST WATER DISTRICT | 94/06/20 | 1200AM | 940620 | 1000AM | 16000 | GAL | ALISO WOODS CANYON PARK | LAGUNA NIGUEL | ORG | ? | BREAK IN SLUDGE FORCE MAIN | PACIFIC OCEAN | NONE
89 | 940622 | 1330PM | GARY K. ORR | 6199664854 | OCEANSIDE CITY, OF | 94/06/21 | 2100PM | 940621 | 2330PM | N | 2500 | GAL | 0 | INTERSECT. OF MISSION AVE & NORTH FOUSSAT RD. | OCEANSIDE | SD | 8" FORCE MAIN | CIVILIAN CONTRACTOR PUNCHED HOLE IN MAIN. | NO | NONE |  | SOAKED AROUND CONSTRUCTION SITE. | Y | N | N/A | FLOWS WERE DOMESTIC WTR/NO SOLIDS EVIDENT. CONTRACTOR'S CREW HAVE LIMITED ACCESS TO FIELD. PUBLIC CONTACT IS NONEXISTENT | 87 | SAN DIEGO, CITY OF | 94/06/21 | 0756AM | 940621 | 1220PM | 264 | GAL | 2791 TREAT ST. | SAN DIEGO | SD | 6" CP SEWER MAIN | DEBRIS BLOCKAGE | PACIFIC OCEAN | RODDED 230' SECT. BETWEEN M/H 7881 AND 7876 AND EARED DEBRIS.
99 | 940631 | 1100AM | ANNE BRIGGS | 9099257676 | EASTERN MINICIPAL WATER DIST. | 94/06/23 | ? | 940628 | 0200PM | Y | 2000000 | MGD | 0 | NEAR YNEZ BLVD. | TEMECULA | RIV | BLOCKED MANHOLE | ROCKS AND DEBRIS IN MANHOLE. | NO | NONE |  | DID NOT REACH ROUT 115 | Y | N | N/A | EMWD PUT DOWN HTH TO COVER OVERFLOW. | 88 | SAN DIEGO, CITY OF | 94/06/21 | 1924PM | 940621 | 2124PM | 2400 | GAL | CAMINO LINDO & CAMINITO NOGUERA | SAN DIEGO | SD | 12" PVC SEWER MAIN | ROOT BLOCKAGE | NONE | RELIEVE STOPPAGE WITH FORK AND EXTENSION BAR. HEAVY ROOTS IN MH#31940.
92 | 940624 | 1140PM | RONALD D. ROBY | 6195258682 | SAN DIEGO, CITY OF | 94/06/24 | 0635PM | 940624 | 1035PM | N | 240 | GAL | 0 | 3068 NEWTON AVE | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | NO | NONE |  | UNDER CONSUMERS HOUSE | Y | N | N/A | CLAIMS CALLED TO CLEAN UP OVERFLOW UNDER HOUSE | 89 | OCEANSIDE CITY, OF | 94/06/21 | 2100PM | 940621 | 2330PM | 2500 | GAL | INTERSECT. OF MISSION AVE & NORTH FOUSSAT RD. | OCEANSIDE | SD | 8" FORCE MAIN | CIVILIAN CONTRACTOR PUNCHED HOLE IN MAIN. | NONE | FLOWS WERE DOMESTIC WTR/NO SOLIDS EVIDENT. CONTRACTOR'S CREW HAVE LIMITED ACCESS TO FIELD. PUBLIC CONTACT IS NONEXISTENT
93 | 940624 | 1030PM | RONALD D. ROBY | 6195258682 | SAN DIEGO, CITY OF | 94/06/24 | 0113PM | 940624 | 0513PM | N | 240 | GAL | 0 | JACARANDA DR. & MORLEY FIELD DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | MAIN BREAK | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | FLOW SOAKED INTO GROUND IN CANYON AT END OF STORM DRAIN, CREW DUG UP AND REPAIRED MAIN. | 99 | EASTERN MINICIPAL WATER DIST. | 94/06/23 | ? | 940628 | 0200PM | 2000000 | MGD | NEAR YNEZ BLVD. | TEMECULA | RIV | BLOCKED MANHOLE | ROCKS AND DEBRIS IN MANHOLE. | NONE | EMWD PUT DOWN HTH TO COVER OVERFLOW.
94 | 940624 | 0700AM | EMERGENCY CREW | 6195277443 | SAN DIEGO, CITY OF | 94/06/24 | 0700AM | 940624 | 0900AM | N | 120 | GAL | 0 | 4265 41TH STREET | SAN DIEGO | SD | 4" SEWER LATERAL | 4" COLLAPSE LATERAL ALLEY | NO | NONE |  | DOWNSTREAM MANHOLE | Y | N | N/A | WASHED DOWN AND VACTORED. | 92 | SAN DIEGO, CITY OF | 94/06/24 | 0635PM | 940624 | 1035PM | 240 | GAL | 3068 NEWTON AVE | SAN DIEGO | SD | 6" VC SEWER MAIN | GREASE BLOCKAGE | NONE | CLAIMS CALLED TO CLEAN UP OVERFLOW UNDER HOUSE
95 | 940626 | 0820PM | RONALD D. ROBY | 6195258682 | SAN DIEGO, CITY OF | 94/06/26 | 1135AM | 940626 | 0135PM | N | 3600 | GAL | 0 | 3600 CERVANTES AVE. | SAN DIEGO | SD | 8" PVC SEWER MAIN | VANDALISM i.e.ROCKS | Y | PACIFIC OCEAN |  |  | Y | N | N/A | STOP WAS IN CANYON WHERE IT DRIED. | 93 | SAN DIEGO, CITY OF | 94/06/24 | 0113PM | 940624 | 0513PM | 240 | GAL | JACARANDA DR. & MORLEY FIELD DR. | SAN DIEGO | SD | 8" VC SEWER MAIN | MAIN BREAK | STORM DRAIN, PACIFIC OCEAN | FLOW SOAKED INTO GROUND IN CANYON AT END OF STORM DRAIN, CREW DUG UP AND REPAIRED MAIN.
165 | 940725 | 1050AM | NOAH C. SANCHEZ |  | LOS ALISOS WATER DISTRICT | 94/06/26 | 0630AM | 940626 | 0800AM | Y | 90000 | GAL |  | AVENIDA DE LA CARLOTA AND RIDGE RTE. DR. | ? | ? | ? | DAMAGE TO THE TRANSMISSION MAIN | Y | STORM DRAIN, SAN DIEGO CREEK |  |  | ? | ? | ? | REPAIRS TO THE MAIN COMMENCED IMMEDIATELY IN EFFORTS TO MINIMIZE DOWN TIME. | 94 | SAN DIEGO, CITY OF | 94/06/24 | 0700AM | 940624 | 0900AM | 120 | GAL | 4265 41TH STREET | SAN DIEGO | SD | 4" SEWER LATERAL | 4" COLLAPSE LATERAL ALLEY | NONE | WASHED DOWN AND VACTORED.
96 | 940627 | 2330PM | D. A. BRANCO | 6195258687 | SAN DIEGO, CITY OF | 94/06/27 | 1606PM | 940627 | 1906PM | N | 900 | GAL | 0 | 3634 7TH AVE. | SAN DIEGO | SD | 8" VC | ROOT BLOCKAGE | Y | PACIFIC OCEAN |  |  | Y | N | N/A | HAND RODDED IN CANYON TO RELIEVE STOP. | 95 | SAN DIEGO, CITY OF | 94/06/26 | 1135AM | 940626 | 0135PM | 3600 | GAL | 3600 CERVANTES AVE. | SAN DIEGO | SD | 8" PVC SEWER MAIN | VANDALISM i.e.ROCKS | PACIFIC OCEAN | STOP WAS IN CANYON WHERE IT DRIED.
97 | 940627 | 1225PM | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 94/06/27 | 1033AM | 940627 | 1215PM | N | 2550 | GAL | 0 | 3930 BEYER BLVD. | SAN DIEGO | SD | 8" VC | ROOT BLOCKAGE | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | FLUSHED MAIN. | 165 | LOS ALISOS WATER DISTRICT | 94/06/26 | 0630AM | 940626 | 0800AM | 90000 | GAL | AVENIDA DE LA CARLOTA AND RIDGE RTE. DR. | ? | ? | ? | DAMAGE TO THE TRANSMISSION MAIN | STORM DRAIN, SAN DIEGO CREEK | REPAIRS TO THE MAIN COMMENCED IMMEDIATELY IN EFFORTS TO MINIMIZE DOWN TIME.
98 | 940628 | 0800AM | CITY OF ESCONDIDO | 6197414854 | ESCONDIDO, CITY OF | 94/06/27 | ? PM | 940628 | 0530PM | N | 25000 | GAL | 0 | 1404 N. BROADWAY ST. AND EL NORTE PKWY | ESCONDIDO | SD | PRIVATE CLEANOUT | ROOT BLOCKAGE | Y | STORM DRAIN, REIDY CREEK/ESC. CREEK |  |  | Y | N | N/A | CITY TREATED DIRT AREA AND POSTED SIGNS IN THE IMMEDIATE AREA. WE ALSO WITNESSED THE PLUMBER CLEAR THE LINE. | 96 | SAN DIEGO, CITY OF | 94/06/27 | 1606PM | 940627 | 1906PM | 900 | GAL | 3634 7TH AVE. | SAN DIEGO | SD | 8" VC | ROOT BLOCKAGE | PACIFIC OCEAN | HAND RODDED IN CANYON TO RELIEVE STOP.
119 | 940627 | 1612PM | JOHN ROBERTSON | 6197253868 | CAMP PENDLETON | 94/06/27 | 1300PM | 940627 | 1500PM | N | 2500 | GAL | 0 | DEL MAR BOAT BASIN, BLDG 210579 | CAMP PANDLETON | SD | BLDG 210579 | BLOCKED LINE | Y | OCEAN INLET TO BASIN, PACIFIC OCEAN |  |  | Y | N | N/A | NONE | 97 | SAN DIEGO, CITY OF | 94/06/27 | 1033AM | 940627 | 1215PM | 2550 | GAL | 3930 BEYER BLVD. | SAN DIEGO | SD | 8" VC | ROOT BLOCKAGE | STORM DRAIN, PACIFIC OCEAN | FLUSHED MAIN.
100 | 940628 | 2310PM | D. A. BRANCO | 6195258687 | SAN DIEGO, CITY OF | 94/06/28 | 1607PM | 940628 | 1807PM | N | 240 | GAL | 0 | 6200 JEFF ST. | SAN DIEGO | SD | 8" VC | ROOT BLOCKAGE | Y | PACIFIC OCEAN |  |  | Y | N | N/A | MACHINE RODDED TO RELIEVE STOP. | 98 | ESCONDIDO, CITY OF | 94/06/27 | ? PM | 940628 | 0530PM | 25000 | GAL | 1404 N. BROADWAY ST. AND EL NORTE PKWY | ESCONDIDO | SD | PRIVATE CLEANOUT | ROOT BLOCKAGE | STORM DRAIN, REIDY CREEK/ESC. CREEK | CITY TREATED DIRT AREA AND POSTED SIGNS IN THE IMMEDIATE AREA. WE ALSO WITNESSED THE PLUMBER CLEAR THE LINE.
101 | 940630 | 0823AM | MARK STROHMAN | 6195258682 | SAN DIEGO, CITY OF | 94/06/29 | 1156AM | 940629 | 1630PM | N | 274 | GAL | 0 | 4310 RANDOLPH | SAN DIEGO | SD | 6" CP | ROOT BLOCKAGE | Y | PACIFIC OCEAN |  |  | Y | N | N/A | RODDED BY HAND 10' SECTOR IN ABOVE LOCATION. | 119 | CAMP PENDLETON | 94/06/27 | 1300PM | 940627 | 1500PM | 2500 | GAL | DEL MAR BOAT BASIN, BLDG 210579 | CAMP PANDLETON | SD | BLDG 210579 | BLOCKED LINE | OCEAN INLET TO BASIN, PACIFIC OCEAN | NONE
102 | 940630 | 0212AM | M. A. WHELAN | 6195258686 | SAN DIEGO, CITY OF | 94/06/29 | 1532PM | 940629 | 1702PM | N | 90 | GAL | 0 | 2615 BEYER BLVD. | SAN DIEGO | SD | 6" VC SEWER MAIN | DEBRIS IN SEWER MAIN. | Y | STORM DRAIN, PACIFIC OCEAN |  |  | Y | N | N/A | FLUSHED AND VACTORED MAN HOLE. WASHED DOWN SIDE WALKS AND GUTTERS. | 100 | SAN DIEGO, CITY OF | 94/06/28 | 1607PM | 940628 | 1807PM | 240 | GAL | 6200 JEFF ST. | SAN DIEGO | SD | 8" VC | ROOT BLOCKAGE | PACIFIC OCEAN | MACHINE RODDED TO RELIEVE STOP.
103 | 940701 | 0154AM | M. A. WHELAN | 6195258682 | SAN DIEGO, CITY OF | 94/06/30 | 1657PM | 940630 | 1757PM | N | 900 | GAL | 0 | 39TH ST. & LANDIS | SAN DIEGO | SD | 8" VC SEWER MAIN | ROCK BLOCKAGE | Y | PACIFIC OCEAN |  |  | Y | N | N/A | RODDED MAIN AND REMOVED ROCK. | 101 | SAN DIEGO, CITY OF | 94/06/29 | 1156AM | 940629 | 1630PM | 274 | GAL | 4310 RANDOLPH | SAN DIEGO | SD | 6" CP | ROOT BLOCKAGE | PACIFIC OCEAN | RODDED BY HAND 10' SECTOR IN ABOVE LOCATION.
104 | 940630 | 1700PM | R. H. PARKER | 6195258685 | SAN DIEGO, CITY OF | 94/06/30 | ? | 940630 | 1545PM | N | 50 | GAL | 0 | ALLEY ARIZONA & ARNOLD AT UPAS | SAN DIEGO | SD | 8" VC PIPE | GRAVITY MAIN BREAK | NO | NONE |  | POOLED IN ALLEY, VACTORED UP | Y | N | N/A | SEWAGE RETURNED TO SYSTEM BY VACTOR. | 102 | SAN DIEGO, CITY OF | 94/06/29 | 1532PM | 940629 | 1702PM | 90 | GAL | 2615 BEYER BLVD. | SAN DIEGO | SD | 6" VC SEWER MAIN | DEBRIS IN SEWER MAIN. | STORM DRAIN, PACIFIC OCEAN | FLUSHED AND VACTORED MAN HOLE. WASHED DOWN SIDE WALKS AND GUTTERS.
| 940809 | 13:01 | MICHAEL DUNBAR | 8347200 | COASTAL TREATMENT PLANT | 94/01/17 | 1120AM | ? |  | Y | 1000 | GAL |  | COASTAL TREATMENT PLANT | LAGUNA BEACH | ORG |  | SHAFT ON ROTATING SCREEN BROKE. | Y | ALISO CREEK, ALISO BEACH |  |  | Y | Y | ? | NONE | 103 | SAN DIEGO, CITY OF | 94/06/30 | 1657PM | 940630 | 1757PM | 900 | GAL | 39TH ST. & LANDIS | SAN DIEGO | SD | 8" VC SEWER MAIN | ROCK BLOCKAGE | PACIFIC OCEAN | RODDED MAIN AND REMOVED ROCK.
| 940808 | 13:02 | JIM SMITH | 6432006 | MOULTON NIGUEL WATER DISTRICT | 94/05/19 | 1045AM | ? |  | Y | 4000 | GAL |  | LAGUNA NIGUEL REGIONAL PARK | LAGUNA NIGUEL | ORG |  | RUPTURE IN 24" FORCE MAIN | Y | ALISO CREEK, ALISO BEACH |  |  | Y | Y | ? | NONE | 104 | SAN DIEGO, CITY OF | 94/06/30 | ? | 940630 | 1545PM | 50 | GAL | ALLEY ARIZONA & ARNOLD AT UPAS | SAN DIEGO | SD | 8" VC PIPE | GRAVITY MAIN BREAK | NONE | SEWAGE RETURNED TO SYSTEM BY VACTOR.
| 940809 | 13:01 | KEN KREGER | 7144994555 | COASTAL TREATMENT PLANT | 94/05/25 | 1130AM | ? |  | Y | 5000 | GAL |  | COASTAL TREATMENT PLANT | LAGUNA BEACH | ORG |  | PUMP STATION UNABLE TO HANDLE INCREASED FLOW. | Y | ALISO CREEK, ALISO BEACH |  |  | Y | Y | ? | NONE |  | COASTAL TREATMENT PLANT | 94/01/17 | 1120AM | ? |  | 1000 | GAL | COASTAL TREATMENT PLANT | LAGUNA BEACH | ORG |  | SHAFT ON ROTATING SCREEN BROKE. | ALISO CREEK, ALISO BEACH | NONE
| 940809 | 13:04 | REGINA | 7144994885 | SOUTH COASTAL WATER DISTRICT | 94/06/19 | 1200AM | ? |  | Y | 16000 | GAL |  | ALISO WOODS CANYON PARK ENTRANCE | ? | ORG |  | LINE BREAK IN SLUDGE LINE (FORCE MAIN) | Y | ALISO CREEK, LAGUNA NIGUEL |  |  | Y | Y | ? | NONE |  | MOULTON NIGUEL WATER DISTRICT | 94/05/19 | 1045AM | ? |  | 4000 | GAL | LAGUNA NIGUEL REGIONAL PARK | LAGUNA NIGUEL | ORG |  | RUPTURE IN 24" FORCE MAIN | ALISO CREEK, ALISO BEACH | NONE
| 940620 | 10:30 | KEN TAYLOR |  | SOUTH COASTAL WATER DISTRICT | 94/06/20 | 12OOAM | ? |  | Y | 16000 | GAL |  | ALISO WOODS CANYON PARK |  | ORG |  | BREAK IN SLUDGE FORCE MAIN AT AWMACTP. | Y | BAY/OCEAN |  |  | Y | Y | ? | SIGNS HAVE BEEN POSTED NORTH TO THE SOUTHERN BOUNDARIES OF TREASURE ISLAND. |  | COASTAL TREATMENT PLANT | 94/05/25 | 1130AM | ? |  | 5000 | GAL | COASTAL TREATMENT PLANT | LAGUNA BEACH | ORG |  | PUMP STATION UNABLE TO HANDLE INCREASED FLOW. | ALISO CREEK, ALISO BEACH | NONE
[28 empty] | SOUTH COASTAL WATER DISTRICT | 94/06/19 | 1200AM | ? |  | 16000 | GAL | ALISO WOODS CANYON PARK ENTRANCE | ? | ORG |  | LINE BREAK IN SLUDGE LINE (FORCE MAIN) | ALISO CREEK, LAGUNA NIGUEL | NONE
[28 empty] | SOUTH COASTAL WATER DISTRICT | 94/06/20 | 12OOAM | ? |  | 16000 | GAL | ALISO WOODS CANYON PARK |  | ORG |  | BREAK IN SLUDGE FORCE MAIN AT AWMACTP. | BAY/OCEAN | SIGNS HAVE BEEN POSTED NORTH TO THE SOUTHERN BOUNDARIES OF TREASURE ISLAND.