CALIFORNIA REGIONAL WATER QUALITY CONTROL BOARD

SAN FRANCISCO BAY REGION

1515 CLAY STREET, SUITE 1400

OAKLAND, CA  94612

(510) 622 – 2300     Fax: (510) 622 - 2460

FACT SHEET

for

NPDES PERMIT and WASTE DISCHARGE REQUIREMENTS for

TESORO REFINING & MARKETING COMPANY

GOLDEN EAGLE REFINERY

MARTINEZ, CONTRA COSTA COUNTY

NPDES Permit No. CA0004961

ORDER NO. R2-2005-0041

PUBLIC NOTICE:

# Written Comments

- Interested persons are invited to submit written comments concerning this draft permit.

- Comments must be submitted to the Regional Board no later than 5:00 p.m. on August 8, 2005.

- Send comments to the Attention of Robert Schlipf.

# Public Hearing

- The draft permit will be considered for adoption by the Board at a public hearing during the Board’s regular monthly meeting at: Elihu Harris State Office Building, 1515 Clay Street, Oakland, CA; 1st floor Auditorium.

- This meeting will be held on:		September 21, 2005, starting at 9:00 am.

# Additional Information

- For additional information about this matter, interested persons should contact Regional Board staff member:	Mr. Robert Schlipf, Phone: (510) 622-2478; email: rschlipf@waterboards.ca.gov

This Fact Sheet contains information regarding an application for waste discharge requirements and National Pollutant Discharge Elimination System (NPDES) permit for the Tesoro Golden Eagle Refinery for industrial wastewater and storm water discharges.  The Fact Sheet describes the factual, legal, and methodological basis for the proposed permit and provides supporting documentation to explain the rationale and assumptions used in deriving the limits.

I.	INTRODUCTION

Tesoro (hereinafter called the Discharger) has applied to the Board for reissuance of waste discharge requirements and a permit to discharge industrial wastewater and storm water to waters of the State and the United States under the National Pollutant Discharge Elimination System (NPDES).  The application and Report of Waste Discharge is dated August 20, 2004, and was supplemented on February 11, 2005.

The Discharger owns and operates a petroleum refinery with an average crude-run throughput of approximately 157,000 barrels per day.  The Golden Eagle Refinery receives crude oil and other feedstocks by tankers or pipelines.  Crude oil is cracked and processed at the site to produce gasoline and diesel fuel.  According to 40 CFR Part 419.20, the U.S. Environmental Protection Agency (USEPA) has classified this facility as a cracking refinery.  The USEPA and the Board have classified Tesoro as a major discharger.

The receiving water for the subject discharges is Suisun Bay and Carquinez Strait.  Beneficial uses for Suisun Bay and Carquinez Strait, as identified in the Basin Plan, and based on known uses of the receiving waters in the vicinity of the discharge, are:

- Industrial Service Supply

- Navigation

- Water Contact Recreation

- Non-contact Water Recreation

- Commercial and Sport Fishing

- Wildlife Habitat

- Preservation of Rare and Endangered Species

- Fish Migration

- Fish Spawning

- Estuarine Habitat

The receiving waters for the subject discharge is Suisun Bay and Carquinez Strait, which are tidally influenced water body, with significant fresh water inflows during the wet weather season.  Furthermore, based on Regional Monitoring Program data, Suisun Bay and Carquinez Strait meet the definition of estuarine under the definitions included in the Basin Plan.  Therefore, the effluent limitations specified in this Order for discharges to Suisun Bay and Carquinez Strait are based on the lower of the marine and freshwater Basin Plan WQOs and CTR and NTR WQC.

II.	DESCRIPTION OF EFFLUENT

Board Order Nos. 00-011, 00-056, and 01-138 (hereinafter the Previous Order), presently regulates the discharges.  The discharges are described below and are based on information contained in the Report of Waste Discharge and recent self-monitoring reports.

- Waste 001 consists of an average of 5.1 million gallons per day (mgd) of treated process wastewaters, including wastewater from sour water strippers, ammonia recovery unit, acid plant effluent, sanitary wastewater, cooling tower blowdown, boiler blowdown, cooling tower and boiler blowdown from the Foster Wheeler Cogeneration Plant, neutralized demineralizer regeneration water (hereinafter the Reject Water) from the water treatment system, fire water system, groundwater from remediation activities; non-hazardous wastewater generated from offsite Discharger-owned facilities, process wastewater from the Monsanto Company Catalyst Plant, and cooling tower and boiler blowdown from Air Liquide Carbon Dioxide Plant.  During wet weather, Waste 001 has an additional component consisting of stormwater runoff from various onsite developed areas of Tracts 1, 2 and 3, and offsite facilities.  Waste 001 is treated at the onsite wastewater treatment plant prior to being discharged to Suisun Bay through a 27-inch diameter outfall.  The outfall, referred to as E-001, terminates with a multi-port diffuser (lat. 380254, long. 1220522) located under the Avon Wharf 45 feet below mean lower low water.  Table 1 below describes the quality of treated effluent (E-001) based on self-monitoring data from 2001 through 2004.

Table 1:  Summary of Pollutants in Treated Wastewater at E-001

| Parameter | Average1 | Daily Maximum |
| --- | --- | --- |
| pH, standard units | 6.0 (minimum) | 8.9 |
| Temperature (F) | 44 (minimum) | 89 |
| Total Coliform Organisms2 (MPN/ 100 mL) | Nondetect | 16,000 |
| Total Coliform Organisms3 (MPN/100 mL) | Nondetect | 1,100 |
| BOD (mg/L) | 8.2 | 18.3 |
| COD (mg/L) | 66 | 240 |
| TSS (mg/L) | 12.8 | 84 |
| Ammonia as N (mg/L) | 7.8 | 29.4 |
| Oil and Grease (mg/L) | Nondetect | 9.4 |
| Total Phenols (g/L) | Nondetect | 10 |
| Arsenic (g/L) | 4.1 | 11 |
| Cadmium (g/L) | 0.09 | 0.4 |
| Chromium VI (g/L) | Nondetect | 2.0 |
| Copper (g/L) | 4.6 | 20 |
| Lead (g/L) | 0.9 | 3.5 |
| Mercury (g/L) | 0.0073 | 0.0375 |
| Nickel (g/L) | 15.1 | 87 |
| Selenium (g/L) | 11.6 | 41 |
| Silver (g/L) | Nondetect | 0.09 |
| Zinc (g/L) | 11.1 | 26 |
| Cyanide (g/L) | Nondetect | 28 |

1   	Nondetect (ND) values were replaced with ½ the detection limit. In cases where more than half the data are ND, the average indicated in Table 1 is ND.

2      Refers to E-001-D2 – a description is included in the Self-Monitoring Program

3 	Refers to E-001-D1 – a description is included in the Self-Monitoring Program

The wastewater treatment system begins with the Discharger routing process wastewater to a central pump station (i.e., No. 1 pump station).  From this pump station, process wastewater flows to an API oil and water separator that consists of a head channel that feeds four concrete channels.  The API Separator uses a chain driven surface skimmer to remove oil and solids.  The Discharger pumps this material to Tanks 699 and 700 for additional oil and water separation and recovery.  After the API separator, wastewater flows by gravity to four Dissolved Nitrogen Flotation (DNF) units where additional oil and solids are removed.  The Discharger also pumps this material to Tanks 699 and 700.

From the DNF units, wastewater is routed through an air stripper where a blower forces air through a grid of perforated tubes.  The vapors from the air stripper, DNF units, and API Separator are destroyed in a thermal oxidizer.  The Discharger pumps wastewater from the Air Stripper to Surge Pond No. 1 for biotreatment.  Surge Pond No. 1 is a 14-acre rectangular basin that is baffled into five sections.  The first section is extensively aerated whereas subsequent sections are lightly aerated.  To enhance treatment in Surge Pond No. 1, the Discharger adds phosphoric acid, and occasionally specialized bacteria.  From Surge Pond No. 1, wastewater flows by gravity to Surge Pond No. 2.  Surge Pond No. 2 is an 8-acre rectangular basin that contains two aerators to ensure aerobic conditions near the surface, and functions mainly as a settling basin for biosolids with some bio-treatment activity.  The Discharger may pump up to 900 gallons per minute of wastewater from Surge Pond No. 2 to the refinery for reuse as industrial water.  The remaining wastewater from Surge Pond No. 2 is pumped to the oxpond.  The oxpond is about 108 acres with an estimated capacity of 216 million gallons, but typically operates with a volume of around 150 million gallons.  The oxpond contains five aerators at the inlet section of the pond to ensure oxygen levels in wastewater are adequate.  It passively treats wastewater by providing a retention time of about 30 days.

From the oxpond, the Discharger routes wastewater to two clarifiers that operate in parallel.  In the clarifiers, the Discharger adds coagulants and flocculants to enhance settling of wastewater solids.  Clarifiers solids are centrifuged, and disposed of offsite.  The supernatant from the centrifuge is routed to Surge Pond No. 1.  From the clarifiers, wastewater flows through a toothed weir to two filters (Round and Zimpro) that operate in parallel.  The Round filter is multimedia (sand and antracite) and consists of six chambers, while the Zimpro filter is a six-celled trickling sand filter.  Both of these filters contain automatic backwash functions that allow them to maintain continuous operation.  Backwash water from the filters is routed to Surge Pond No. 1 for treatment, and treated wastewater is routed to 12 Granular Activated Carbon (GAC) columns that operate in pairs (i.e., lead and lag).  The Discharger uses GAC columns, as needed, to ensure treated wastewater is not toxic to aquatic life.  Backwash water from the GAC columns is also discharged to Surge Pond No. 1 for further treatment.

After the GAC columns, the Discharger routes wastewater to a 26-acre Coke Pond.  The Discharger indicates that the purpose of discharging treated wastewater to the Coke Pond is to (a) provide water for reuse for coke sluicing operations, (b) provide water for reuse in the dust abatement sprinklers, (c) use as backup fire water supply, and (d) to keep water in motion in order to avoid odors from stagnation, and (e) provide additional polishing of final effluent.

From the Coke Pond, the Discharger routes treated wastewater to the Clean Canal.  The Clean Canal conveys treated wastewater to a sump containing three pumps that discharge water to the Bay through a deepwater diffuser located near the Avon Wharf.  The Clean Canal also receives stormwater runoff, and neutralized demineralizer reject water from the Discharger’s water treatment plant.

- Waste 003 consists of stormwater runoff from an area of approximately 120 acres in the central and western portions of the Tract 4 tank farm.  Stormwater that falls on the west side of Tract 4 is collected within tank dikes and several retention ponds downhill of the tanks.  A long retention basin further downhill serves as a backup for these ponds.  If runoff is excessive, stormwater will be discharged indirectly to Pacheco Slough via L-shaped overflow pipes at two possible locations that draw water from below the surface, thereby keeping oil and other floating material in the pond for subsequent removal.  Since these two locations are in proximity to each other, they are collectively designated as E-003 (lat. 3800’44”, long. 12203’55”).  The Discharger has not discharged stormwater through this outfall in the past five years.

- Waste 004 consists of stormwater runoff from an area of 140 to 150 acres including the southeast portion of the Tract 4 tank farm and all of the Tract 6 tank farm, and offsite facilities including the Monsanto Company Catalyst Plant, Air Liquide, Chevron Bulk Terminal Station, Kinder Morgan Energy Partners, Texaco Pump Station, and PG&E Substation.  Stormwater is collected, conveyed through ditches, and discharged to the Cardox Pond, from which stormwater is pumped to E-001 or discharged indirectly via L-shaped overflow pipes at six possible locations to Hastings Slough.  These six discharge locations are approximately a foot away from each other, and the quality of water leaving the six pipes is expected to be similar.  These discharge locations are collectively designated as E-004 (lat. 3801’21”, long. 12203’30”).

- Waste 005 consists of stormwater runoff from various small areas.  Table 2 below describes the discharge locations and pollutants of concern.

Table 2: Discharge Locations & Potential Pollutants at E-005

| Area | Location | Current E-005 Discharge | Potential Pollutants1 |
| --- | --- | --- | --- |
| U-1TE | East side of Tract 1 | None | TPHs, O&G |
| U-T2N | North end of Tract 2 | None | Sed, O&G |
| U-T2NW | NW corner of Tract 2 | E-005-T2NW | Sed, O&G |
| U-T2S | South end of Tract 2 | E-005-T2S(a),(b),(c) | Sed, Metals, O&G |
| U-T2SW | SW corner of Tract 2 | E-005-T2SW | Sed, Metals, O&G, TPHs |
| U-T3N | North end of Tract 3 | None | TPHs, O&G |
| U-T3SE | SE corner of Tract 3 | None | None |
| U-T3SW | SW corner of Tract 3 | None | None |
| U-T4NW | NW corner of Tract 4 | E-005-T4NW | Sed, O&G |
| U-T4SW | SW corner of Tract 4 | E-005-T4SW | Sed, O&G |
| U-T6NE | NE corner of Tract 6 | None | Sed, Metals, O&G, TPHs |
| U-T6SW | SW corner of Tract 6 | None | None |
| U-AW | West end of Amorco | None | Sed., O&G, TPHs |
| U-AS | South side of Amorco | E-005-AS2 | Sed., O&G, TPHs |

1 TPH=Total Petroleum Hydrocarbons, O&G=Oil and Grease, Sed=Sediment

2 E-005-AS has not discharged in the past five years

III.	GENERAL RATIONALE

The following documents are the bases for the requirements contained in the proposed Order, and are referred to under the specific rationale section of this Fact Sheet.

- Federal Water Pollution Control Act, as amended (hereinafter the CWA).

- Federal Code of Regulations, Title 40 - Protection of Environment, Chapter 1, Environmental Protection Agency, Subchapter D, Water Programs, Parts 122-129 (hereinafter referred to as 40 CFR specific part number).

- Water Quality Control Plan, San Francisco Bay Basin, adopted by the Board on June 21, 1995 (hereinafter the Basin Plan). The California State Water Resources Control Board (hereinafter the State Board) approved the Basin Plan on July 20, 1995 and by California State Office of Administrative Law approved it on November 13, 1995.  The Board amended the Basin Plan on January 21, 2004, to adopt California Toxics Rule criteria for eight metals in lieu of existing Basin Plan objectives.  The SWRCB and Office of Administrative Law approved this amendment on July 22, 2004, and October 4, 2004, respectively.  The Basin Plan defines beneficial uses and contains WQOs for waters of the State, including Suisun Bay.

- California Toxics Rules, Federal Register, Vol. 65, No. 97, May 18, 2000 (hereinafter the CTR).

- National Toxics Rules 57 FR 60848, December 22, 1992, as amended (hereinafter the NTR).

- State Board’s Policy for Implementation of Toxics Standards for Inland Surface Waters, Enclosed Bays, and Estuaries of California, March 2, 2000 (hereinafter the State Implementation Policy, or SIP).

- Quality Criteria for Water, USEPA 440/5-86-001, 1986.

- Ambient Water Quality Criteria for Bacteria – 1986, USEPA440/5-84-002, January 1986.

- Technical Support Document for Water Quality-Based Toxics Control – USEPA/505/2-90-001, March 1991

IV.	SPECIFIC RATIONALE

Several specific factors affecting the development of limitations and requirements in the proposed Order are discussed as follows:

1.	Recent Plant Performance

Section 402(o) of CWA and 40 CFR § 122.44(l) require that water quality-based effluent limits (WQBELs) in re-issued permits be at least as stringent as in the previous permit.  The SIP specifies that interim effluent limitations, if required, must be based on current treatment facility performance or on existing permit limitations whichever is more stringent.  In determining what constitutes “recent plant performance”, best professional judgment (BPJ) was used.  Effluent monitoring data collected from 2001-2004 are considered representative of recent plant performance.  These data specifically account for flow variation due to wet and dry years.

2.	Impaired Water Bodies in 303(d) List

On June 6, 2003, U.S. EPA approved a revised list of impaired waterbodies prepared by the State. The list (hereinafter referred to as the 2002 303(d) list) was prepared in accordance with Section 303(d) of the Federal Clean Water Act to identify specific waterbodies where water quality standards are not expected to be met after implementation of technology-based effluent limitations on point sources. Suisun Bay is listed as an impaired waterbody. The pollutants impairing Suisun Bay include mercury, nickel, selenium, PCBs total, dioxins and furans, chlordane, DDT, dieldrin, diazinon, and dioxin-like PCBs.  Suisun Bay is also impaired by exotic species. Copper, which was previously identified as impairing Suisun Bay, was not included as an impairing pollutant in the 2002 303(d) list and has been placed on the new Monitoring List.

3.	Effluent Limitations

The SIP requires final effluent limitations for all 303(d)-listed pollutants to be based on total maximum daily loads (TMDLs) and associated wasteload allocations (WLAs).  The SIP and USEPA regulations also require that final concentration-based WQBELs be included for all pollutants having Reasonable Potential to cause or contribute to an exceedence of applicable water quality standards (having Reasonable Potential or RP).  The SIP requires that where the discharger has demonstrated infeasibility to meet the final WQBELs, interim performance-based limitations (IPBLs) or previous permit limitations (whichever is more stringent) be established in the permit, together with a compliance schedule in effect until final effluent limitations are adopted.  The SIP also requires the inclusion of appropriate provisions for waste minimization and source control where interim limitations are established.

4.	Dilution

The Board believes a conservative 10:1 dilution credit for discharges of non-bioaccumulative pollutants to San Francisco Bay is necessary for protection of beneficial uses.  The basis for limiting the dilution credit is based on SIP provisions in Section 1.4.2.  The following outlines the basis for limiting the dilution credit:

(1) A far-field background station is appropriate because the San Francisco Bay watershed, including the receiving waters, is a very complex estuarine system with highly variable and seasonal upstream freshwater inflows and diurnal tidal saltwater inputs.

(2) Due to the complex hydrology of the San Francisco Bay watershed, a mixing zone cannot be accurately established.

(3) Previous dilution studies do not fully account for the cumulative effects of other wastewater discharges to the system.

(4) The SIP allows limiting a mixing zone and dilution credit for persistent pollutants (e.g., copper and nickel).

The main justification for limiting dilution credit is uncertainty in accurately determining ambient background and uncertainty in accurately determining the mixing zone in a complex estuarine system with multiple wastewater discharges.  The basis for using 10:1 is that it was granted in the previous permit.  This 10:1 limit is also based on the Basin Plan’s prohibition number 1, which prohibits discharges like Waste 001 with less than 10:1.  The following gives more detailed rational.

- (1) Complex Estuarine System Necessitates Far-Field Background - The SIP allows background to be determined on a discharge-by-discharge or water body-by-water body basis (SIP section 1.4.3).  Consistent with the SIP, Board staff has chosen to use a water body-by-water body basis because of the uncertainties inherent in accurately characterizing ambient background in a complex estuarine system on a discharge-by-discharge basis.

- With this in mind, the Yerba Buena Island Station fits the guidance for ambient background in the SIP compared to other stations in the RMP.  The SIP states that background data are applicable if they are “representative of the ambient receiving water column that will mix with the discharge.”  Board Staff believe that data from this station are representative of water that will mix with the discharge from Outfalls E-001.  Although this station is located near the Golden Gate, it would represent the typical water flushing in and out in the Bay Area each tidal cycle.  For most of the Bay Area, the waters represented by this station make up a large part of the receiving water that will mix with the discharge.

- (2) Uncertainties Prevent Accurate Mixing Zones in Complex Estuarine Systems - There are uncertainties in accurately determining the mixing zones for each discharge.  The models that have been used by dischargers to predict dilution have not considered the three-dimensional nature of the currents in the estuary resulting from the interaction of tidal flushes and seasonal fresh water outflows.  Saltwater is heavier than fresh water.  Colder saltwater from the ocean flushes in twice a day generally under the warmer fresh river waters that flow out annually.  When these waters mix and interact, complex circulation patterns occur due to the different densities of these waters.  These complex patterns occur throughout the estuary but are most prevalent in the San Pablo Bay, Carquinez Strait, and Suisun Bay areas.  The locations change depending on the strength of each tide and the variable rate of delta outflow.  Additionally, sediment loads to the Bay from the Central Valley also change on a longer-term basis.  These changes can result in changes to the depths of different parts of the Bay making some areas more shallow and/or other areas more deep.  These changes affect flow patterns that in turn can affect the initial dilution achieved by a discharger’s diffuser.

- (3)	Dye studies do not account for cumulative effects from other discharges - The tracer and dye studies conducted are often not long enough in duration to fully assess the long residence time of a portion of the discharge that is not flushed out of the system.  In other words, some of the discharge, albeit a small portion, makes up part of the dilution water.  So unless the dye studies are of long enough duration, the diluting effect on the dye measures only the initial dilution with “clean” dilution water rather than the actual dilution with “clean” dilution water plus some amount of original discharge that resides in the system.  Furthermore, both models and dye studies that have been conducted have not considered the effects of discharges from other nearby discharge sources, nor the cumulative effect of discharges from over 20 other major dischargers to San Francisco Bay system.  While it can be argued the effects from other discharges are accounted for by factoring in the local background concentration in calculating the limitations, accurate characterization of local background levels are also subject to uncertainties resulting from the interaction of tidal flushing and seasonal fresh water outflows described above.

(4)  Mixing Zone Is Further Limited for Persistent Pollutants - Discharges to the Bay Area waters are not completely-mixed discharges as defined by the SIP.  Thus, the dilution credit should be determined using site-specific information for incompletely-mixed discharges.  The SIP in section 1.4.2.2 specifies that the Regional Board “significantly limit a mixing zone and dilution credit as necessary…  For example, in determining the extent of a mixing zone or dilution credit, the RWQCB shall consider the presence of pollutants in the discharge that are … persistent.”  The SIP defines persistent pollutants to be “substances for which degradation or decomposition in the environment is nonexistent or very slow.”  The pollutants at issue here are persistent pollutants (e.g., copper, lead, nickel, silver, and zinc).  The dilution studies that estimate actual dilution do not address the effects of these persistent pollutants in the Bay environment, such as their long-term effects on sediment concentrations.”

5.	Basis for Prohibitions

- Prohibition A.1 (no discharges other than as described in the permit): This prohibition is based on the Basin Plan, previous Order, and BPJ.

- Prohibition A.2 (10:1 dilution): This prohibition is based on the Basin Plan. The Basin Plan prohibits discharges of wastewater not receiving a minimum dilution of 10:1 (Chapter 4, Discharge Prohibition No. 1).

- Prohibition A.3 (no bypass or overflow): This prohibition is based on the previous Order and BPJ.

6.	Basis for Effluent Limitations

- Effluent Limitations B.1:

The refinery is classified as a “cracking refinery” as defined by the USEPA in 40 CFR § 419.20.  Therefore, the USEPA Effluent Guidelines and Standards for Petroleum Refining Point Sources (40 CFR § 419 Subpart B) based on Best Available Technology Economically Achievable (BAT), Best Practicable Control Technology (BPT), and/or Best Conventional Pollutant Control technology (BCT), whichever are more stringent, are applicable to the Discharger.

This section contains production-based mass emission limits for the following constituents: Biochemical oxygen demand (BOD), total suspended solids (TSS), chemical oxygen demand (COD), oil & grease, phenolic compounds, ammonia (expressed as nitrogen), sulfide, and total and hexavalent chromium based on 40 CFR § 419 Subpart B.  The application of these guidelines and standards is based on production rates at the refinery.  In calculating currently applicable effluent limitations, Board staff used annual facility production rate from 2003.  A detailed description of the methodology and data used to calculate the technology-based effluent limitations is included in Attachment 1.

The limits for settleable solids are based on existing limits and the Basin Plan, and the concentration limits for oil and grease are based on existing limits and BPJ.  The facility’s ability to comply with all of the limits in B.1 has been demonstrated by existing plant performance.

- Effluent Limitation B.2:

Concentration limits for pollutants contained in storm water and ballast water are based on existing limits, which were developed from the requirements in 40 CFR Part 419.22(e)(2), 419.23(f)(2), and 419.22(c).  The Order retains the requirement that the Discharger record storm water and ballast flow on a daily basis and report daily maximum and monthly average flows.  These flows are then used along with the above concentration limits to calculate the mass allowances that are added to the mass limits included in B.1.

- Effluent Limitation B.3 - Whole Effluent Acute Toxicity:  The Basin Plan specifies a narrative objective for toxicity, requiring that all waters shall be maintained free of toxic substances in concentrations that are lethal to or produce other detrimental response on aquatic organisms.  Detrimental response includes but is not limited to decreased growth rate, decreased reproductive success of resident or indicator species, and/or significant alternations in population, community ecology, or receiving water biota.  These effluent toxicity limits are necessary to ensure that this objective is protected.  The acute toxicity limit is consistent with the previous permit and is based on the Basin Plan Table 4-2, page 4-69.

- Effluent Limitation B.4 - Chronic Toxicity:  The chronic toxicity limit is consistent with the previous permit and is based on the Basin Plan’s narrative toxicity definition on page 3-4.

- Effluent Limitation B.5 - Toxic Substances:

1.	Reasonable Potential Analysis (RPA):

- 40 CFR 122.44(d)(1)(i) specifies that permits are required to include WQBELs for all pollutants “which the Director determines are or may be discharged at a level which will cause, have the reasonable potential to cause, or contribute to an excursion above any State water quality standard”.  Thus, the fundamental step in determining whether or not a WQBEL is required is to assess a pollutant’s reasonable potential of excursion of its applicable WQO or WQC.  The following section describes the RPA methodology and the results of such an analysis for the pollutants identified in the Basin Plan and the CTR.

- i)	WQOs and WQC:  The RPA involves the comparison of effluent data with appropriate WQOs including narrative toxicity objectives in the Basin Plan, applicable WQC in the CTR/NTR, and USEPA’s 1986 Quality Criteria for Water.  The Basin Plan objectives and CTR criteria are shown in Attachment 2 of this Fact Sheet.

- ii)	Methodology:  The RPA is conducted using the method and procedures prescribed in Section 1.3 of the SIP, and guidance in the USEPA TSD for pollutants not subject to the SIP.  Board staff have analyzed the effluent and background data and the nature of facility operations to determine if the discharge has reasonable potential to cause or contribute to exceedances of applicable WQOs or WQC.  Attachment 2 of this Fact Sheet shows the step-wise process.

  - Effluent and background data:  The RPA is based on effluent data collected by the Discharger from January 2001 through July 2004 (see Attachment 2 of this Fact Sheet).  Water quality data collected from San Francisco Bay at the Yerba Buena Island monitoring station through the RMP in 1993 to 2001 were reviewed to determine the maximum observed background values.  The RMP station at Yerba Buena Island located in the Central Bay has been sampled for most of the inorganic and some of the organic toxic pollutants; however, not all the constituents listed in the CTR were analyzed by the RMP during this time.  On May 15, 2003, a group of several San Francisco Bay Region dischargers (known as the Bay Area Clean Water Agencies, or BACWA) submitted a collaborative receiving water study, entitled the San Francisco Bay Ambient Water Monitoring Interim Report.  This study summarizes the monitoring results from sampling events in 2002 and 2003 for the remaining priority pollutants not monitored by the RMP.  The RPA was conducted and the WQBELs were calculated using RMP data from 1993 through 2001 for inorganics and organics at the Yerba Buena Island, and additional data from the BACWA Ambient Water Monitoring Interim Report for the Yerba Buena Island RMP station.

- iv)	RPA determination: The RPA results are shown below in Table 3 and Attachment 2 of this Fact Sheet.  Pollutants that exhibit RP are copper, lead, mercury, nickel, selenium, thallium, cyanide, dioxin (dioxin-TEQ), and PCBs.

#### Table 3.  Summary of Reasonable Potential Results

| - # in CTR | - PRIORITY POLLUTANTS | - MEC or Minimum DL1 - (g/L) | - Governing WQO/WQC (ug/L) | - Maximum Background - (g/L) | - RPA Results2 |
| --- | --- | --- | --- | --- | --- |
| - 2 | - Arsenic | 10 | 36 | 2.46 | N |
| - 4 | - Cadmium | 0.9 | 1.4 | 0.1268 | N |
| - 5b | - Chromium (VI) | 10 | 11 | 4.4 | N |
| - 6 | - Copper | 20 | 3.7 | 2.45 | Y |
| - 7 | - Lead | 3.5 | 1.2 | 0.8 | Y |
| - 8 | ###### Mercury | 0.04 | 0.025 | 0.0064 | Y |
| - 9 | - Nickel | 87 | 8.3 | 3.7 | Y |
| - 10 | - Selenium | 41 | 5 | 0.39 | Y |
| - 11 | ###### Silver | 0.05 | 1.1 | 0.0683 | N |
| - 12 | - Thallium | 13 | 6.3 | 0.21 | Y |
| - 13 | - Zinc | 26 | 64 | 4.6 | N |
| - 14 | ###### Cyanide | 28 | 1 | NA | Y |
| - 16 | - 2.3.7.8-TCDD | <3.6*E-7 | 1.4xE-08 | <3.5*E-7 | N |
|  | - Dioxin-TEQ | 4.2*E-7 | 1.4E-08 | 7.1*E-8 | Y |
| - 17 | - Acrolein | 5 | 780 | NA | N |
| - 18 | - Acrylonitrile | 2 | 0.66 | NA | N |
| - 19 | - Benzene | 0.5 | 71 | NA | N |
| - 20 | ###### Bromoform | 0.5 | 360 | NA | N |
| - 21 | - Carbon Tetrachloride | 0.5 | 4.4 | NA | N |
| - 22 | - Chlorobenzene | 0.5 | 21000 | NA | N |
| - 23 | - Chlordibromomethane | 0.5 | 34 | NA | N |
| - 24 | - Chloroethane | 0.5 | NA | NA | Uo |
| - 25 | - 2-Chloroethylvinyl Ether | 1 | NA | NA | Uo |
| - 26 | - Chloroform | 1 | NA | NA | Uo |
| - 27 | - Dichlorobromomethane | 0.5 | 46 | NA | N |
| - 28 | - 1,1-Dichloroethane | 0.5 | NA | NA | Uo |
| - 29 | - 1,2-Dichloroethane | 0.5 | 99 | NA | N |
| - 30 | - 1,1-Dichloroethylene | 0.5 | 3.2 | NA | N |
| - 31 | - 1,2-Dichloropropane | 0.5 | 39 | NA | N |
| - 32 | - 1,3-Dichloropropylene | 0.5 | 1700 | NA | N |
| - 33 | - Ethylbenzene | 0.5 | 29000 | NA | N |
| - 34 | - Methyl Bromide | 0.5 | 4000 | NA | N |
| - 35 | - Methyl Chloride | 0.5 | NA | NA | Uo |
| - 36 | - Methylene Chloride | 0.5 | 1600 | NA | N |
| - 37 | - 1,1,2,2-Tetrachloroethane | 0.5 | 11 | NA | N |
| - 38 | - Tetrachloroethylene | 0.5 | 8.85 | NA | N |
| - 39 | - Toluene | 0.5 | 200000 | NA | N |
| - 40 | - 1,2-Trans-Dichloroethylene | 0.5 | 140000 | NA | N |
| - 41 | - 1,1,1-Trichloroethane | 0.5 | NA | NA | Uo |
| - 42 | - 1,1,2-Trichloroethane | 0.5 | 42 | NA | N |
| - 43 | - Trichloroethylene | 0.5 | 81 | NA | N |
| - 44 | - Vinyl Chloride | 0.5 | 525 | NA | N |
| - 45 | - Chlorophenol | 2 | 400 | NA | N |
| - 46 | - 2,4-Dichlorophenol | 1 | 790 | NA | N |
| - 47 | - 2,4-Dimethylphenol | 2 | 2300 | NA | N |
| - 48 | - 2-Methyl-4,6-Dinitrophenol | 5 | 765 | NA | N |
| - 49 | - 2,4-Dinitrophenol | 5 | 14000 | NA | N |
| - 50 | - 2-Nitrophenol | 5 | NA | NA | Uo |
| - 51 | - 4-Nitrophenol | 5 | NA | NA | Uo |
| - 52 | - 3-Methyl-4-Chlorophenol | 1 | NA | NA | Uo |
| - 53 | - Pentachlorophenol | 1 | 7.9 | NA | N |
| - 55 | - 2,4,6-Trichlorophenol | 5 | 6.5 | NA | N |
| - 56 | - Acenaphthene | 0.1 | 2700 | 0.0015 | N |
| - 57 | - Acenaphthylene | 0.1 | NA | 0.00053 | Uo |
| - 58 | - Anthracene | 0.1 | 110000 | 0.005 | N |
| - 59 | - Benzidine | 5 | 0.00054 | NA | N |
| - 60 | - Benzo(a)Anthracene | 0.1 | 0.049 | 0.0053 | N |
| - 61 | - Benzo(a)Pyrene | 0.1 | 0.049 | 0.00029 | N |
| - 62 | - Benzo(b)Fluoranthene | 0.1 | 0.049 | 0.0046 | N |
| - 63 | - Benzo(ghi)Perylene | 0.1 | NA | 0.0027 | Uo |
| - 64 | - Benzo(k)Fluoranthene | 0.05 | 0.049 | 0.0015 | N |
| - 65 | - Bis(2-Chloroethoxy)Methane | 5 | NA | NA | Uo |
| - 66 | - Bis(2-Chloroethyl)Ether | 1 | 1.4 | NA | N |
| - 67 | - Bis(2-Chloroisopropyl)Ether | 2 | 170000 | NA | N |
| - 68 | - Bis(2-Ethylhexyl)Phthalate | 5 | 5.9 | NA | N |
| - 69 | - 4-Bromophenyl Phenyl Ether | 5 | NA | NA | Uo |
| - 70 | - Butylbenzyl Phthalate | 5 | 5200 | NA | N |
| - 71 | - 2-Chloronaphthalene | 5 | 4300 | NA | N |
| - 72 | - 4-Chlorophenyl Phenyl Ether | 5 | NA | NA | Uo |
| - 73 | - Chrysene | 1 | 0.049 | 0.0024 | N |
| - 74 | - Dibenzo(a,h)Anthracene | 1 | 0.049 | 0.00064 | N |
| - 75 | - 1,2 Dichlorobenzene | 0.5 | 17000 | NA | N |
| - 76 | - 1,3 Dichlorobenzene | 0.5 | 2600 | NA | N |
| - 77 | - 1,4 Dichlorobenzene | 0.5 | 2600 | NA | N |
| - 78 | - 3,3-Dichlorobenzidine | 5 | 0.077 | NA | N |
| - 79 | - Diethyl Phthalate | 2 | 120000 | NA | N |
| - 80 | - Dimethyl Phthalate | 2 | 2900000 | NA | N |
| - 81 | - Di-n-Butyl Phthalate | 5 | 12000 | NA | N |
| - 82 | - 2,4-Dinitrotoluene | 5 | 9.1 | NA | N |
| - 83 | - 2,6-Dinitrotoluene | 5 | NA | NA | Uo |
| - 84 | - Di-n-Octyl Phthalate | 5 | NA | NA | Uo |
| - 85 | - 1,2-Diphenylhydrazine | 1 | 0.54 | NA | N |
| - 86 | - Fluoranthene | 0.1 | 370 | 0.011 | N |
| - 87 | - Fluorene | 0.1 | 14000 | 0.00208 | N |
| - 88 | - Hexachlorobenzene | 1 | 0.00077 | 0.0000202 | N |
| - 89 | - Hexachlorobutadiene | 1 | 50 | NA | N |
| - 90 | - Hexachlorocyclopentadiene | 5 | 17000 | NA | N |
| - 91 | - Hexachloroethane | 1 | 8.9 | NA | N |
| - 92 | ###### Indeno(1,2,3-cd) Pyrene | 0.1 | 0.049 | 0.004 | N |
| - 93 | - Isophorone | 1 | 600 | NA | N |
| - 94 | - Naphthalene | 0.1 | NA | 0.0023 | Uo |
| - 95 | - Nitrobenzene | 1 | 1900 | NA | N |
| - 96 | - N-Nitrosodimethylamine | 5 | 8.1 | NA | N |
| - 97 | - N-Nitrosodi-n-Propylamine | 5 | 1.4 | NA | N |
| - 98 | - N-Nitrosodiphenylamine | 1 | 16 | NA | N |
| - 99 | - Phenanthrene | 0.1 | NA | 0.0061 | Uo |
| - 100 | - Pyrene | 0.1 | 11000 | 0.0051 | N |
| - 101 | - 1,2,4-Trichlorobenzene | 5 | NA | NA | Uo |
| - 102 | - Aldrin | 0.01 | 0.00014 | NA | N |
| - 103 | - alpha-BHC | 0.01 | 0.013 | NA | N |
| - 104 | - beta-BHC | 0.01 | 0.046 | NA | N |
| - 105 | - gamma-BHC | 0.01 | 0.063 | NA | N |
| - 106 | - delta-BHC | 0.01 | NA | NA | Uo |
| - 107 | - Chlordane | 0.02 | 0.00059 | 0.00018 | N |
| - 108 | - 4,4’-DDT | 0.01 | 0.00059 | 0.000066 | N |
| - 109 | - 4,4’-DDE | 0.01 | 0.00059 | 0.00069 | N |
| - 110 | - 4,4’-DDD | 0.01 | 0.00084 | 0.000313 | N |
| - 111 | - Dieldrin | 0.01 | 0.00014 | 0.000264 | N |
| - 112 | - alpha-Endosulfan | 0.01 | 0.0087 | 0.000031 | N |
| - 113 | - beta-Endosulfan | 0.01 | 0.0087 | 0.000069 | N |
| - 114 | - Endosulfan Sulfate | 0.01 | 240 | 0.0000819 | N |
| - 115 | - Endrin | 0.01 | 0.0023 | 0.000036 | N |
| - 116 | - Endrin Aldehyde | 0.01 | 0.81 | NA | N |
| - 117 | - Heptachlor | 0.01 | 0.00021 | 0.000019 | N |
| - 118 | - Heptachlor Epoxide | 0.01 | 0.00011 | 0.000094 | N |
| - 119-125 | - PCBs | 0.000148 | 0.00017 | NA | Y |
| - 126 | - Toxaphene | 0.5 | 0.0002 | NA | N |
|  | - Tributyltin | NA | 0.005 | NA | Ub, Ud |

- 1)	Maximum Effluent Concentration (MEC) in bold is the actual detected MEC, otherwise the MEC shown is the minimum detection level.

- NA = Not Available (there is not monitoring data for this constituent).

- 2)	RP =Yes, if either MEC or Background > WQO/WQC.

- RP = No, if (1) both MEC and background < WQO/WQC or (2) no background and all effluent data non-detect, or no background and MEC<WQO/WQC (per WQ 2001-16 Napa Sanitation Remand)

- RP = Ud (undetermined due to lack of effluent monitoring data).

- RP = Uo (undetermined if no objective promulgated).

- RP = Ub (undetermined due to lack of background data)

- .

v)	Pollutants with no Reasonable Potential:  WQBELs are not included in the Order for constituents that do not have Reasonable Potential to cause or contribute to exceedance of applicable WQOs or WQC.  However, monitoring for those pollutants is still required, under the provisions of the Board’s August 6, 2001 Letter.  If concentrations of these constituents are found to have increased significantly, the Discharger will be required to investigate the source(s) of the increase(s).  Remedial measures are required if the increases pose a threat to water quality in the receiving water.

- vi)	Permit reopener:  The permit includes a reopener provision to allow numeric effluent limitations to be added for any constituent that in the future exhibits Reasonable Potential to cause or contribute to exceedance of a WQO or WQC.  This determination, based on monitoring results, will be made by the Board.

- Final Water Quality-Based Effluent Limits:  The final WQBELs were developed for the toxic and priority pollutants that were determined to have reasonable potential to cause or contribute to exceedances of the WQOs or WQC.  Final effluent limitations were calculated based on appropriate WQOs/WQC, background concentrations at the Yerba Buena Island and Richardson Bay RMP Stations, a maximum dilution ratio of 10:1 (for non-bioaccumulative pollutants), and the appropriate procedures specified in Section 1.4 of the SIP or USEPA TSD (See Attachment 3 of this Fact Sheet).  For the purpose of the Proposed Order, final WQBELs refer to all non-interim effluent limitations.  The WQO or WQC used for each pollutant with reasonable potential is indicated in Table 4 below as well as in Attachment 3.

- Table 4. Water Quality Objectives/Criteria for Pollutants with RP

| Pollutant | Chronic WQO/WQC (μg/L) | Acute WQO/WQC (μg/L) | Human Health WQC (μg/L) | Basis of Lowest WQO /WQC Used in RP |
| --- | --- | --- | --- | --- |
| Copper | 3.7 | 5.8 | -- | CTR |
| Lead | 1.2 | 30 | -- | CTR |
| Mercury | 0.025 | 2.1 | 0.051 | BP |
| Nickel | 8.3 | 75 | 4,600 | CTR |
| Selenium | 5 | 20 | -- | NTR |
| Thallium | -- | -- | 6.3 | CTR |
| Cyanide | 1 | 1 | 22,000 | NTR |
| TCDD TEQ | -- | -- | 1.410-8 | BP |
| PCBs (sum) | 0.014 | -- | 0.00017 | CTR |

- Feasibility Evaluation:  The Discharger submitted infeasibility to comply reports on February 11, 2005, for selenium, cyanide, and dioxin (Dioxin TEQ).  For constituents that Board staff could perform a meaningful statistical analysis (i.e., selenium), it used self-monitoring data from January 2001- July 2004 to compare the mean, 95th percentile, and 99th percentile with the long-term average (LTA), AMEL, and MDEL to confirm if it is feasible for the Discharger to comply with WQBELs.  If the LTA, AMEL, and MDEL all exceed the mean, 95th percentile, and 99th percentile, it is feasible for the Discharger to comply with WQBELs.  Table 5 below shows these comparisons in g/L

- Table 5.  Summary of Feasibility Analysis

| Constituent | - Median / LTA | - 95th / AMEL | - 99th / MDEL | - Feasible to Comply |
| --- | --- | --- | --- | --- |
| - Selenium1 | - 10 > 2.9 | - 20 > 4.2 | - 29 > 7.8 | No |

- 1  Selenium data does not fit a normal distribution.  Therefore, the percentiles shown are based on data representing the whole population as opposed to a subset of the population.

- For PCBs compliance with the final WQBELs cannot be determined at this time as the minimum levels (MLs) are higher than the final calculated WQBELs.   For cyanide and dioxins and furans compounds it was not possible to perform a robust statistical analysis due to the number of nondetects.  For cyanide, the Board determined that it infeasible for the Discharger to comply with final WQBELs since the maximum effluent concentration exceeds the AMEL.  For dioxin-TEQ, the Board used the numeric limits calculated by the SIP methodology as guidance for determining if the Discharger can comply with numeric WQBELs.  Even though the SIP does not apply to dioxin-TEQ, this comparison is reasonable since the methodology for calculating final WQBELs in the SIP is in part based on the TSD.  In this case, the Board determined that it is infeasible for the Discharger to comply with WQBELs for Dioxin TEQ since the maximum effluent concentration exceeds the AMEL.

- Table 6 below summarizes the calculated WQBELs, and the feasibility to comply analysis for all pollutants with effluent limitations. The WQBELs calculation is attached as Attachment 3 of this Fact Sheet.

- Table 6.  Final WQBELs and Feasibility to Comply

| - Pollutant | MDEL g/L | AMEL g/L | - Feasible to Comply? |
| --- | --- | --- | --- |
| Copper | - 24 | - 13 | - Yes |
| Lead | - 7.8 | - 3.7 | - Yes |
| Mercury | - 0.044 | - 0.019 | - Yes |
| Nickel | - 77 | - 42 | Yes |
| Selenium | - 7.8 | - 4.2 | No |
| Cyanide | - 6.4 | - 3.2 | No |
| - Thallium | - 120 | - 61 | Yes |
| TCDD TEQ | - 0.000000028 | - 0.000000014 | No |
| PCBs (sum) | - 0.00034 | - 0.00017 | No |

- Interim Concentration Limits and Compliance Schedules:  Interim effluent limitations were derived for those constituents (selenium, cyanide, dioxin TEQ, and PCBs) for which the Discharger has shown infeasibility of complying with the respective final limitations and has demonstrated that compliance schedules are justified based on the Discharger’s source control and pollution minimization efforts in the past, and continued efforts in the present and future.  The interim effluent concentration limitations for selenium, cyanide, and TCDD TEQ are based on the previous permit effluent limitation.  For PCBs there were insufficient effluent data (i.e., detected values) to develop statistically valid performance-based interim limits.  Therefore, for PCBs the interim effluent concentration limits are based on the minimum levels contained in the SIP.  These interim limits are discussed in more detail below.

- This permit establishes compliance schedules until May 17, 2010, for PCBs, until April 27, 2010 for cyanide and selenium, and until July 1, 2010 for TCDD-TEQ.  Since these compliance schedules are within the effective date of the permit, this Order includes final WQBELs.  Attachment 4 provides the general basis for the above compliance schedules.

- Selenium - Further Discussion and Rationale for Interim Effluent Limitation:  An interim effluent limitation is required for selenium since the Discharger has demonstrated, and the Board has verified that the final effluent limitations calculated according to the SIP (AMEL of 4.2 μg/L and MDEL of 7.8 μg/L) will be infeasible to meet.  Self-monitoring data from January 2001- July 2004 indicate that effluent selenium concentrations ranged from <1 μg/L to 41 μg/L (180 samples).  Since selenium data did not fit a normal distribution, it was not possible to perform a meaningful statistical evaluation of current treatment performance.  Therefore, interim limits for selenium are the same as the limits included in the previous Order and are based on a Settlement Agreement between the Western States Petroleum Association (WSPA) and the Board.  The previous permit contained a daily maximum concentration limit of 50 g/L, and an annual average mass emission limit of 1.0 lbs/day.  These interim limits will remain in effect until April 27, 2010, or until the Board amends the limitation based on additional data or a TMDL.

- Cyanide - Further Discussion and Rationale for Interim Effluent Limitation:  An interim effluent limitation is required for cyanide since the Discharger has demonstrated, and the Board has verified that the final effluent limitations calculated according to the SIP (AMEL of 3.2 μg/L and MDEL of 6.4 μg/L) will be infeasible to meet.  Self-monitoring data from January 2001- July 2004 indicate that effluent cyanide concentrations ranged from < 3 μg/L to 28 μg/L (177 samples).  Board staff could not perform a meaningful statistical analysis on these data because it contained too many nondetects.  Therefore, the previous permit limitation of 25 µg/L is established in this Order as the interim limitation, and will remain in effect until April 27, 2010, or until the Board amends the limitation based on additional data or SSOs

- PCBs (sum) - Further Discussion and Rationale for Interim Effluent Limitations:  Interim effluent limitations are required for PCBs because compliance with the final WQBELs (AMEL of 0.00017 μg/L and MDEL of 0.00034 μg/L) cannot be determined at this time as the MLs are higher than the final calculated WQBELs.  The Interim limitation is therefore established at the respective MLs.  The interim limitations are 0.5 μg/L for each PCB. This interim limits shall remain in effect until May 17, 2010, or until the Board amends the limitation based on WLAs in the TMDL for PCBs.

- Dioxin-TEQ – Further Discussion and Rationale for Interim Effluent Limitation:  While the SIP does not apply to dioxin-TEQ, it is reasonable to use final WQBELs calculated in accordance with the SIP, as guidance for determining if it is feasible for the Discharger to comply with final limits.  For dioxin-TEQ, an interim effluent limitation is required since the Discharger cannot immediately comply with an AMEL of 0.014 pg/L, or MDEL of 0.028 pg/L.  Statistical analyses indicate that the 99.87th percentile of dioxin-TEQ from 2000 to 2004 is 0.82 pg/L (based on the five congeners regularly detected, which include: 1,2,3,4,6,7,8 HpCDD, OCDD, 1,2,3,4,6,7,8 HpCDF, 1,2,3,4,7,8,9 HpCDF, and OCDF).  The previous permit included an interim limitation of 0.65 pg/L as a monthly average, which is more stringent than the 99.87th percentile of the recent effluent data.  Therefore, the previous permit limitation of 0.65 pg/L (for the five regularly detected congeners) is established in this Order as the interim limitation, expressed as a monthly average limitation.  This interim limitation shall remain in effect until July 1, 2010, at which time the Discharger shall comply with the WLA in a TMDL, or no net loading if there is no TMDL.  This approach is consistent with CBE v. State Water Resources Control Board, et al., 109 Cal. App.4th 1089 (2003), in which the court ruled that final WQBELs are not required to be numeric.

- Effluent Limitation B.6 – Selenium Interim Mass Limit:  As mentioned above, this Order includes an interim mass emission limit for selenium of 1.0 lbs/day.  This limitation is based on a Settlement Agreement between WSPA and the Board.

- Effluent Limitation B.7 – Total Coliform Organisms Limit:  The purpose of this effluent limitation is to ensure adequate disinfection of the discharge in order to protect beneficial uses of the receiving waters.  Effluent limits are based on water quality objectives for bacteriological parameters for receiving water beneficial uses. Water quality objectives are given in terms of parameters, which serve as surrogates for pathogenic organisms. The traditional parameter for this purpose is coliform bacteria, either as total coliform or as fecal coliform. The Basin Plan’s Table 4-2 (pg. 4–69) and its footnotes allow fecal coliform limitations to be substituted for total coliform limitations provided that the Discharger conclusively demonstrates “through a program approved by the Board that such substitution will not result in unacceptable adverse impacts on the beneficial uses of the receiving waters.”  Until the Discharger undertakes a bacteriological study to conclusively demonstrate that substitution of fecal coliform for total coliform limits would be protective of the beneficial uses of the receiving water, the coliform effluent limitation will continue to be expressed as total coliform. Total coliform limits are:

- The moving median value for the Most Probable Number (MPN) of total coliform bacteria in five (5) consecutive samples shall not exceed 240 MPN/100 ml; and,

- Any single sample shall not exceed 10,000 MPN/100 ml.

- Effluent Limitation B.8 – Residual Chlorine Limit:  This limit is a technology-based limit representative of, and intended to ensure, adequate and reliable secondary level wastewater treatment. This limit is based on the Basin Plan (Chapter 4, pg 4-8, and Table 4-2, at pg 4-69).

- Effluent Limitation B.9 – pH Limit:  This effluent limit is a standard secondary treatment requirement and is unchanged from the existing permit. The limit is based on the Basin Plan (Chapter 4, Table 4-2), which is derived from federal requirements (40 CFR 133.102). This is an existing permit effluent limitation and compliance has been demonstrated by existing plant performance.

- Effluent Limitation B.10 – Stormwater Limits at Outfalls E-003, E-004, and E-005:  These limits are based on based on 40 CFR § 419 Subpart B.

- Effluent Limitation B.11 – Credit for Recycled Water Use:  This credit is to encourage the Discharger to use reclaimed water provided it will not cause acute toxicity to aquatic life.

7.	Basis for Receiving Water Limitations

a)	Receiving water limitations C.1, C.2, and C.3 (conditions to be avoided): These limits are based on the previous Order and the narrative/numerical objectives contained in Chapter 3 of the Basin Plan, page 3-2 – 3-5.

- Receiving water limitation C.4 (compliance with State Law): This requirement is in the previous permit, requires compliance with Federal and State law, and is self-explanatory.

8.	Basis for Self-Monitoring Requirements

The SMP includes monitoring at the outfalls for conventional, non-conventional, and toxic pollutants, and acute and chronic toxicity.  For a number of constituents that the Board has granted interim limits (selenium, and cyanide), this Order contains weekly monitoring.  The exceptions to this requirement are dioxin TEQ, and PCBs.  For dioxins, due to the considerable costs, high detection limits, and ambient nature of the source, this Order requires quarterly monitoring.  For PCBs due to the considerable costs and the non-detects the Discharger has found, this Order requires twice yearly monitoring, which is also consistent with the SIP.  Further, this Order requires monthly monitoring of mercury, copper, nickel, lead, and thallium to demonstrate compliance with final effluent limitations.  In lieu of near field discharge specific ambient monitoring, it is acceptable that the Discharger participate in collaborative receiving water monitoring with other dischargers under the provisions of the August 6, 2001 letter, and the RMP.

9.	Basis for Provisions

- Provisions D.1. (Permit Compliance and Rescission of Previous Permit): Time of compliance is based on 40 CFR 122. The basis of this Order superceding and rescinding the previous permit is 40 CFR 122.46.

- Provision D.2 (Dioxins and Furans Accelerated Monitoring):  This provision requires the Discharger to accelerate monitoring and submit a technical report if it detects dioxin and furan congeners that are not regulated under this Order.  The purpose of this provision is to ensure that the Discharger will implement corrective measures if its performance declines for dioxin TEQ.

- Provision D.3 (Mass and Concentration Credits).  This provision is necessary to protect beneficial uses identified in the Basin Plan (the Discharger must ensure that granting it pollutant credits for the use of recycled water will not cause acute toxicity).

- Provision D.4. (Storm Water Pollution Prevention Plan and Annual Report): This provision, is based on and consistent with Basin Plan objectives, statewide storm water requirements for industrial facilities, and applicable USEPA regulations.

- Provision D.5 (Effluent Characterization for Selected Constituents):  This provision establishes monitoring requirements as stated in the Board’s August 6, 2001 Letter under Effluent Monitoring for major dischargers.  Interim and final reports shall be submitted to the Board in accordance with the schedule specified in the August 6, 2001 Letter.  This provision is based on the Basin Plan and the SIP.

- Provision D.6 (Receiving Water Monitoring).  This provision, which requires the Discharger to continue to conduct receiving water monitoring is based on the previous Order and the Basin Plan.

- Provision D.7 (Pollutant Prevention and Minimization Program):  This provision is based on the Basin Plan, page 4-25 – 4-28, and the SIP, Section 2.1, Compliance Schedules.

- Provision D.8 (Whole Effluent Acute Toxicity):  This provision establishes conditions by which compliance with permit effluent limits for acute toxicity will be demonstrated.  Conditions include the use of flow through bioassays with rainbow trout, in accordance with Methods for Measuring the Acute Toxicity of Effluents and Receiving Water to Freshwater and Marine Organisms, 5th Edition.  These conditions are based on the effluent limits for acute toxicity given in the Basin Plan, Chapter 4, and BPJ.

- Provision D.9 (Whole Effluent Chronic Toxicity):  This provision establishes conditions and protocol by which compliance with the Basin Plan narrative WQO for toxicity will be demonstrated.  Conditions include required monitoring and evaluation of the effluent for chronic toxicity and numerical values for chronic toxicity evaluation to be used as 'triggers' for initiating accelerated monitoring and toxicity reduction evaluation(s).  These conditions apply to the discharges to San Francisco Bay and the numerical values for chronic toxicity evaluation are based on a minimum initial dilution ratio of 10:1.  This provision also requires the Discharger to conduct a screening phase monitoring requirement and implement toxicity identification and reduction evaluations when there is consistent chronic toxicity in the discharge.  New testing species and/or test methodology may be available before the next permit renewal.  Characteristics, and thus toxicity, of the process wastewater may also have been changed during the life of the permit.  This screening phase monitoring is important to help determine which test species is most sensitive to the toxicity of the effluent for future compliance monitoring.  The proposed conditions in the draft permit for chronic toxicity are based on the Basin Plan narrative WQO for toxicity, Basin Plan effluent limitations for chronic toxicity (Basin Plan, Chapter 4), U.S. EPA and SWRCB Task Force guidance, applicable federal regulations [40 CFR 122.44(d)(1)(v)], and BPJ.

- Provision D.10 (Contingency Plan Update): This provision is based on the requirements stipulated in Board Resolution No. 74-10.

- Provision D.11 (Dilution Study):  This provision is necessary to ensure that the Discharger’s deepwater diffuser achieves a minimum initial dilution of at least 10:1, as required by the Basin Plan.

- Provision D.12 (Collection System Maintenance):  This provision, based on the Basin Plan, is necessary to document that the Discharger implements appropriate operation and maintenance of its collection system to avoid spills to the maximum extent feasible.

- Provision D.13 (Actions for Compliance Schedule Pollutants):  This provision, based on the SIP, requires that the Discharger participate in the development of a TMDL or SSO for cyanide, selenium, PCBs, and dioxin-TEQ.  In accordance with Section 2.1 of the SIP, and Chapter 4 of the Basin Plan, for the Board to authorize compliance schedules in a permit the Discharger must, in part, propose a schedule for additional or future source control measures, pollution minimization actions, or waste treatment.  In the case of cyanide, selenium, PCBs, and dioxin-TEQ, the Discharger indicates that it proposes to achieve compliance with final limits through the SSO or TMDL process.  Therefore, annual reporting on Discharger’s efforts to facilitate SSO or TMDL development along with implementation of its Pollution Minimization Plan (required by Provision D.7) satisfy the intent of Section 2.1 of the SIP.  In the event TMDL(s) or SSO(s) are not developed for selenium, cyanide, or PCBs by July 1, 2009, this provision also requires the Discharger to submit a schedule that documents how it will further reduce pollutant concentrations to ensure compliance with the final limits.  Additionally, in the absence of a TMDL for dioxin-TEQ, this provision requires that the Discharger propose a mass offset program, by no later than July 1, 2009, to achieve no net loading by July 1, 2010.

- Provision D.14 (Self-Monitoring Program):  The Discharger is required to conduct monitoring of the permitted discharges in order to evaluate compliance with permit conditions.  Monitoring requirements are contained in the Self Monitoring Program (SMP) of the Permit.  This provision requires compliance with the SMP, and is based on 40 CFR 122.44(i), 122.62, 122.63 and 124.5.  The SMP is a standard requirement in almost all NPDES permits issued by the Board, including this Order.  It contains definitions of terms, specifies general sampling and analytical protocols, and sets out requirements for reporting of spills, violations, and routine monitoring data in accordance with NPDES regulations, the California Water Code, and Board’s policies.  The SMP also contains a sampling program specific for the facility.  It defines the sampling stations and frequency, the pollutants to be monitored, and additional reporting requirements.  Pollutants to be monitored include all parameters for which effluent limitations are specified.  Monitoring for additional constituents, for which no effluent limitations are established, is also required to provide data for future completion of RPAs for them.

- Provision D.15  (Standard Provisions and Reporting Requirements):  The purpose of this provision is to require compliance with the standard provisions and reporting requirements given in this Board's document titled Standard Provisions and Reporting Requirements for NPDES Surface Water Discharge Permits, August 1993 (the Standard Provisions), or any amendments thereafter.  That document is incorporated in the permit as an attachment to it. Where provisions or reporting requirements specified in the permit are different from equivalent or related provisions or reporting requirements given in the Standard Provisions, the permit specifications shall apply.  The standard provisions and reporting requirements given in the above document are based on various state and federal regulations with specific references cited therein.

- Provision D.16 (Change in Control or Ownership): This provision is based on 40 CFR 122.61.

- Provision D.17 (Permit Reopener): This provision is based on 40 CFR 123.

- Provision D.18 (Permit Expiration and Reapplication):  This provision is based on 40 CFR 122.46 (a).

V.	WASTE DISCHARGE REQUIREMENT APPEALS

Any person may petition the State Water Resources Control Board to review the decision of the Board regarding the Waste Discharge Requirements.  A petition must be made within 30 days of the Board public hearing.

VI.  ATTACHMENTS

Attachment 1:  Calculations for Production-Based Effluent Limitations

Attachment 2:  RPA Results for Priority Pollutants at E-001

Attachment 3:  Calculation of Final WQBELs at E-001

Attachment 4:  General Basis for Compliance Schedules