## IntroTab
State Water Resources Control Board
Cost-Benefit Analysis Model: Water Loss Performance Standards
Version 2.0: April 13, 2020
The primary objective of this model is to calculate water loss performance standards for urban retail water suppliers in California pursuant to Water Code 10608.34. This spreadsheet was developed to conduct a cost-benefit analysis for any additional actions anticipated to be taken by urban retail water suppliers to reduce water loss from leakage to an economically feasible levels. The model uses data from water loss audit reports submitted annually in California from 2016 to 2019, industry and literature based estimates for costs and benefits associated with water loss control actions that are anticipated to be accrued. The model calculates water loss performance standards based on economically feasible water loss reductions by 2028 from active leak detection and repair only due to availability of data.
Spreadsheet tabs
Inputs: All inputs to the model are summarized here. Any changes to inputs can be made in this tab. Inputs are color-coded to show which cells are from water loss audits, user-inputs, calculated,or determined by the State Water Board.
Calculations: This tab uses the inputs from the input tab to calculate the system-specific background, reported and unreported leakage, an economic intervention frequency for leakage surveying, and the associated cost-benefit analysis.
Output: This tab summarizes the economic level of leakage for each year beginning 2022, with a view to determine the economically feasible level of leakage for 2028, and the Benefit-Cost ratio across the time horizon, including the compliance period.
Equations: This tab provides all equations with unit conversions in detail.
CollectedData_References: This tab summarizes all data that the Water Board used to develop the model and the respective references.
For questions, please contact:
Kartiki Naik at kartiki.naik@waterboards.ca.gov or 1-916-319-9468
Max Gomberg at max.gomberg@waterboards.ca.gov

## Inputs
Inputs to model to determine economic and cost-effective water loss performance standards
Color code for cells
From water loss audit reports provided by urban retail water suppliers |  |  | Superscripted numbers denote a numbered reference in the "CollectedData_References" tab.
Default inputs or supplier-specific inputs if known
Water Board determined input values
From water loss audit reports submitted by urban retail water suppliers as per Water Code 10608.34 to the California Department of Water Resources1
Three-year average real loss for supplier | 10171 | acre-feet per year | Three-year average current real loss, From water loss audits submitted annually (2016 to 2019)
Total length of mains | 3347 | miles | Three-year average, From water loss audits submitted annually (2016 to 2019)
Number of service connections | 284399 | # | Three-year average, From water loss audits submitted annually (2016 to 2019)
Variable production cost of water | 1282 | $ per acre-feet | Three-year average, From water loss audits submitted annually (2016 to 2019)
Average operating pressure | 95 | psi | Three-year average, From water loss audits submitted annually (2016 to 2019)
Default values determined by Water Board that can be replaced by supplier-specific inputs provided by urban retail water supplier with supporting supplier records
This model determines the background leakage (undetectable by active leak detection and repair), reported leakage (visible) and unreported leakage (hidden but detectable by active leak detection equipment) for the distribution system. These components are calculated based on the length of distribution mains and number of connections owned by the supplier and the average operational pressure. The model calculates the unreported leakage component, which is can be reduced by active leak detection and repair by surveying the distribution system using specialized equipment. It uses established equations and estimates for typical flow rates and number of leaks for each type of leakage (background, reported and unreported) as applicable from the AWWA M36 manual (2016)2, the Water Research Foundation 4372a Report (2015)3, and a publication by AWWA's Water Loss Control Committee4 on the IWA International Methodology for determining these leakage components. The following default inputs (green cells) are based on these references, and can be adjusted by the supplier if the supplier has supplier-specific data based on field measurements and analysis.
Note: For a summary of the data collected by the Water Board, see 'CollectedData_References' tab
Rate of rise of leakage, if known |  | gallons per connection per day per year | The cell here is blank for possible supplier input. A default rise of 4 gallons per connection per day per year, adapted from the EU Reference document: Good Practices on Leakage Management (Main Report)5 is used. To check applicability to North American water systems, references of a California and a Tenessee system are used from the Water Research foundation Report 4372a, 20153, which had rates of rise of leakage of 3 and 3.9 gallons per connection per day per year. As per the EU Report, this value is very low as compared to water systems in the U.K., and is selected as a representative rate for California systems, based on field experience of technical experts. The low rate of rise of leakage means that the model relies more on the backlog of leakage (represented by the real loss reported by suppliers) than the default value for rate of rise in leakage.
Infrastructure Condition Factor (ICF) | 1 |  | For background leakage calculation; From AWWA M36 Manual, Fourth Edition (2016)2 (Table 3-22)
Background leakage, if known |  | acre-feet per year | The cell here is blank for possible supplier input. By default, the 'Calculations' tab calculates the background leakage volume, using Equation (7-5), AWWA M36 Manual, 20162
Average time between reporting of and repair of reported bursts | 3 | days | For reported leakage calculation From AWWA M36 Manual, Fourth Edition (2016)2 (Table 3-22), AWWA Water Loss Control Committee Report: Applying worldwide BMPs in water loss control, 20036 (Table 4), and Lambert, 19994 (Table 3)
Number of reported bursts within past year | 0.2 | bursts per mile per year
Estimated average flow rate for reported leaks | 50 | gallons per minute per burst
If supplier has information on unreported leakage, enter as volume below, or enter average flow rates and number of leaks per mile below, based on prior leak detection surveys.
Unreported leakage, if known |  | acre-feet per year | The cell here is blank for possible supplier input. By default, the 'Calculations' tab calculates the unreported leakage volume based on the calculated background and reported leakage.
OR
Estimated average flow rate for unreported leaks | 25 | gallons per minute per leak | For unreported leakage calculation From AWWA M36 Manual, Fourth Edition (2016)2 (Table 3-22), AWWA Water Loss Control Committee Report: Applying worldwide BMPs in water loss control, 20036 (Table 4), and Lambert, 19994 (Table 3)
AND Estimated average number of unreported leaks |  | leaks per mile per year
Average leak detection survey frequency |  | miles per month | Average survey rate based on communications with vendors, and water suppliers. The cell here is blank for possible supplier input. By default, the 'Calculations' tab calculates the average survey frequency for the following system sizes based on the following survey frequencies:6000 miles and above - 130 miles per month; 4000 miles and above - 114 miles per month (Based on EBMUD's current practices, this is determined as a reasonable and achievable survey frequency for the two largest systems, EBMUD and LADWP); 1000 miles and above: Once in three years; 500 miles and above: Once in 2.5 years; Below 500 miles: Once every 2 years. Refer to the 'CollectedData_References' for data establishing these survey rates.
Surveying costs per mile (including upfront and maintenance costs) | 605 | $ per mile | For calculation of intervention costs for reducing unreported leakage, includes surveying and pinpointing (see row 34 for repair costs)
Efficiency of leak detection equipment | 70% | in percent | Represents the average percentage of actual leaks found on excavation v/s the total detected leaks including false positives expected to be pinpointed by leak detection equipment over the time horizon. As per vendor and water supplier knowledge based on field implementation, this efficiency increases with higher training and experience. This parameter adds the cost of additional excavation associated with locating leaks pinpointed by false positives, without the benefits of water loss reduction, to the overall costs of leak detection and repair.
Average leak repair costs | 5946 | $ per mile | Based on data from Irvine Ranch Water District and PGE Report ET13PGE1451: Water System Leak Identification and Control Field Evaluation7
Marginal avoided cost of water | 1126 | $ per acre-feet | Based on the average cost of alternative suplies for stormwater capture, brackish desalination, nonpotable reuse, indirect potable reuse, based on a Pacific Institute study, suported by an NRDC issue brief (2016)8,9 and imported water costs as per historical rates from the Metropolitan Water District
Note: For a summary of the data collected by the Water BoardSee 'CollectedData_References' tab
Input values determined by Water Board for the model
The model conducts a cost-benefit analysis to evaluate cost-effectiveness between reducing real loss and maintaining current real loss. The time horizon for the cost-benefit analysis is 30 years, which includes the lifecycles of water loss control actions and covers costs and benefits occuring beyond the compliance timeline of the regulation. The benefits associated with real loss reduction depend on the rise of price water, discount rate, value of avoided cost of water (previous section) and the volume of real loss reduced. The rise in price of water and discount rate are determined by Water Board staff and are fixed for the model. Additional details are presented in the 'CollectedData_References' tab.
Nominal discount rate | 3.5% | percent | State Water Board staff proposal based on stakeholder input
Average annual rise in price of water | 5.6% | in percent | Based on Historical data from Metropolitan Water District: 2008 - 2018 - Converted to real prices in 2019$
Assumed effective timeline for lifecycle benefit-cost analysis | 30 | years | Anticipated timeline as lifecycle for accruing costs and benefits associated with real loss reduction.This timeline aims to cover the lifecycle of active leak detection and repair implementation, and associated leakage reduction or maintenance.

## Calculations
Color code for cells |  |  | Notes
Inputs from water loss audit reports |  |  | Calculations to determine unreported leakage volume are below.
Default inputs or supplier-specific inputs |  |  | The benefit-cost analysis and standard calculation begin at row 54 of this tab.
Water Board determined input values |  |  | The 'Output' tab provides the Cost-Benefit ratios and calculated standards
Calculated values |  |  | Detailed equations are available in the 'Equations' tab.
Parameter | Value | Unit of Measurement | Explanation/Formula
System leakage characteristics
Three-year average real loss for supplier | 10171 | acre-feet per year | Three-year average, From water loss audits submitted annually (2016 to 2019)
Total length of mains | 3347 | miles | Three-year average, From water loss audits submitted annually (2016 to 2019)
Rate of rise of leakage | 1274.2712 | acre-feet per year | Based on Table 6 of EU Reference document: Good Practices on Leakage Management (Main Report)5, and Water Research foundation Report 4372a, (2015)3, if supplier does not have system-specific estimate.
Average operating pressure | 95 | psi | Three-year average, From water loss audits submitted annually (2016 to 2019)
Number of service connections | 284399 | # | Three-year average, From water loss audits submitted annually (2016 to 2019)
Calculation of leakage components - Background, Reported and Unreported leakage
This section calculates the different components associated with the unavoidable annual real loss: Background, reported and unreported leakage. It estimates the fraction of unreported leakage for the system from this calculation. The background (undetectable leakage) is calculated first using an established formula also used in the Leakage Component Analysis Model (WRF) 4372a, 2014. The Reported leakage is calculated based on typical flow rates and break rates based on AWWA Water Loss Control Committee Report, 2003. The unreported leakage is calculated as the remaining leakage. The calculation is based on typical flow rates and number of leaks per mile associated with these different types of leakages from the AWWA M36 manual.
Infrastructure Condition Factor (ICF) | 1 |  | Default=1, Adapted from Water Research Foundation 4372a Leakage Component Analysis Model3
Total background leakage | 5214.7955 | acre-feet per year | Equation (7-5), AWWA M36 Manual, 20162 or supplier input
Estimated number of reported leaks | 0.2 | bursts per mile per year | From AWWA M36 Manual, Fourth Edition (2016)2 (Table 3-22); 0.2 breaks per mile per year at 50 gallons per minute over 3 days' duration
Average time between reporting and repair of reported leaks | 3 | days
Estimated average flow rate for reported leaks | 50 | gallons per minute per burst
Reported leakage | 602.2072 | acre-feet per year | Average flowrate for reported leakage x Number of reported leaks per mile x Total length of mains
Unreported leakage | 4353.9973 | acre-feet per year | Total leakage - (background leakage + reported leakage)
Calculation of anticipated number of unreported leaks for the system
Unreported leakage fraction for the system | 0.42808 | fraction of total annual leakage | Unreported leakage / (Unreported+Reported+Background) leakages from UARL
Estimated average flow rate for unreported leaks | 25 | gallons per minute per leak per hour | Adapted from AWWA M36 Manual, Fourth Edition (2016)2 (Table 3-22); 0.01 breaks per mile per year at 25 gallons per minute
Average annual flow rate per unreported leak | 40.3252 | acre-feet per year per leak | Typical flow for detected leaks = 25 gallons per minute, AWWA M36 Manual, Fourth Edition (2016)2 (Table 3-22)
Number of unreported leaks | 0.032259 | leaks per mile of main | Detectable leakage / Total length of mains / Assumed average flow rate for unreported leaks
Value of water for supplier
Nominal discount rate | 3.5% | percent | State Water Board staff proposal based on stakeholder input
Variable production cost of water | 1282 | $ per acre-feet | Three-year average, From water loss audits submitted annually (2016 to 2019)
Avoided cost of alternative supplies | 1126 | $/acre-feet | User-reported or default value, used to value the volume of real loss reduced
Average annual rise in price of water | 5.6% | percent | Historical data from Metropolitan Water District: 2008 - 2018
Assumed effective timeline | 30 | years | Expected timeline for costs and benefits associated with real loss reduction
Active leak detection and repair costs (Based on data collected by State Water Board staff or data provided by supplier,supported by supplier records) Note: See 'CollectedData_References' tab for a summary of the data collected by the Water Board
Leak surveying and pinpointing costs per mile | 605 | $ per mile of mains surveyed | Based on data from vendors and water suppliers
Efficiency of leak detection equipment | 70% | in percent | Represents the average percentage of actual leaks found on excavation v/s the total detected leaks, including false positives expected to be pinpointed by leak detection equipment over the time horizon. As per vendor and water supplier knowledge based on field implementation, this efficiency increases with higher training and experience. This parameter adds the cost of additional excavation associated with locating leaks pinpointed by false positives, without the benefits of water loss reduction, to the overall costs of leak detection and repair.
Repair costs per mile | 5946 | $ per leak repaired | Based on data from Irvine Ranch Water District and PGE Report ET13PGE1451: Water System Leak Identification and Control Field Evaluation7
Estimate time taken to survey full distribution system | 36 | months | This represents an average frequency for leak detection surveying based on the miles of pipe in a water distribution system. This average frequency is derived from vendor and water supplier estimates, and used as a basis to calculate the economically recoverable leakage. Complying with this survey frequency is not a regulatory requirement.
Tracking leakage reduction across time horizon (Assumptions: 1. The system is divided into parts based on how many parts can be reasonably surveyed in each time step. 2. Uniform leakage throughout system) This method is used such that the model can consider cases of partial distribution system surveys. This is a simplifying method for the calculations, and calculates benefit and cost after each month.
Time step | 0.083333 | year | Time step of one month to allow for incremental and partial surveys
Average number of miles surveyed in each month | 92.9722 | miles | Total length of mains / Economic Intervention frequency
Number of parts of system to be surveyed in a full survey | 36 | # | Total length of mains / Average number of miles surveyed each month
Leakage per part of system | 120.9444 | acre-feet per year | Average detectable leakage for supplier / Number of parts of system
Annual average rise in leakage per part of system | 35.3964 | acre-feet per year per part per year | Rate of rise of leakage / Number of parts of system
Cost for leak detection in each time step | 56248.1944 | $ per part | Cost of leak detection per mile x Total length of mains / Number of parts of system
Note: Repair costs per mile included in cost-benefit analysis, based on leakage corresponding to each survey cycle and leaks/mile
Calculation of Leakage reduction and Benefit-Cost Analysis across 30 years
| Water lost during implementation of additional intervention (from residual backlog and natural rise of leakage) |  |  |  |  | Baseline - Without additional intervention |  | Water savings and cost for additional intervention |  | Calculations for leaks repaired during active leak detection |  |  |  |  | Analysis of additional benefits or costs due to additional intervention for leakage reduction
(1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13) | (14) |  | (15) | (16) |  | (17) | (18) | (19)
Time steps from 2022 (Based on a 30 year time horizon) | Water loss due to backlog of leakage from unsurveyed parts in each time step | Water loss due to natural rise in leakage in never surveyed parts in each time step | Water loss due to natural rise in leakage in previously surveyed parts in each time step | Total water loss occuring in time step with intervention | Cumulative water loss occurring with intervention | Water loss occuring without intervention in each time step | Cumulative water loss occuring without intervention | Water saved due to water loss control in each time step with intervention | Cost associated with leak detection in each time step with intervention | Initial leakage level for part surveyed during time step (to calculate number of leaks) with intervention | Leaks found per part of the system with intervention | Incremental cost associated with leak repair in each time step with intervention | Total cost of leak detection and repair in each time step with intervention | Present value of total cost of leak detection and repair for each time step with intervention | Marginal cost of water including rise in cost of water and avoided cost of alternative supplies in each time step (begins in year 2022) | Value of water loss reduced in each time step with intervention | Present value of value of water loss reduced for each time step with intervention | Net benefit for each time step with intervention | Present value of net benefit (Benefit - Cost) corresponding to each time step with intervention (red indicates negative) | Year
# | (acre-feet) | (acre-feet) | (acre-feet) | (acre-feet) | (acre-feet) | (acre-feet) | (acre-feet) | (acre-feet) | ($) | (acre-feet) | # | ($) | ($) |  | ($ per acre-feet) | ($) |  | ($) | ($) in 2020
1 | 362.8331 | 4.4246 | 0 | 367.2577 | 367.2577 | 367.2577 | 367.2577 | 0 | 56248.1944 | 123.8941 | 3.0724 | 26097.6306 | 82345.825 | 82345.825 | 1425.584 | 0 | 0 | -82345.825 | -76786.5614 | 2022
2 | 352.7544 | 12.9049 | 0.1229 | 365.7823 | 733.0399 | 367.2577 | 734.5153 | 1.4754 | 56248.1944 | 126.8438 | 3.1455 | 26718.9697 | 82967.1641 | 82725.8803 | 1432.2367 | 2113.1227 | 1964.7328 | -80854.0414 | -75176.2259 | 2022
3 | 342.6757 | 20.8937 | 0.49162 | 364.061 | 1097.101 | 367.2577 | 1101.773 | 3.1966 | 56248.1944 | 129.7935 | 3.2187 | 27340.3087 | 83588.5032 | 83103.0286 | 1438.8895 | 4599.5674 | 4264.1348 | -78988.9358 | -73228.5104 | 2022
4 | 332.597 | 28.3909 | 1.1061 | 362.094 | 1459.195 | 367.2577 | 1469.0306 | 5.1636 | 56248.1944 | 132.7432 | 3.2918 | 27961.6478 | 84209.8423 | 83477.2836 | 1445.5422 | 7464.2402 | 6899.7713 | -76745.6021 | -70941.8625 | 2022
5 | 322.5183 | 35.3964 | 1.9665 | 359.8812 | 1819.0762 | 367.2577 | 1836.2883 | 7.3765 | 56248.1944 | 135.6929 | 3.365 | 28582.9869 | 84831.1814 | 83848.6589 | 1452.1949 | 10712.0468 | 9873.172 | -74119.1346 | -68314.7652 | 2022
6 | 312.4396 | 41.9103 | 3.0726 | 357.4226 | 2176.4988 | 367.2577 | 2203.546 | 9.8351 | 56248.1944 | 138.6426 | 3.4381 | 29204.326 | 85452.5204 | 84217.1682 | 1458.8476 | 14347.8932 | 13185.8317 | -71104.6272 | -65345.7363 | 2022
7 | 302.3609 | 47.9327 | 4.4246 | 354.7181 | 2531.2169 | 367.2577 | 2570.8036 | 12.5395 | 56248.1944 | 141.5923 | 3.5113 | 29825.6651 | 86073.8595 | 84582.8249 | 1465.5004 | 18376.6853 | 16839.2103 | -67697.1743 | -62033.3285 | 2022
8 | 292.2822 | 53.4633 | 6.0223 | 351.7679 | 2882.9848 | 367.2577 | 2938.0613 | 15.4898 | 56248.1944 | 144.542 | 3.5844 | 30447.0042 | 86695.1986 | 84945.6426 | 1472.1531 | 22803.3289 | 20834.7333 | -63891.8697 | -58376.1289 | 2022
9 | 282.2035 | 58.5024 | 7.8659 | 348.5718 | 3231.5566 | 367.2577 | 3305.3189 | 18.6858 | 56248.1944 | 147.4917 | 3.6576 | 31068.3433 | 87316.5377 | 85305.6346 | 1478.8058 | 27632.7299 | 25173.7919 | -59683.8078 | -54372.7588 | 2022
10 | 272.1248 | 63.0499 | 9.9552 | 345.1299 | 3576.6865 | 367.2577 | 3672.5766 | 22.1277 | 56248.1944 | 150.4414 | 3.7307 | 31689.6823 | 87937.8768 | 85662.8143 | 1485.4585 | 32869.7943 | 29857.7435 | -55068.0825 | -50021.8733 | 2022
11 | 262.0461 | 67.1057 | 12.2904 | 341.4423 | 3918.1288 | 367.2577 | 4039.8342 | 25.8154 | 56248.1944 | 153.3911 | 3.8039 | 32311.0214 | 88559.2159 | 86017.1951 | 1492.1113 | 38519.4279 | 34887.9119 | -50039.788 | -45322.1611 | 2022
12 | 251.9674 | 70.6699 | 14.8714 | 337.5088 | 4255.6376 | 367.2577 | 4407.0919 | 29.7489 | 56248.1944 | 156.3408 | 3.877 | 32932.3605 | 89180.555 | 86368.7902 | 1498.764 | 44586.5366 | 40265.5873 | -44594.0184 | -40272.3441 | 2022
13 | 241.8887 | 73.7425 | 17.6982 | 333.3295 | 4588.9671 | 367.2577 | 4774.3496 | 33.9282 | 56248.1944 | 159.2905 | 3.9501 | 33553.6996 | 89801.894 | 86717.6128 | 1505.4167 | 51076.0263 | 45992.0273 | -38725.8678 | -34871.1773 | 2023
14 | 231.81 | 76.3235 | 20.7708 | 328.9044 | 4917.8715 | 367.2577 | 5141.6072 | 38.3533 | 56248.1944 | 162.2402 | 4.0233 | 34175.0387 | 90423.2331 | 87063.676 | 1512.0694 | 57992.8028 | 52068.4563 | -32430.4303 | -29117.4484 | 2023
15 | 221.7313 | 78.4129 | 24.0892 | 324.2335 | 5242.105 | 367.2577 | 5508.8649 | 43.0242 | 56248.1944 | 165.1899 | 4.0964 | 34796.3778 | 91044.5722 | 87406.993 | 1518.7222 | 65341.7722 | 58496.0665 | -25702.8001 | -23009.9774 | 2023
16 | 211.6526 | 80.0107 | 27.6535 | 319.3168 | 5561.4217 | 367.2577 | 5876.1225 | 47.9409 | 56248.1944 | 168.1396 | 4.1696 | 35417.7169 | 91665.9113 | 87747.5768 | 1525.3749 | 73127.8402 | 65276.0179 | -18538.0711 | -16547.6166 | 2023
17 | 201.5739 | 81.1168 | 31.4635 | 314.1542 | 5875.576 | 367.2577 | 6243.3802 | 53.1034 | 56248.1944 | 171.0893 | 4.2427 | 36039.0559 | 92287.2504 | 88085.4403 | 1532.0276 | 81355.9127 | 72409.4384 | -10931.3377 | -9729.2501 | 2023
18 | 191.4953 | 81.7313 | 35.5193 | 308.7459 | 6184.3219 | 367.2577 | 6610.6379 | 58.5118 | 56248.1944 | 174.039 | 4.3159 | 36660.395 | 92908.5895 | 88420.5966 | 1538.6803 | 90030.8957 | 79897.4244 | -2877.6938 | -2553.7936 | 2023
19 | 181.4166 | 81.8542 | 39.821 | 303.0918 | 6487.4136 | 367.2577 | 6977.8955 | 64.1659 | 56248.1944 | 176.9887 | 4.389 | 37281.7341 | 93529.9286 | 88753.0586 | 1545.3331 | 99157.695 | 87741.0411 | 5627.7664 | 4979.806 | 2023
20 | 171.3379 | 81.4855 | 44.3684 | 297.1918 | 6784.6054 | 367.2577 | 7345.1532 | 70.0659 | 56248.1944 | 179.9384 | 4.4622 | 37903.0732 | 94151.2676 | 89082.8389 | 1551.9858 | 108741.2165 | 95941.3221 | 14589.9489 | 12872.5706 | 2023
21 | 161.2592 | 80.6252 | 49.1617 | 291.046 | 7075.6515 | 367.2577 | 7712.4108 | 76.2116 | 56248.1944 | 182.8881 | 4.5353 | 38524.4123 | 94772.6067 | 89409.9506 | 1558.6385 | 118786.3662 | 104499.2708 | 24013.7594 | 21125.4914 | 2023
22 | 151.1805 | 79.2732 | 54.2008 | 284.6545 | 7360.3059 | 367.2577 | 8079.6685 | 82.6032 | 56248.1944 | 185.8378 | 4.6085 | 39145.7514 | 95393.9458 | 89734.4062 | 1565.2912 | 129298.0498 | 113415.8597 | 33904.104 | 29739.529 | 2023
23 | 141.1018 | 77.4297 | 59.4857 | 278.0171 | 7638.323 | 367.2577 | 8446.9261 | 89.2406 | 56248.1944 | 188.7875 | 4.6816 | 39767.0904 | 96015.2849 | 90056.2184 | 1571.944 | 140281.1733 | 122692.031 | 44265.8884 | 38715.614 | 2023
24 | 131.0231 | 75.0945 | 65.0163 | 271.1339 | 7909.4569 | 367.2577 | 8814.1838 | 96.1238 | 56248.1944 | 191.7372 | 4.7548 | 40388.4295 | 96636.624 | 90375.4 | 1578.5967 | 151740.6426 | 132328.6971 | 55104.0186 | 48054.6468 | 2023
25 | 120.9444 | 72.2677 | 70.7928 | 264.0049 | 8173.4618 | 367.2577 | 9181.4415 | 103.2528 | 56248.1944 | 194.6869 | 4.8279 | 41009.7686 | 97257.9631 | 90691.9634 | 1585.2494 | 163681.3635 | 142326.7404 | 66423.4005 | 57757.4983 | 2024
26 | 110.8657 | 68.9493 | 76.8152 | 256.6301 | 8430.0919 | 367.2577 | 9548.6991 | 110.6276 | 56248.1944 | 197.6366 | 4.9011 | 41631.1077 | 97879.3021 | 91005.9212 | 1591.9021 | 176108.242 | 152687.0141 | 78228.9399 | 67825.0098 | 2024
27 | 100.787 | 65.1392 | 83.0833 | 249.0095 | 8679.1014 | 367.2577 | 9915.9568 | 118.2482 | 56248.1944 | 200.5863 | 4.9742 | 42252.4468 | 98500.6412 | 91317.2859 | 1598.5549 | 189026.184 | 163410.3419 | 90525.5427 | 78257.9936 | 2024
28 | 90.7083 | 60.8376 | 89.5972 | 241.1431 | 8920.2445 | 367.2577 | 10283.2144 | 126.1146 | 56248.1944 | 203.536 | 5.0474 | 42873.7859 | 99121.9803 | 91626.0699 | 1605.2076 | 202440.0952 | 174497.5188 | 103318.1149 | 89057.2329 | 2024
29 | 80.6296 | 56.0443 | 96.3569 | 233.0308 | 9153.2753 | 367.2577 | 10650.4721 | 134.2268 | 56248.1944 | 206.4857 | 5.1205 | 43495.125 | 99743.3194 | 91932.2856 | 1611.8603 | 216354.8817 | 185949.311 | 116611.5623 | 100223.4823 | 2024
30 | 70.5509 | 50.7595 | 103.3625 | 224.6728 | 9377.9481 | 367.2577 | 11017.7298 | 142.5849 | 56248.1944 | 209.4354 | 5.1937 | 44116.464 | 100364.6585 | 92235.9452 | 1618.513 | 230775.4493 | 197766.4561 | 130410.7908 | 111757.4682 | 2024
31 | 60.4722 | 44.983 | 110.6138 | 216.069 | 9594.0171 | 367.2577 | 11384.9874 | 151.1887 | 56248.1944 | 212.3851 | 5.2668 | 44737.8031 | 100985.9976 | 92537.0612 | 1625.1658 | 245706.7039 | 209949.6638 | 144720.7063 | 123659.8886 | 2024
32 | 50.3935 | 38.7148 | 118.111 | 207.2193 | 9801.2364 | 367.2577 | 11752.2451 | 160.0384 | 56248.1944 | 215.3348 | 5.34 | 45359.1422 | 101607.3367 | 92835.6457 | 1631.8185 | 261153.5513 | 222499.6156 | 159546.2147 | 135931.4137 | 2024
33 | 40.3148 | 31.9551 | 125.8539 | 198.1238 | 9999.3602 | 367.2577 | 12119.5027 | 169.1338 | 56248.1944 | 218.2845 | 5.4131 | 45980.4813 | 102228.6757 | 93131.7108 | 1638.4712 | 277120.8976 | 235416.9655 | 174892.2218 | 148572.6862 | 2024
34 | 30.2361 | 24.7038 | 133.8427 | 188.7826 | 10188.1428 | 367.2577 | 12486.7604 | 178.4751 | 56248.1944 | 221.2342 | 5.4863 | 46601.8204 | 102850.0148 | 93425.2688 | 1645.1239 | 293613.6485 | 248702.34 | 190763.6336 | 161584.3212 | 2024
35 | 20.1574 | 16.9608 | 142.0773 | 179.1955 | 10367.3383 | 367.2577 | 12854.018 | 188.0622 | 56248.1944 | 224.1839 | 5.5594 | 47223.1595 | 103471.3539 | 93716.3317 | 1651.7767 | 310636.7099 | 262356.3385 | 207165.356 | 174966.9067 | 2024
36 | 10.0787 | 8.7262 | 150.5577 | 169.3626 | 10536.7009 | 367.2577 | 13221.2757 | 197.8951 | 56248.1944 | 227.1336 | 5.6326 | 47844.4986 | 104092.693 | 94004.9114 | 1658.4294 | 328194.9878 | 276379.5332 | 224102.2948 | 188721.0041 | 2024
37 | 0 | 0 | 159.2839 | 159.2839 | 10695.9848 | 367.2577 | 13588.5334 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 70791.0922 | 1665.0821 | 346293.388 | 290772.47 | 267676.9865 | 224760.5678 | 2025
38 | 0 | 0 | 159.2839 | 159.2839 | 10855.2687 | 367.2577 | 13955.791 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 70585.2186 | 1671.7348 | 347676.9803 | 291085.2335 | 269060.5788 | 225265.3062 | 2025
39 | 0 | 0 | 159.2839 | 159.2839 | 11014.5526 | 367.2577 | 14323.0487 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 70379.9438 | 1678.3876 | 349060.5726 | 291393.7187 | 270444.1711 | 225765.2078 | 2025
40 | 0 | 0 | 159.2839 | 159.2839 | 11173.8365 | 367.2577 | 14690.3063 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 70175.2659 | 1685.0403 | 350444.1649 | 291697.9478 | 271827.7634 | 226260.2967 | 2025
41 | 0 | 0 | 159.2839 | 159.2839 | 11333.1204 | 367.2577 | 15057.564 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 69971.1833 | 1691.693 | 351827.7572 | 291997.9429 | 273211.3557 | 226750.5966 | 2025
42 | 0 | 0 | 159.2839 | 159.2839 | 11492.4043 | 367.2577 | 15424.8217 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 69767.6942 | 1698.3457 | 353211.3495 | 292293.726 | 274594.948 | 227236.131 | 2025
43 | 0 | 0 | 159.2839 | 159.2839 | 11651.6881 | 367.2577 | 15792.0793 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 69564.7969 | 1704.9985 | 354594.9418 | 292585.3192 | 275978.5403 | 227716.9237 | 2025
44 | 0 | 0 | 159.2839 | 159.2839 | 11810.972 | 367.2577 | 16159.337 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 69362.4896 | 1711.6512 | 355978.5342 | 292872.7443 | 277362.1326 | 228192.998 | 2025
45 | 0 | 0 | 159.2839 | 159.2839 | 11970.2559 | 367.2577 | 16526.5946 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 69160.7707 | 1718.3039 | 357362.1265 | 293156.023 | 278745.7249 | 228664.3774 | 2025
46 | 0 | 0 | 159.2839 | 159.2839 | 12129.5398 | 367.2577 | 16893.8523 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 68959.6384 | 1724.9566 | 358745.7188 | 293435.1772 | 280129.3173 | 229131.0852 | 2025
47 | 0 | 0 | 159.2839 | 159.2839 | 12288.8237 | 367.2577 | 17261.1099 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 68759.0911 | 1731.6094 | 360129.3111 | 293710.2282 | 281512.9096 | 229593.1444 | 2025
48 | 0 | 0 | 159.2839 | 159.2839 | 12448.1076 | 367.2577 | 17628.3676 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 68559.127 | 1738.2621 | 361512.9034 | 293981.1978 | 282896.5019 | 230050.5783 | 2025
49 | 0 | 0 | 159.2839 | 159.2839 | 12607.3915 | 367.2577 | 17995.6253 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 68359.7444 | 1744.9148 | 362896.4957 | 294248.1072 | 284280.0942 | 230503.4097 | 2026
50 | 0 | 0 | 159.2839 | 159.2839 | 12766.6754 | 367.2577 | 18362.8829 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 68160.9416 | 1751.5675 | 364280.088 | 294510.9778 | 285663.6865 | 230951.6617 | 2026
51 | 0 | 0 | 159.2839 | 159.2839 | 12925.9593 | 367.2577 | 18730.1406 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 67962.717 | 1758.2203 | 365663.6803 | 294769.8309 | 287047.2788 | 231395.3569 | 2026
52 | 0 | 0 | 159.2839 | 159.2839 | 13085.2432 | 367.2577 | 19097.3982 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 67765.0689 | 1764.873 | 367047.2726 | 295024.6875 | 288430.8711 | 231834.5182 | 2026
53 | 0 | 0 | 159.2839 | 159.2839 | 13244.5271 | 367.2577 | 19464.6559 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 67567.9956 | 1771.5257 | 368430.8649 | 295275.5688 | 289814.4634 | 232269.1682 | 2026
54 | 0 | 0 | 159.2839 | 159.2839 | 13403.811 | 367.2577 | 19831.9136 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 67371.4954 | 1778.1784 | 369814.4572 | 295522.4957 | 291198.0557 | 232699.3293 | 2026
55 | 0 | 0 | 159.2839 | 159.2839 | 13563.0949 | 367.2577 | 20199.1712 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 67175.5667 | 1784.8312 | 371198.0495 | 295765.489 | 292581.648 | 233125.024 | 2026
56 | 0 | 0 | 159.2839 | 159.2839 | 13722.3788 | 367.2577 | 20566.4289 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 66980.2077 | 1791.4839 | 372581.6418 | 296004.5696 | 293965.2403 | 233546.2746 | 2026
57 | 0 | 0 | 159.2839 | 159.2839 | 13881.6627 | 367.2577 | 20933.6865 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 66785.4169 | 1798.1366 | 373965.2341 | 296239.7582 | 295348.8326 | 233963.1035 | 2026
58 | 0 | 0 | 159.2839 | 159.2839 | 14040.9466 | 367.2577 | 21300.9442 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 66591.1926 | 1804.7893 | 375348.8264 | 296471.0754 | 296732.4249 | 234375.5326 | 2026
59 | 0 | 0 | 159.2839 | 159.2839 | 14200.2305 | 367.2577 | 21668.2018 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 66397.5331 | 1811.4421 | 376732.4187 | 296698.5417 | 298116.0172 | 234783.5842 | 2026
60 | 0 | 0 | 159.2839 | 159.2839 | 14359.5144 | 367.2577 | 22035.4595 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 66204.4369 | 1818.0948 | 378116.011 | 296922.1775 | 299499.6095 | 235187.2802 | 2026
61 | 0 | 0 | 159.2839 | 159.2839 | 14518.7983 | 367.2577 | 22402.7172 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 66011.9022 | 1824.7475 | 379499.6033 | 297142.0033 | 300883.2018 | 235586.6424 | 2027
62 | 0 | 0 | 159.2839 | 159.2839 | 14678.0822 | 367.2577 | 22769.9748 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 65819.9274 | 1831.4002 | 380883.1956 | 297358.0392 | 302266.7941 | 235981.6927 | 2027
63 | 0 | 0 | 159.2839 | 159.2839 | 14837.3661 | 367.2577 | 23137.2325 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 65628.5109 | 1838.053 | 382266.7879 | 297570.3055 | 303650.3864 | 236372.4527 | 2027
64 | 0 | 0 | 159.2839 | 159.2839 | 14996.65 | 367.2577 | 23504.4901 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 65437.6511 | 1844.7057 | 383650.3802 | 297778.8223 | 305033.9787 | 236758.9441 | 2027
65 | 0 | 0 | 159.2839 | 159.2839 | 15155.9339 | 367.2577 | 23871.7478 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 65247.3463 | 1851.3584 | 385033.9725 | 297983.6095 | 306417.571 | 237141.1884 | 2027
66 | 0 | 0 | 159.2839 | 159.2839 | 15315.2178 | 367.2577 | 24239.0055 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 65057.595 | 1858.0111 | 386417.5648 | 298184.6872 | 307801.1633 | 237519.2071 | 2027
67 | 0 | 0 | 159.2839 | 159.2839 | 15474.5017 | 367.2577 | 24606.2631 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 64868.3955 | 1864.6639 | 387801.1571 | 298382.0751 | 309184.7556 | 237893.0214 | 2027
68 | 0 | 0 | 159.2839 | 159.2839 | 15633.7856 | 367.2577 | 24973.5208 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 64679.7462 | 1871.3166 | 389184.7494 | 298575.793 | 310568.3479 | 238262.6526 | 2027
69 | 0 | 0 | 159.2839 | 159.2839 | 15793.0695 | 367.2577 | 25340.7784 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 64491.6456 | 1877.9693 | 390568.3417 | 298765.8606 | 311951.9402 | 238628.122 | 2027
70 | 0 | 0 | 159.2839 | 159.2839 | 15952.3534 | 367.2577 | 25708.0361 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 64304.092 | 1884.622 | 391951.9341 | 298952.2975 | 313335.5325 | 238989.4505 | 2027
71 | 0 | 0 | 159.2839 | 159.2839 | 16111.6373 | 367.2577 | 26075.2938 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 64117.0838 | 1891.2748 | 393335.5264 | 299135.1232 | 314719.1248 | 239346.6592 | 2027
72 | 0 | 0 | 159.2839 | 159.2839 | 16270.9212 | 367.2577 | 26442.5514 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 63930.6195 | 1897.9275 | 394719.1187 | 299314.3571 | 316102.7172 | 239699.769 | 2027
73 | 0 | 0 | 159.2839 | 159.2839 | 16430.2051 | 367.2577 | 26809.8091 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 63744.6975 | 1904.5802 | 396102.711 | 299490.0185 | 317486.3095 | 240048.8006 | 2028
74 | 0 | 0 | 159.2839 | 159.2839 | 16589.489 | 367.2577 | 27177.0667 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 63559.3162 | 1911.2329 | 397486.3033 | 299662.1268 | 318869.9018 | 240393.7749 | 2028
75 | 0 | 0 | 159.2839 | 159.2839 | 16748.7729 | 367.2577 | 27544.3244 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 63374.4739 | 1917.8857 | 398869.8956 | 299830.7011 | 320253.4941 | 240734.7125 | 2028
76 | 0 | 0 | 159.2839 | 159.2839 | 16908.0568 | 367.2577 | 27911.582 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 63190.1693 | 1924.5384 | 400253.4879 | 299995.7605 | 321637.0864 | 241071.634 | 2028
77 | 0 | 0 | 159.2839 | 159.2839 | 17067.3407 | 367.2577 | 28278.8397 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 63006.4006 | 1931.1911 | 401637.0802 | 300157.324 | 323020.6787 | 241404.5597 | 2028
78 | 0 | 0 | 159.2839 | 159.2839 | 17226.6246 | 367.2577 | 28646.0974 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 62823.1664 | 1937.8439 | 403020.6725 | 300315.4106 | 324404.271 | 241733.5102 | 2028
79 | 0 | 0 | 159.2839 | 159.2839 | 17385.9085 | 367.2577 | 29013.355 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 62640.465 | 1944.4966 | 404404.2648 | 300470.0391 | 325787.8633 | 242058.5056 | 2028
80 | 0 | 0 | 159.2839 | 159.2839 | 17545.1924 | 367.2577 | 29380.6127 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 62458.295 | 1951.1493 | 405787.8571 | 300621.2283 | 327171.4556 | 242379.5664 | 2028
81 | 0 | 0 | 159.2839 | 159.2839 | 17704.4763 | 367.2577 | 29747.8703 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 62276.6548 | 1957.802 | 407171.4494 | 300768.9969 | 328555.0479 | 242696.7124 | 2028
82 | 0 | 0 | 159.2839 | 159.2839 | 17863.7602 | 367.2577 | 30115.128 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 62095.5428 | 1964.4548 | 408555.0417 | 300913.3635 | 329938.6402 | 243009.9639 | 2028
83 | 0 | 0 | 159.2839 | 159.2839 | 18023.0441 | 367.2577 | 30482.3857 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 61914.9575 | 1971.1075 | 409938.634 | 301054.3466 | 331322.2325 | 243319.3409 | 2028
84 | 0 | 0 | 159.2839 | 159.2839 | 18182.328 | 367.2577 | 30849.6433 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 61734.8973 | 1977.7602 | 411322.2263 | 301191.9647 | 332705.8248 | 243624.863 | 2028
85 | 0 | 0 | 159.2839 | 159.2839 | 18341.6119 | 367.2577 | 31216.901 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 61555.3609 | 1984.4129 | 412705.8186 | 301326.2363 | 334089.4171 | 243926.5503 | 2029
86 | 0 | 0 | 159.2839 | 159.2839 | 18500.8958 | 367.2577 | 31584.1586 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 61376.3465 | 1991.0657 | 414089.4109 | 301457.1795 | 335473.0094 | 244224.4224 | 2029
87 | 0 | 0 | 159.2839 | 159.2839 | 18660.1797 | 367.2577 | 31951.4163 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 61197.8528 | 1997.7184 | 415473.0032 | 301584.8126 | 336856.6017 | 244518.499 | 2029
88 | 0 | 0 | 159.2839 | 159.2839 | 18819.4636 | 367.2577 | 32318.6739 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 61019.8781 | 2004.3711 | 416856.5955 | 301709.1538 | 338240.194 | 244808.7995 | 2029
89 | 0 | 0 | 159.2839 | 159.2839 | 18978.7475 | 367.2577 | 32685.9316 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 60842.4211 | 2011.0238 | 418240.1878 | 301830.2211 | 339623.7863 | 245095.3435 | 2029
90 | 0 | 0 | 159.2839 | 159.2839 | 19138.0314 | 367.2577 | 33053.1893 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 60665.4801 | 2017.6766 | 419623.7801 | 301948.0325 | 341007.3786 | 245378.1504 | 2029
91 | 0 | 0 | 159.2839 | 159.2839 | 19297.3153 | 367.2577 | 33420.4469 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 60489.0537 | 2024.3293 | 421007.3724 | 302062.6059 | 342390.9709 | 245657.2395 | 2029
92 | 0 | 0 | 159.2839 | 159.2839 | 19456.5992 | 367.2577 | 33787.7046 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 60313.1404 | 2030.982 | 422390.9647 | 302173.9592 | 343774.5632 | 245932.63 | 2029
93 | 0 | 0 | 159.2839 | 159.2839 | 19615.8831 | 367.2577 | 34154.9622 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 60137.7386 | 2037.6347 | 423774.557 | 302282.1101 | 345158.1555 | 246204.3411 | 2029
94 | 0 | 0 | 159.2839 | 159.2839 | 19775.167 | 367.2577 | 34522.2199 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 59962.847 | 2044.2875 | 425158.1493 | 302387.0764 | 346541.7478 | 246472.3918 | 2029
95 | 0 | 0 | 159.2839 | 159.2839 | 19934.4509 | 367.2577 | 34889.4776 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 59788.464 | 2050.9402 | 426541.7416 | 302488.8755 | 347925.3401 | 246736.8012 | 2029
96 | 0 | 0 | 159.2839 | 159.2839 | 20093.7348 | 367.2577 | 35256.7352 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 59614.5881 | 2057.5929 | 427925.3339 | 302587.5251 | 349308.9324 | 246997.5881 | 2029
97 | 0 | 0 | 159.2839 | 159.2839 | 20253.0187 | 367.2577 | 35623.9929 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 59441.2179 | 2064.2456 | 429308.9263 | 302683.0426 | 350692.5247 | 247254.7714 | 2030
98 | 0 | 0 | 159.2839 | 159.2839 | 20412.3025 | 367.2577 | 35991.2505 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 59268.3518 | 2070.8984 | 430692.5186 | 302775.4454 | 352076.117 | 247508.3698 | 2030
99 | 0 | 0 | 159.2839 | 159.2839 | 20571.5864 | 367.2577 | 36358.5082 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 59095.9885 | 2077.5511 | 432076.1109 | 302864.7508 | 353459.7094 | 247758.402 | 2030
100 | 0 | 0 | 159.2839 | 159.2839 | 20730.8703 | 367.2577 | 36725.7658 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 58924.1265 | 2084.2038 | 433459.7032 | 302950.976 | 354843.3017 | 248004.8867 | 2030
101 | 0 | 0 | 159.2839 | 159.2839 | 20890.1542 | 367.2577 | 37093.0235 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 58752.7643 | 2090.8565 | 434843.2955 | 303034.1382 | 356226.894 | 248247.8422 | 2030
102 | 0 | 0 | 159.2839 | 159.2839 | 21049.4381 | 367.2577 | 37460.2812 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 58581.9004 | 2097.5093 | 436226.8878 | 303114.2545 | 357610.4863 | 248487.2872 | 2030
103 | 0 | 0 | 159.2839 | 159.2839 | 21208.722 | 367.2577 | 37827.5388 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 58411.5334 | 2104.162 | 437610.4801 | 303191.3419 | 358994.0786 | 248723.2399 | 2030
104 | 0 | 0 | 159.2839 | 159.2839 | 21368.0059 | 367.2577 | 38194.7965 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 58241.6619 | 2110.8147 | 438994.0724 | 303265.4173 | 360377.6709 | 248955.7186 | 2030
105 | 0 | 0 | 159.2839 | 159.2839 | 21527.2898 | 367.2577 | 38562.0541 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 58072.2844 | 2117.4674 | 440377.6647 | 303336.4976 | 361761.2632 | 249184.7415 | 2030
106 | 0 | 0 | 159.2839 | 159.2839 | 21686.5737 | 367.2577 | 38929.3118 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 57903.3995 | 2124.1202 | 441761.257 | 303404.5996 | 363144.8555 | 249410.3268 | 2030
107 | 0 | 0 | 159.2839 | 159.2839 | 21845.8576 | 367.2577 | 39296.5695 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 57735.0057 | 2130.7729 | 443144.8493 | 303469.74 | 364528.4478 | 249632.4925 | 2030
108 | 0 | 0 | 159.2839 | 159.2839 | 22005.1415 | 367.2577 | 39663.8271 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 57567.1017 | 2137.4256 | 444528.4416 | 303531.9355 | 365912.0401 | 249851.2566 | 2030
109 | 0 | 0 | 159.2839 | 159.2839 | 22164.4254 | 367.2577 | 40031.0848 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 57399.6859 | 2144.0783 | 445912.0339 | 303591.2026 | 367295.6324 | 250066.6371 | 2031
110 | 0 | 0 | 159.2839 | 159.2839 | 22323.7093 | 367.2577 | 40398.3424 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 57232.7571 | 2150.7311 | 447295.6262 | 303647.5579 | 368679.2247 | 250278.6516 | 2031
111 | 0 | 0 | 159.2839 | 159.2839 | 22482.9932 | 367.2577 | 40765.6001 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 57066.3137 | 2157.3838 | 448679.2185 | 303701.0177 | 370062.817 | 250487.3181 | 2031
112 | 0 | 0 | 159.2839 | 159.2839 | 22642.2771 | 367.2577 | 41132.8577 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 56900.3543 | 2164.0365 | 450062.8108 | 303751.5985 | 371446.4093 | 250692.6542 | 2031
113 | 0 | 0 | 159.2839 | 159.2839 | 22801.561 | 367.2577 | 41500.1154 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 56734.8776 | 2170.6892 | 451446.4031 | 303799.3166 | 372830.0016 | 250894.6774 | 2031
114 | 0 | 0 | 159.2839 | 159.2839 | 22960.8449 | 367.2577 | 41867.3731 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 56569.8821 | 2177.342 | 452829.9954 | 303844.1881 | 374213.5939 | 251093.4054 | 2031
115 | 0 | 0 | 159.2839 | 159.2839 | 23120.1288 | 367.2577 | 42234.6307 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 56405.3664 | 2183.9947 | 454213.5877 | 303886.2292 | 375597.1862 | 251288.8555 | 2031
116 | 0 | 0 | 159.2839 | 159.2839 | 23279.4127 | 367.2577 | 42601.8884 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 56241.3292 | 2190.6474 | 455597.18 | 303925.456 | 376980.7785 | 251481.0452 | 2031
117 | 0 | 0 | 159.2839 | 159.2839 | 23438.6966 | 367.2577 | 42969.146 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 56077.7691 | 2197.3001 | 456980.7723 | 303961.8845 | 378364.3708 | 251669.9917 | 2031
118 | 0 | 0 | 159.2839 | 159.2839 | 23597.9805 | 367.2577 | 43336.4037 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 55914.6846 | 2203.9529 | 458364.3646 | 303995.5307 | 379747.9631 | 251855.7124 | 2031
119 | 0 | 0 | 159.2839 | 159.2839 | 23757.2644 | 367.2577 | 43703.6614 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 55752.0743 | 2210.6056 | 459747.9569 | 304026.4105 | 381131.5554 | 252038.2243 | 2031
120 | 0 | 0 | 159.2839 | 159.2839 | 23916.5483 | 367.2577 | 44070.919 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 55589.937 | 2217.2583 | 461131.5492 | 304054.5395 | 382515.1477 | 252217.5446 | 2031
121 | 0 | 0 | 159.2839 | 159.2839 | 24075.8322 | 367.2577 | 44438.1767 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 55428.2712 | 2223.911 | 462515.1415 | 304079.9337 | 383898.74 | 252393.6903 | 2032
122 | 0 | 0 | 159.2839 | 159.2839 | 24235.1161 | 367.2577 | 44805.4343 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 55267.0756 | 2230.5638 | 463898.7338 | 304102.6085 | 385282.3323 | 252566.6783 | 2032
123 | 0 | 0 | 159.2839 | 159.2839 | 24394.4 | 367.2577 | 45172.692 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 55106.3487 | 2237.2165 | 465282.3262 | 304122.5798 | 386665.9246 | 252736.5256 | 2032
124 | 0 | 0 | 159.2839 | 159.2839 | 24553.6839 | 367.2577 | 45539.9496 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 54946.0893 | 2243.8692 | 466665.9185 | 304139.8629 | 388049.5169 | 252903.2488 | 2032
125 | 0 | 0 | 159.2839 | 159.2839 | 24712.9678 | 367.2577 | 45907.2073 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 54786.296 | 2250.5219 | 468049.5108 | 304154.4734 | 389433.1092 | 253066.8648 | 2032
126 | 0 | 0 | 159.2839 | 159.2839 | 24872.2517 | 367.2577 | 46274.465 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 54626.9673 | 2257.1747 | 469433.1031 | 304166.4266 | 390816.7016 | 253227.3902 | 2032
127 | 0 | 0 | 159.2839 | 159.2839 | 25031.5356 | 367.2577 | 46641.7226 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 54468.102 | 2263.8274 | 470816.6954 | 304175.7378 | 392200.2939 | 253384.8416 | 2032
128 | 0 | 0 | 159.2839 | 159.2839 | 25190.8195 | 367.2577 | 47008.9803 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 54309.6987 | 2270.4801 | 472200.2877 | 304182.4225 | 393583.8862 | 253539.2355 | 2032
129 | 0 | 0 | 159.2839 | 159.2839 | 25350.1034 | 367.2577 | 47376.2379 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 54151.7561 | 2277.1328 | 473583.88 | 304186.4956 | 394967.4785 | 253690.5884 | 2032
130 | 0 | 0 | 159.2839 | 159.2839 | 25509.3873 | 367.2577 | 47743.4956 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 53994.2728 | 2283.7856 | 474967.4723 | 304187.9725 | 396351.0708 | 253838.9167 | 2032
131 | 0 | 0 | 159.2839 | 159.2839 | 25668.6712 | 367.2577 | 48110.7533 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 53837.2475 | 2290.4383 | 476351.0646 | 304186.8681 | 397734.6631 | 253984.2366 | 2032
132 | 0 | 0 | 159.2839 | 159.2839 | 25827.9551 | 367.2577 | 48478.0109 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 53680.6788 | 2297.091 | 477734.6569 | 304183.1974 | 399118.2554 | 254126.5644 | 2032
133 | 0 | 0 | 159.2839 | 159.2839 | 25987.239 | 367.2577 | 48845.2686 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 53524.5655 | 2303.7437 | 479118.2492 | 304176.9754 | 400501.8477 | 254265.9164 | 2033
134 | 0 | 0 | 159.2839 | 159.2839 | 26146.5229 | 367.2577 | 49212.5262 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 53368.9062 | 2310.3965 | 480501.8415 | 304168.217 | 401885.44 | 254402.3085 | 2033
135 | 0 | 0 | 159.2839 | 159.2839 | 26305.8068 | 367.2577 | 49579.7839 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 53213.6996 | 2317.0492 | 481885.4338 | 304156.9369 | 403269.0323 | 254535.7568 | 2033
136 | 0 | 0 | 159.2839 | 159.2839 | 26465.0907 | 367.2577 | 49947.0415 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 53058.9443 | 2323.7019 | 483269.0261 | 304143.1499 | 404652.6246 | 254666.2774 | 2033
137 | 0 | 0 | 159.2839 | 159.2839 | 26624.3746 | 367.2577 | 50314.2992 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 52904.6391 | 2330.3546 | 484652.6184 | 304126.8707 | 406036.2169 | 254793.886 | 2033
138 | 0 | 0 | 159.2839 | 159.2839 | 26783.6585 | 367.2577 | 50681.5569 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 52750.7827 | 2337.0074 | 486036.2107 | 304108.1138 | 407419.8092 | 254918.5986 | 2033
139 | 0 | 0 | 159.2839 | 159.2839 | 26942.9424 | 367.2577 | 51048.8145 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 52597.3737 | 2343.6601 | 487419.803 | 304086.8939 | 408803.4015 | 255040.4309 | 2033
140 | 0 | 0 | 159.2839 | 159.2839 | 27102.2263 | 367.2577 | 51416.0722 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 52444.4108 | 2350.3128 | 488803.3953 | 304063.2254 | 410186.9938 | 255159.3986 | 2033
141 | 0 | 0 | 159.2839 | 159.2839 | 27261.5102 | 367.2577 | 51783.3298 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 52291.8928 | 2356.9655 | 490186.9876 | 304037.1228 | 411570.5861 | 255275.5173 | 2033
142 | 0 | 0 | 159.2839 | 159.2839 | 27420.7941 | 367.2577 | 52150.5875 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 52139.8183 | 2363.6183 | 491570.5799 | 304008.6003 | 412954.1784 | 255388.8026 | 2033
143 | 0 | 0 | 159.2839 | 159.2839 | 27580.078 | 367.2577 | 52517.8452 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 51988.1861 | 2370.271 | 492954.1722 | 303977.6724 | 414337.7707 | 255499.2699 | 2033
144 | 0 | 0 | 159.2839 | 159.2839 | 27739.3619 | 367.2577 | 52885.1028 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 51836.9949 | 2376.9237 | 494337.7645 | 303944.3531 | 415721.363 | 255606.9348 | 2033
145 | 0 | 0 | 159.2839 | 159.2839 | 27898.6458 | 367.2577 | 53252.3605 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 51686.2433 | 2383.5764 | 495721.3568 | 303908.6568 | 417104.9553 | 255711.8126 | 2034
146 | 0 | 0 | 159.2839 | 159.2839 | 28057.9297 | 367.2577 | 53619.6181 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 51535.9302 | 2390.2292 | 497104.9491 | 303870.5975 | 418488.5476 | 255813.9186 | 2034
147 | 0 | 0 | 159.2839 | 159.2839 | 28217.2136 | 367.2577 | 53986.8758 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 51386.0542 | 2396.8819 | 498488.5414 | 303830.1892 | 419872.1399 | 255913.268 | 2034
148 | 0 | 0 | 159.2839 | 159.2839 | 28376.4975 | 367.2577 | 54354.1335 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 51236.6141 | 2403.5346 | 499872.1337 | 303787.4459 | 421255.7322 | 256009.876 | 2034
149 | 0 | 0 | 159.2839 | 159.2839 | 28535.7814 | 367.2577 | 54721.3911 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 51087.6086 | 2410.1873 | 501255.726 | 303742.3816 | 422639.3245 | 256103.7577 | 2034
150 | 0 | 0 | 159.2839 | 159.2839 | 28695.0653 | 367.2577 | 55088.6488 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 50939.0364 | 2416.8401 | 502639.3184 | 303695.0101 | 424022.9168 | 256194.9281 | 2034
151 | 0 | 0 | 159.2839 | 159.2839 | 28854.3492 | 367.2577 | 55455.9064 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 50790.8963 | 2423.4928 | 504022.9107 | 303645.3453 | 425406.5091 | 256283.4022 | 2034
152 | 0 | 0 | 159.2839 | 159.2839 | 29013.633 | 367.2577 | 55823.1641 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 50643.187 | 2430.1455 | 505406.503 | 303593.4007 | 426790.1015 | 256369.195 | 2034
153 | 0 | 0 | 159.2839 | 159.2839 | 29172.9169 | 367.2577 | 56190.4217 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 50495.9072 | 2436.7983 | 506790.0953 | 303539.1903 | 428173.6938 | 256452.3212 | 2034
154 | 0 | 0 | 159.2839 | 159.2839 | 29332.2008 | 367.2577 | 56557.6794 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 50349.0558 | 2443.451 | 508173.6876 | 303482.7274 | 429557.2861 | 256532.7957 | 2034
155 | 0 | 0 | 159.2839 | 159.2839 | 29491.4847 | 367.2577 | 56924.9371 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 50202.6315 | 2450.1037 | 509557.2799 | 303424.0258 | 430940.8784 | 256610.6332 | 2034
156 | 0 | 0 | 159.2839 | 159.2839 | 29650.7686 | 367.2577 | 57292.1947 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 50056.633 | 2456.7564 | 510940.8722 | 303363.099 | 432324.4707 | 256685.8482 | 2034
157 | 0 | 0 | 159.2839 | 159.2839 | 29810.0525 | 367.2577 | 57659.4524 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 49911.0591 | 2463.4092 | 512324.4645 | 303299.9602 | 433708.063 | 256758.4556 | 2035
158 | 0 | 0 | 159.2839 | 159.2839 | 29969.3364 | 367.2577 | 58026.71 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 49765.9085 | 2470.0619 | 513708.0568 | 303234.623 | 435091.6553 | 256828.4696 | 2035
159 | 0 | 0 | 159.2839 | 159.2839 | 30128.6203 | 367.2577 | 58393.9677 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 49621.18 | 2476.7146 | 515091.6491 | 303167.1007 | 436475.2476 | 256895.9049 | 2035
160 | 0 | 0 | 159.2839 | 159.2839 | 30287.9042 | 367.2577 | 58761.2254 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 49476.8725 | 2483.3673 | 516475.2414 | 303097.4064 | 437858.8399 | 256960.7759 | 2035
161 | 0 | 0 | 159.2839 | 159.2839 | 30447.1881 | 367.2577 | 59128.483 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 49332.9846 | 2490.0201 | 517858.8337 | 303025.5535 | 439242.4322 | 257023.0968 | 2035
162 | 0 | 0 | 159.2839 | 159.2839 | 30606.472 | 367.2577 | 59495.7407 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 49189.5152 | 2496.6728 | 519242.426 | 302951.5551 | 440626.0245 | 257082.882 | 2035
163 | 0 | 0 | 159.2839 | 159.2839 | 30765.7559 | 367.2577 | 59862.9983 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 49046.463 | 2503.3255 | 520626.0183 | 302875.4242 | 442009.6168 | 257140.1457 | 2035
164 | 0 | 0 | 159.2839 | 159.2839 | 30925.0398 | 367.2577 | 60230.256 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 48903.8269 | 2509.9782 | 522009.6106 | 302797.1739 | 443393.2091 | 257194.902 | 2035
165 | 0 | 0 | 159.2839 | 159.2839 | 31084.3237 | 367.2577 | 60597.5136 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 48761.6055 | 2516.631 | 523393.2029 | 302716.8171 | 444776.8014 | 257247.165 | 2035
166 | 0 | 0 | 159.2839 | 159.2839 | 31243.6076 | 367.2577 | 60964.7713 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 48619.7978 | 2523.2837 | 524776.7952 | 302634.3668 | 446160.3937 | 257296.9489 | 2035
167 | 0 | 0 | 159.2839 | 159.2839 | 31402.8915 | 367.2577 | 61332.029 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 48478.4024 | 2529.9364 | 526160.3875 | 302549.8359 | 447543.986 | 257344.2675 | 2035
168 | 0 | 0 | 159.2839 | 159.2839 | 31562.1754 | 367.2577 | 61699.2866 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 48337.4183 | 2536.5891 | 527543.9798 | 302463.237 | 448927.5783 | 257389.1348 | 2035
169 | 0 | 0 | 159.2839 | 159.2839 | 31721.4593 | 367.2577 | 62066.5443 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 48196.8442 | 2543.2419 | 528927.5721 | 302374.583 | 450311.1706 | 257431.5646 | 2036
170 | 0 | 0 | 159.2839 | 159.2839 | 31880.7432 | 367.2577 | 62433.8019 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 48056.6789 | 2549.8946 | 530311.1644 | 302283.8866 | 451694.7629 | 257471.5708 | 2036
171 | 0 | 0 | 159.2839 | 159.2839 | 32040.0271 | 367.2577 | 62801.0596 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 47916.9212 | 2556.5473 | 531694.7567 | 302191.1603 | 453078.3552 | 257509.167 | 2036
172 | 0 | 0 | 159.2839 | 159.2839 | 32199.311 | 367.2577 | 63168.3173 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 47777.5699 | 2563.2 | 533078.349 | 302096.4168 | 454461.9475 | 257544.367 | 2036
173 | 0 | 0 | 159.2839 | 159.2839 | 32358.5949 | 367.2577 | 63535.5749 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 47638.6239 | 2569.8528 | 534461.9413 | 301999.6686 | 455845.5398 | 257577.1843 | 2036
174 | 0 | 0 | 159.2839 | 159.2839 | 32517.8788 | 367.2577 | 63902.8326 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 47500.082 | 2576.5055 | 535845.5336 | 301900.9281 | 457229.1321 | 257607.6326 | 2036
175 | 0 | 0 | 159.2839 | 159.2839 | 32677.1627 | 367.2577 | 64270.0902 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 47361.943 | 2583.1582 | 537229.1259 | 301800.2078 | 458612.7244 | 257635.7253 | 2036
176 | 0 | 0 | 159.2839 | 159.2839 | 32836.4466 | 367.2577 | 64637.3479 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 47224.2058 | 2589.8109 | 538612.7182 | 301697.5199 | 459996.3167 | 257661.4759 | 2036
177 | 0 | 0 | 159.2839 | 159.2839 | 32995.7305 | 367.2577 | 65004.6055 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 47086.8691 | 2596.4637 | 539996.3106 | 301592.8768 | 461379.909 | 257684.8977 | 2036
178 | 0 | 0 | 159.2839 | 159.2839 | 33155.0144 | 367.2577 | 65371.8632 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 46949.9318 | 2603.1164 | 541379.9029 | 301486.2907 | 462763.5013 | 257706.0042 | 2036
179 | 0 | 0 | 159.2839 | 159.2839 | 33314.2983 | 367.2577 | 65739.1209 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 46813.3927 | 2609.7691 | 542763.4952 | 301377.7739 | 464147.0937 | 257724.8085 | 2036
180 | 0 | 0 | 159.2839 | 159.2839 | 33473.5822 | 367.2577 | 66106.3785 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 46677.2507 | 2616.4218 | 544147.0875 | 301267.3384 | 465530.686 | 257741.3238 | 2036
181 | 0 | 0 | 159.2839 | 159.2839 | 33632.8661 | 367.2577 | 66473.6362 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 46541.5047 | 2623.0746 | 545530.6798 | 301154.9963 | 466914.2783 | 257755.5634 | 2037
182 | 0 | 0 | 159.2839 | 159.2839 | 33792.15 | 367.2577 | 66840.8938 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 46406.1534 | 2629.7273 | 546914.2721 | 301040.7596 | 468297.8706 | 257767.5403 | 2037
183 | 0 | 0 | 159.2839 | 159.2839 | 33951.4339 | 367.2577 | 67208.1515 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 46271.1957 | 2636.38 | 548297.8644 | 300924.6404 | 469681.4629 | 257777.2676 | 2037
184 | 0 | 0 | 159.2839 | 159.2839 | 34110.7178 | 367.2577 | 67575.4092 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 46136.6306 | 2643.0327 | 549681.4567 | 300806.6505 | 471065.0552 | 257784.7582 | 2037
185 | 0 | 0 | 159.2839 | 159.2839 | 34270.0017 | 367.2577 | 67942.6668 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 46002.4567 | 2649.6855 | 551065.049 | 300686.8018 | 472448.6475 | 257790.0251 | 2037
186 | 0 | 0 | 159.2839 | 159.2839 | 34429.2856 | 367.2577 | 68309.9245 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 45868.6731 | 2656.3382 | 552448.6413 | 300565.1061 | 473832.2398 | 257793.0812 | 2037
187 | 0 | 0 | 159.2839 | 159.2839 | 34588.5695 | 367.2577 | 68677.1821 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 45735.2785 | 2662.9909 | 553832.2336 | 300441.5751 | 475215.8321 | 257793.9391 | 2037
188 | 0 | 0 | 159.2839 | 159.2839 | 34747.8534 | 367.2577 | 69044.4398 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 45602.2719 | 2669.6436 | 555215.8259 | 300316.2206 | 476599.4244 | 257792.6118 | 2037
189 | 0 | 0 | 159.2839 | 159.2839 | 34907.1373 | 367.2577 | 69411.6974 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 45469.6521 | 2676.2964 | 556599.4182 | 300189.0543 | 477983.0167 | 257789.112 | 2037
190 | 0 | 0 | 159.2839 | 159.2839 | 35066.4212 | 367.2577 | 69778.9551 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 45337.4179 | 2682.9491 | 557983.0105 | 300060.0876 | 479366.609 | 257783.4521 | 2037
191 | 0 | 0 | 159.2839 | 159.2839 | 35225.7051 | 367.2577 | 70146.2128 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 45205.5684 | 2689.6018 | 559366.6028 | 299929.3322 | 480750.2013 | 257775.645 | 2037
192 | 0 | 0 | 159.2839 | 159.2839 | 35384.989 | 367.2577 | 70513.4704 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 45074.1022 | 2696.2545 | 560750.1951 | 299796.7995 | 482133.7936 | 257765.703 | 2037
193 | 0 | 0 | 159.2839 | 159.2839 | 35544.2729 | 367.2577 | 70880.7281 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 44943.0184 | 2702.9073 | 562133.7874 | 299662.5011 | 483517.3859 | 257753.6387 | 2038
194 | 0 | 0 | 159.2839 | 159.2839 | 35703.5568 | 367.2577 | 71247.9857 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 44812.3158 | 2709.56 | 563517.3797 | 299526.4482 | 484900.9782 | 257739.4646 | 2038
195 | 0 | 0 | 159.2839 | 159.2839 | 35862.8407 | 367.2577 | 71615.2434 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 44681.9934 | 2716.2127 | 564900.972 | 299388.6522 | 486284.5705 | 257723.1929 | 2038
196 | 0 | 0 | 159.2839 | 159.2839 | 36022.1246 | 367.2577 | 71982.5011 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 44552.0499 | 2722.8654 | 566284.5643 | 299249.1245 | 487668.1628 | 257704.836 | 2038
197 | 0 | 0 | 159.2839 | 159.2839 | 36181.4085 | 367.2577 | 72349.7587 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 44422.4843 | 2729.5182 | 567668.1566 | 299107.8762 | 489051.7551 | 257684.4062 | 2038
198 | 0 | 0 | 159.2839 | 159.2839 | 36340.6924 | 367.2577 | 72717.0164 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 44293.2955 | 2736.1709 | 569051.7489 | 298964.9186 | 490435.3474 | 257661.9156 | 2038
199 | 0 | 0 | 159.2839 | 159.2839 | 36499.9763 | 367.2577 | 73084.274 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 44164.4825 | 2742.8236 | 570435.3412 | 298820.2627 | 491818.9397 | 257637.3765 | 2038
200 | 0 | 0 | 159.2839 | 159.2839 | 36659.2602 | 367.2577 | 73451.5317 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 44036.044 | 2749.4763 | 571818.9335 | 298673.9197 | 493202.532 | 257610.8009 | 2038
201 | 0 | 0 | 159.2839 | 159.2839 | 36818.5441 | 367.2577 | 73818.7893 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 43907.9791 | 2756.1291 | 573202.5258 | 298525.9006 | 494586.1243 | 257582.201 | 2038
202 | 0 | 0 | 159.2839 | 159.2839 | 36977.828 | 367.2577 | 74186.047 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 43780.2866 | 2762.7818 | 574586.1181 | 298376.2164 | 495969.7166 | 257551.5886 | 2038
203 | 0 | 0 | 159.2839 | 159.2839 | 37137.1119 | 367.2577 | 74553.3047 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 43652.9654 | 2769.4345 | 575969.7105 | 298224.8781 | 497353.3089 | 257518.9758 | 2038
204 | 0 | 0 | 159.2839 | 159.2839 | 37296.3958 | 367.2577 | 74920.5623 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 43526.0145 | 2776.0872 | 577353.3028 | 298071.8964 | 498736.9012 | 257484.3744 | 2038
205 | 0 | 0 | 159.2839 | 159.2839 | 37455.6797 | 367.2577 | 75287.82 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 43399.4329 | 2782.74 | 578736.8951 | 297917.2823 | 500120.4936 | 257447.7963 | 2039
206 | 0 | 0 | 159.2839 | 159.2839 | 37614.9636 | 367.2577 | 75655.0776 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 43273.2193 | 2789.3927 | 580120.4874 | 297761.0465 | 501504.0859 | 257409.2532 | 2039
207 | 0 | 0 | 159.2839 | 159.2839 | 37774.2474 | 367.2577 | 76022.3353 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 43147.3728 | 2796.0454 | 581504.0797 | 297603.1998 | 502887.6782 | 257368.757 | 2039
208 | 0 | 0 | 159.2839 | 159.2839 | 37933.5313 | 367.2577 | 76389.593 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 43021.8923 | 2802.6981 | 582887.672 | 297443.7529 | 504271.2705 | 257326.3192 | 2039
209 | 0 | 0 | 159.2839 | 159.2839 | 38092.8152 | 367.2577 | 76756.8506 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 42896.7767 | 2809.3509 | 584271.2643 | 297282.7163 | 505654.8628 | 257281.9516 | 2039
210 | 0 | 0 | 159.2839 | 159.2839 | 38252.0991 | 367.2577 | 77124.1083 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 42772.0249 | 2816.0036 | 585654.8566 | 297120.1008 | 507038.4551 | 257235.6657 | 2039
211 | 0 | 0 | 159.2839 | 159.2839 | 38411.383 | 367.2577 | 77491.3659 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 42647.636 | 2822.6563 | 587038.4489 | 296955.9169 | 508422.0474 | 257187.473 | 2039
212 | 0 | 0 | 159.2839 | 159.2839 | 38570.6669 | 367.2577 | 77858.6236 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 42523.6088 | 2829.309 | 588422.0412 | 296790.175 | 509805.6397 | 257137.3851 | 2039
213 | 0 | 0 | 159.2839 | 159.2839 | 38729.9508 | 367.2577 | 78225.8813 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 42399.9423 | 2835.9618 | 589805.6335 | 296622.8855 | 511189.232 | 257085.4133 | 2039
214 | 0 | 0 | 159.2839 | 159.2839 | 38889.2347 | 367.2577 | 78593.1389 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 42276.6355 | 2842.6145 | 591189.2258 | 296454.059 | 512572.8243 | 257031.5691 | 2039
215 | 0 | 0 | 159.2839 | 159.2839 | 39048.5186 | 367.2577 | 78960.3966 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 42153.6872 | 2849.2672 | 592572.8181 | 296283.7058 | 513956.4166 | 256975.8637 | 2039
216 | 0 | 0 | 159.2839 | 159.2839 | 39207.8025 | 367.2577 | 79327.6542 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 42031.0965 | 2855.9199 | 593956.4104 | 296111.8361 | 515340.0089 | 256918.3085 | 2039
217 | 0 | 0 | 159.2839 | 159.2839 | 39367.0864 | 367.2577 | 79694.9119 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 41908.8623 | 2862.5727 | 595340.0027 | 295938.4603 | 516723.6012 | 256858.9146 | 2040
218 | 0 | 0 | 159.2839 | 159.2839 | 39526.3703 | 367.2577 | 80062.1695 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 41786.9836 | 2869.2254 | 596723.595 | 295763.5884 | 518107.1935 | 256797.6933 | 2040
219 | 0 | 0 | 159.2839 | 159.2839 | 39685.6542 | 367.2577 | 80429.4272 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 41665.4594 | 2875.8781 | 598107.1873 | 295587.2308 | 519490.7858 | 256734.6557 | 2040
220 | 0 | 0 | 159.2839 | 159.2839 | 39844.9381 | 367.2577 | 80796.6849 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 41544.2885 | 2882.5308 | 599490.7796 | 295409.3976 | 520874.3781 | 256669.8129 | 2040
221 | 0 | 0 | 159.2839 | 159.2839 | 40004.222 | 367.2577 | 81163.9425 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 41423.4701 | 2889.1836 | 600874.3719 | 295230.0987 | 522257.9704 | 256603.1759 | 2040
222 | 0 | 0 | 159.2839 | 159.2839 | 40163.5059 | 367.2577 | 81531.2002 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 41303.003 | 2895.8363 | 602257.9642 | 295049.3443 | 523641.5627 | 256534.7557 | 2040
223 | 0 | 0 | 159.2839 | 159.2839 | 40322.7898 | 367.2577 | 81898.4578 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 41182.8862 | 2902.489 | 603641.5565 | 294867.1442 | 525025.155 | 256464.5632 | 2040
224 | 0 | 0 | 159.2839 | 159.2839 | 40482.0737 | 367.2577 | 82265.7155 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 41063.1188 | 2909.1417 | 605025.1488 | 294683.5086 | 526408.7473 | 256392.6093 | 2040
225 | 0 | 0 | 159.2839 | 159.2839 | 40641.3576 | 367.2577 | 82632.9732 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 40943.6997 | 2915.7945 | 606408.7411 | 294498.4471 | 527792.3396 | 256318.9049 | 2040
226 | 0 | 0 | 159.2839 | 159.2839 | 40800.6415 | 367.2577 | 83000.2308 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 40824.6278 | 2922.4472 | 607792.3334 | 294311.9698 | 529175.9319 | 256243.4607 | 2040
227 | 0 | 0 | 159.2839 | 159.2839 | 40959.9254 | 367.2577 | 83367.4885 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 40705.9023 | 2929.0999 | 609175.9257 | 294124.0863 | 530559.5242 | 256166.2875 | 2040
228 | 0 | 0 | 159.2839 | 159.2839 | 41119.2093 | 367.2577 | 83734.7461 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 40587.522 | 2935.7527 | 610559.518 | 293934.8065 | 531943.1165 | 256087.3959 | 2040
229 | 0 | 0 | 159.2839 | 159.2839 | 41278.4932 | 367.2577 | 84102.0038 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 40469.486 | 2942.4054 | 611943.1103 | 293744.1401 | 533326.7088 | 256006.7967 | 2041
230 | 0 | 0 | 159.2839 | 159.2839 | 41437.7771 | 367.2577 | 84469.2614 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 40351.7933 | 2949.0581 | 613326.7027 | 293552.0967 | 534710.3011 | 255924.5005 | 2041
231 | 0 | 0 | 159.2839 | 159.2839 | 41597.061 | 367.2577 | 84836.5191 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 40234.4428 | 2955.7108 | 614710.295 | 293358.6859 | 536093.8934 | 255840.5177 | 2041
232 | 0 | 0 | 159.2839 | 159.2839 | 41756.3449 | 367.2577 | 85203.7768 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 40117.4336 | 2962.3636 | 616093.8873 | 293163.9173 | 537477.4858 | 255754.8589 | 2041
233 | 0 | 0 | 159.2839 | 159.2839 | 41915.6288 | 367.2577 | 85571.0344 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 40000.7647 | 2969.0163 | 617477.4796 | 292967.8005 | 538861.0781 | 255667.5345 | 2041
234 | 0 | 0 | 159.2839 | 159.2839 | 42074.9127 | 367.2577 | 85938.2921 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 39884.4351 | 2975.669 | 618861.0719 | 292770.3449 | 540244.6704 | 255578.555 | 2041
235 | 0 | 0 | 159.2839 | 159.2839 | 42234.1966 | 367.2577 | 86305.5497 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 39768.4438 | 2982.3217 | 620244.6642 | 292571.56 | 541628.2627 | 255487.9307 | 2041
236 | 0 | 0 | 159.2839 | 159.2839 | 42393.4805 | 367.2577 | 86672.8074 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 39652.7899 | 2988.9745 | 621628.2565 | 292371.4553 | 543011.855 | 255395.6719 | 2041
237 | 0 | 0 | 159.2839 | 159.2839 | 42552.7644 | 367.2577 | 87040.0651 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 39537.4722 | 2995.6272 | 623011.8488 | 292170.0399 | 544395.4473 | 255301.789 | 2041
238 | 0 | 0 | 159.2839 | 159.2839 | 42712.0483 | 367.2577 | 87407.3227 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 39422.49 | 3002.2799 | 624395.4411 | 291967.3233 | 545779.0396 | 255206.2921 | 2041
239 | 0 | 0 | 159.2839 | 159.2839 | 42871.3322 | 367.2577 | 87774.5804 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 39307.8421 | 3008.9326 | 625779.0334 | 291763.3148 | 547162.6319 | 255109.1914 | 2041
240 | 0 | 0 | 159.2839 | 159.2839 | 43030.6161 | 367.2577 | 88141.838 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 39193.5277 | 3015.5854 | 627162.6257 | 291558.0235 | 548546.2242 | 255010.4971 | 2041
241 | 0 | 0 | 159.2839 | 159.2839 | 43189.9 | 367.2577 | 88509.0957 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 39079.5457 | 3022.2381 | 628546.218 | 291351.4587 | 549929.8165 | 254910.2192 | 2042
242 | 0 | 0 | 159.2839 | 159.2839 | 43349.1839 | 367.2577 | 88876.3533 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 38965.8951 | 3028.8908 | 629929.8103 | 291143.6295 | 551313.4088 | 254808.3678 | 2042
243 | 0 | 0 | 159.2839 | 159.2839 | 43508.4678 | 367.2577 | 89243.611 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 38852.5751 | 3035.5435 | 631313.4026 | 290934.5449 | 552697.0011 | 254704.9529 | 2042
244 | 0 | 0 | 159.2839 | 159.2839 | 43667.7517 | 367.2577 | 89610.8687 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 38739.5847 | 3042.1963 | 632696.9949 | 290724.2142 | 554080.5934 | 254599.9845 | 2042
245 | 0 | 0 | 159.2839 | 159.2839 | 43827.0356 | 367.2577 | 89978.1263 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 38626.9228 | 3048.849 | 634080.5872 | 290512.6462 | 555464.1857 | 254493.4724 | 2042
246 | 0 | 0 | 159.2839 | 159.2839 | 43986.3195 | 367.2577 | 90345.384 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 38514.5886 | 3055.5017 | 635464.1795 | 290299.8499 | 556847.778 | 254385.4266 | 2042
247 | 0 | 0 | 159.2839 | 159.2839 | 44145.6034 | 367.2577 | 90712.6416 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 38402.5811 | 3062.1544 | 636847.7718 | 290085.8343 | 558231.3703 | 254275.8567 | 2042
248 | 0 | 0 | 159.2839 | 159.2839 | 44304.8873 | 367.2577 | 91079.8993 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 38290.8993 | 3068.8072 | 638231.3641 | 289870.6083 | 559614.9626 | 254164.7728 | 2042
249 | 0 | 0 | 159.2839 | 159.2839 | 44464.1712 | 367.2577 | 91447.157 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 38179.5423 | 3075.4599 | 639614.9564 | 289654.1807 | 560998.5549 | 254052.1843 | 2042
250 | 0 | 0 | 159.2839 | 159.2839 | 44623.4551 | 367.2577 | 91814.4146 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 38068.5091 | 3082.1126 | 640998.5487 | 289436.5604 | 562382.1472 | 253938.1011 | 2042
251 | 0 | 0 | 159.2839 | 159.2839 | 44782.739 | 367.2577 | 92181.6723 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 37957.7989 | 3088.7653 | 642382.141 | 289217.756 | 563765.7395 | 253822.5329 | 2042
252 | 0 | 0 | 159.2839 | 159.2839 | 44942.0229 | 367.2577 | 92548.9299 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 37847.4106 | 3095.4181 | 643765.7333 | 288997.7764 | 565149.3318 | 253705.4891 | 2042
253 | 0 | 0 | 159.2839 | 159.2839 | 45101.3068 | 367.2577 | 92916.1876 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 37737.3433 | 3102.0708 | 645149.3256 | 288776.6302 | 566532.9241 | 253586.9793 | 2043
254 | 0 | 0 | 159.2839 | 159.2839 | 45260.5907 | 367.2577 | 93283.4452 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 37627.5962 | 3108.7235 | 646532.9179 | 288554.326 | 567916.5164 | 253467.0132 | 2043
255 | 0 | 0 | 159.2839 | 159.2839 | 45419.8746 | 367.2577 | 93650.7029 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 37518.1682 | 3115.3762 | 647916.5102 | 288330.8725 | 569300.1087 | 253345.6 | 2043
256 | 0 | 0 | 159.2839 | 159.2839 | 45579.1585 | 367.2577 | 94017.9606 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 37409.0584 | 3122.029 | 649300.1026 | 288106.2782 | 570683.701 | 253222.7494 | 2043
257 | 0 | 0 | 159.2839 | 159.2839 | 45738.4424 | 367.2577 | 94385.2182 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 37300.266 | 3128.6817 | 650683.6949 | 287880.5517 | 572067.2933 | 253098.4706 | 2043
258 | 0 | 0 | 159.2839 | 159.2839 | 45897.7263 | 367.2577 | 94752.4759 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 37191.7899 | 3135.3344 | 652067.2872 | 287653.7015 | 573450.8856 | 252972.7731 | 2043
259 | 0 | 0 | 159.2839 | 159.2839 | 46057.0102 | 367.2577 | 95119.7335 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 37083.6294 | 3141.9871 | 653450.8795 | 287425.7359 | 574834.478 | 252845.666 | 2043
260 | 0 | 0 | 159.2839 | 159.2839 | 46216.2941 | 367.2577 | 95486.9912 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 36975.7833 | 3148.6399 | 654834.4718 | 287196.6634 | 576218.0703 | 252717.1587 | 2043
261 | 0 | 0 | 159.2839 | 159.2839 | 46375.5779 | 367.2577 | 95854.2489 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 36868.2509 | 3155.2926 | 656218.0641 | 286966.4923 | 577601.6626 | 252587.2605 | 2043
262 | 0 | 0 | 159.2839 | 159.2839 | 46534.8618 | 367.2577 | 96221.5065 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 36761.0312 | 3161.9453 | 657601.6564 | 286735.2311 | 578985.2549 | 252455.9804 | 2043
263 | 0 | 0 | 159.2839 | 159.2839 | 46694.1457 | 367.2577 | 96588.7642 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 36654.1234 | 3168.598 | 658985.2487 | 286502.8879 | 580368.8472 | 252323.3276 | 2043
264 | 0 | 0 | 159.2839 | 159.2839 | 46853.4296 | 367.2577 | 96956.0218 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 36547.5264 | 3175.2508 | 660368.841 | 286269.471 | 581752.4395 | 252189.3112 | 2043
265 | 0 | 0 | 159.2839 | 159.2839 | 47012.7135 | 367.2577 | 97323.2795 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 36441.2395 | 3181.9035 | 661752.4333 | 286034.9887 | 583136.0318 | 252053.9402 | 2044
266 | 0 | 0 | 159.2839 | 159.2839 | 47171.9974 | 367.2577 | 97690.5371 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 36335.2616 | 3188.5562 | 663136.0256 | 285799.4491 | 584519.6241 | 251917.2237 | 2044
267 | 0 | 0 | 159.2839 | 159.2839 | 47331.2813 | 367.2577 | 98057.7948 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 36229.592 | 3195.2089 | 664519.6179 | 285562.8602 | 585903.2164 | 251779.1707 | 2044
268 | 0 | 0 | 159.2839 | 159.2839 | 47490.5652 | 367.2577 | 98425.0525 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 36124.2297 | 3201.8617 | 665903.2102 | 285325.2304 | 587286.8087 | 251639.79 | 2044
269 | 0 | 0 | 159.2839 | 159.2839 | 47649.8491 | 367.2577 | 98792.3101 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 36019.1737 | 3208.5144 | 667286.8025 | 285086.5675 | 588670.401 | 251499.0906 | 2044
270 | 0 | 0 | 159.2839 | 159.2839 | 47809.133 | 367.2577 | 99159.5678 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 35914.4233 | 3215.1671 | 668670.3948 | 284846.8796 | 590053.9933 | 251357.0813 | 2044
271 | 0 | 0 | 159.2839 | 159.2839 | 47968.4169 | 367.2577 | 99526.8254 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 35809.9776 | 3221.8198 | 670053.9871 | 284606.1747 | 591437.5856 | 251213.7709 | 2044
272 | 0 | 0 | 159.2839 | 159.2839 | 48127.7008 | 367.2577 | 99894.0831 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 35705.8355 | 3228.4726 | 671437.5794 | 284364.4607 | 592821.1779 | 251069.1682 | 2044
273 | 0 | 0 | 159.2839 | 159.2839 | 48286.9847 | 367.2577 | 100261.3408 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 35601.9964 | 3235.1253 | 672821.1717 | 284121.7456 | 594204.7702 | 250923.2819 | 2044
274 | 0 | 0 | 159.2839 | 159.2839 | 48446.2686 | 367.2577 | 100628.5984 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 35498.4592 | 3241.778 | 674204.764 | 283878.0371 | 595588.3625 | 250776.1207 | 2044
275 | 0 | 0 | 159.2839 | 159.2839 | 48605.5525 | 367.2577 | 100995.8561 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 35395.2231 | 3248.4307 | 675588.3563 | 283633.3432 | 596971.9548 | 250627.6933 | 2044
276 | 0 | 0 | 159.2839 | 159.2839 | 48764.8364 | 367.2577 | 101363.1137 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 35292.2873 | 3255.0835 | 676971.9486 | 283387.6716 | 598355.5471 | 250478.0082 | 2044
277 | 0 | 0 | 159.2839 | 159.2839 | 48924.1203 | 367.2577 | 101730.3714 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 35189.6508 | 3261.7362 | 678355.5409 | 283141.0301 | 599739.1394 | 250327.074 | 2045
278 | 0 | 0 | 159.2839 | 159.2839 | 49083.4042 | 367.2577 | 102097.6291 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 35087.3128 | 3268.3889 | 679739.1332 | 282893.4264 | 601122.7317 | 250174.8993 | 2045
279 | 0 | 0 | 159.2839 | 159.2839 | 49242.6881 | 367.2577 | 102464.8867 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 34985.2725 | 3275.0416 | 681122.7255 | 282644.8681 | 602506.324 | 250021.4926 | 2045
280 | 0 | 0 | 159.2839 | 159.2839 | 49401.972 | 367.2577 | 102832.1444 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 34883.5288 | 3281.6944 | 682506.3178 | 282395.363 | 603889.9163 | 249866.8623 | 2045
281 | 0 | 0 | 159.2839 | 159.2839 | 49561.2559 | 367.2577 | 103199.402 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 34782.0811 | 3288.3471 | 683889.9101 | 282144.9186 | 605273.5086 | 249711.0168 | 2045
282 | 0 | 0 | 159.2839 | 159.2839 | 49720.5398 | 367.2577 | 103566.6597 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 34680.9284 | 3294.9998 | 685273.5024 | 281893.5425 | 606657.1009 | 249553.9645 | 2045
283 | 0 | 0 | 159.2839 | 159.2839 | 49879.8237 | 367.2577 | 103933.9173 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 34580.0698 | 3301.6525 | 686657.0948 | 281641.2423 | 608040.6932 | 249395.7137 | 2045
284 | 0 | 0 | 159.2839 | 159.2839 | 50039.1076 | 367.2577 | 104301.175 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 34479.5046 | 3308.3053 | 688040.6871 | 281388.0254 | 609424.2855 | 249236.2727 | 2045
285 | 0 | 0 | 159.2839 | 159.2839 | 50198.3915 | 367.2577 | 104668.4327 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 34379.2319 | 3314.958 | 689424.2794 | 281133.8993 | 610807.8779 | 249075.6499 | 2045
286 | 0 | 0 | 159.2839 | 159.2839 | 50357.6754 | 367.2577 | 105035.6903 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 34279.2507 | 3321.6107 | 690807.8717 | 280878.8715 | 612191.4702 | 248913.8534 | 2045
287 | 0 | 0 | 159.2839 | 159.2839 | 50516.9593 | 367.2577 | 105402.948 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 34179.5603 | 3328.2634 | 692191.464 | 280622.9493 | 613575.0625 | 248750.8913 | 2045
288 | 0 | 0 | 159.2839 | 159.2839 | 50676.2432 | 367.2577 | 105770.2056 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 34080.1599 | 3334.9162 | 693575.0563 | 280366.1401 | 614958.6548 | 248586.772 | 2045
289 | 0 | 0 | 159.2839 | 159.2839 | 50835.5271 | 367.2577 | 106137.4633 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 33981.0485 | 3341.5689 | 694958.6486 | 280108.4512 | 616342.2471 | 248421.5033 | 2046
290 | 0 | 0 | 159.2839 | 159.2839 | 50994.811 | 367.2577 | 106504.721 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 33882.2253 | 3348.2216 | 696342.2409 | 279849.8899 | 617725.8394 | 248255.0935 | 2046
291 | 0 | 0 | 159.2839 | 159.2839 | 51154.0949 | 367.2577 | 106871.9786 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 33783.6896 | 3354.8743 | 697725.8332 | 279590.4635 | 619109.4317 | 248087.5506 | 2046
292 | 0 | 0 | 159.2839 | 159.2839 | 51313.3788 | 367.2577 | 107239.2363 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 33685.4404 | 3361.5271 | 699109.4255 | 279330.1792 | 620493.024 | 247918.8826 | 2046
293 | 0 | 0 | 159.2839 | 159.2839 | 51472.6627 | 367.2577 | 107606.4939 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 33587.4769 | 3368.1798 | 700493.0178 | 279069.0441 | 621876.6163 | 247749.0973 | 2046
294 | 0 | 0 | 159.2839 | 159.2839 | 51631.9466 | 367.2577 | 107973.7516 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 33489.7983 | 3374.8325 | 701876.6101 | 278807.0654 | 623260.2086 | 247578.2028 | 2046
295 | 0 | 0 | 159.2839 | 159.2839 | 51791.2305 | 367.2577 | 108341.0092 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 33392.4038 | 3381.4852 | 703260.2024 | 278544.2503 | 624643.8009 | 247406.207 | 2046
296 | 0 | 0 | 159.2839 | 159.2839 | 51950.5144 | 367.2577 | 108708.2669 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 33295.2925 | 3388.138 | 704643.7947 | 278280.6057 | 626027.3932 | 247233.1176 | 2046
297 | 0 | 0 | 159.2839 | 159.2839 | 52109.7983 | 367.2577 | 109075.5246 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 33198.4637 | 3394.7907 | 706027.387 | 278016.1389 | 627410.9855 | 247058.9426 | 2046
298 | 0 | 0 | 159.2839 | 159.2839 | 52269.0822 | 367.2577 | 109442.7822 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 33101.9164 | 3401.4434 | 707410.9793 | 277750.8567 | 628794.5778 | 246883.6896 | 2046
299 | 0 | 0 | 159.2839 | 159.2839 | 52428.3661 | 367.2577 | 109810.0399 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 33005.6499 | 3408.0961 | 708794.5716 | 277484.7661 | 630178.1701 | 246707.3665 | 2046
300 | 0 | 0 | 159.2839 | 159.2839 | 52587.65 | 367.2577 | 110177.2975 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 32909.6634 | 3414.7489 | 710178.1639 | 277217.8741 | 631561.7624 | 246529.9809 | 2046
301 | 0 | 0 | 159.2839 | 159.2839 | 52746.9339 | 367.2577 | 110544.5552 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 32813.956 | 3421.4016 | 711561.7562 | 276950.1877 | 632945.3547 | 246351.5405 | 2047
302 | 0 | 0 | 159.2839 | 159.2839 | 52906.2178 | 367.2577 | 110911.8129 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 32718.527 | 3428.0543 | 712945.3485 | 276681.7136 | 634328.947 | 246172.0529 | 2047
303 | 0 | 0 | 159.2839 | 159.2839 | 53065.5017 | 367.2577 | 111279.0705 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 32623.3755 | 3434.7071 | 714328.9408 | 276412.4588 | 635712.5393 | 245991.5258 | 2047
304 | 0 | 0 | 159.2839 | 159.2839 | 53224.7856 | 367.2577 | 111646.3282 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 32528.5007 | 3441.3598 | 715712.5331 | 276142.4299 | 637096.1316 | 245809.9666 | 2047
305 | 0 | 0 | 159.2839 | 159.2839 | 53384.0695 | 367.2577 | 112013.5858 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 32433.9018 | 3448.0125 | 717096.1254 | 275871.6339 | 638479.7239 | 245627.383 | 2047
306 | 0 | 0 | 159.2839 | 159.2839 | 53543.3534 | 367.2577 | 112380.8435 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 32339.5781 | 3454.6652 | 718479.7177 | 275600.0775 | 639863.3162 | 245443.7825 | 2047
307 | 0 | 0 | 159.2839 | 159.2839 | 53702.6373 | 367.2577 | 112748.1011 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 32245.5286 | 3461.318 | 719863.31 | 275327.7674 | 641246.9085 | 245259.1724 | 2047
308 | 0 | 0 | 159.2839 | 159.2839 | 53861.9212 | 367.2577 | 113115.3588 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 32151.7527 | 3467.9707 | 721246.9023 | 275054.7102 | 642630.5008 | 245073.5602 | 2047
309 | 0 | 0 | 159.2839 | 159.2839 | 54021.2051 | 367.2577 | 113482.6165 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 32058.2494 | 3474.6234 | 722630.4946 | 274780.9126 | 644014.0931 | 244886.9534 | 2047
310 | 0 | 0 | 159.2839 | 159.2839 | 54180.489 | 367.2577 | 113849.8741 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 31965.0181 | 3481.2761 | 724014.087 | 274506.3812 | 645397.6854 | 244699.3591 | 2047
311 | 0 | 0 | 159.2839 | 159.2839 | 54339.7729 | 367.2577 | 114217.1318 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 31872.058 | 3487.9289 | 725397.6793 | 274231.1227 | 646781.2777 | 244510.7849 | 2047
312 | 0 | 0 | 159.2839 | 159.2839 | 54499.0568 | 367.2577 | 114584.3894 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 31779.3681 | 3494.5816 | 726781.2716 | 273955.1435 | 648164.8701 | 244321.2379 | 2047
313 | 0 | 0 | 159.2839 | 159.2839 | 54658.3407 | 367.2577 | 114951.6471 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 31686.9479 | 3501.2343 | 728164.8639 | 273678.4502 | 649548.4624 | 244130.7255 | 2048
314 | 0 | 0 | 159.2839 | 159.2839 | 54817.6246 | 367.2577 | 115318.9048 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 31594.7964 | 3507.887 | 729548.4562 | 273401.0492 | 650932.0547 | 243939.2548 | 2048
315 | 0 | 0 | 159.2839 | 159.2839 | 54976.9084 | 367.2577 | 115686.1624 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 31502.9129 | 3514.5398 | 730932.0485 | 273122.9471 | 652315.647 | 243746.833 | 2048
316 | 0 | 0 | 159.2839 | 159.2839 | 55136.1923 | 367.2577 | 116053.4201 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 31411.2966 | 3521.1925 | 732315.6408 | 272844.1502 | 653699.2393 | 243553.4672 | 2048
317 | 0 | 0 | 159.2839 | 159.2839 | 55295.4762 | 367.2577 | 116420.6777 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 31319.9468 | 3527.8452 | 733699.2331 | 272564.6649 | 655082.8316 | 243359.1647 | 2048
318 | 0 | 0 | 159.2839 | 159.2839 | 55454.7601 | 367.2577 | 116787.9354 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 31228.8626 | 3534.4979 | 735082.8254 | 272284.4977 | 656466.4239 | 243163.9324 | 2048
319 | 0 | 0 | 159.2839 | 159.2839 | 55614.044 | 367.2577 | 117155.193 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 31138.0433 | 3541.1507 | 736466.4177 | 272003.6548 | 657850.0162 | 242967.7775 | 2048
320 | 0 | 0 | 159.2839 | 159.2839 | 55773.3279 | 367.2577 | 117522.4507 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 31047.4881 | 3547.8034 | 737850.01 | 271722.1425 | 659233.6085 | 242770.7069 | 2048
321 | 0 | 0 | 159.2839 | 159.2839 | 55932.6118 | 367.2577 | 117889.7084 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 30957.1963 | 3554.4561 | 739233.6023 | 271439.9671 | 660617.2008 | 242572.7276 | 2048
322 | 0 | 0 | 159.2839 | 159.2839 | 56091.8957 | 367.2577 | 118256.966 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 30867.167 | 3561.1088 | 740617.1946 | 271157.1348 | 662000.7931 | 242373.8466 | 2048
323 | 0 | 0 | 159.2839 | 159.2839 | 56251.1796 | 367.2577 | 118624.2237 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 30777.3996 | 3567.7616 | 742000.7869 | 270873.6519 | 663384.3854 | 242174.0708 | 2048
324 | 0 | 0 | 159.2839 | 159.2839 | 56410.4635 | 367.2577 | 118991.4813 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 30687.8933 | 3574.4143 | 743384.3792 | 270589.5245 | 664767.9777 | 241973.4071 | 2048
325 | 0 | 0 | 159.2839 | 159.2839 | 56569.7474 | 367.2577 | 119358.739 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 30598.6472 | 3581.067 | 744767.9715 | 270304.7588 | 666151.57 | 241771.8623 | 2049
326 | 0 | 0 | 159.2839 | 159.2839 | 56729.0313 | 367.2577 | 119725.9967 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 30509.6607 | 3587.7197 | 746151.5638 | 270019.3608 | 667535.1623 | 241569.4433 | 2049
327 | 0 | 0 | 159.2839 | 159.2839 | 56888.3152 | 367.2577 | 120093.2543 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 30420.933 | 3594.3725 | 747535.1561 | 269733.3367 | 668918.7546 | 241366.1568 | 2049
328 | 0 | 0 | 159.2839 | 159.2839 | 57047.5991 | 367.2577 | 120460.512 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 30332.4633 | 3601.0252 | 748918.7484 | 269446.6926 | 670302.3469 | 241162.0096 | 2049
329 | 0 | 0 | 159.2839 | 159.2839 | 57206.883 | 367.2577 | 120827.7696 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 30244.2509 | 3607.6779 | 750302.3407 | 269159.4344 | 671685.9392 | 240957.0085 | 2049
330 | 0 | 0 | 159.2839 | 159.2839 | 57366.1669 | 367.2577 | 121195.0273 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 30156.295 | 3614.3306 | 751685.933 | 268871.5681 | 673069.5315 | 240751.1601 | 2049
331 | 0 | 0 | 159.2839 | 159.2839 | 57525.4508 | 367.2577 | 121562.2849 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 30068.595 | 3620.9834 | 753069.5253 | 268583.0998 | 674453.1238 | 240544.4711 | 2049
332 | 0 | 0 | 159.2839 | 159.2839 | 57684.7347 | 367.2577 | 121929.5426 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 29981.15 | 3627.6361 | 754453.1176 | 268294.0353 | 675836.7161 | 240336.9481 | 2049
333 | 0 | 0 | 159.2839 | 159.2839 | 57844.0186 | 367.2577 | 122296.8003 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 29893.9592 | 3634.2888 | 755836.7099 | 268004.3805 | 677220.3084 | 240128.5977 | 2049
334 | 0 | 0 | 159.2839 | 159.2839 | 58003.3025 | 367.2577 | 122664.0579 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 29807.0221 | 3640.9415 | 757220.3022 | 267714.1414 | 678603.9007 | 239919.4265 | 2049
335 | 0 | 0 | 159.2839 | 159.2839 | 58162.5864 | 367.2577 | 123031.3156 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 29720.3378 | 3647.5943 | 758603.8945 | 267423.3238 | 679987.493 | 239709.441 | 2049
336 | 0 | 0 | 159.2839 | 159.2839 | 58321.8703 | 367.2577 | 123398.5732 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 29633.9055 | 3654.247 | 759987.4869 | 267131.9334 | 681371.0853 | 239498.6477 | 2049
337 | 0 | 0 | 159.2839 | 159.2839 | 58481.1542 | 367.2577 | 123765.8309 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 29547.7247 | 3660.8997 | 761371.0792 | 266839.9762 | 682754.6776 | 239287.0532 | 2050
338 | 0 | 0 | 159.2839 | 159.2839 | 58640.4381 | 367.2577 | 124133.0886 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 29461.7945 | 3667.5524 | 762754.6715 | 266547.4578 | 684138.27 | 239074.6638 | 2050
339 | 0 | 0 | 159.2839 | 159.2839 | 58799.722 | 367.2577 | 124500.3462 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 29376.1141 | 3674.2052 | 764138.2638 | 266254.384 | 685521.8623 | 238861.4859 | 2050
340 | 0 | 0 | 159.2839 | 159.2839 | 58959.0059 | 367.2577 | 124867.6039 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 29290.683 | 3680.8579 | 765521.8561 | 265960.7604 | 686905.4546 | 238647.526 | 2050
341 | 0 | 0 | 159.2839 | 159.2839 | 59118.2898 | 367.2577 | 125234.8615 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 29205.5002 | 3687.5106 | 766905.4484 | 265666.5929 | 688289.0469 | 238432.7904 | 2050
342 | 0 | 0 | 159.2839 | 159.2839 | 59277.5737 | 367.2577 | 125602.1192 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 29120.5653 | 3694.1633 | 768289.0407 | 265371.887 | 689672.6392 | 238217.2854 | 2050
343 | 0 | 0 | 159.2839 | 159.2839 | 59436.8576 | 367.2577 | 125969.3768 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 29035.8773 | 3700.8161 | 769672.633 | 265076.6483 | 691056.2315 | 238001.0172 | 2050
344 | 0 | 0 | 159.2839 | 159.2839 | 59596.1415 | 367.2577 | 126336.6345 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 28951.4356 | 3707.4688 | 771056.2253 | 264780.8824 | 692439.8238 | 237783.9923 | 2050
345 | 0 | 0 | 159.2839 | 159.2839 | 59755.4254 | 367.2577 | 126703.8922 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 28867.2395 | 3714.1215 | 772439.8176 | 264484.5949 | 693823.4161 | 237566.2167 | 2050
346 | 0 | 0 | 159.2839 | 159.2839 | 59914.7093 | 367.2577 | 127071.1498 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 28783.2882 | 3720.7742 | 773823.4099 | 264187.7913 | 695207.0084 | 237347.6968 | 2050
347 | 0 | 0 | 159.2839 | 159.2839 | 60073.9932 | 367.2577 | 127438.4075 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 28699.5811 | 3727.427 | 775207.0022 | 263890.4772 | 696590.6007 | 237128.4386 | 2050
348 | 0 | 0 | 159.2839 | 159.2839 | 60233.2771 | 367.2577 | 127805.6651 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 28616.1174 | 3734.0797 | 776590.5945 | 263592.658 | 697974.193 | 236908.4483 | 2050
349 | 0 | 0 | 159.2839 | 159.2839 | 60392.561 | 367.2577 | 128172.9228 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 28532.8965 | 3740.7324 | 777974.1868 | 263294.3391 | 699357.7853 | 236687.732 | 2051
350 | 0 | 0 | 159.2839 | 159.2839 | 60551.8449 | 367.2577 | 128540.1805 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 28449.9176 | 3747.3851 | 779357.7791 | 262995.526 | 700741.3776 | 236466.2959 | 2051
351 | 0 | 0 | 159.2839 | 159.2839 | 60711.1288 | 367.2577 | 128907.4381 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 28367.18 | 3754.0379 | 780741.3714 | 262696.2241 | 702124.9699 | 236244.1459 | 2051
352 | 0 | 0 | 159.2839 | 159.2839 | 60870.4127 | 367.2577 | 129274.6958 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 28284.683 | 3760.6906 | 782124.9637 | 262396.4388 | 703508.5622 | 236021.2881 | 2051
353 | 0 | 0 | 159.2839 | 159.2839 | 61029.6966 | 367.2577 | 129641.9534 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 28202.4259 | 3767.3433 | 783508.556 | 262096.1754 | 704892.1545 | 235797.7285 | 2051
354 | 0 | 0 | 159.2839 | 159.2839 | 61188.9805 | 367.2577 | 130009.2111 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 28120.408 | 3773.996 | 784892.1483 | 261795.4391 | 706275.7468 | 235573.473 | 2051
355 | 0 | 0 | 159.2839 | 159.2839 | 61348.2644 | 367.2577 | 130376.4688 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 28038.6287 | 3780.6488 | 786275.7406 | 261494.2354 | 707659.3391 | 235348.5276 | 2051
356 | 0 | 0 | 159.2839 | 159.2839 | 61507.5483 | 367.2577 | 130743.7264 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 27957.0872 | 3787.3015 | 787659.3329 | 261192.5695 | 709042.9314 | 235122.8982 | 2051
357 | 0 | 0 | 159.2839 | 159.2839 | 61666.8322 | 367.2577 | 131110.9841 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 27875.7828 | 3793.9542 | 789042.9252 | 260890.4465 | 710426.5237 | 234896.5906 | 2051
358 | 0 | 0 | 159.2839 | 159.2839 | 61826.1161 | 367.2577 | 131478.2417 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 27794.7149 | 3800.6069 | 790426.5175 | 260587.8718 | 711810.116 | 234669.6108 | 2051
359 | 0 | 0 | 159.2839 | 159.2839 | 61985.4 | 367.2577 | 131845.4994 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 27713.8828 | 3807.2597 | 791810.1098 | 260284.8505 | 713193.7083 | 234441.9646 | 2051
360 | 0 | 0 | 159.2839 | 159.2839 | 62144.6839 | 367.2577 | 132212.757 | 207.9738 | 56248.1944 | 106.1893 | 2.6333 | 22368.2071 | 78616.4015 | 27633.2857 | 3813.9124 | 793193.7021 | 259981.3877 | 714577.3006 | 234213.6577 | 2051
0

## Output
Water Loss Volumetric Performance Standard
|  | Current leakage level (gallons per connection per day) | Current leakage level (gallons per mile per day) |  | Average annual leakage reduced with active leak detection and repair (acre-feet per year) | Water loss volumetric performance standard - 2028 (gallons per connection per day) | Water loss volumetric performance standard - 2028 (gallons per mile per day)
|  | 31.9273 | N/A |  | 2335.6024 | 24.2599 | N/A
| Years | Estimated real loss for distribution system |  |  | Benefit/Cost Ratio over 30 years
|  | (acre-feet per year) | (gallons per connection per day) | (gallons per mile per day) | 5.4319
| 2022 | 10171 | 31.9273 | N/A
| 2028 | 7728.4095 | 24.2599 | N/A | Benefit/Cost Ratio over 20 years
4.6973
Benefit/Cost Ratio over 10 years
3.7068
Benefit/Cost Ratio over 5 years
2.822
If there is no net benefit for additional interventions towards active leak detection and repair by the supplier, the volumetric standard remains the same as the current leakage level.

## Equations
Equations in the model
Term | Formula | References as applicable
Tab: Calculation
Total background leakage (acre-feet per year)
Reported leakage (acre-feet per year) |  | Equation (7-5), AWWA M36 Manual, 2016
Unreported leakage (acre-feet per year) |  | Table 3-22, AWWA M36 Manual, 2016
Unreported leakage fraction for the system
Unreported leaks found per mile per year
Time taken to survey full distribution system (months)
Water loss due to backlog of leakage in unsurveyed parts in each time step (acre-feet) |  | See row 32 for calculation
Water loss due to natural rise in leakage in never surveyed parts in each time step (acre-feet)
Water loss due to natural rise in leakage in previously surveyed parts in each time step (acre-feet)
Total water loss occuring in time step with intervention (acre-feet)
Water loss occuring without intervention in each time step (acre-feet)
Water saved due to water loss control in each time step (acre-feet) | Total water loss occuring in time step with intervention - Water loss occuring without intervention in each time step
Intitial leakage level for part surveyed during time step (acre-feet)
Leaks found per part per system
Incremental cost associated with leak repair in each time step ($)
Cost associated with leak repair in each time step ($)
Cost associated with leak detection and repair in each time step ($) | Cost associated with leak detection per part + Cost associated with leak repair in each time step
Marginal cost of water including rising cost and avoided cost of alternative supplies (at the beginning of 2022) ($ per acre-feet)
Marginal cost of water including rising cost and avoided cost of alternative supplies (for each incremental month after 2022 begins) ($ per acre-feet)
Value of water loss reduced in each time step ($)
Net benefit for each time step ($)
Net Present Value of net benefit corresponding to each time step ($)
Tab: Output
Benefit/Cost Ratio
Figure: Rise in leakage in parts of the system never surveyed before.
Figure: Rise in leakage in parts of the system that have been surveyed before.
(0.2×Total length of mains (miles)+0.008×Number of service connections)×((Average operational pressure)/70)^1.5
×Infrastructure Condition Factor
×(1000 gallons)/(325851 acrefeet)×(365 days)/year
(50 gallons )/(burst∙minute)×(1 acrefeet)/(325,851 gallons)×(0.2 bursts)/(mile∙year)×Total length of mains (miles)×(60 minutes)/hour×(24 hours)/day×(3 days)/year
Three year average leakage −total background leakage−reported leakage
(Unreported leakage component)/((Background leakage component+Reported leakage component+Unreported leakage component))
(Average unreported leakage for supplier (acrefeet per year))/(Average total flow rate for unreported leaks (acrefeet per year)×Total length of mains (miles))
(Total length of mains (miles))/(Maximum average leak detection survey frequency (miles per month))
(Number of parts of system −current incremental time step )×Leakage per part of system×Time step
(Number of parts in system−current incremental time step+1)×annual average rise in leakage per part of system
×(current incremental time step−1/2)×(time step)^2
Before entire system is surveyed once:
Before entire system is surveyed once:
Annual average natural rise in leakage per part of system×〖time step〗^2×〖(current incremental time step−1)^2/2 〗^
After entire system is surveyed once:
After entire system is surveyed once:
Annual average natural rise in leakage per part of system×〖time step〗^2×〖〖number of parts in system〗^2/2 〗^
Number of parts in system×time step×(three year average leakage per part of system+Annual average rise in leakage per part of system×(current incremental time step− 1/2)×timestep)
Before entire system is surveyed once:
Before entire system is surveyed once:
(Unreported leakage for supplier)/(Number of parts of the system surveyed in each cycle)
+𝑐𝑢𝑟𝑟𝑒𝑛𝑡 𝑖𝑛𝑐𝑟𝑒𝑚𝑒𝑛𝑡𝑎𝑙 𝑡𝑖𝑚𝑒 𝑠𝑡𝑒𝑝×𝑡𝑖𝑚𝑒 𝑠𝑡𝑒𝑝×𝑎𝑛𝑛𝑢𝑎𝑙 𝑎𝑣𝑒𝑟𝑎𝑔𝑒 𝑟𝑖𝑠𝑒 𝑖𝑛 𝑙𝑒𝑎𝑘𝑎𝑔𝑒 𝑝𝑒𝑟 𝑝𝑎𝑟𝑡 𝑜𝑓 𝑠𝑦𝑠𝑡𝑒𝑚
After entire system is surveyed once:
After entire system is surveyed once:
Annual average rise in leakage in each part×time step×Number of parts of system surveyed in each cycle
(Intitial leakage level for part surveyed during time step)/(Average flow rate for reported leaks per leak)
Leaks found per part of system×(Repair costs per mile)/(Efficiency of leak detection equipment)
(Cost of leak repair for each part)/(1+discount rate×time step)^((time step×current incremental time step) )
(Avoided cost of alternative supplies)/((1+Average annual rise in price of water×current incremental time step×24 months from 2020×time step) )
(Avoided cost of alternative supplies)/((1+Average annual rise in price of water×(current incremental time step−1)×time step) )
Water saved due to water loss control in each time step×Marginal cost of water in each time step
Value of cost associated with leak detection and repair in each time step −Value of water loss reduced in each time step
(Total present value of value of water)/(Total present value of total cost of leak detection and repair)
The water loss occuring in any year is calculated by adding up the water loss occuring in each time step in that year.
Water loss due to backlog of leakage in unsurveyed parts in each time step
+ Water loss due to natural rise in leakage in never surveyed parts in each time step
+ Water loss due to natural rise in leakage in previously surveyed parts in each time step
The water loss occuring in any year is calculated by adding up the water loss occuring in each time step in that year.
Calculation of water lost at every time step with intervention
Variables used:
N = Number of parts into which the distribution system is divided (based on rate of surveying)
ΔT = time between surveys
Lo = Initial total unreported leakage
lo = Initial unreported leakage per part =
R = Natural rise in leakage for the entire system
r = Rate of natural rise of leakage per part =
The general method used is as follows:
It is assumed, for simplicity, that at any point in time, a part of the system is being surveyed. The rate of surveying is an average rate for the entire system.
The model determines the economically achievable volumetric water loss by calculating how much water loss occurs at that time. Thus, the 2027 standard is calculated by calculating the water loss occurring at the time step coinciding with the beginning of 2027.
The model divides the water lost during regular leak detection and surveying into three elements for ease of calculation:
  Water lost due to backlog of unreported leakage
  Water lost due to natural rise in leakage for the never surveyed parts of the system (for the first survey)
  Water lost due to natural rise in leakage for rest of the parts of the system not being surveyed in current time step
An equation is developed to represent water loss occurring in one part, after which the water loss is summed up to represent the entire system. ‘i’ represents the current time step, so that we can develop a general formula for each of these categories. The spreadsheet uses these formulae in columns 2 through 4 (B through D)
Water lost due to backlog of unreported leakage:
The schematic shows how the backlog unreported leakage for the entire system is impacted after each part of the system is surveyed. Note that the backlog element considered here does not include any rise in leakage, as elements including rising leakage are calculated separately.
Calculation of water lost at every time step with intervention
Variables used:
N = Number of parts into which the distribution system is divided (based on rate of surveying)
ΔT = time between surveys
Lo = Initial total unreported leakage
lo = Initial unreported leakage per part = Lo/N
R = Natural rise in leakage for the entire system
r = Rate of natural rise of leakage per part = R/N
The general method used is as follows:
It is assumed, for simplicity, that at any point in time, a part of the system is being surveyed. The rate of surveying is an average rate for the entire system.
The model determines the economically achievable volumetric water loss by calculating how much water loss occurs at that time. Thus, the 2027 standard is calculated by calculating the water loss occurring at the time step coinciding with the beginning of 2027.
The model divides the water lost during regular leak detection and surveying into three elements for ease of calculation:
  Water lost due to backlog of unreported leakage
  Water lost due to natural rise in leakage for the never surveyed parts of the system (for the first survey)
  Water lost due to natural rise in leakage for rest of the parts of the system not being surveyed in current time step
An equation is developed to represent water loss occurring in one part, after which the water loss is summed up to represent the entire system. ‘i’ represents the current time step, so that we can develop a general formula for each of these categories. The spreadsheet uses these formulae in columns 2 through 4 (B through D)
Water lost due to backlog of unreported leakage:
The schematic shows how the backlog unreported leakage for the entire system is impacted after each part of the system is surveyed. Note that the backlog element considered here does not include any rise in leakage, as elements including rising leakage are calculated separately.
Figure: Decrease in backlog unreported leakage as each part of the distribution system is surveyed
As parts of the system are surveyed serially, the overall backlog of unreported leakage drops by lo in each time step (the backlog unreported leakage per part).
At time step ‘i’, the survey would begin for the ith part of the system. Thus, the only leakage would be from the parts that have not been surveyed yet (N - i), and the one part to be surveyed by the end of the current time step.
Number of parts not surveyed yet = (N – i) + 1
Each part will leak at lo for the time during the current time step ΔT.
The water loss occurring in time step 1 due to backlog leakage only is represented as:
ΔT x lo x (N – i + 1)
Water lost due to natural rise in leakage for the never surveyed parts of the system
Till the beginning of time step ‘i’, (i – 1) parts have been surveyed.
Water loss in parts of the system never surveyed:
Leakage level for each part has been increasing as the rate of rise of leakage, till the part is surveyed. Thus, for a time step, all the parts which have not been surveyed before will be leakage at the same leakage level.
During the first survey, while the ‘i’th part is being surveyed, (i-1) parts have been surveyed. Hence, out of ‘N’ parts, (N - i +1) parts remain to be surveyed and have been leaking due to the naturally rising leakage.
The total leakage due to this component is:
After the entire system is surveyed once, this component becomes zero.
Water lost only due to natural rise in leakage in parts of the system surveyed previously:
Each part of the system starts leaking after a survey as the leakage rises naturally in the distribution system after being surveyed. The leakage occurring in each time step is the rise in leakage that occurs over that time step for all parts in the system.
The following schematic shows how leakage occurs in different parts of the system that were surveyed at different times.
The rise in leakage to the beginning of the time step is represented by: Rate of rise of leakage x time passed prior to current time step
If ‘i’ time steps have passed, time passed after ‘i’ time steps = i x ΔT
The leakage level only due to natural rise in leakage, at the beginning of the ‘i’th step, or at the end of the (i-1)th step is = r x (i-1) x ΔT
The leakage level at the end of the ‘i’th step is = r x i x ΔT.
The leakage volume lost during this time step is represented by the transition from the lower leakage level to the higher leakage level across time step ΔT, which is the area under the curve summed for all the parts of the system.
Each part of the system will contribute to the overall leakage in this component as follows:
Where the leakage volume lost during the ‘j’th step for a single part is:
If the distribution system is being surveyed for the first time, only ‘(i-1)’ parts have been surveyed when the ‘i’th step begins, and will contribute to this element of leakage:
The summation of an integer is represented by:
The summation of a constant is represented by:
Thus,
If the system has undergone a complete survey and this is the next round of surveying, ‘N’ parts have been surveyed before, and all will contribute to this element of leakage. After one survey, and the backlog of leakage is reduced, this element of leakage is the only one that constitutes the overall leakage for the distribution system:
Water loss occurring without intervention:
Without any intervention, the real loss for the system increases from the initial real loss (three-year average of real loss reported by supplier) increases with time at the natural rate of rise of leakage.
The water loss occurring in a time step without any intervention is represented by the transition from the lower leakage level to the higher leakage level across time step ΔT, which is the area under the curve summed for all the parts of the system.
To determine the leakage occurring in time step ‘i’:
The leakage level rises to lo + r x (i-1) x ΔT by the beginning of the ‘i’th step.
The leakage level then rises to lo + r x (i) x ΔT by the end of the ‘i’th step.
The water loss occurring during the time step is:
For ‘N’ parts, the total leakage without intervention would be:
(Net benefit)/((1+Average annual rise in price of water×(current incremental time step−1)×time step) )

## CollectedData_References
Collected Data |  | (Scroll down for additional references for 'Input tab")
Rise in price of water, based on historical rates for Tier 1 Treated Water rates for water sold by the Metropolitan Water District
consumer price index for 2019 |  | 187.445 | (From the Bureau of Labor Statistics, https://www.bls.gov/cpi/data.htm
Year | Price (Tier 1, treated) | Consumer price indices (commodities) | Real price as 2019$ | Percent increase | Source: Metropolitan Water district, Historical Water rates, obtained from Metropolitan Water District
2008 | 579 | 173.193 | 626.6457
2009 | 701 | 168.093 | 781.7038 | 24.74%
2010 | 701 | 172.129 | 763.3748 | -2.345%
2011 | 744 | 180.192 | 773.9471 | 1.385%
2012 | 794 | 183.705 | 810.1648 | 4.68%
2013 | 847 | 183.443 | 865.4782 | 6.827%
2014 | 890 | 183.92 | 907.0577 | 4.804%
2015 | 923 | 180.26 | 959.7899 | 5.814%
2016 | 942 | 178.01 | 991.9285 | 3.348%
2017 | 979 | 180.509 | 1016.6178 | 2.489%
2018 | 1015 | 184.966 | 1028.6035 | 1.179%
Average annual price increase (2008-2018) |  | 5.293%
Avoided Cost of Water
Stormwater: $590 per acre-feet
Indirect potable reuse: $1800 per acre-feet
Brackish water desalination: $1100 per acre-feet
Imported water (Based on estimates for 2019 from the Meteropilatan Water District): $ 1015 per acre-feet
Average avoided cost ($): |  | 1126.25
Typical number of miles surveyed per day
Services provided by Municipal Water District of Orange County: 10 miles a week ~ 2 miles a day ~ 40 miles per month
Services provided by M.E. Simpson: 5 miles a day ~ 100 miles per month
Irvine Ranch Water District: 3.5 miles per day ~ 70 miles per month
East Bay Municipal Utility District: 74 miles of manual surveying; 61 miles of automated acoustic surveying; 1236 miles of satellite surveying throughout the year ~ 114.25 miles per month
The following surveying schedule has been planned for member agencies of the Municipal Water District of Orange county
Agency | Total length of mains (Miles) | Target Miles (Annual) | % of system planned to be surveyed annually
Seal Beach | 75 | 75 | 100%
TCWD | 66 | 66.5 | 100.8%
La Habra | 165 | 83 | 50.3%
Tustin | 172 | 102 | 59.3%
EOCWD | 23.7 | 48 | 202.5%
Huntington Beach | 607.2 | 18 | 2.964%
Mesa | 328.4 | 32 | 9.744%
Orange | 462 | 30 | 6.494%
San Clemente | 212.6 | 30 | 14.11%
YLWD | 367.1 | 110 | 29.96%
Systems above 6000 miles of dstribution pipeline:
Los Angeles Department of Water and Power is the only system with distribution system pipeline greater than 6000 miles. As per conversations, LADWP is currently planning its active leak detection program. To address the size of the system, and estimate a reasonable leak detection survey rate, staff compared its total operating cost with that of East Bay Municipal Utility District. LADWP has an operating budget of $1,194,818,812 per year, and EBMUD has an operating budget of $345,821,000 per year, and surveys 114 miles per month. LADWP has about 3.5 the operating budget of EBMUD, hence staff estimated a leak detection survey rate of about 15 additional miles per month, rounded up to 130 miles per month.
Leak detection costs - Summary (Scroll down for individual vendor quotes)
Equipment type | Lifecycle | Efficiency range | Cost | Cost per mile | Average efficiency
Leak Survey | 4 - 7 years | 98 - 99%a | $170 - $595c / Mile | 595 | 98.5
Leak Pinpoint | 9 - 10 years | 50 - 92%b | $347 - $991d /Leak | 9.91 | 71 | Based on an average of 0.01 leaks found per mile (AWWA M36, Table 3-22)
|  |  | Total average cost | 604.91 | 69.93% | Product of efficiencies for surveying and pinpointing
a. Highly trained and experienced staff.
b. Expected Efficiency of a new program (variable).
c/d. Costs (low range) are typically utilities that do not include detection equipment cost. Variances in costs are also due to size of
survey, type of pipe material and logistical issues withing the water system.
Vendor - Subsurface
Type | Item No. | Equipment | Part # | Items Incld. | Unit Cost | Upfront Cost | Labor | External Vendor
Acoustic Leak Detection | 1 | Listening Rod + Ground Microphones | LD-12a | 1 | 3695 |  | 50 < miles $278 / mi 50 > 100 mile $350 / mi 100 > miles $300 / mi | $295 / mile for metal pipes $595 / mile for non-metallic pipe
|  |  | w/ optional 6ft sensor cable |  | 35
| 2 |  | LD-15b | 1 | 3750
|  |  | 40 in. extension rod |  | 75
|  |  | 60 in. extension rod |  | 95
|  |  | Sensor w/ steel base & adapter |  | 30
| 3 |  | LD-18b | 1 | 5995
|  |  | Sensor w/ magnet & 9.8 ft cable |  | 750
|  |  | 40 in. extension rod |  | 105
|  |  | 60 in. extension rod |  | 125
Correlator | 4 | Leak Noise Correlators | ZCorr3c | 3 | 8495 |  | $347 / Leak
| 5 |  | ZCorr8d | 8 | 15995
| 6 |  | LC-5000 | 4 | 32000
a. LD-12 Series includes apmlifier, meter display unit, ground microphone, headphones, 10mm nutfriver, aluminum sensor base and 39" contact rod.
b. LD-15/18 Series includes apmlifier w/meter display unit, 9.75 ft long cable, base plate, and headphones.
c. ZCorr3 includes 3 digital correlating loggers, 1 docking station (supports up to 8 loggers) and basic software.
d. ZCorr8 includes 8 digital correlating loggers, 1 docking station (supports up to 8 loggers) and PRO software.
e. LC-5000 includes 4 wireless/GPS correlator (real time and programmable), 5 charging cables and headphones.
* Pricing does not include applicable taxes or shipping costs.
http://www.subsurfaceleak.com/waterleakdetec.html
Vendor - Sewerin
Type | Item No. | Equipment | Part # | Items Incld. | Unit Cost | Labor | External Vendor | DI | PVC | AC | Median | Average
Acoustic & Special Leak dectetion | 1 | Stethophon 04 Kita | EA15-10002B |  | 1415 | 50 < miles $278 / mi 50 > 100 mile $350 / mi 100 > miles $300 / mi | $295 / mile for metal pipes $595 / mile for non-metallic pipe | 87.5% | 76.5% | 69.2% | 76.5% | 77.73%
|  |  | EA15-10002S |  | 1885
|  |  | EA15-10002C |  | 1969
| 2 | Stethophon 04 SDR Kita | EA15-10102B |  | 1766
|  |  | EA15-10102S |  | 2236
|  |  | EA15-10102C |  | 2320
| 3 | Aqua Test T-10 Kitb | EA16-10002B |  | 2352
|  |  | EA16-10002C |  | 2634
|  |  | EA16-10002P |  | 3049
| 4 | Aqua Test T-10 SDR Kitb | EA16-10102B |  | 2885
|  |  | EA16-10102C |  | 3167
|  |  | EA16-10102P |  | 3581
| 5 | Aquaphon A50 Kit "Entry Level Pro." | EA50-10002BP |  | 3225
|  |  | EA50-10002C |  | 3969
|  |  | EA50-10002P |  | 4996
| 6 | Aquaphon A50 SDR Kit | EA50-10011B |  | 3708
|  |  | EA50-10011C |  | 4478
|  |  | EA50-10011P |  | 5506
| 7 | Aquaphon A100 Pro Kit "Stnd Pro kit" | EA14-10222B |  | 5552
|  |  | EA14-10222P |  | 7082
|  |  | EA14-10222C |  | 8250
| 8 | Aquaphon A200 Pro Kit "Pro. Kit" | EA20-10022B |  | 5952
|  |  | EA20-10022PB |  | 7908
|  |  | EA20-10022P |  | 9085
|  |  | EA20-10022C |  | 10132
| 9 | Combiphon Striker Kitc | SA01-10002K |  | 4207
|  | Combiphon Stopper Kit | SA01-10002S |  | 4930
|  | Combiphon Complete Kit | SA01-10002C |  | 6459
| 10 | Variotec VT 460 Tracergas Kit | VT10-10502B |  | 7659
Logger/Correlator | 11 | SeCorr C200 Kit | KR20-10202B | 2 | 10495 | $347 / Leak
|  | SeCorrPhon AC200 Kit | KR08-22202B | 2 | 14866
|  |  | KR20-20202P | 2 | 16249
| 12 | SeCorr 300 Digital Correlator Pro Kit | KR30-S0004P | 2 | 20214
| 13 | SePem 01 Starter Kit | SF01-10002S | 10 | 9455
|  |  | SePem 155 Logger | 1 | 685
Vendor - FCS
Type | Item No. | Equipment | Part # | Items Incld. | Unit Cost | Upfront Cost | Labor | External Vendor | DI | PVC | AC | Median | Average
Acoustic Leak Detection | 1 | DXMic System | DXMICSYS | 1 | 4950 |  | 50 < miles $278 / mi 50 > 100 mile $350 / mi 100 > miles $300 / mi | $295 / mile for metal pipes $595 / mile for non-metallic pipe | 93.7% | 41.2% | 53.8% | 53.8% | 62.9%
|  | DXMic Pro System | DXPROSYS | 1 | 5380
| 2 | Bmic System | BMICSYS | 1 | 4950
| 3 | TMic - FCS Portable Electronic Listening Stick | TMICFCS | 1 | 995
| 4 | L-Mic System | LMICSYS | 1 | 1950
|  | L-Mic System Deluxe | LMICSYSDEL | 1 | 3950
Correlator / Logger | 5 | S-30 System | S30SYS | 1 | 4500 |  | $347 / Leak
|  | TriCorr Touch Pro | TCTOUCH |  | 25000
|  | Hydrophone Kit | HYDKITMCTUSA | 1 | 9144
|  | Additional Correlating Pods | RDL 5014L/4 | 1 | 1700
|  | 3 Pod with 8 Pod Case | - | 3 | 11885
|  | 4 Pod with 8 Pod Case | - | 4 | 13202
|  | 6 Pod with 8 Pod Case | - | 6 | 15428
|  | 8 Pod with 8 Pod Case | - | 8 | 17950
Permalog+
|  | 1-25 Permalogs | PR4US | 1 | 700
|  | 26-50 Permalogs | PR4US | 1 | 650
|  | 51-100 Permalogs | PR4US | 1 | 600
|  | 101-200 Permalogs | PR4US | 1 | 550
|  | 201-300 Permalogs | PR4US | 1 | 500
|  | 301-500 Permalogs | PR4US | 1 | 450
|  | 501-750 Permalogs | PR4US | 1 | 400
|  | 751 + Permalogs | PR4US | 1 | 350
Pcorr+
|  | 1-25 Pcorr+ | PR5US | 1 | 800
|  | 26-50 Pcorr+ | PR5US | 1 | 750
|  | 51-100 Pcorr+ | PR5US | 1 | 700
|  | 101-200 Pcorr+ | PR5US | 1 | 650
|  | 201-300 Pcorr+ | PR5US | 1 | 600
|  | 301-500 Pcorr+ | PR5US | 1 | 550
|  | 501-750 Pcorr+ | PR5US | 1 | 500
|  | 751 + Pcorr+ | PR5US | 1 | 450
* Pricing does not include applicable taxes or shipping costs.
http://www.subsurfaceleak.com/waterleakdetec.html
Vendor - SEBA
Type | Item No. | Equipment | Part # | Items Incld. | Unit Cost | Upfront Cost | Labor | External Vendor | DI | PVC | AC | Median | Average
Acoustic Leak Detection | 1 | HL-7000 Electro-Acoustic Leak Detector | seba-HL7000-US-PRO | 1 | 5595 |  | 50 < miles $278 / mi 50 > 100 mile $350 / mi 100 > miles $300 / mi | $295 / mile for metal pipes $595 / mile for non-metallic pipe | 93.7% | 41.2% | 53.8% | 53.8% | 62.9%
| 2 | HL50 Bluetooth Municipal Digital Leak Locator | SEBA-HL50BT-kit | 1 | 2150
|  | Listining Rod add on | PAM T-3-1 | 1
| 3 | N3-C10: 1 Commander 3a | SEBA-WP12389 | 1 | 14500 |  | $347 / Leak
|  | N3-M logger add on | SEBA-WP12391 | 31 | 21700
| 4 | Correlux C-3 Seba Pro Correlatorb | SEBA-WP12399 | 1 | 22000
a. Includes 10 Loggers
b. Includes 3 Correlators
* Pricing does not include applicable taxes or freight.
Vendor - Gutermann
Type | Labor | External Vendor | DI | PVC | AC | Median | Average
Acoustic Leak Detection | 50 < miles $278 / mi 50 > 100 mile $350 / mi 100 > miles $300 / mi | $295 / mile for metal pipes $595 / mile for non-metallic pipe | 93.7% | 82.3% | 66.6% | 82.3% | 80.87%
Correlator / Logger | $347 / Leak
Repair costs
From Irvine Ranch Water district
Repair costs for leaks found in area surveyed ($) | Average Cost/Foot | Leak Repair Rangea |  | Reported Water Saved | 2" & 3" PVC | 4" PVC | 6" PVC | 6" ACP | 8" C-900 / ACP | 8" DIP | 10" ACP | 12" CML/ACP | 16" CML&C
234000 | 207 | $3500 - $30000 |  | 263 AF | $3000 - 5,000 | $3000 - 6,000 | $4000 - 6,000 | $3000 - 12,000 | $3000 - 9,000 | 6000 | $4000 - 6,000 | $6000 - 15,000 | $4000 - 31,650 | 2018
[5 empty] | $2000 - 6,000 | $4000 - 9,000 | $4000 - 9,000 | $4000 - 5,000 | $4000 - 6,000 | 12000 | 7000 | 15000 | $6000 - 12,000 | 2017
Average
[5 empty] | Averages: | 4000 | 5500 | 5750 | 6000 | 5500 | 9000 | 5666.6667 | 12000 | 13412.5 | 7425.463
From Pacific Gas and Electric's Report ET13PGE1451: Water System Leak Identification and Control Field Evaluation (2015)
Repairs costs for the leaks detected:
Tehama County Water system | Kings County Water System | Alpine County Water System | Madera County System
2745 | 2500 | 2500 | 1500 |  | Average cost: | 4466.25
|  | 6000 | 1500
7900
4100
8600
7500
6800
1950
Based on these two data sets, the average repair cost is assumed to be: |  |  | 5945.8565
Additional references for model:
1. Water loss audit reports, 2020, Department of Water Resources: https://wuedata.water.ca.gov/, Accessed: March 2020
2. American Water Works Association, 2016, Water Audits and Loss Control Programs (M36 Manual), Fourth Edition
3. Water Research Foundation, 2015, Water Audits and Real Loss Component Analysis, Report 4372a
4. A.O. Lambert, 1999, International Report: Water losses management and techniques, Water Science and Technology: Water Supply Vol 2 No 4 pp 1–20
5. European Union, 2015, EU Reference document Good Practices on Leakage Management: Main Report
6. American Water Works Association Water Loss Control Committee, 2003, Committee Report: Applying worldwide BMPs in water loss control, Volume 95, Issue 8, Pages 65-79
7. California Rural Water Association, 2015, Water System Leak Identification and Control Field Evaluation, Emerging Technologies Report:ET13PGE1451, Pacific Gas and Electric Company
8. Pacific Institute, 2016, The Cost of Alternative Water Supply and Efficiency Options in California
9. Natural Resources Defense Council, 2016, Issue Brief: Proceed with Caution II: California's Droughts and Desalination in Context