## Tables
DISCHARGE 001
[9 empty] | TEMPERATURE (DEG F) | [18 empty] | FLOW (MGD)
[9 empty] | INFLUENT | [6 empty] | EFFLUENT | [6 empty] | DELTA T
[6 empty] | Month |  |  | high |  | low |  | avg |  |  | high |  | low |  | avg |  |  | high |  | avg |  |  | high |  | low |  | avg | [5 empty] | Double Click in box for Instructions
[7 empty] | JAN |  | 54.5 |  | 51.9 |  | 53.4 |  |  | 74.2 |  | 71.3 |  | 72.5 |  |  | 20 |  | 19.1 |  |  | 2486 |  | 2486 |  | 2486
[7 empty] | FEB |  | 53.8 |  | 51.6 |  | 52.8 |  |  | 73 |  | 67.3 |  | 70.9 |  |  | 19.2 |  | 18.2 |  |  | 2486 |  | 1239 |  | 1363
[7 empty] | MAR |  | 53.6 |  | 48.8 |  | 50.6 |  |  | 71.6 |  | 66.7 |  | 68.8 |  |  | 18.9 |  | 18.2 |  |  | 1239 |  | 1239 |  | 1239
[7 empty] | APR |  | 50.2 |  | 47 |  | 48.6 |  |  | 67.9 |  | 59.8 |  | 65.1 |  |  | 18.9 |  | 16.5 |  |  | 2486 |  | 1239 |  | 2244
[7 empty] | MAY |  | 52.2 |  | 47.7 |  | 50 |  |  | 71 |  | 66.5 |  | 68.7 |  |  | 19.4 |  | 18.8 |  |  | 2486 |  | 1874 |  | 2400
[7 empty] | JUN |  | 54 |  | 48.6 |  | 51.3 |  |  | 72.6 |  | 67.2 |  | 70 |  |  | 18.9 |  | 18.1 |  |  | 2486 |  | 2486 |  | 2486
[7 empty] | JUL |  | 56.7 |  | 51.5 |  | 54.0613 |  |  | 75.4 |  | 70.2 |  | 72.7903 |  |  | 18.9 |  | 18.729 |  |  | 2486 |  | 2486 |  | 2486
[7 empty] | AUG |  | 57.8 |  | 54 |  | 55.6742 |  |  | 75.6 |  | 56.2 |  | 69.6677 |  |  | 19 |  | 13.9935 |  |  | 2486 |  | 1862 |  | 2441.5484
[7 empty] | SEP |  | 58 |  | 54.4 |  | 56.3867 |  |  | 76.7 |  | 65.5 |  | 73.52 |  |  | 19.2 |  | 17.1333 |  |  | 2486 |  | 2486 |  | 2486
[7 empty] | OCT |  | 58 |  | 52.8 |  | 55.1484 |  |  | 76.8 |  | 65.1 |  | 73.0903 |  |  | 19.2 |  | 17.9419 |  |  | 2486 |  | 1239 |  | 2430.6774
[7 empty] | NOV |  | 60.6 |  | 53.5 |  | 56.7467 |  |  | 79.5 |  | 72.4 |  | 75.79 |  |  | 19.4 |  | 19.0433 |  |  | 2486 |  | 2486 |  | 2486
[7 empty] | DEC |  | 58.2 |  | 53.1 |  | 55.271 |  |  | 77.4 |  | 72.4 |  | 74.529 |  |  | 19.4 |  | 19.2581 |  |  | 2486 |  | 2486 |  | 2486
[7 empty] | limit: |  |  |  | - | [6 empty] | - |  |  |  |  | 22 |  |  |  |  | 2760
DISCHARGE 001
[11 empty] | TOTAL RESIDUAL | [10 empty] | TOTAL CHLORINE
[11 empty] | CHLORINE (daily max. ug/l) | [10 empty] | USED (lbs/day)
[12 empty] | Month |  | high |  | low |  | avg |  |  |  | high |  | low |  | avg
[12 empty] | JAN |  | 54 |  | 28 |  | 42.5161 |  |  |  | 489.6 |  | 369.6 |  | 435.1742
[12 empty] | FEB |  | 207 |  | <20 |  | 41.2759 |  |  |  | 345.6 |  | 156 |  | 227.0897
[12 empty] | MAR |  | 52 |  | <20 |  | <20 |  |  |  | 230.4 |  | 163.2 |  | 196.5677
[12 empty] | APR |  | 65 |  | 21 |  | 34.0667 |  |  |  | 403.2 |  | 194.4 |  | 335.76
[12 empty] | MAY |  | 41 |  | <10 |  | 15.2903 |  |  |  | 460.8 |  | 201.6 |  | 359.7677
[12 empty] | JUN |  | 30 |  | <10 |  | 20.9333 |  |  |  | 547.2 |  | 336 |  | 475.32
[12 empty] | JUL |  | 43 |  | <10 |  | 21.2258 |  |  |  | 705.6 |  | 525.6 |  | 651.871
[12 empty] | AUG |  | 39 |  | <10 |  | 18.9032 |  |  |  | 705.6 |  | 408 |  | 629.4968
[12 empty] | SEP |  | 63 |  | <10 |  | 27.7 |  |  |  | 676.8 |  | 573.6 |  | 629.36
[12 empty] | OCT |  | 60 |  | <10 |  | 32 |  |  |  | 619 |  | 204 |  | 498
[12 empty] | NOV |  | 36 |  | 12 |  | 27 |  |  |  | 518 |  | 496 |  | 518
[12 empty] | DEC |  | 52 |  | 25 |  | 35 |  |  |  | 547 |  | 346 |  | 484
Note that the residual chlorine limits in Permit CA0003751, Order 90-09, is an instantaneous max of 200 ug/l, and
includes a time-based limit (per the Ocean Plan) which depends on the length of the respective chlorination cycle.
DISCHARGE 001
METALS (monthly avg. ug/l)
[9 empty] | CHROMIUM | [6 empty] | COPPER | [6 empty] | NICKEL | [6 empty] | *ZINC
[5 empty] | Month |  |  |  | Influent |  |  | Effluent |  |  |  | Influent |  |  | Effluent |  |  |  | Influent |  |  | Effluent |  |  |  | Influent |  |  | Effluent
[6 empty] | JAN |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10)
[6 empty] | FEB |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10)
[6 empty] | MAR |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10)
[6 empty] | APR |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10)
[6 empty] | MAY |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10)
[6 empty] | JUN |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | 13 |  |  | 11 |  |  |  | ND(10) |  |  | ND(10)
[6 empty] | JUL |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10)
[6 empty] | AUG |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10)
[6 empty] | SEP |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10)
[6 empty] | OCT |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10)
[6 empty] | NOV |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10)
[6 empty] | DEC |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10) |  |  |  | ND(10) |  |  | ND(10)
[5 empty] | 6-month median limit: | [6 empty] | 10 |  |  |  | - |  |  | 10 |  |  |  | - |  |  | 30 |  |  |  | - |  |  | 70
DISCHARGE 001
VARIOUS ANNUAL ANALYSES
[19 empty] | (monthly avg. ug/l) | [6 empty] | 6-Mo. Med.
Effluent
[11 empty] | Parameter | [7 empty] | Influent |  |  |  | Effluent |  |  | Limit
[11 empty] | Arsenic | [6 empty] | 1.2 |  |  |  | 1.2 |  |  |  | 30
[11 empty] | Cadmium | [6 empty] | 0.027 |  |  |  | 0.038 |  |  |  | 10
[11 empty] | Cyanide | [6 empty] | ND(10) |  |  |  | ND(10) |  |  |  | 30
[11 empty] | Lead | [6 empty] | 0.025 |  |  |  | 0.031 |  |  |  | 10
[11 empty] | Mercury | [6 empty] | 0.2 |  |  |  | 0.2 |  |  |  | 0.2
[11 empty] | Silver | [6 empty] | 0.025 |  |  |  | 0.025 |  |  |  | 2.9
[11 empty] | Titanium | [6 empty] | - |  |  |  | 2.5 |  |  |  | none
[11 empty] | *Phenolic Compounds | [6 empty] | ND(13.27) |  |  |  | ND(15.12) |  |  |  | 150
(non-chlorinated)
[11 empty] | **Phenolic Cmpds | [6 empty] | ND(3.92) |  |  |  | ND(3.75) |  |  |  | 10
(chlorinated)
[11 empty] | ***PCB's | [6 empty] | ND(1.59) |  |  |  | ND(1.59) |  |  |  |  | none
*Reporting limits shown are the sum of individual Reporting Limits for 7 target compounds.
**Reporting limits shown are the sum of individual Reporting Limits for 6 target compounds.
***Reporting limits shown are the sum of individual Reporting Limits for 7 target compounds.
DISCHARGE 001
AMMONIA (as N) (ug/l)
[15 empty] | Month |  |  |  | Influent |  |  | Effluent
[15 empty] | JAN |  |  |  | ND(200) |  |  | ND(200)
FEB
MAR
[15 empty] | APR |  |  |  | ND(200) |  |  | ND(200)
MAY
JUN
[15 empty] | JUL |  |  |  | ND(200) |  |  | ND(200)
AUG
SEP
[15 empty] | OCT |  |  |  | ND(200) |  |  | ND(200)
NOV
DEC
[15 empty] | 6-month median limit: | [7 empty] | 3060
MONTHLY pH (averages)
[7 empty] | Discharge: |  |  |  |  | 001 | [6 empty] | 002 |  |  |  | 003 |  |  |  | 004 |  |  |  | 001P
[7 empty] | Month |  |  |  |  | Influent |  |  | Effluent
[7 empty] | JAN |  |  |  |  | 7.9 |  |  | 7.9 |  |  |  | 8 |  |  |  | 8 |  |  |  | 7.9 |  |  |  | 7.6
[7 empty] | FEB |  |  |  |  | 7.9 |  |  | 7.9 |  |  |  | 8 |  |  |  | 7.9 |  |  |  | 7.9 |  |  |  | 7.7
[7 empty] | MAR |  |  |  |  | 7.9 |  |  | 7.9 |  |  |  | 7.9 |  |  |  | 8 |  |  |  | 8 |  |  |  | 7.7
[7 empty] | APR |  |  |  |  | 7.8 |  |  | 7.8 |  |  |  | 7.9 |  |  |  | 7.9 |  |  |  | 7.9 |  |  |  | 7.7
[7 empty] | MAY |  |  |  |  | 7.7 |  |  | 7.8 |  |  |  | 7.8 |  |  |  | 7.7 |  |  |  | 7.7 |  |  |  | 7.5
[7 empty] | JUN |  |  |  |  | 7.6 |  |  | 7.7 |  |  |  | 7.8 |  |  |  | 7.7 |  |  |  | 7.7 |  |  |  | 7.6
[7 empty] | JUL |  |  |  |  | 7.9 |  |  | 7.9 |  |  |  | 7.8 |  |  |  | 7.8 |  |  |  | 7.8 |  |  |  | 7.7
[7 empty] | AUG |  |  |  |  | 8 |  |  | 8 |  |  |  | 7.9 |  |  |  | 7.9 |  |  |  | 7.9 |  |  |  | 7.6
[7 empty] | SEP |  |  |  |  | 8 |  |  | 7.9 |  |  |  | 7.8 |  |  |  | 7.7 |  |  |  | 7.7 |  |  |  | 7.7
[7 empty] | OCT |  |  |  |  | 7.9 |  |  | 7.9 |  |  |  | 8 |  |  |  | 8.1 |  |  |  | 8 |  |  |  | 7.7
[7 empty] | NOV |  |  |  |  | 7.9 |  |  | 7.9 |  |  |  | 7.9 |  |  |  | 7.8 |  |  |  | 7.7 |  |  |  | 7.6
[7 empty] | DEC |  |  |  |  | 7.9 |  |  | 7.9 |  |  |  | 8 |  |  |  | 8 |  |  |  | 8 |  |  |  | 7.8
DISCHARGE 001F
SUSPENDED
[15 empty] | GREASE & OIL (mg/l) | [6 empty] | SOLIDS (mg/l)
[11 empty] | Month |  |  |  | high |  |  | avg |  |  |  | high |  |  | avg
[11 empty] | JAN |  |  |  | 19 |  |  | 10 |  |  |  | 17 |  |  | 16
[11 empty] | FEB |  |  |  | ND(5) |  |  | ND(5) |  |  |  | 7 |  |  | 7
[11 empty] | MAR |  |  |  | ND(5) |  |  | ND(5) |  |  |  | 16 |  |  | 12
[11 empty] | APR |  |  |  | ND(5) |  |  | ND(5) |  |  |  | 16 |  |  | 16
[11 empty] | MAY |  |  |  | ND(5) |  |  | ND(5) |  |  |  | 14 |  |  | 13
[11 empty] | JUN |  |  |  | ND(5) |  |  | ND(5) |  |  |  | 14 |  |  | 14
[11 empty] | JUL |  |  |  | ND(5) |  |  | ND(5) |  |  |  | 18 |  |  | 18
[11 empty] | AUG |  |  |  | ND(5) |  |  | ND(5) |  |  |  | 11 |  |  | 10
[11 empty] | SEP |  |  |  | ND(5) |  |  | ND(5) |  |  |  | 6 |  |  | 6
[11 empty] | OCT |  |  |  | ND(5) |  |  | ND(5) |  |  |  | 5 |  |  | 5
[11 empty] | NOV |  |  |  | ND(5) |  |  | ND(5) |  |  |  | 6 |  |  | 6
[11 empty] | DEC |  |  |  | ND(5) |  |  | ND(5) |  |  |  | 45 |  |  | 9
[12 empty] | limit: |  |  | 20 |  |  | 15 |  |  |  | 100 |  |  | 30
Note: "high" limits based upon Daily Maximum limits. "avg" limits based upon Monthly Average Limits.
DISCHARGE 001N
(Monthly Summary of Weekly Data)
[18 empty] | SUSPENDED | [9 empty] | SETTLEABLE
[8 empty] | GREASE & OIL (mg/l) | [9 empty] | SOLIDS (mg/l) | [9 empty] | SOLIDS (ml/l)
|  |  |  | Month |  |  |  | high |  |  | low |  |  | avg |  |  |  | high |  |  | low |  |  | avg |  |  |  | high |  |  | low |  |  | avg
|  |  |  | JAN |  |  |  | 10 |  |  | ND(5) |  |  | <5 |  |  |  | 50 |  |  | 15 |  |  | 29 |  |  |  | ND(0.1) |  |  | ND(0.1) |  |  | ND(0.1)
|  |  |  | FEB |  |  |  | 8 |  |  | ND(5) |  |  | <5 |  |  |  | 60 |  |  | 25 |  |  | 40 |  |  |  | ND(0.1) |  |  | ND(0.1) |  |  | ND(0.1)
|  |  |  | MAR |  |  |  | ND(5) |  |  | ND(5) |  |  | ND(5) |  |  |  | 34 |  |  | 11 |  |  | 21 |  |  |  | 0.3 |  |  | ND(0.1) |  |  | <0.1
|  |  |  | APR |  |  |  | 7 |  |  | ND(5) |  |  | <5 |  |  |  | 37 |  |  | 10 |  |  | 22 |  |  |  | ND(0.1) |  |  | ND(0.1) |  |  | ND(0.1)
|  |  |  | MAY |  |  |  | 8 |  |  | ND(5) |  |  | <5 |  |  |  | 12 |  |  | 7 |  |  | 10 |  |  |  | ND(0.1) |  |  | ND(0.1) |  |  | ND(0.1)
|  |  |  | JUN |  |  |  | 8 |  |  | ND(5) |  |  | <5 |  |  |  | 32 |  |  | ND(5) |  |  | 14 |  |  |  | ND(0.1) |  |  | ND(0.1) |  |  | ND(0.1)
|  |  |  | JUL |  |  |  | ND(5) |  |  | ND(5) |  |  | ND(5) |  |  |  | 23 |  |  | 7 |  |  | 16 |  |  |  | ND(0.1) |  |  | ND(0.1) |  |  | ND(0.1)
|  |  |  | AUG |  |  |  | 7 |  |  | ND(5) |  |  | <5 |  |  |  | 36 |  |  | 14 |  |  | 26.6 |  |  |  | ND(0.1) |  |  | ND(0.1) |  |  | ND(0.1)
|  |  |  | SEP |  |  |  | ND(5) |  |  | ND(5) |  |  | ND(5) |  |  |  | 42 |  |  | ND(5) |  |  | 20 |  |  |  | ND(0.1) |  |  | ND(0.1) |  |  | ND(0.1)
|  |  |  | OCT |  |  |  | ND(5) |  |  | ND(5) |  |  | ND(5) |  |  |  | 20 |  |  | 14 |  |  | 16 |  |  |  | ND(0.1) |  |  | ND(0.1) |  |  | ND(0.1)
|  |  |  | NOV |  |  |  | ND(5) |  |  | ND(5) |  |  | ND(5) |  |  |  | 27 |  |  | 16 |  |  | 21 |  |  |  | ND(0.1) |  |  | ND(0.1) |  |  | ND(0.1)
|  |  |  | DEC |  |  |  | ND(5) |  |  | ND(5) |  |  | ND(5) |  |  |  | 35 |  |  | 17 |  |  | 26 |  |  |  | 0.2 |  |  | ND(0.1) |  |  | <0.1
[5 empty] | limit: |  |  | 20 |  |  | - |  |  | 15 |  |  |  | - |  |  | - |  |  | 60 |  |  |  | 3 |  |  | - |  |  | 1
Note: "high" limits based upon Daily Maximum limits. "avg" limits based upon Monthly Average limits.
DISCHARGE 001D, H, L, F, METALS (avg. ug/l)
|  |  | 001D | [8 empty] | 001 H | [8 empty] | 001L | [8 empty] | 001F
Month |  |  |  | Ag |  | Cd |  | Cr |  | Cu |  |  | Ag |  | Cd |  | Cr |  | Cu |  |  | Ag |  | Cd |  | Cr |  | Cu |  |  | Ag |  | Cd |  | Cr | Cu
JAN |  |  |  | ND(10) |  | ND(10) |  | ND(10) |  | ND(10) |  |  | ND(10) |  | ND(10) |  | 20 |  | 27 |  |  | ND(10) |  | ND(10) |  | ND(10) |  | ND(10) |  |  | 25 |  | ND(10) |  | ND(10) | ND(10)
FEB
MAR
APR |  |  |  | ND(10) |  | ND(10) |  | ND(10) |  | 10 |  |  | ND(10) |  | ND(10) |  | 21 |  | 69 |  |  | ND(10) |  | ND(10) |  | ND(10) |  | <10 |  |  | ND(10) |  | ND(10) |  | ND(10) | 38
MAY
JUN
JUL |  |  |  | ND(10) |  | ND(10) |  | ND(10) |  | ND(10) |  |  | ND(10) |  | ND(10) |  | 40 |  | 67 |  |  | ND(10) |  | ND(10) |  | ND(10) |  | ND(10) |  |  | ND(10) |  | ND(10) |  | ND(10) | ND(10)
AUG
SEP
OCT |  |  |  | ND(10) |  | ND(10) |  | ND(10) |  | ND(10) |  |  | ND(10) |  | ND(10) |  | 19 |  | 62 |  |  | ND(10) |  | ND(10) |  | ND(10) |  | ND(10) |  |  | ND(10) |  | ND(10) |  | 23 | ND(10)
NOV
DEC
limit: none
Note: 001D, 001H and 001L analyses performed on quarterly composites.
001F analyses performed quarterly on a composite of weekly samples.
DISCHARGE 001D, H, L, F, METALS (avg. ug/l)
|  |  | 001D | [8 empty] | 001 H | [8 empty] | 001L | [8 empty] | 001F
Month |  |  |  | Hg |  | Ni |  | Pb |  | Zn |  |  | Hg |  | Ni |  | Pb |  | Zn |  |  | Hg |  | Ni |  | Pb |  | Zn |  |  | Hg |  | Ni |  | Pb | Zn
JAN |  |  |  | ND(0.20) |  | ND(10) |  | ND(10) |  | 46 |  |  | ND(0.20) |  | 18 |  | 50 |  | <10 |  |  | ND(0.20) |  | ND(10) |  | ND(10) |  | ND(10) |  |  | ND(0.20) |  | ND(10) |  | 39 | 49
FEB
MAR
APR |  |  |  | ND(0.20) |  | ND(10) |  | ND(10) |  | 155 |  |  | <0.20 |  | 16 |  | ND(10) |  | ND(10) |  |  | ND(0.20) |  | <10 |  | ND(10) |  | ND(10) |  |  | ND(0.20) |  | 20 |  | ND(10) | 28
MAY
JUN
JUL |  |  |  | ND(0.20) |  | ND(10) |  | ND(10) |  | 58 |  |  | ND(0.20) |  | 24 |  | ND(10) |  | <10 |  |  | ND(0.20) |  | ND(10) |  | ND(10) |  | ND(10) |  |  | ND(0.20) |  | ND(10) |  | ND(10) | ND(10)
AUG
SEP
OCT |  |  |  | ND(0.20) |  | ND(10) |  | ND(10) |  | 174 |  |  | <0.20 |  | 22 |  | ND(10) |  | 12 |  |  | ND(0.20) |  | ND(10) |  | ND(10) |  | ND(10) |  |  | ND(0.20) |  | 33 |  | ND(10) | 42
NOV
DEC
limit: none
Note: 001D, 001H and 001L analyses performed on quarterly composites.
001F analyses performed quarterly on a composite of weekly samples.
MONTHLY TOTAL SUSPENDED SOLIDS
Averages (mg/l)
| Month |  |  |  | 001D* |  |  | 001G |  |  | 001H |  |  | 001I |  |  | 001J |  |  | 001K |  |  | 001L |  |  | 001M |  |  | 001P |  |  | 002 |  |  | 003
| JAN |  |  |  | <5 |  |  | ND(5) |  |  | ND(5) | [11 empty] | ND(5) | [5 empty] | ND(5) |  |  | <5 |  |  | 5
| FEB |  |  |  | <5 |  |  | ND(5) |  |  | ND(5) | [5 empty] | ND(5) | [5 empty] | ND(5) | [5 empty] | ND(5) |  |  | <5 |  |  | <5
| MAR |  |  |  | 6 |  |  | ND(5) |  |  | ND(5) | [11 empty] | ND(5) | [5 empty] | ND(5) |  |  | 5 |  |  | 5
| APR |  |  |  | <5 |  |  | ND(5) |  |  | ND(5) | [5 empty] | ND(5) | [5 empty] | ND(5) |  |  | 5 |  |  | ND(5) |  |  | ND(5) |  |  | ND(5)
| MAY |  |  |  | <5 |  |  | ND(5) |  |  | ND(5) | [11 empty] | ND(5) | [5 empty] | ND(5) |  |  | ND(5) |  |  | ND(5)
| JUN |  |  |  | <5 |  |  | ND(5) |  |  | ND(5) | [11 empty] | ND(5) | [5 empty] | ND(5) |  |  | ND(5) |  |  | <5
| JUL |  |  |  | <5 |  |  | ND(5) |  |  | ND(5) | [11 empty] | ND(5) | [5 empty] | 6 |  |  | ND(5) |  |  | ND(5)
| AUG |  |  |  | <5 |  |  | ND(5) |  |  | ND(5) | [5 empty] | ND(5) | [5 empty] | ND(5) | [5 empty] | ND(5) |  |  | 7 |  |  | 9
| SEP |  |  |  | <5 |  |  | ND(5) |  |  | 6 | [5 empty] | ND(5) | [5 empty] | ND(5) | [5 empty] | ND(5) |  |  | ND(5) |  |  | ND(5)
| OCT |  |  |  | <5 |  |  | ND(5) |  |  | ND(5) | [5 empty] | ND(5) | [5 empty] | ND(5) |  |  | ND(5) |  |  | ND(5) |  |  | ND(5) |  |  | ND(5)
| NOV |  |  |  | <5 |  |  | ND(5) |  |  | ND(5) | [11 empty] | ND(5) | [5 empty] | ND(5) |  |  | ND(5) |  |  | 5
| DEC |  |  |  | <5 |  |  | ND(5) |  |  | <5 | [11 empty] | ND(5) | [5 empty] | 27 |  |  | ND(5) |  |  | ND(5)
|  | Limit: |  |  | 30 |  |  | 30 |  |  | 30 |  |  | 30 |  |  | 30 |  |  | 30 |  |  | 30 |  |  | 30 |  |  | 30 |  |  | 30 |  |  | -
QUARTERLY GREASE & OIL
Averages by Month (mg/l)
Month |  |  |  | 001D* |  |  | 001G |  |  | 001H |  |  | 001I |  |  | 001J |  |  | 001K |  |  | 001L |  |  | 001M |  |  | 001P |  |  | 002 |  |  | 003 |  | 004
JAN |  |  |  | <5 |  |  | ND(5) |  |  | ND(5) | [11 empty] | ND(5) | [5 empty] | ND(5) |  |  | ND(5) |  |  | ND(5) |  | ND(5)
FEB | [15 empty] | ND(5)
MAR |  |  |  | ND(5)
APR |  |  |  | 8 |  |  | ND(5) | [8 empty] | ND(5) | [5 empty] | ND(5) |  |  | ND(5) |  |  | ND(5) |  |  | ND(5) |  |  | ND(5) |  | ND(5)
MAY | [9 empty] | <5 | [11 empty] | ND(5)
JUN
JUL |  |  |  | ND(5) |  |  | ND(5) |  |  | ND(5) | [11 empty] | ND(5) | [5 empty] | ND(5) |  |  | ND(5) |  |  | ND(5) |  | ND(5)
AUG |  |  |  | <5 | [11 empty] | ND(5) | [14 empty] | 10
SEP
OCT |  |  |  | 5 |  |  | ND(5) |  |  | ND(5) | [5 empty] | ND(5) | [5 empty] | ND(5) |  |  | ND(5) |  |  | ND(5) |  |  | ND(5) |  |  | ND(5) |  | ND(5)
NOV
DEC
| Limit: |  |  | 15 |  |  | 15 |  |  | 15 |  |  | 15 |  |  | 15 |  |  | 15 |  |  | 15 |  |  | 15 |  |  | 15 |  |  | 15 |  |  | 15 |  | 15
QUARTERLY ACUTE AND CHRONIC TOXICITY TESTING
(toxicity units, tua and tuc)
[13 empty] | ACUTE | [9 empty] | *CHRONIC
[14 empty] | Test |  |  | 6-Month | [5 empty] | Test
[10 empty] | Month |  |  |  | Result |  |  | Median | [5 empty] | Result
[10 empty] | JAN |  |  | 0 |  |  | 0.41 | [20 empty] | 5.11 | 0.26 | 0
[10 empty] | FEB |  |  | 0 |  |  | 0 | [6 empty] | 1 | [13 empty] | 5.11 | 0.26
[10 empty] | MAR |  |  | 0 |  |  | 0 | [20 empty] | 5.11 | 0.26
[10 empty] | APR |  |  | 0 |  |  | 0 | [6 empty] | 1 | [13 empty] | 5.11 | 0.26
[10 empty] | MAY | [26 empty] | 5.11 | 0.26 | 0
[10 empty] | JUN | [26 empty] | 5.11 | 0.26
[10 empty] | JUL |  |  | 0 |  |  | 0 | [6 empty] | 1 | [13 empty] | 5.11 | 0.26
[10 empty] | AUG | [26 empty] | 5.11 | 0.26 | 0
[10 empty] | SEP | [26 empty] | 5.11 | 0.26
[10 empty] | OCT |  |  | 0.23 |  |  | 0 | [6 empty] | 1 | [13 empty] | 5.11 | 0.26
[10 empty] | NOV | [26 empty] | 5.11 | 0.26 | 0
[10 empty] | DEC | [26 empty] | 5.11 | 0.26
[10 empty] | 6-month median limit: | [5 empty] | 0.26 | [6 empty] | 5.1
[9 empty] | * | This parameter is monitored for the State Ocean Plan
instead of the NPDES Permit. A value of 1.0 indicates no chronic toxicity.
NOTE:
Increased acute toxicity testing in January, February and March were due
to acute tests in the 4th quarter of 2007 that reported mortalities. The
additional tests were negative for toxicity.
DISCHARGE 001N
ANNUAL ANALYSES
Sludge
[9 empty] | Parameter | [9 empty] | Result |  |  |  |  | Limit
[9 empty] | Percent Moisture | [9 empty] | 99% |  |  |  |  | None
[9 empty] | Total Kjeldahl Nitrogen | [9 empty] | 720 mg/kg |  |  |  |  | None
[9 empty] | Ammonia (N) | [9 empty] | 170 mg/kg |  |  |  |  | None
[9 empty] | Nitrate (N) | [9 empty] | ND(1) mg/kg |  |  |  |  | None
[9 empty] | Total Phosphorus | [9 empty] | 140 mg/kg |  |  |  |  | None
[9 empty] | pH | [9 empty] | 6.9 |  |  |  |  | None
[9 empty] | Oil and Grease | [9 empty] | 96 mg/kg |  |  |  |  | None
[9 empty] | Boron | [9 empty] | 20 mg/kg |  |  |  |  | None
[9 empty] | Cadmium | [9 empty] | ND(0.3) mg/kg |  |  |  |  | 10 X STLC*
[9 empty] | Copper | [9 empty] | 4.6 mg/kg |  |  |  |  | 10 X STLC
[9 empty] | Chromium | [9 empty] | ND(0.5) mg/kg |  |  |  |  | 10 X STLC
[9 empty] | Lead | [9 empty] | ND(1) mg/kg |  |  |  |  | 10 X STLC
[9 empty] | Nickel | [9 empty] | ND(0.5) mg/kg |  |  |  |  | 10 X STLC
[9 empty] | Mercury | [9 empty] | ND(0.04) mg/kg |  |  |  |  | 10 X STLC
[9 empty] | Zinc | [9 empty] | 8 mg/kg |  |  |  |  | 10 X STLC
[9 empty] | Volume | [9 empty] | 1.05 tons |  |  |  |  | None
Note: Annual samples were collected in October.
* STLC = Soluble Threshold Limit Concentration
|  |  | D | E | F |  |  |  | J | K | L |  |  | O | P | Q |  |  |  | Column D = Flow limit | [12 empty] | NOTE: NDs PLOTTED AS ZERO
| Jan |  | 2760 |  | 22 |  |  |  | 54 | 28 | 42.5161 |  |  |  |  | 3060 |  |  |  | Column E = | [12 empty] | LESS THANs PLOTTED AT THE VALUE
| Feb |  | 2760 |  | 22 |  |  |  | 207 | <20 | 41.2759 |  |  | 0 | 0 | 3060 |  |  |  | Column F = Delta T Limit
| Mar |  | 2760 |  | 22 |  |  |  | 52 | <20 | <20 |  |  |  |  | 3060
| Apr |  | 2760 |  | 22 |  |  |  | 65 | 20 | 34.0667 |  |  | 0 | 0 | 3060 |  |  |  | Column J = Chlorine - high values | [14 empty] | NOT
| May |  | 2760 |  | 22 |  |  |  | 41 | 7 | 15.2903 |  |  |  |  | 3060 |  |  |  | Column K = Chlorine - low values | [14 empty] | NEEDED
| Jun |  | 2760 |  | 22 |  |  |  | 30 | 7 | 20.9333 |  |  |  |  | 3060 |  |  |  | Column L = Chlorine - average values | [14 empty] | NOT GRAPHED
| Jul |  | 2760 |  | 22 |  |  |  | 43 | 10 | 21.2258 |  |  | 0 | 0 | 3060
| Aug |  | 2760 |  | 22 |  |  |  | 39 | 7 | 18.9032 |  |  |  |  | 3060 |  |  |  | Column O = |  |  |  | Ammonia - Influent
| Sep |  | 2760 |  | 22 |  |  |  | 63 | 7 | 27.7 |  |  |  |  | 3060 |  |  |  | Column P = |  |  |  | Ammonia - Effluent
| Oct |  | 2760 |  | 22 |  |  |  | 60 | <10 | 32 |  |  | 0 | 0 | 3060 |  |  |  | Column Q = |  |  |  | Ammonia Limit
| Nov |  | 2760 |  | 22 |  |  |  | 36 | 12 | 27 |  |  |  |  | 3060
| Dec |  | 2760 |  | 22 |  |  |  | 52 | 7 | 35 |  |  |  |  | 3060
| CR |  |  | CU |  |  | NI |  |  | ZN |  |  |  | 001 Metals - Influent and Effluent
| Inf | Eff | Lim | Inf | Eff | Lim | Inf | Eff | Lim | Inf | Eff | Lim
| 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 30 | 0 | 0 | 70 | Jan
| 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 30 | 0 | 0 | 70 | Feb
| 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 30 | 0 | 0 | 70 | Mar
| 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 30 | 0 | 0 | 70 | Apr
| 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 30 | 0 | 0 | 70 | May
| 0 | 0 | 10 | 0 | 0 | 10 | 13 | 11 | 30 | 0 | 0 | 70 | Jun
| 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 30 | 0 | 0 | 70 | Jul
| 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 30 | 0 | 0 | 70 | Aug
| 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 30 | 0 | 0 | 70 | Sep
| 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 30 | 0 | 0 | 70 | Oct
| 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 30 | 0 | 0 | 70 | Nov
| 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 30 | 0 | 0 | 70 | Dec
|  | Limits |  | 001F
| Mo | M. Max | D. Max | O&G | M. Max | D. Max | SS
C = monthly O & G limit
| JAN | 20 | 15 | 19 | 30 | 100 | 17 | [5 empty] | 5.11 |  |  | D = daily O & G limit
| FEB | 20 | 15 | 0 | 30 | 100 | 7 | [5 empty] | 5.11
| MAR | 20 | 15 | 0 | 30 | 100 | 16 | [5 empty] | 5.11 |  |  | F = monthly SS limit
| APR | 20 | 15 | 0 | 30 | 100 | 16 | [5 empty] | 5.11 |  |  | G= daily SS limit
| MAY | 20 | 15 | 0 | 30 | 100 | 14 | [5 empty] | 5.11
| JUN | 20 | 15 | 0 | 30 | 100 | 14 | [5 empty] | 5.11 |  |  | Note: Use Maximum values
| JUL | 20 | 15 | 0 | 30 | 100 | 18 | [5 empty] | 5.11
| AUG | 20 | 15 | 0 | 30 | 100 | 11 | [5 empty] | 5.11
| SEP | 20 | 15 | 0 | 30 | 100 | 6 | [5 empty] | 5.11
| OCT | 20 | 15 | 0 | 30 | 100 | 5 | [5 empty] | 5.11
| NOV | 20 | 15 | 0 | 30 | 100 | 6 | [5 empty] | 5.11
| DEC | 20 | 15 | 0 | 30 | 100 | 45 | [5 empty] | 5.11
| 001N | G&O |  |  | SS |  |  | Sett. Solids |  |  | G&O |  | sus. sol. | Sett. Sol
| Mo | hi | low | avg | hi | low | avg | hi | low | avg | hi | avg | avg | hi | avg
| JAN | 10 |  | 0 | 50 |  | 29 | 0 |  | 0 | 20 | 15 | 60 | 3 | 1 |  |  | Columns L, M, N, O, P are limits for 001N
| FEB | 8 |  | 0 | 60 |  | 40 | 0 |  | 0 | 20 | 15 | 60 | 3 | 1
| MAR | 0 |  | 0 | 34 |  | 21 | 0.3 |  | 0 | 20 | 15 | 60 | 3 | 1
| APR | 7 |  | 0 | 37 |  | 22 | 0 |  | 0 | 20 | 15 | 60 | 3 | 1 |  |  | NOTE: Do not input low values - don't need lows on plots
| MAY | 8 |  | 0 | 12 |  | 10 | 0 |  | 0 | 20 | 15 | 60 | 3 | 1
| JUN | 8 |  | 0 | 32 |  | 14 | 0 |  | 0 | 20 | 15 | 60 | 3 | 1
| JUL | 0 |  | 0 | 23 |  | 16 | 0 |  | 0 | 20 | 15 | 60 | 3 | 1
| AUG | 7 |  | 0 | 36 |  | 26.6 | 0 |  | 0 | 20 | 15 | 60 | 3 | 1
| SEP | 0 |  | 0 | 42 |  | 20 | 0 |  | 0 | 20 | 15 | 60 | 3 | 1
| OCT | 0 |  | 0 | 20 |  | 16 | 0 |  | 0 | 20 | 15 | 60 | 3 | 1
| NOV | 0 |  | 0 | 27 |  | 21 | 0 |  | 0 | 20 | 15 | 60 | 3 | 1
| DEC | 0 |  | 0 | 35 |  | 26 | 0.2 |  | 0 | 20 | 15 | 60 | 3 | 1
|  | 001D |  |  |  | 001H |  |  |  | 001L |  |  |  | 001F
| Month | Ag | Cd | Cr | Cu | Ag | Cd | Cr | Cu | Ag | Cd | Cr | Cu | Ag | Cd | Cr | Cu
| JAN | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.5 | 20 | 27 | 0.1 | 0.1 | 0.1 | 0.1 | 25 | 0.2 | 0.2 | 0.2
FEB
MAR
| APR | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.5 | 21 | 69 | 0.1 | 0.1 | 0.1 | 10 | 0.2 | 0.2 | 0.2 | 38
| MAY | [19 empty] | Use .1 for ND values and < values for plotting purposes.
| JUN | [19 empty] | Except 001H & 001F - Use .5 for ND values for plotting purposes.
| JUL | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.5 | 40 | 67 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  | due to some higher values.
AUG
SEP
| OCT | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.5 | 19 | 62 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 23 | 0.2
NOV
DEC
|  | 001D |  |  |  | 001H |  |  |  | 001L |  |  |  | 001F
| Month | Hg | Ni | Pb | Zn | Hg | Ni | Pb | Zn | Hg | Ni | Pb | Zn | Hg | Ni | Pb | Zn
| JAN | 1 | 1 | 1 | 46 | 0.3 | 18 | 50 | 10 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 39 | 49
FEB
MAR
| APR | 1 | 1 | 1 | 155 | 0.3 | 16 | 0.1 | 0.1 | 0.05 | 10 | 0.05 | 0.05 | 1 | 20 | 1 | 28
MAY
| JUN | [18 empty] | Use 1 for ND and < values for plotting purposes.
| JUL | 1 | 1 | 1 | 58 | 0.3 | 24 | 0.1 | 10 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 1 | 1 | 1 |  |  | Use 2 for ND and < values for plotting purposes for some mercury plots.
AUG
SEP
| OCT | 1 | 1 | 1 | 174 | 0.3 | 22 | 0.1 | 12 | 0.05 | 0.05 | 0.05 | 0.05 | 1 | 33 | 1 | 42
NOV
DEC
Suspended Solids
| Mo | 1D | 1G | 1H | 1I | 1J | 1K | 1L | 1M | 1P | 2 | 3 | LIMIT
| JAN | 001D Hg: 5; 001D Ni: 0; 001D Pb: 0; 001H Pb: 0; 001L Hg: 0; 001L Ni: 5; 001L Pb: 5; 001L Zn: 30
| FEB | 001D Hg: 5; 001D Ni: 0; 001D Pb: 0; 001H Hg: 0; 001H Pb: 0; 001L Hg: 0; 001L Ni: 5; 001L Pb: 5; 001L Zn: 30
| MAR | 001D Hg: 6; 001D Ni: 0; 001D Pb: 0; 001H Pb: 0; 001L Hg: 0; 001L Ni: 5; 001L Pb: 5; 001L Zn: 30
| APR | 5 | 0 | 0 |  | 0 |  | 0 | 5 | 0 | 0 | 0 | 30
| MAY | 001D Hg: 5; 001D Ni: 0; 001D Pb: 0; 001H Pb: 0; 001L Hg: 0; 001L Ni: 0; 001L Pb: 0; 001L Zn: 30
| JUN | 001D Hg: 5; 001D Ni: 0; 001D Pb: 0; 001H Pb: 0; 001L Hg: 0; 001L Ni: 0; 001L Pb: 5; 001L Zn: 30 | Use 5 for <5 values for plotting purposes.
| JUL | 001D Hg: 5; 001D Ni: 0; 001D Pb: 0; 001H Pb: 0; 001L Hg: 6; 001L Ni: 0; 001L Pb: 0; 001L Zn: 30
| AUG | 001D Hg: 5; 001D Ni: 0; 001D Pb: 0; 001H Hg: 0; 001H Pb: 0; 001L Hg: 0; 001L Ni: 7; 001L Pb: 9; 001L Zn: 30
| SEP | 001D Hg: 5; 001D Ni: 0; 001D Pb: 6; 001H Hg: 0; 001H Pb: 0; 001L Hg: 0; 001L Ni: 0; 001L Pb: 0; 001L Zn: 30
| OCT | 5 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 30
| NOV | 001D Hg: 5; 001D Ni: 0; 001D Pb: 0; 001H Pb: 0; 001L Hg: 0; 001L Ni: 0; 001L Pb: 5; 001L Zn: 30
| DEC | 001D Hg: 5; 001D Ni: 0; 001D Pb: 5; 001H Pb: 0; 001L Hg: 27; 001L Ni: 0; 001L Pb: 0; 001L Zn: 30
Quarterly Oil & Grease
| Mo | 1D | 1G | 1H | 1I | 1J | 1K | 1L | 1M | 1P | 2 | 3 | 4 | Limit
| JAN | 001D Hg: 5; 001D Ni: 0.1; 001D Pb: 0.1; 001H Pb: 0.1; 001L Hg: 0.1; 001L Ni: 0.1; 001L Pb: 0.1; 001L Zn: 0.1; 001F Hg: 15
| FEB | 001H Hg: 0.1; 001F Hg: 15
| MAR | 001D Hg: 0.1; 001F Hg: 15
| APR | 8 | 0.1 |  |  | 0.1 |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 15
| MAY | 001D Pb: 5; 001H Pb: 0.1; 001F Hg: 15 | Use 0.1 for <3 values for plotting purposes.
| JUN | 001F Hg: 15
| JUL | 001D Hg: 0.1; 001D Ni: 0.1; 001D Pb: 0.1; 001H Pb: 0.1; 001L Hg: 0.1; 001L Ni: 0.1; 001L Pb: 0.1; 001L Zn: 0.1; 001F Hg: 15
| AUG | 001D Hg: 5; 001H Hg: 0.1; 001L Ni: 10; 001F Hg: 15
| SEP | 001F Hg: 15
| OCT | 5 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 15
| NOV | 001F Hg: 15
| DEC | 001F Hg: 15
Rows 1101 to 1224 contain limit data for plots.
The Influent and Effluent "high" and "low" temperture values correspond to the highest and lowest daily average value for that month. The Influent high and low temperature does not necessarily correspond to the same day as the Effluent high and low temperature for that month. The "avg" temperature for Influent and Effluent is the average for the entire month. The Monthly Delta T "high" is the highest Delta T for a day of the month based on daily average Influent and Effluent temperature values. The "Avg" temperature is calculated from Influent and Effluent monthly avg values.
Press to Change Year
Press to Print Report
Press to Remove Links
* Discharges from 001D are batched. Monthly averages are flow weighted.
Note: No discharges occurred from 001I and 001K during 2008.
Blank spots for other discharge points indicate that no discharge occurred during that particular month.
* Discharges from 001D are batched. Monthly averages are flow weighted.
Note: No discharges occurred from 001I and 001K during 2008.

## Plots
Note: Values plotted at zero were below the reporting limit.
Note: The analyte was not detected at or above the reporting limit for values plotted at zero.
The 6-month median limit (the most conservative limit) is plotted on this chart.
The daily maximum limit for Copper is 50 ug/l.
Note: The analyte was not detected at or above the reporting limit for values plotted at zero.
The 6-month median limit (the most conservative limit) is plotted on this chart.
The daily maximum limit for Nickel is 100 ug/l.
Note: The analyte was not detected at or above the reporting limit for values plotted at zero.
Note: The analyte was not detected at or above the reporting limit for values plotted at zero.
The 6-month median limit is plotted on this chart. The daily maximum limit for chromium is 40 ug/l.
Note: Several data points on this chart overlap.
Note: The analyte was not detected at or above the reporting limit for values plotted at zero.
Influent and Effluent values overlap at four points on this plot.
Note: Values plotted at zero were below the reporting limit.
Note: Maximum values are plotted.
Note: Values plotted at zero were below the reporting limit.
High, low and average values overlap at eleven points on this plot.
Note: Values plotted at zero were below the reporting limit.
High, average, and low values overlap at ten points on this plot.
Note: The analyte was not detected at or above the reporting limit for values plotted at zero.
Note: The analyte was not detected at or above the reporting limit for values plotted at zero.
Note: The analyte was not detected at or above the reporting limit for values plotted at zero.
001F
|  |  | Month | Ag | Cd | Cr | Cu | Ag | Cd | Cr | Cu | Ag | Cd | Cr | Ag | Cd | Cr | Cu
|  |  | JAN | 10 | 5 | 10 | 10 | 18 | 1 | 21 | 86 | 1 | 1 | 4 | 12 | 29.5 | 22 | 75
FEB
MAR
|  |  | APR | 1 | 1 | 14 | 44 | 17 | 1 | 18 | 56 | 1 | 1 | 4 | 10 | 5 | 10 | 85
MAY
JUN
|  |  | JUL | Ag: 10; 001F Cd: 5; 001F Cr: 20; 001F Cu: 80
AUG
|  |  | SEP | 50 | 25 | 50 | 50 | 1 | 1 | 10 | 118 | 1 | 1 | 4
|  |  | OCT | 10 | 5 | 10 | 10 | 20 | 2 | 36 | 66 | 2 | 2 | 8 | 10 | 5 | 10 | 45
NOV
DEC
Note: The analyte was not detected at or above the reporting limit for values plotted at zero.
Note: The analyte was not detected at or above the reporting limit for values plotted at zero.
Note: The analyte was not detected at or above the reporting limit for values plotted at zero.
Note: The analyte was not detected at or above the reporting limit for values plotted at zero.
Note: The analyte was not detected at or above the reporting limit for values plotted at zero.
Note: Points on chart may overlap. Values plotted at zero were below the reporting limit.
Note: Points on chart may overlap. Values plotted at zero were below the reporting limit.
Note: Points on chart may overlap. Values plotted at zero were below the reporting limit.
Note: Values plotted at zero were below the reporting limit. Less than values are plotted at the value.
Note: Values plotted at zero were below the reporting limit.
Note: Values plotted at zero were below the reporting limit.
Note: High acute 6-month median value in January due to positive test results in late 2007.