## DSMR
CALIFORNIA REGIONAL WATER QUALITY | [6 empty] | DISCHARGE SELF MONITORING REPORT | [8 empty] | PACIFIC GAS AND ELECTRIC CO.
CONTROL BOARD | [15 empty] | DIABLO CANYON NUCLEAR POWER PLANT
CENTRAL COAST REGION | [15 empty] | PO BOX 56
81 HIGUERA | [15 empty] | AVILA BEACH, CALIF 93424
SAN LUIS OBISPO, CA 93401
[18 empty] | PAGE: (M) | 1
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | INFLUENT |  |  | EFFLUENT 001 |  |  | DELTA TEMP |  |  | EFFLUENT 001 |  |  | INFLUENT |  |  | EFFLUENT 001 |  |  | EFFLUENT 001P |  |  | EFFLUENT 002
ANALYSIS | TEMPERATURE |  |  | TEMPERATURE |  |  | TEMPERATURE |  |  | FLOW |  |  | pH |  |  | pH |  |  | pH |  |  | pH
UNITS | DEGREES F |  |  | DEGREES F |  |  | DEGREES F |  |  | MGD |  |  | pH UNITS |  |  | pH UNITS |  |  | pH UNITS |  |  | pH UNITS
SMPL TYPE | METERED |  |  | METERED |  |  | METERED |  |  | RECORDED |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB
FREQ. | CONTINUOUS |  |  | CONTINUOUS |  |  | CONTINUOUS |  |  | DAILY |  |  | MONTHLY |  |  | MONTHLY (***) |  |  | MONTHLY |  |  | MONTHLY
| * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | delta | Flow
1 |  |  | 50.3 |  |  | 68.8 |  |  | 18.5 |  |  | 2486 | [12 empty] | 18.5 | 2486
2 |  |  | 50.7 |  |  | 69.2 |  |  | 18.5 |  |  | 2486 | [12 empty] | 18.5 | 2486
3 |  |  | 51.1 |  |  | 69.5 |  |  | 18.4 |  |  | 2486 | [12 empty] | 18.4 | 2486
4 |  |  | 51.7 |  |  | 70.2 |  |  | 18.5 |  |  | 2486 | [12 empty] | 18.5 | 2486
5 |  |  | 51.2 |  |  | 69.8 |  |  | 18.6 |  |  | 2486 | [12 empty] | 18.6 | 2486
6 |  |  | 50.7 |  |  | 69.3 |  |  | 18.6 |  |  | 2486 | [12 empty] | 18.6 | 2486
7 |  |  | 50.8 |  |  | 69.4 |  |  | 18.6 |  |  | 2486 | [12 empty] | 18.6 | 2486
8 |  |  | 51.9 |  |  | 70.5 |  |  | 18.6 |  |  | 2486 | [6 empty] | 2 |  | 7.6 | 2 |  | 7.8 | 18.6 | 2486
9 |  |  | 52 |  |  | 70.6 |  |  | 18.6 |  |  | 2486 | [12 empty] | 18.6 | 2486
10 |  |  | 52.1 |  |  | 70.7 |  |  | 18.6 |  |  | 2486 | [12 empty] | 18.6 | 2486
11 |  |  | 52.3 |  |  | 70.9 |  |  | 18.6 |  |  | 2486 | [12 empty] | 18.6 | 2486
12 |  |  | 52.2 |  |  | 70.8 |  |  | 18.6 |  |  | 2486 | [12 empty] | 18.6 | 2486
13 |  |  | 51.9 |  |  | 70.6 |  |  | 18.7 |  |  | 2486 | [12 empty] | 18.7 | 2486
14 |  |  | 51.9 |  |  | 70.5 |  |  | 18.6 |  |  | 2486 | [12 empty] | 18.6 | 2486
15 |  |  | 51.5 |  |  | 70.2 |  |  | 18.7 |  |  | 2486 | [12 empty] | 18.7 | 2486
16 |  |  | 52.2 |  |  | 70.9 |  |  | 18.7 |  |  | 2486 | [12 empty] | 18.7 | 2486
17 |  |  | 52.6 |  |  | 71.3 |  |  | 18.7 |  |  | 2486 | [12 empty] | 18.7 | 2486
18 |  |  | 52.9 |  |  | 71.3 |  |  | 18.4 |  |  | 2486 | [12 empty] | 18.4 | 2486
19 |  |  | 55.7 |  |  | 74.4 |  |  | 18.7 |  |  | 2486 | [12 empty] | 18.7 | 2486
20 |  |  | 56.5 |  |  | 75.2 |  |  | 18.7 |  |  | 2486 |  |  | 8 |  |  | 8 | [6 empty] | 18.7 | 2486
21 |  |  | 56.6 |  |  | 75.4 |  |  | 18.8 |  |  | 2486 | [12 empty] | 18.8 | 2486
22 |  |  | 56.5 |  |  | 74.9 |  |  | 18.4 |  |  | 2486 | [12 empty] | 18.4 | 2486
23 |  |  | 57 |  |  | 75.3 |  |  | 18.3 |  |  | 2486 | [12 empty] | 18.3 | 2486
24 |  |  | 56.6 |  |  | 75.3 |  |  | 18.7 |  |  | 2486 | [12 empty] | 18.7 | 2486
25 |  |  | 56.4 |  |  | 75.2 |  |  | 18.8 |  |  | 2486 | [12 empty] | 18.8 | 2486
26 |  |  | 56.6 |  |  | 75.4 |  |  | 18.8 |  |  | 2486 | [12 empty] | 18.8 | 2486
27 |  |  | 56.2 |  |  | 74.7 |  |  | 18.5 |  |  | 2486 | [12 empty] | 18.5 | 2486
28 |  |  | 57.5 |  |  | 76.1 |  |  | 18.6 |  |  | 2486 | [12 empty] | 18.6 | 2486
29 |  |  | 58.5 |  |  | 77.1 |  |  | 18.6 |  |  | 2486 | [12 empty] | 18.6 | 2486
30 |  |  | 58.4 |  |  | 76.9 |  |  | 18.5 |  |  | 2486 | [12 empty] | 18.5 | 2486
31 |  |  | 58.1 |  |  | 76.2 |  |  | 18.1 |  |  | 2486 | [12 empty] | 18.1 | 2486
[25 empty] | delta | flow
MONTHLY AVG |  |  | 53.9 |  |  | 72.5 |  |  | 18.6 |  |  | 2486 |  |  | 8 |  |  | 8 |  |  | 7.6 |  |  | 7.8 | >22 | >2760
MONTHLY HIGH |  |  | 58.5 |  |  | 77.1 |  |  | 18.8 |  |  | 2486 |  |  | 8 |  |  | 8 |  |  | 7.6 |  |  | 7.8 | 0 | 0
MONTHLY LOW |  |  | 50.3 |  |  | 68.8 |  |  | 18.1 |  |  | 2486 |  |  | 8 |  |  | 8 |  |  | 7.6 |  |  | 7.8
TIMES EXCEEDED |  |  | NO LIMIT |  |  | NO LIMIT |  |  | MAX 22 = 0 |  |  | MAX 2760 = 0 |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT
TIMES EXCEEDED | [8 empty] | (**)
TIMES EXCEEDED
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
** EXCEPT DURING DEMUSSELING.
*** DAILY WHEN DISCHARGING CHEMICAL CLEANING WASTES FROM DISCHARGES 001D, F, I, L, AND/OR M.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (M) | 2
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | EFFLUENT 003 |  |  | EFFLUENT 004 |  |  | EFFLUENT 001N |  |  | EFFLUENT 001P |  |  | EFFLUENT 003 |  |  | EFFLUENT 001F |  |  | EFFLUENT 001 |  |  | EFFLUENT 001
ANALYSIS | pH |  |  | pH |  |  | OIL & GREASE |  |  | OIL & GREASE |  |  | OIL & GREASE |  |  | OIL & GREASE |  |  | T CHLOR RES |  |  | CHLORINE USED
UNITS | pH UNITS |  |  | pH UNITS |  |  | mg/l |  |  | mg/l |  |  | mg/l |  |  | mg/l |  |  | ug/l |  |  | lbs/day
SMPL TYPE | GRAB |  |  | GRAB |  |  | COMPOSITE |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB (****) |  |  | RECORDED
FREQ. | MONTHLY |  |  | MONTHLY |  |  | WEEKLY |  |  | WEEKLY (**) |  |  | WEEKLY (***) |  |  | MONTHLY |  |  | 2 per CYCLE |  |  | MONTHLY
0 | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | OG01N | OG01P | OG003 | OG01F | CLRES
1 | [20 empty] | 66 |  |  | 504 | 0 | 0 | 0 | 0 | 66
2 | [20 empty] | 60 |  |  | 504 | 0 | 0 | 0 | 0 | 60
3 | [20 empty] | 66 |  |  | 504 | 0 | 0 | 0 | 0 | 66
4 | [20 empty] | 66 |  |  | 504 | 0 | 0 | 0 | 0 | 66
5 | [20 empty] | 66 |  |  | 504 | 0 | 0 | 0 | 0 | 66
6 | [20 empty] | 60 |  |  | 490 | 0 | 0 | 0 | 0 | 60
7 | [6 empty] | 3 |  | ND(5) | [11 empty] | 55 |  |  | 456 | ND(5) | 0 | 0 | 0 | 55
8 |  |  | 7.8 |  |  | 7.8 | [11 empty] | ND(5) |  |  | 38 |  |  | 446 | 0 | 0 | 0 | ND(5) | 38
9 | [20 empty] | 32 |  |  | 446 | 0 | 0 | 0 | 0 | 32
10 | [20 empty] | 32 |  |  | 446 | 0 | 0 | 0 | 0 | 32
11 | [20 empty] | 26 |  |  | 482 | 0 | 0 | 0 | 0 | 26
12 | [20 empty] | 32 |  |  | 518 | 0 | 0 | 0 | 0 | 32
13 | [6 empty] | 3 | < | 5 | [11 empty] | 73 |  |  | 518 | 5 | 0 | 0 | 0 | 73
14 | [20 empty] | 38 |  |  | 518 | 0 | 0 | 0 | 0 | 38
15 | [20 empty] | 38 |  |  | 518 | 0 | 0 | 0 | 0 | 38
16 | [20 empty] | 35 |  |  | 518 | 0 | 0 | 0 | 0 | 35
17 | [20 empty] | 32 |  |  | 528 | 0 | 0 | 0 | 0 | 32
18 | [20 empty] | 32 |  |  | 547 | 0 | 0 | 0 | 0 | 32
19 | [6 empty] | 3 |  | *****ND(5) | [11 empty] | 17 |  |  | 557 | *****ND(5) | 0 | 0 | 0 | 17
20 | [20 empty] | 45 |  |  | 576 | 0 | 0 | 0 | 0 | 45
21 | [20 empty] | 46 |  |  | 576 | 0 | 0 | 0 | 0 | 46
22 | [20 empty] | 53 |  |  | 576 | 0 | 0 | 0 | 0 | 53
23 | [20 empty] | 38 |  |  | 576 | 0 | 0 | 0 | 0 | 38
24 | [20 empty] | 45 |  |  | 576 | 0 | 0 | 0 | 0 | 45
25 | [20 empty] | 49 |  |  | 576 | 0 | 0 | 0 | 0 | 49
26 | [6 empty] | 3 |  | ND(5) | [11 empty] | 41 |  |  | 590 | ND(5) | 0 | 0 | 0 | 41
27 | [6 empty] | 3 |  | ND(5) | [11 empty] | 47 |  |  | 576 | ND(5) | 0 | 0 | 0 | 47
28 | [20 empty] | 22 |  |  | 595 | 0 | 0 | 0 | 0 | 22
29 | [20 empty] | 14 |  |  | 634 | 0 | 0 | 0 | 0 | 14
30 | [19 empty] | < | 10 |  |  | 634 | 0 | 0 | 0 | 0 | 10
31 | [19 empty] | < | 10 |  |  | 667 | 0 | 0 | 0 | 0 | 10
[25 empty] | OG01N | OG01P | OG003 | OG01F | CLRES
MONTHLY AVG |  |  | 7.8 |  |  | 7.8 |  | < | 5 |  |  | NO |  |  | NO |  |  | ND(5) |  |  | 41 |  |  | 538 | >20 | >20 | >20 | >20 | >200
MONTHLY HIGH |  |  | 7.8 |  |  | 7.8 |  |  | 6 |  |  | DISCHARGE |  |  | DISCHARGE |  |  | ND(5) |  |  | 73 |  |  | 667 | 0 | 0 | 0 | 0 | 0
MONTHLY LOW |  |  | 7.8 |  |  | 7.8 |  |  | ND(5) | [8 empty] | ND(5) |  | < | 10 |  |  | 446
TIMES EXCEEDED |  |  | NO LIMIT |  |  | NO LIMIT |  |  | MO AVG 15 = 0 |  |  | MO AVG 15 = 0 |  |  | MO AVG 15 = 0 |  |  | MO AVG 15 = 0 |  |  | I MAX 200 = 0 |  |  | NO LIMIT
TIMES EXCEEDED | [8 empty] | D MAX 20 = 0 |  |  | D MAX 20 = 0 |  |  | D MAX 20 = 0 |  |  | D MAX 20 = 0
TIMES EXCEEDED
* NUMBER OF SAMPLES TAKEN DURING THE DAY.
REMARKS: | ** WHEN 001N IS DISCHARGING TO 001P.
*** WHEN 001P IS DISCHARGING TO 003.
**** CONTINUOUS CHLORINE MONITORING USED INSTEAD OF GRAB SAMPLE ANALYSIS
***** RESULTS IDENTIFIED BY CONTRACT LAB AS SUSPECT DUE TO LOW QC RECOVERY. SEE COVER LETTER.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (M) | 3
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | EFF 001N=>003 |  |  | EFF 001N=>003 |  |  | EFFLUENT 001D | [8 empty] | EFFLUENT 001F
ANALYSIS | TOTL COLIFORM |  |  | FECAL COLIFORM |  |  | SUSPENDED SOLIDS | [8 empty] | SUSPENDED SOLIDS
UNITS | MPN/100ml |  |  | MPN/100ml |  |  | mg/1 1st FLTR |  |  | mg/1 2nd FLTR |  |  | mg/1 NET |  |  | mg/1 1st FLTR |  |  | mg/1 2nd FLTR |  |  | mg/1 NET
SMPL TYPE | GRAB |  |  | GRAB |  |  | GRAB | [8 empty] | GRAB
FREQ. | 4 TIMES/WEEK |  |  | 4 TIMES/WEEK |  |  | MONTHLY | [8 empty] | MONTHLY
0 | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | SS01D | SS01F
1 | [24 empty] | 0 | 0
2 | [24 empty] | 0 | 0
3 | [24 empty] | 0 | 0
4 | [24 empty] | 0 | 0
5 | [24 empty] | 0 | 0
6 | [24 empty] | 0 | 0
7 | [6 empty] | 2 | < | 1 |  |  |  | 2 |  | ND(5) | [9 empty] | ND(5) | 0
8 | [15 empty] | 2 |  | 11 | 2 | < | 1 | 2 |  | 11 | 0 | 11
9 | [24 empty] | 0 | 0
10 | [6 empty] | 2 |  | 30 | 2 |  | 2 | 2 |  | 29 | [9 empty] | 29 | 0
11 | [24 empty] | 0 | 0
12 | [24 empty] | 0 | 0
13 | [24 empty] | 0 | 0
14 | [8 empty] | 1 | [5 empty] | ND(5) | [9 empty] | ND(5) | 0
15 | [24 empty] | 0 | 0
16 | [24 empty] | 0 | 0
17 | [24 empty] | 0 | 0
18 | [24 empty] | 0 | 0
19 | [24 empty] | 0 | 0
20 | [24 empty] | 0 | 0
21 | [24 empty] | 0 | 0
22 | [24 empty] | 0 | 0
23 | [24 empty] | 0 | 0
24 | [24 empty] | 0 | 0
25 | [24 empty] | 0 | 0
26 | [24 empty] | 0 | 0
27 | [24 empty] | 0 | 0
28 | [24 empty] | 0 | 0
29 | [24 empty] | 0 | 0
30 | [24 empty] | 0 | 0
31 | [6 empty] | 2 |  | 31 | 2 |  | 1 | 2 |  | 30 | [9 empty] | 30 | 0
[25 empty] | SS01D | SS01F
MONTHLY AVG |  |  | NO |  |  | NO | [7 empty] | **< | 5 | [8 empty] | 11 | >100 | >100
MONTHLY HIGH |  |  | DISCHARGE |  |  | DISCHARGE | [8 empty] | 31 | [8 empty] | 11 | 0 | 0
MONTHLY LOW | [14 empty] | ND(5) | [8 empty] | 11
TIMES EXCEEDED |  | 80% SMPLS>1K |  |  | MEAN>200 = |  |  | NO LIMIT |  |  | NO LIMIT |  |  |  | MO AVG 30 = 0 |  | NO LIMIT |  |  | NO LIMIT |  |  |  | MO AVG 30 = 0
TIMES EXCEEDED |  |  |  |  | 90 % SMPLS>400 | [9 empty] | D MAX 100 = 0 | [8 empty] | D MAX 100 = 0
TIMES EXCEEDED |  | I MAX >10K
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
** FLOW-WEIGHTED AVERAGES REPORTED.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (M) | 4
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | EFFLUENT 001G | [8 empty] | EFFLUENT 001H
ANALYSIS | SUSPENDED SOLIDS | [8 empty] | SUSPENDED SOLIDS
UNITS | mg/1 1st FLTR |  |  | mg/1 2nd FLTR |  |  | mg/1 NET |  |  | mg/1 1st FLTR |  |  | mg/1 2nd FLTR |  |  | mg/1 NET
SMPL TYPE | GRAB | [8 empty] | GRAB
FREQ. | MONTHLY | [8 empty] | MONTHLY
0 | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | SS01G | SS01H
1 | [11 empty] | 8 |  | < | 1 |  |  | 8 | [6 empty] | 0 | 8
2 | [24 empty] | 0 | 0
3 | [24 empty] | 0 | 0
4 | [24 empty] | 0 | 0
5 | [24 empty] | 0 | 0
6 | [24 empty] | 0 | 0
7 | [24 empty] | 0 | 0
8 | [24 empty] | 0 | 0
9 | [24 empty] | 0 | 0
10 | [24 empty] | 0 | 0
11 |  | < | 1 | [5 empty] | ND(5) | [15 empty] | ND(5) | 0
12 | [24 empty] | 0 | 0
13 | [24 empty] | 0 | 0
14 | [24 empty] | 0 | 0
15 | [24 empty] | 0 | 0
16 | [24 empty] | 0 | 0
17 | [24 empty] | 0 | 0
18 | [24 empty] | 0 | 0
19 | [24 empty] | 0 | 0
20 | [24 empty] | 0 | 0
21 | [24 empty] | 0 | 0
22 | [24 empty] | 0 | 0
23 | [24 empty] | 0 | 0
24 | [24 empty] | 0 | 0
25 | [24 empty] | 0 | 0
26 | [24 empty] | 0 | 0
27 | [24 empty] | 0 | 0
28 | [24 empty] | 0 | 0
29 | [24 empty] | 0 | 0
30 | [24 empty] | 0 | 0
31 | [24 empty] | 0 | 0
[25 empty] | SS01G | SS01H
MONTHLY AVG | [8 empty] | ND(5) | [8 empty] | 8 | [6 empty] | >100 | >100
MONTHLY HIGH | [8 empty] | ND(5) | [8 empty] | 8 | [6 empty] | 0 | 0
MONTHLY LOW | [8 empty] | ND(5) | [8 empty] | 8
TIMES EXCEEDED |  |  | NO LIMIT |  |  | NO LIMIT |  |  | MO AVG 30=0 |  | NO LIMIT |  |  | NO LIMIT |  |  |  | MO AVG 30=0
TIMES EXCEEDED | [8 empty] | D MAX 100 = 0 | [8 empty] | D MAX 100 = 0
TIMES EXCEEDED
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (M) | 5
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | EFFLUENT 001I | [8 empty] | EFFLUENT 001J
ANALYSIS | SUSPENDED SOLIDS | [8 empty] | SUSPENDED SOLIDS
UNITS | mg/1 1st FLTR |  |  | mg/1 2nd FLTR |  |  | mg/1 NET |  |  | mg/1 1st FLTR |  |  | mg/1 2nd FLTR |  |  | mg/1 NET
SMPL TYPE | GRAB | [8 empty] | GRAB
FREQ. | MONTHLY | [8 empty] | MONTHLY
0 | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | SS01I | SS01J
1 | [24 empty] | 0 | 0
2 | [24 empty] | 0 | 0
3 | [24 empty] | 0 | 0
4 | [24 empty] | 0 | 0
5 | [24 empty] | 0 | 0
6 | [24 empty] | 0 | 0
7 | [24 empty] | 0 | 0
8 | [24 empty] | 0 | 0
9 | [24 empty] | 0 | 0
10 | [24 empty] | 0 | 0
11 | [24 empty] | 0 | 0
12 | [24 empty] | 0 | 0
13 | [24 empty] | 0 | 0
14 | [24 empty] | 0 | 0
15 | [24 empty] | 0 | 0
16 | [24 empty] | 0 | 0
17 | [24 empty] | 0 | 0
18 | [24 empty] | 0 | 0
19 | [24 empty] | 0 | 0
20 | [24 empty] | 0 | 0
21 | [24 empty] | 0 | 0
22 | [24 empty] | 0 | 0
23 | [24 empty] | 0 | 0
24 | [24 empty] | 0 | 0
25 | [24 empty] | 0 | 0
26 | [24 empty] | 0 | 0
27 | [24 empty] | 0 | 0
28 | [24 empty] | 0 | 0
29 | [24 empty] | 0 | 0
30 | [24 empty] | 0 | 0
31 | [24 empty] | 0 | 0
[25 empty] | SS01I | SS01J
MONTHLY AVG | [8 empty] | NO | [8 empty] | NO | [6 empty] | >100 | >100
MONTHLY HIGH | [8 empty] | DISCHARGE | [8 empty] | DISCHARGE | [6 empty] | 0 | 0
MONTHLY LOW
TIMES EXCEEDED |  | NO LIMIT |  |  | NO LIMIT |  |  |  | MO AVG 30 = 0 |  |  | NO LIMIT |  |  | NO LIMIT |  |  | MO AVG 30 = 0
TIMES EXCEEDED | [8 empty] | MAX 100 = 0 | [8 empty] | MAX 100 = 0
TIMES EXCEEDED
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (M) | 6
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | EFFLUENT 001K | [8 empty] | EFFLUENT 001L
ANALYSIS | SUSPENDED SOLIDS | [8 empty] | SUSPENDED SOLIDS
UNITS | mg/1 1st FLTR |  |  | mg/1 2nd FLTR |  |  | mg/1 NET |  |  | mg/1 1st FLTR |  |  | mg/1 2nd FLTR |  |  | mg/1 NET
SMPL TYPE | GRAB | [8 empty] | GRAB
FREQ. | MONTHLY | [8 empty] | MONTHLY
0 | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * | [8 empty] | SS01K | SS01L
1 | [24 empty] | 0 | 0
2 | [24 empty] | 0 | 0
3 | [24 empty] | 0 | 0
4 | [24 empty] | 0 | 0
5 | [24 empty] | 0 | 0
6 | [24 empty] | 0 | 0
7 | [24 empty] | 0 | 0
8 | [9 empty] | 2 | < | 1 |  |  |  | 2 |  | ND(5) | [6 empty] | 0 | ND(5)
9 | [24 empty] | 0 | 0
10 | [24 empty] | 0 | 0
11 | [24 empty] | 0 | 0
12 | [24 empty] | 0 | 0
13 | [24 empty] | 0 | 0
14 | [24 empty] | 0 | 0
15 | [24 empty] | 0 | 0
16 | [24 empty] | 0 | 0
17 | [24 empty] | 0 | 0
18 | [24 empty] | 0 | 0
19 | [24 empty] | 0 | 0
20 | [24 empty] | 0 | 0
21 | [24 empty] | 0 | 0
22 | [24 empty] | 0 | 0
23 | [24 empty] | 0 | 0
24 | [24 empty] | 0 | 0
25 | [24 empty] | 0 | 0
26 | [24 empty] | 0 | 0
27 | [24 empty] | 0 | 0
28 | [24 empty] | 0 | 0
29 | [24 empty] | 0 | 0
30 | [24 empty] | 0 | 0
31 | [24 empty] | 0 | 0
[25 empty] | SS01K | SS01L
MONTHLY AVG | [8 empty] | NO | [8 empty] | ND(5) | [6 empty] | >100 | >100
MONTHLY HIGH | [8 empty] | DISCHARGE | [8 empty] | ND(5) | [6 empty] | 0 | 0
MONTHLY LOW | [17 empty] | ND(5)
TIMES EXCEEDED |  |  | NO LIMIT |  |  | NO LIMIT |  |  | MO AVG 30 = 0 |  |  | NO LIMIT |  |  | NO LIMIT |  |  | MO AVG 30 = 0
TIMES EXCEEDED | [8 empty] | D MAX 100 = 0 | [8 empty] | D MAX 100 = 0
TIMES EXCEEDED
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (M) | 7
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | EFFLUENT 001M | [8 empty] | EFFLUENT 001N |  |  | EFFLUENT 001P
ANALYSIS | SUSPENDED SOLIDS | [8 empty] | SUSPENDED SLDS |  |  | SUSPENDED SOLIDS
UNITS | mg/1 1st FLTR |  |  | mg/1 2nd FLTR |  |  | mg/1 NET |  |  | mg/1 |  |  | mg/1 1st FLTR |  |  | mg/1 2nd FLTR |  |  | mg/1 NET
SMPL TYPE | GRAB | [8 empty] | COMPOSITE |  |  | GRAB
FREQ. | MONTHLY | [8 empty] | WEEKLY |  |  | MONTHLY
0 | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * | [5 empty] | SS01M | SS01P
1 | [24 empty] | 0 | 0
2 | [24 empty] | 0 | 0
3 | [24 empty] | 0 | 0
4 | [24 empty] | 0 | 0
5 | [24 empty] | 0 | 0
6 | [24 empty] | 0 | 0
7 | [11 empty] | 27 | [12 empty] | 0 | 0
8 | [14 empty] | 1 |  | < | 1 |  |  | ND(5) |  |  |  | 0 | ND(5)
9 | [24 empty] | 0 | 0
10 | [24 empty] | 0 | 0
11 | [24 empty] | 0 | 0
12 | [24 empty] | 0 | 0
13 | [11 empty] | 11 | [12 empty] | 0 | 0
14 | [24 empty] | 0 | 0
15 | [24 empty] | 0 | 0
16 | [24 empty] | 0 | 0
17 | [24 empty] | 0 | 0
18 | [24 empty] | 0 | 0
19 | [11 empty] | 7 | [12 empty] | 0 | 0
20 | [24 empty] | 0 | 0
21 | [24 empty] | 0 | 0
22 | [24 empty] | 0 | 0
23 | [24 empty] | 0 | 0
24 | [24 empty] | 0 | 0
25 | [24 empty] | 0 | 0
26 | [11 empty] | 6 | [12 empty] | 0 | 0
27 | [24 empty] | 0 | 0
28 | [24 empty] | 0 | 0
29 | [24 empty] | 0 | 0
30 | [24 empty] | 0 | 0
31 | [24 empty] | 0 | 0
[25 empty] | SS01M | SS01P
MONTHLY AVG | [8 empty] | NO |  |  | 13 | [8 empty] | ND(5) |  |  |  | >100 | >100
MONTHLY HIGH | [8 empty] | DISCHARGE |  |  | 27 | [8 empty] | ND(5) |  |  |  | 0 | 0
MONTHLY LOW | [11 empty] | 6 | [8 empty] | ND(5)
TIMES EXCEEDED |  |  | NO LIMIT |  |  | NO LIMIT |  |  | MO AVG 30 = 0 |  |  | MO AVG 60 = 0 |  |  | NO LIMIT |  |  | NO LIMIT |  |  | MO AVG 30 = 0
TIMES EXCEEDED | [8 empty] | D MAX 100 = 0 | [11 empty] | D MAX 100 = 0
TIMES EXCEEDED
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (M) | 8
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | EFFLUENT 002 | [8 empty] | EFFLUENT 003
ANALYSIS | SUSPENDED SOLIDS | [8 empty] | SUSPENDED SOLIDS
UNITS | mg/1 1st FLTR |  |  | mg/1 2nd FLTR |  |  | mg/1 NET |  |  | mg/1 1st FLTR |  |  | mg/1 2nd FLTR |  |  | mg/1 NET
SMPL TYPE | GRAB | [8 empty] | GRAB
FREQ. | MONTHLY | [8 empty] | MONTHLY
0 | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * | [8 empty] | SS02 | SS03
1 | [24 empty] | 0 | 0
2 | [24 empty] | 0 | 0
3 | [24 empty] | 0 | 0
4 | [24 empty] | 0 | 0
5 | [24 empty] | 0 | 0
6 | [24 empty] | 0 | 0
7 | [24 empty] | 0 | 0
8 | 2 |  | 1 | 2 | < | 1 | 2 |  | ND(5) | 2 |  | 7 | 2 | < | 1 | 2 |  | 7 | [6 empty] | ND(5) | 7
9 | [24 empty] | 0 | 0
10 | [24 empty] | 0 | 0
11 | [24 empty] | 0 | 0
12 | [24 empty] | 0 | 0
13 | [24 empty] | 0 | 0
14 | [24 empty] | 0 | 0
15 | [24 empty] | 0 | 0
16 | [24 empty] | 0 | 0
17 | [24 empty] | 0 | 0
18 | [24 empty] | 0 | 0
19 | [24 empty] | 0 | 0
20 | [24 empty] | 0 | 0
21 | [24 empty] | 0 | 0
22 | [24 empty] | 0 | 0
23 | [24 empty] | 0 | 0
24 | [24 empty] | 0 | 0
25 | [24 empty] | 0 | 0
26 | [24 empty] | 0 | 0
27 | [24 empty] | 0 | 0
28 | [24 empty] | 0 | 0
29 | [24 empty] | 0 | 0
30 | [24 empty] | 0 | 0
31 | [24 empty] | 0 | 0
[25 empty] | SS02 | SS03
MONTHLY AVG | [8 empty] | ND(5) | [8 empty] | 7 | [6 empty] | >100 | >100
MONTHLY HIGH | [8 empty] | ND(5) | [8 empty] | 8 | [6 empty] | 0 | 0
MONTHLY LOW | [8 empty] | ND(5) | [8 empty] | 7
TIMES EXCEEDED |  |  | NO LIMIT |  |  | NO LIMIT |  |  | MO AVG 30 = 0 |  |  | NO LIMIT |  |  | NO LIMIT |  |  | MO AVG 30 = 0
TIMES EXCEEDED | [8 empty] | D MAX 100 = 0 | [8 empty] | D MAX 100 = 0
TIMES EXCEEDED
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (M) | 9
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | EFFLUENT 003 | [8 empty] | EFFLUENT 001N |  |  | EFFLUENT 001 |  |  | EFFLUENT 001 |  |  | EFFLUENT 001 |  |  | EFFLUENT 001
ANALYSIS | SUSPENDED SOLIDS | [8 empty] | SETTL SOLIDS |  |  | T CHROMIUM |  |  | COPPER |  |  | NICKEL |  |  | ZINC
UNITS | mg/1 1st FLTR |  |  | mg/1 2nd FLTR |  |  | mg/1 NET |  |  | ml/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1
SMPL TYPE | GRAB | [8 empty] | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB
FREQ. | WEEKLY WHEN 001N & 001P => 003 | [8 empty] | WEEKLY |  |  | MONTHLY |  |  | MONTHLY |  |  | MONTHLY |  |  | MONTHLY
0 | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | SS03X | SSOL01N | 01CHR | 01COP | 01NIC | 01ZIN
1 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
2 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
3 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
4 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
5 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
6 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
7 | [11 empty] | ND(0.1) | [12 empty] | 0 | ND(0.1) | 0 | 0 | 0 | 0
8 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
9 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
10 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
11 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
12 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
13 | [11 empty] | ND(0.1) | [12 empty] | 0 | ND(0.1) | 0 | 0 | 0 | 0
14 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
15 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
16 | [24 empty] | 0 |  | 0 | 0 | 0 | 0
17 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
18 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
19 | [11 empty] | ND(0.1) | [12 empty] | 0 | ND(0.1) | 0 | 0 | 0 | 0
20 | [14 empty] | ND(10) |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) | 0 | 0 | ND(10) | ND(10) | ND(10) | ND(10)
21 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
22 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
23 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
24 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
25 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
26 | [11 empty] | ND(0.1) | [12 empty] | 0 | ND(0.1) | 0 | 0 | 0 | 0
27 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
28 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
29 | [24 empty] | 0 |  | 0 | 0 | 0 | 0
30 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
31 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0
[25 empty] | SS03X | SSOL01N | 01CHR | 01COP | 01NIC | 01ZIN
MONTHLY AVG | [8 empty] | NO |  |  | ND(0.1) |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) | >100 | >3 | >40 | >50 | >100 | >380
MONTHLY HIGH | [8 empty] | DISCHARGE |  |  | ND(0.1) |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) | 0 | 0 | 0 | 0 | 0 | 0
MONTHLY LOW | [11 empty] | ND(0.1) |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) |  |  | ND(10)
TIMES EXCEEDED |  |  | NO LIMIT |  |  | NO LIMIT |  |  | MO AVG 30 = 0 |  |  | MO AVG 1.0 = 0 |  |  | 6M-MED 10 =0 |  |  | 6M-MED 10 =0 |  |  | 6M-MED 30 =0 |  |  | 6M-MED 70=0
TIMES EXCEEDED | [8 empty] | D MAX 100 = 0 |  |  | D MAX 3.0 = 0 |  |  | D MAX 40 = 0 |  |  | D MAX 50 = 0 |  |  | D MAX 100 = 0 |  |  | D MAX 380 = 0
TIMES EXCEEDED | [14 empty] | I MAX 100 = 0 |  |  | I MAX 140 = 0 |  |  | I MAX 260 = 0 |  |  | I MAX 990 = 0
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (Q) | 1
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | INFLUENT |  |  | INFLUENT |  |  | INFLUENT |  |  | INFLUENT |  |  | EFFLUENT 001 |  |  | EFFLUENT 001D |  |  | EFFLUENT 001G |  |  | EFFLUENT 001H
ANALYSIS | T CHROMIUM |  |  | COPPER |  |  | NICKEL |  |  | AMMONIA (N) |  |  | AMMONIA (N) |  |  | OIL & GREASE |  |  | OIL & GREASE |  |  | OIL & GREASE
UNITS | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | mg/1 |  |  | mg/1 |  |  | mg/1
SMPL TYPE | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB
FREQ. | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT
0 | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | 01AMM | OG01D | OG01G | OG01H
1 | [23 empty] | ND(5) | 0 | 0 | 0 | ND(5)
2 | [24 empty] | 0 | 0 | 0 | 0
3 | [24 empty] | 0 | 0 | 0 | 0
4 | [24 empty] | 0 | 0 | 0 | 0
5 | [24 empty] | 0 | 0 | 0 | 0
6 | [24 empty] | 0 | 0 | 0 | 0
7 | [24 empty] | 0 | 0 | 0 | 0
8 | [24 empty] | 0 | 0 | 0 | 0
9 | [24 empty] | 0 | 0 | 0 | 0
10 | [17 empty] | ND(5) | [6 empty] | 0 | ND(5) | 0 | 0
11 | [20 empty] | ND(5) |  |  |  | 0 | 0 | ND(5) | 0
12 | [24 empty] | 0 | 0 | 0 | 0
13 | [24 empty] | 0 | 0 | 0 | 0
14 | [17 empty] | ND(5) | [6 empty] | 0 | ND(5) | 0 | 0
15 | [24 empty] | 0 | 0 | 0 | 0
16 | [24 empty] | 0 | 0 | 0 | 0
17 | [24 empty] | 0 | 0 | 0 | 0
18 | [24 empty] | 0 | 0 | 0 | 0
19 | [24 empty] | 0 | 0 | 0 | 0
20 |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) |  |  | ND(200) |  |  | ND(200) | [9 empty] | ND(200) | 0 | 0 | 0
21 | [24 empty] | 0 | 0 | 0 | 0
22 | [24 empty] | 0 | 0 | 0 | 0
23 | [24 empty] | 0 | 0 | 0 | 0
24 | [24 empty] | 0 | 0 | 0 | 0
25 | [24 empty] | 0 | 0 | 0 | 0
26 | [24 empty] | 0 | 0 | 0 | 0
27 | [24 empty] | 0 | 0 | 0 | 0
28 | [24 empty] | 0 | 0 | 0 | 0
29 | [24 empty] | 0 | 0 | 0 | 0
30 | [24 empty] | 0 | 0 | 0 | 0
31 | [17 empty] | ND(5) | [6 empty] | 0 | ND(5) | 0 | 0
[25 empty] | 01AMM | OG01D | OG01G | OG01H
MONTHLY AVG |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) |  |  | ND(200) |  |  | ND(200) | ** |  | ND(5) |  |  | ND(5) |  |  | ND(5) | >12240 | >20 | >20 | >20
MONTHLY HIGH |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) |  |  | ND(200) |  |  | ND(200) |  |  | ND(5) |  |  | ND(5) |  |  | ND(5) | 0 | 0 | 0 | 0
MONTHLY LOW |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) |  |  | ND(200) |  |  | ND(200) |  |  | ND(5) |  |  | ND(5) |  |  | ND(5)
TIMES EXCEEDED |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | 6M-MED 3060 = 0 |  |  | MO AVG 15 = 0 |  |  | MO AVG 15 = 0 |  |  | MO AVG 15 = 0
TIMES EXCEEDED | [14 empty] | D MAX 12240 = 0 |  |  | D MAX 20 = 0 |  |  | D MAX 20 = 0 |  |  | D MAX 20 = 0
TIMES EXCEEDED | [14 empty] | I MAX 30600 = 0
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
** FLOW-WEIGHTED AVERAGE RESULT REPORTED.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (Q) | 2
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | EFFLUENT 001I |  |  | EFFLUENT 001J |  |  | EFFLUENT 001K |  |  | EFFLUENT 001L |  |  | EFFLUENT 001M |  |  | EFFLUENT 001P |  |  | EFFLUENT 002 |  |  | EFFLUENT 003
ANALYSIS | OIL & GREASE |  |  | OIL & GREASE |  |  | OIL & GREASE |  |  | OIL & GREASE |  |  | OIL & GREASE |  |  | OIL & GREASE |  |  | OIL & GREASE |  |  | OIL & GREASE
UNITS | mg/1 |  |  | mg/1 |  |  | mg/1 |  |  | mg/1 |  |  | mg/1 |  |  | mg/1 |  |  | mg/1 |  |  | mg/1
SMPL TYPE | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB
FREQ. | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT
0 | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | OG01I | OG01J | OG01K | OG01L | OG01M | OG01P | OG02 | OG03
1 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | [9 empty] | 2 |  | ND(5) | [5 empty] | ND(5) | 2 |  | ND(5) |  |  | ND(5) | 0 | 0 | 0 | ND(5) | 0 | ND(5) | ND(5) | ND(5)
9 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[25 empty] | OG01I | OG01J | OG01K | OG01L | OG01M | OG01P | OG02 | OG03
MONTHLY AVG |  |  | NO |  |  | NO |  |  | NO |  |  | ND(5) |  |  | NO |  |  | ND(5) |  |  | ND(5) |  |  | ND(5) | >20 | >20 | >20 | >20 | >20 | >20 | >20 | >20
MONTHLY HIGH |  |  | DISCHARGE |  |  | DISCHARGE |  |  | DISCHARGE |  |  | ND(5) |  |  | DISCHARGE |  |  | ND(5) |  |  | ND(5) |  |  | ND(5) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MONTHLY LOW | [11 empty] | ND(5) | [5 empty] | ND(5) |  |  | ND(5) |  |  | ND(5)
TIMES EXCEEDED |  |  | MO AVG 15 = 0 |  |  | MO AVG 15 = 0 |  |  | MO AVG 15 = 0 |  |  | MO AVG 15 = 0 |  |  | MO AVG 15 = 0 |  |  | MO AVG 15 = 0 |  |  | MO AVG 15 = 0 |  |  | MO AVG 15 = 0
TIMES EXCEEDED |  |  | D MAX 20 = 0 |  |  | D MAX 20 = 0 |  |  | D MAX 20 = 0 |  |  | D MAX 20 = 0 |  |  | D MAX 20 = 0 |  |  | D MAX 20 = 0 |  |  | D MAX 20 = 0 |  |  | D MAX 20 = 0
TIMES EXCEEDED
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (Q) | 3
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | EFFLUENT 004 |  |  | EFFLUENT 001 |  |  | EFFLUENT 001D |  |  | EFFLUENT 001H |  |  | EFFLUENT 001L |  |  | EFFLUENT 001F
ANALYSIS | OIL & GREASE |  |  | TOX CONCEN |  |  | CADMIUM |  |  | CADMIUM |  |  | CADMIUM |  |  | CADMIUM
UNITS | mg/1 |  |  | TU |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1
SMPL TYPE | GRAB |  |  | GRAB |  |  | QTRLY COMP |  |  | QTRLY COMP |  |  | QTRLY COMP |  |  | 1 WEEK COMP
FREQ. | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT
0 | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * | [8 empty] | OG04
1 | [24 empty] | 0
2 | [24 empty] | 0
3 | [24 empty] | 0
4 | [24 empty] | 0
5 | [9 empty] | 2 |  | ND(10) | 2 |  | ND(10) | [9 empty] | 0
6 | [24 empty] | 0
7 | [8 empty] | ND(10) | [8 empty] | ND(10) | [6 empty] | 0
8 |  |  | ND(5) | [21 empty] | ND(5)
9 | [24 empty] | 0
10 | [24 empty] | 0
11 | [24 empty] | 0
12 | [24 empty] | 0
13 | [24 empty] | 0
14 | [24 empty] | 0
15 | [24 empty] | 0
16 | [24 empty] | 0
17 | [24 empty] | 0
18 | [24 empty] | 0
19 | [24 empty] | 0
20 | [24 empty] | 0
21 | [24 empty] | 0
22 | [24 empty] | 0
23 | [24 empty] | 0
24 | [24 empty] | 0
25 | [24 empty] | 0
26 | [24 empty] | 0
27 | [24 empty] | 0
28 | [24 empty] | 0
29 | [24 empty] | 0
30 | [24 empty] | 0
31 | [24 empty] | 0
OG04
MONTHLY AVG |  |  | ND(5) |  |  | ** |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) | [6 empty] | >20
MONTHLY HIGH |  |  | ND(5) | [5 empty] | ND(10) |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) | [6 empty] | 0
MONTHLY LOW |  |  | ND(5) | [5 empty] | ND(10) |  |  | ND(10) |  |  | ND(10) |  |  | ND(10)
TIMES EXCEEDED |  |  | MO AVG 15 = 0 | [5 empty] | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT
TIMES EXCEEDED |  |  | D MAX 20 = 0
TIMES EXCEEDED | [5 empty] | 6M-MED 0.26=0
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
** TOXICITY TESTING PERFORMED AND REPORTED IN AUGUST.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (Q) | 4
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | EFFLUENT 001D |  |  | EFFLUENT 001H |  |  | EFFLUENT 001L |  |  | EFFLUENT 001F |  |  | EFFLUENT 001D |  |  | EFFLUENT 001H |  |  | EFFLUENT 001L |  |  | EFFLUENT 001F
ANALYSIS | CHROMIUM |  |  | T CHROMIUM |  |  | T CHROMIUM |  |  | T CHROMIUM |  |  | COPPER |  |  | COPPER |  |  | COPPER |  |  | COPPER
UNITS | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1
SMPL TYPE | QTRLY COMP |  |  | QTRLY COMP |  |  | QTRLY COMP |  |  | 1 WEEK COMP |  |  | QTRLY COMP |  |  | QTRLY COMP |  |  | QTRLY COMP |  |  | 1 WEEK COMP
FREQ. | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT
0 | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | *
1
2
3
4
5 |  |  |  | 2 |  | 21 | 2 |  | ND(10) | [6 empty] | 2 |  | 38 | 2 |  | ND(10)
6
7 |  |  | ND(10) | [8 empty] | ND(10) |  |  | ND(10) | [8 empty] | ND(10)
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
MONTHLY AVG |  |  | ND(10) |  |  | 21 |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) |  |  | 38 |  |  | ND(10) |  |  | ND(10)
MONTHLY HIGH |  |  | ND(10) |  |  | 22 |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) |  |  | 65 |  |  | ND(10) |  |  | ND(10)
MONTHLY LOW |  |  | ND(10) |  |  | 20 |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) |  |  | 11 |  |  | ND(10) |  |  | ND(10)
TIMES EXCEEDED |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT
TIMES EXCEEDED
TIMES EXCEEDED
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (Q) | 5
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | EFFLUENT 001D |  |  | EFFLUENT 001H |  |  | EFFLUENT 001L |  |  | EFFLUENT 001F |  |  | EFFLUENT 001D |  |  | EFFLUENT 001H |  |  | EFFLUENT 001L |  |  | EFFLUENT 001F
ANALYSIS | LEAD |  |  | LEAD |  |  | LEAD |  |  | LEAD |  |  | MERCURY |  |  | MERCURY |  |  | MERCURY |  |  | MERCURY
UNITS | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1
SMPL TYPE | QTRLY COMP |  |  | QTRLY COMP |  |  | QTRLY COMP |  |  | 1 WEEK COMP |  |  | QTRLY COMP |  |  | QTRLY COMP |  |  | QTRLY COMP |  |  | 1 WEEK COMP
FREQ. | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT
0 | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | *
1
2
3
4
5 |  |  |  | 2 |  | ND(10) | 2 |  | ND(10)
6
7 |  |  | ND(10) | [8 empty] | ND(10)
8
9
10
11
12
13
14
15
16
17
18
19
20
21 | [14 empty] | ND(0.20) | 2 |  | 0.23 | 2 |  | ND(0.20) |  |  | ND(0.20)
22
23
24
25
26
27
28
29
30
31
MONTHLY AVG |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) |  |  | ND(0.20) |  |  | 0.23 |  |  | ND(0.20) |  |  | ND(0.20)
MONTHLY HIGH |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) |  |  | ND(0.20) |  |  | 0.26 |  |  | ND(0.20) |  |  | ND(0.20)
MONTHLY LOW |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) |  |  | ND(10) |  |  | ND(0.20) |  |  | **0.19 |  |  | ND(0.20) |  |  | ND(0.20)
TIMES EXCEEDED |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT
TIMES EXCEEDED
TIMES EXCEEDED
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
** RESULT IS BELOW CONTRACT LAB REPORTING LIMIT. VALUE IS ESTIMATED.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (Q) | 6
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | EFFLUENT 001D |  |  | EFFLUENT 001H |  |  | EFFLUENT 001L |  |  | EFFLUENT 001F |  |  | EFFLUENT 001D |  |  | EFFLUENT 001H |  |  | EFFLUENT 001L |  |  | EFFLUENT 001F
ANALYSIS | NICKEL |  |  | NICKEL |  |  | NICKEL |  |  | NICKEL |  |  | SILVER |  |  | SILVER |  |  | SILVER |  |  | SILVER
UNITS | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1
SMPL TYPE | QTRLY COMP |  |  | QTRLY COMP |  |  | QTRLY COMP |  |  | 1 WEEK COMP |  |  | QTRLY COMP |  |  | QTRLY COMP |  |  | QTRLY COMP |  |  | 1 WEEK COMP
FREQ. | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT
0 | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | *
1
2
3
4
5 |  |  |  | 2 |  | 16 | 2 |  | ND(10)
6
7 |  |  | ND(10) | [8 empty] | 10
8
9
10
11
12
13
14
15
16
17
18
19
20
21 | [14 empty] | ND(10.0) | 2 |  | ND(10.0) | 2 |  | ND(10.0) |  |  | ND(10.0)
22
23
24
25
26
27
28
29
30
31
MONTHLY AVG |  |  | ND(10) |  |  | 16 |  |  | ND(10) |  |  | 10 |  |  | ND(10.0) |  |  | ND(10.0) |  |  | ND(10.0) |  |  | ND(10.0)
MONTHLY HIGH |  |  | ND(10) |  |  | 23 |  |  | ND(10) |  |  | 10 |  |  | ND(10.0) |  |  | ND(10.0) |  |  | ND(10.0) |  |  | ND(10.0)
MONTHLY LOW |  |  | ND(10) |  |  | 10 |  |  | ND(10) |  |  | 10 |  |  | ND(10.0) |  |  | ND(10.0) |  |  | ND(10.0) |  |  | ND(10.0)
TIMES EXCEEDED |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT
TIMES EXCEEDED
TIMES EXCEEDED
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (Q) | 7
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | EFFLUENT 001D |  |  | EFFLUENT 001H |  |  | EFFLUENT 001L |  |  | EFFLUENT 001F
ANALYSIS | ZINC |  |  | ZINC |  |  | ZINC |  |  | ZINC
UNITS | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1
SMPL TYPE | QTRLY COMP |  |  | QTRLY COMP |  |  | QTRLY COMP |  |  | 1 WEEK COMP
FREQ. | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT |  |  | JA/AP/JUL/OCT
0 | * |  |  | * |  |  | * |  |  | *
1
2
3
4
5 |  |  |  | 2 | < | 10 | 2 |  | ND(10)
6
7 |  |  | 214 | [8 empty] | 22
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
MONTHLY AVG |  |  | 214 |  | < | 10 |  |  | ND(10) |  |  | 22
MONTHLY HIGH |  |  | 214 |  |  | 17 |  |  | ND(10) |  |  | 22
MONTHLY LOW |  |  | 214 |  |  | ND(10) |  |  | ND(10) |  |  | 22
TIMES EXCEEDED |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT
TIMES EXCEEDED
TIMES EXCEEDED
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (Q) | 8
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | EFFLUENT 001D |  |  | EFFLUENT 001F |  |  | EFFLUENT 001I |  |  | EFFLUENT 001L |  |  | EFFLUENT 001M
ANALYSIS | COPPER |  |  | COPPER |  |  | COPPER |  |  | COPPER |  |  | COPPER
UNITS | mg/1 |  |  | mg/1 |  |  | mg/1 |  |  | mg/1 |  |  | mg/1
SMPL TYPE | 24-HR COMP. |  |  | 24-HR COMP. |  |  | 24-HR COMP. |  |  | 24-HR COMP. |  |  | 24-HR COMP.
FREQ. | METAL CLNG |  |  | METAL CLNG |  |  | METAL CLNG |  |  | METAL CLNG |  |  | METAL CLNG
0 | * |  |  | * |  |  | * |  |  | * |  |  | * | [11 empty] | 01DCOP | 01FCOP | 01ICOP | 01LCOP | 01MCOP
1 | [24 empty] | 0 | 0 | 0 | 0 | 0
2 | [24 empty] | 0 | 0 | 0 | 0 | 0
3 | [24 empty] | 0 | 0 | 0 | 0 | 0
4 | [24 empty] | 0 | 0 | 0 | 0 | 0
5 | [24 empty] | 0 | 0 | 0 | 0 | 0
6 | [24 empty] | 0 | 0 | 0 | 0 | 0
7 | [24 empty] | 0 | 0 | 0 | 0 | 0
8 | [24 empty] | 0 | 0 | 0 | 0 | 0
9 | [24 empty] | 0 | 0 | 0 | 0 | 0
10 | [24 empty] | 0 | 0 | 0 | 0 | 0
11 | [24 empty] | 0 | 0 | 0 | 0 | 0
12 | [24 empty] | 0 | 0 | 0 | 0 | 0
13 | [24 empty] | 0 | 0 | 0 | 0 | 0
14 | [24 empty] | 0 | 0 | 0 | 0 | 0
15 | [24 empty] | 0 | 0 | 0 | 0 | 0
16 | [24 empty] | 0 | 0 | 0 | 0 | 0
17 | [24 empty] | 0 | 0 | 0 | 0 | 0
18 | [24 empty] | 0 | 0 | 0 | 0 | 0
19 | [24 empty] | 0 | 0 | 0 | 0 | 0
20 | [24 empty] | 0 | 0 | 0 | 0 | 0
21 | [24 empty] | 0 | 0 | 0 | 0 | 0
22 | [24 empty] | 0 | 0 | 0 | 0 | 0
23 | [24 empty] | 0 | 0 | 0 | 0 | 0
24 | [24 empty] | 0 | 0 | 0 | 0 | 0
25 | [24 empty] | 0 | 0 | 0 | 0 | 0
26 | [24 empty] | 0 | 0 | 0 | 0 | 0
27 | [24 empty] | 0 | 0 | 0 | 0 | 0
28 | [24 empty] | 0 | 0 | 0 | 0 | 0
29 | [24 empty] | 0 | 0 | 0 | 0 | 0
30 | [24 empty] | 0 | 0 | 0 | 0 | 0
31 | [24 empty] | 0 | 0 | 0 | 0 | 0
[25 empty] | 01DCOP | 01FCOP | 01ICOP | 01LCOP | 01MCOP
MONTHLY AVG |  |  | NO |  |  | NO |  |  | NO |  |  | NO |  |  | NO | [9 empty] | >1 | >1 | >1 | >1 | >1
MONTHLY HIGH |  |  | DISCHARGE |  |  | DISCHARGE |  |  | DISCHARGE |  |  | DISCHARGE |  |  | DISCHARGE | [9 empty] | 0 | 0 | 0 | 0 | 0
MONTHLY LOW
TIMES EXCEEDED |  |  | MO AVG 1 = 0 |  |  | MO AVG 1 = 0 |  |  | MO AVG 1 = 0 |  |  | MO AVG 1 = 0 |  |  | MO AVG 1 = 0
TIMES EXCEEDED |  |  | D MAX 1 = 0 |  |  | D MAX 1 = 0 |  |  | D MAX 1 = 0 |  |  | D MAX 1 = 0 |  |  | D MAX 1 = 0
TIMES EXCEEDED
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (Q) | 9
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | EFFLUENT 001D |  |  | EFFLUENT 001F |  |  | EFFLUENT 001I |  |  | EFFLUENT 001L |  |  | EFFLUENT 001M
ANALYSIS | IRON |  |  | IRON |  |  | IRON |  |  | IRON |  |  | IRON
UNITS | mg/1 |  |  | mg/1 |  |  | mg/1 |  |  | mg/1 |  |  | mg/1
SMPL TYPE | 24-HR COMP. |  |  | 24-HR COMP. |  |  | 24-HR COMP. |  |  | 24-HR COMP. |  |  | 24-HR COMP.
FREQ. | METAL CLNG |  |  | METAL CLNG |  |  | METAL CLNG |  |  | METAL CLNG |  |  | METAL CLNG
0 | * |  |  | * |  |  | * |  |  | * |  |  | * | [11 empty] | 01DIRN | 01FIRN | 01IIRN | 01LIRN | 01MIRN
1 | [24 empty] | 0 | 0 | 0 | 0 | 0
2 | [24 empty] | 0 | 0 | 0 | 0 | 0
3 | [24 empty] | 0 | 0 | 0 | 0 | 0
4 | [24 empty] | 0 | 0 | 0 | 0 | 0
5 | [24 empty] | 0 | 0 | 0 | 0 | 0
6 | [24 empty] | 0 | 0 | 0 | 0 | 0
7 | [24 empty] | 0 | 0 | 0 | 0 | 0
8 | [24 empty] | 0 | 0 | 0 | 0 | 0
9 | [24 empty] | 0 | 0 | 0 | 0 | 0
10 | [24 empty] | 0 | 0 | 0 | 0 | 0
11 | [24 empty] | 0 | 0 | 0 | 0 | 0
12 | [24 empty] | 0 | 0 | 0 | 0 | 0
13 | [24 empty] | 0 | 0 | 0 | 0 | 0
14 | [24 empty] | 0 | 0 | 0 | 0 | 0
15 | [24 empty] | 0 | 0 | 0 | 0 | 0
16 | [24 empty] | 0 | 0 | 0 | 0 | 0
17 | [24 empty] | 0 | 0 | 0 | 0 | 0
18 | [24 empty] | 0 | 0 | 0 | 0 | 0
19 | [24 empty] | 0 | 0 | 0 | 0 | 0
20 | [24 empty] | 0 | 0 | 0 | 0 | 0
21 | [24 empty] | 0 | 0 | 0 | 0 | 0
22 | [24 empty] | 0 | 0 | 0 | 0 | 0
23 | [24 empty] | 0 | 0 | 0 | 0 | 0
24 | [24 empty] | 0 | 0 | 0 | 0 | 0
25 | [24 empty] | 0 | 0 | 0 | 0 | 0
26 | [24 empty] | 0 | 0 | 0 | 0 | 0
27 | [24 empty] | 0 | 0 | 0 | 0 | 0
28 | [24 empty] | 0 | 0 | 0 | 0 | 0
29 | [24 empty] | 0 | 0 | 0 | 0 | 0
30 | [24 empty] | 0 | 0 | 0 | 0 | 0
31 | [24 empty] | 0 | 0 | 0 | 0 | 0
[25 empty] | 01DIRN | 01FIRN | 01IIRN | 01LIRN | 01MIRN
MONTHLY AVG |  |  | NO |  |  | NO |  |  | NO |  |  | NO |  |  | NO | [9 empty] | >1 | >1 | >1 | >1 | >1
MONTHLY HIGH |  |  | DISCHARGE |  |  | DISCHARGE |  |  | DISCHARGE |  |  | DISCHARGE |  |  | DISCHARGE | [9 empty] | 0 | 0 | 0 | 0 | 0
MONTHLY LOW
TIMES EXCEEDED |  |  | MO AVG 1 = 0 |  |  | MO AVG 1 = 0 |  |  | MO AVG 1 = 0 |  |  | MO AVG 1 = 0 |  |  | MO AVG 1 = 0
TIMES EXCEEDED |  |  | D MAX 1 = 0 |  |  | D MAX 1 = 0 |  |  | D MAX 1 = 0 |  |  | D MAX 1 = 0 |  |  | D MAX 1 = 0
TIMES EXCEEDED
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (A) | 1
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | EFFLUENT 001 |  |  | INFLUENT |  |  | EFFLUENT |  |  | INFLUENT |  |  | EFFLUENT 001 |  |  | INFLUENT |  |  | EFFLUENT 001 |  |  | INFLUENT
ANALYSIS | TITANIUM |  |  | ARSENIC |  |  | ARSENIC |  |  | CADMIUM |  |  | CADMIUM |  |  | LEAD |  |  | LEAD |  |  | ZINC
UNITS | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1
SMPL TYPE | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB
FREQ. | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER
0 | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | 01ARS | 01CAD | 01LEAD
1 | [24 empty] | 0 | 0 | 0
2 | [24 empty] | 0 | 0 | 0
3 | [24 empty] | 0 | 0 | 0
4 | [24 empty] | 0 | 0 | 0
5 | [24 empty] | 0 | 0 | 0
6 | [24 empty] | 0 | 0 | 0
7 | [24 empty] | 0 | 0 | 0
8 | [24 empty] | 0 | 0 | 0
9 | [24 empty] | 0 | 0 | 0
10 | [24 empty] | 0 | 0 | 0
11 | [24 empty] | 0 | 0 | 0
12 | [24 empty] | 0 | 0 | 0
13 | [24 empty] | 0 | 0 | 0
14 | [24 empty] | 0 | 0 | 0
15 | [24 empty] | 0 | 0 | 0
16 | [24 empty] | 0 | 0 | 0
17 | [24 empty] | 0 | 0 | 0
18 | [24 empty] | 0 | 0 | 0
19 | [24 empty] | 0 | 0 | 0
20 | [23 empty] | ND(10) | 0 | 0 | 0
21 | [24 empty] | 0 | 0 | 0
22 | [24 empty] | 0 | 0 | 0
23 | [24 empty] | 0 | 0 | 0
24 | [24 empty] | 0 | 0 | 0
25 | [24 empty] | 0 | 0 | 0
26 | [24 empty] | 0 | 0 | 0
27 | [24 empty] | 0 | 0 | 0
28 | [24 empty] | 0 | 0 | 0
29 | [24 empty] | 0 | 0 | 0
30 | [24 empty] | 0 | 0 | 0
31 | [24 empty] | 0 | 0 | 0
[25 empty] | 01ARS | 01CAD | 01LEAD
MONTHLY AVG | [22 empty] | ** | ND(10) | >150 | >20 | >40
MONTHLY HIGH | [23 empty] | ND(10) | 0 | 0 | 0
MONTHLY LOW | [23 empty] | ND(10)
TIMES EXCEEDED |  |  | NO LIMIT |  |  | NO LIMIT |  |  | 6M-MED 30 = 0 |  |  | NO LIMIT |  |  | 6M-MED 10 = 0 |  |  | NO LIMIT |  |  | 6M-MED 10 = 0 |  |  | NO LIMIT
TIMES EXCEEDED | [8 empty] | D MAX 150 = 0 | [5 empty] | D MAX 20 = 0 | [5 empty] | D MAX 40 = 0
TIMES EXCEEDED | [8 empty] | I MAX 400 = 0 | [5 empty] | I MAX 50 - 0 | [5 empty] | I MAX 100 =0
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
** INFLUENT ANALYSIS PERFORMED FOR COMPARISON TO EFFLUENTS.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (A) | 2
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | INFLUENT |  |  | EFFLUENT 001 |  |  | INFLUENT |  |  | EFFLUENT 001 |  |  | INFLUENT |  |  | EFFLUENT 001 |  |  | INFLUENT |  |  | EFFLUENT 001
ANALYSIS | MERCURY |  |  | MERCURY |  |  | SILVER |  |  | SILVER |  |  | CYANIDE |  |  | CYANIDE |  |  | PHENOLIC CMP |  |  | PHENOLIC CMP
UNITS | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 |  |  | ug/1 (NONCL) |  |  | ug/1 (NONCL)
SMPL TYPE | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB
FREQ. | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER
0 | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | *
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
MONTHLY AVG
MONTHLY HIGH
MONTHLY LOW
TIMES EXCEEDED |  |  | NO LIMIT |  | 6M-MED 0.2=0 |  |  |  | NO LIMIT |  |  | 6M-MED 2.9=0 |  |  | NO LIMIT |  |  | 6M-MED 30=0 |  |  | NO LIMIT |  |  | 6M-MED 150=0
TIMES EXCEEDED |  |  |  |  | DMAX 0.8 = 0 | [6 empty] | DMAX 13.6=0 | [5 empty] | DMAX 100=0 | [5 empty] | DMAX 610= 0
TIMES EXCEEDED |  |  |  |  | IMAX 2 = 0 | [6 empty] | IMAX 35= 0 | [5 empty] | IMAX 260=0 | [5 empty] | IMAX 1530=0
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (A) | 3
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | INFLUENT |  |  | EFFLUENT 001 |  |  | EFFLUENT 001D |  |  | EFFLUENT 001D |  |  | EFFLUENT 001D |  |  | EFFLUENT 005 |  |  | EFFLUENT 008
ANALYSIS | CHLOR PHENOL |  |  | CHLOR PHENOL |  |  | LITHIUM |  |  | BORON |  |  | HYDRAZINE |  |  | OIL & GREASE |  |  | OIL & GREASE
UNITS | ug/1 |  |  | ug/1 |  |  | mg/1 |  |  | mg/1 |  |  | mg/1 |  |  | mg/1 |  |  | mg/1
SMPL TYPE | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB
FREQ. | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER
0 | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | *
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
MONTHLY AVG
MONTHLY HIGH
MONTHLY LOW
TIMES EXCEEDED |  |  | NO LIMIT |  |  | 6M-MED 10=0 |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | MO AVG 15=0 |  |  | MO AVG 15=0
TIMES EXCEEDED | [5 empty] | DMAX 20=0 | [11 empty] | DMAX 20=0 |  |  | DMAX 20=0
TIMES EXCEEDED | [5 empty] | IMAX 50=0
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (A) | 4
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | EFFLUENT 009 |  |  | EFFLUENT 013 |  |  | EFFLUENT 015 |  |  | EFFLUENT 016 |  |  | EFFLUENT 017 |  |  | INFLUENT |  |  | EFFLUENT 001
ANALYSIS | OIL & GREASE |  |  | OIL & GREASE |  |  | OIL & GREASE |  |  | OIL & GREASE |  |  | OIL & GREASE |  |  | PCB'S |  |  | PCB'S
UNITS | mg/1 |  |  | mg/1 |  |  | mg/1 |  |  | mg/1 |  |  | mg/1 |  |  | ug/1 |  |  | ug/1
SMPL TYPE | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB
FREQ. | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER
0 | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | *
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
MONTHLY AVG
MONTHLY HIGH
MONTHLY LOW
TIMES EXCEEDED |  |  | MO AVG 15=0 |  |  | MO AVG 15=0 |  |  | MO AVG 15=0 |  |  | MO AVG 15=0 |  |  | MO AVG 15=0 |  |  | NO LIMIT |  |  | NO LIMIT
TIMES EXCEEDED |  |  | DMAX 20=0 |  |  | DMAX 20=0 |  |  | DMAX 20=0 |  |  | DMAX 20=0 |  |  | DMAX20=0
TIMES EXCEEDED
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (A) | 5
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | EFFLUENT 001N |  |  | EFFLUENT 001N |  |  | EFFLUENT 001N |  |  | EFFLUENT 001N |  |  | EFFLUENT 001N |  |  | EFFLUENT 001N |  |  | EFFLUENT 001N |  |  | EFFLUENT 001N
ANALYSIS | SLUDGE |  |  | SLUDGE |  |  | SLUDGE |  |  | SLUDGE |  |  | SLUDGE |  |  | SLUDGE |  |  | SLUDGE |  |  | SLUDGE
UNITS | MOISTURE |  |  | TOT KJLDL N |  |  | AMMONIA (N) |  |  | NITRATE (N) |  |  | TOT PHOSPHS |  |  | pH |  |  | OIL & GREASE |  |  | BORON
SMPL TYPE | % |  |  | mg/kg |  |  | mg/kg |  |  | mg/kg |  |  | mg/kg |  |  | pH units |  |  | mg/kg |  |  | mg/kg
FREQ. | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB
|  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  |  | OCTOBER
0 | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | *
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
MONTHLY AVG
MONTHLY HIGH
MONTHLY LOW
TIMES EXCEEDED |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT |  |  | NO LIMIT
TIMES EXCEEDED
TIMES EXCEEDED
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER
[18 empty] | PAGE: (A) | 6
FACILITY I.D. | [6 empty] | YEAR / MO / DAY | [5 empty] | YEAR / MO / DAY |  |  | STATE CODE |  |  |  |  | NPDES PERMIT #
3 402003001 |  |  |  | BEGINNING |  | 2006-07-01 |  |  |  | ENDING |  | 2006-07-30 |  |  |  | 6 |  |  |  |  | CA0003751
STATION | EFFLUENT 001N |  |  | EFFLUENT 001N |  |  | EFFLUENT 001N |  |  | EFFLUENT 001N |  |  | EFFLUENT 001N |  |  | EFFLUENT 001N |  |  | EFFLUENT 001N |  |  | EFFLUENT 001N
ANALYSIS | SLUDGE |  |  | SLUDGE |  |  | SLUDGE |  |  | SLUDGE |  |  | SLUDGE |  |  | SLUDGE |  |  | SLUDGE |  |  | SLUDGE
UNITS | CADMIUM |  |  | COPPER |  |  | CHROMIUM |  |  | LEAD |  |  | NICKEL |  |  | MERCURY |  |  | ZINC |  |  | VOLUME
SMPL TYPE | mg/kg |  |  | mg/kg |  |  | mg/kg |  |  | mg/kg |  |  | mg/kg |  |  | mg/kg |  |  | mg/kg |  |  | tons
FREQ. | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB |  |  | GRAB
|  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  | OCTOBER |  |  |  | OCTOBER
0 | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | * |  |  | *
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
MONTHLY AVG
MONTHLY HIGH
MONTHLY LOW
TIMES EXCEEDED |  |  | 10xSTLC=0 |  |  | 10xSTLC=0 |  |  | 10xSTLC=0 |  |  | 10xSTLC=0 |  |  | 10xSTLC=0 |  |  | 10xSTLC=0 |  |  | 10xSTLC=0
TIMES EXCEEDED |  |  | 10 mg/kg=0 |  |  | 250 mg/kg=0 |  |  | 50 mg/kg=0 |  |  | 50 mg/kg=0 |  |  | 200 mg/kg=0 |  |  | 2 mg/kg=0 |  |  | 2500 mg/kg=0
TIMES EXCEEDED |  |  | TTLC>100=0 |  |  | TTLC>2500=0 |  |  | TTLC>500=0 |  |  | TTLC>1000=0 |  |  | TTLC>2000=0 |  |  | TTLC>20=0 |  |  | TTLC>5000=0
REMARKS: | * NUMBER OF SAMPLES TAKEN DURING THE DAY.
PRINCIPAL EXECUTIVE OFFICER | [12 empty] | SIGNATURE OF AUTHORIZED AGENT | [8 empty] | DATE
[13 empty] | Bryan Cunningham | [8 empty] | 2006-10-19
JAMES R. BECKER