## WKLYRecH2O R-1
WEEKLY REQUIREMENTS
Sample Location: R-1 North Fork Arroyo conejo, 50 feet upstream of discharge No. 005 | [9 empty] | #REF!
Date | Time | Total Flow (cfs) | pH Shall not be depressed below 6.5 or raised above 8.5 (pH Units) | Temperature Shall not be altered more than 5°F above natural temp. (°F) | Dissolved Oxygen D.O. shall not be depressed<5 mg/L due to waste discharge. (mg/L) | Total Hardness (CaCO3) (mg/L) | Residual Chlorine (mg/L) | Total Coliform (MPN/100mL) | Fecal Coliform Geo Mean Limit not > 200 MPN/100mL and not > 400 MPN/100mL in a single sample (MPN/100mL) | E. Coli Geo. Mean limit not >126 MPN/100mL and not >400 MPN/100mL in a single sample (MPN/100mL)
1
2
3
4
5
6
7 | 0803 | 2.48 | 8.1 | 66.1 | 8 | 728 | <0.02 | 9000 | 800 | 800 | 800 | 800
8
9
10
11
12
13 | 0933 | 2.4 | 8.2 | 61.9 | 10 | 696 | <0.02 | 5000 | 1700 | 1700 | 1700 | 1700
14
15
16
17
18
19 | 1445 | 2.48 | 8.5 | 73.7 | 14 | 668 | <0.02 | 5000 | 1300 | 1300 | 1300 | 1300
20
21
22
23
24
25
26
27 | 0743 | 2.65 | 8.1 | 66.4 | 7.7 | 720 | <0.02 | 1300 | 800 | 800 | 800 | 800
28
29
30
Average/Geometric Mean |  | 2.5025 | 8.225 | 67.025 | 9.925 | 703 | <0.02 | 5075 | 1090.5437 | 1090.5437 | 1090.5437 | 1090.5437
Maximum |  | 2.65 | 8.5 | 73.7 | 14 | 728 | <0.02 | 9000 | 1700 | 1700
Minimum |  | 2.4 | 8.1 | 61.9 | 7.7 | 668 | <0.002 | 1300 | 800 | 800
Note: Geometric mean limits were exceeded, however, this sample site is upstream of the effluent discharge sample site.

## WKLYRecH2O R-2
WEEKLY REQUIREMENTS
Sample Location: R-2 North Fork Arroyo Conejo, 200 feet downstream of discharge No. 005 | [9 empty] | #REF!
Date | Time | Total Flow (cfs) | pH Shall not be depressed below 6.5 or > 8.5 (pH Units) | Temperature Shall not be altered more than 5°f above natural temp. (°F) | Dissolved Oxygen D.O. shall not be depressed<5 mg/L due to waste disvharge. (mg/L) | Total Hardness (CaCO3) (mg/L) | Residual Chlorine (mg/L) | Total Coliform (MPN/100mL) | Fecal Coliform Geo Mean Limit not > 200 MPN/100mL and not more than 400 MPN/100mL in a single sample (MPN/100mL) | E. Coli Geo. Mean limit not >126 MPN/100mL and not >400 MPN/100mL in a single sample (MPN/100mL)
1
2
3
4
5
6
7 | 0732 | 17.02 | 7.1 | 74.8 | 7 | 252 | <0.02 | 9000 | 70 | 40
8
9
10
11
12
13 | 0924 | 21.28 | 7 | 74 | 7.2 | 234 | <0.02 | 5000 | 130 | 80
14
15
16
17
18
19 | 1438 | 21.19 | 7.2 | 77.7 | 7.4 | 226 | <0.02 | 5000 | 130 | 80
20
21
22
23
24
25
26
27 | 0735 | 22.15 | 7.2 | 75.6 | 6.8 | 234 | <0.02 | 1300 | 70 | 70
28
29
30
Average/Geometric mean |  | 20.41 | 7.125 | 75.525 | 7.1 | 236.5 | <0.02 | 5075 | 95.3939 | 65.0631
Maximum |  | 22.15 | 7.2 | 77.7 | 7.4 | 252 | <0.02 | 9000 | 130 | 80
Minimum |  | 17.02 | 7 | 74 | 6.8 | 226 | <0.02 | 1300 | 70 | 40

## Mo.RecH2O
MONTHLY REQUIREMENTS
Date Sampled: June 7, 2006 | Time: 0803 (R-1) and 0732 (R-2) |  |  | #REF!
CONSTITUENT | Type of Sample | Method Number | Method Detection Limit | Units | Receiving Water Concentration
[5 empty] | R-1 | R-2
Turbidity | Grab | EPA 180.1 | 0.05 | NTU | 0.6 | 0.5
BOD5 20°C | Grab | EPA 405.1 | 2 | mg/L | ND | ND
Total Dissolved Solids | Grab | EPA 160.1 | 1 | mg/L | 1318 | 680
Conductivity | Grab | EPA 120.1 | 1 | umhos/cm | 1878 | 1093
Chloride | Grab | EPA 300.0 | 0.1 | mg/L | 236 | 138
Sulfates | Grab | EPA 300.0 | 0.1 | mg/L | 368 | 159
Boron | Grab | SM4500B-B | 0.1 | mg/L | 0.5 | 0.6
Fluoride | Grab | EPA 300.0 | 0.1 | mg/L | 0.4 | 0.4
Ammonia-N | Grab | EPA 350.2 | 0.05 | mg/L | ND | 1
Nitrate-N | Grab | EPA 300.0 | 0.1 | mg/L | 0.9 | 4.3
Nitrite-N | Grab | EPA 300.0 | 0.1 | mg/L | ND | ND
Organic-N | Grab | Calculated | 1 | mg/L | 0.8 | 2.3
Total Kjeldahl Nitrogen | Grab | EPA 351.3 | 1 | mg/L | 0.8 | 3.3
Total Nitrogen | Grab | Calculated | 1 | mg/L | 1.6 | 7.6
Total Phosphate | Grab | EPA 365.2 | 0.1 | mg/L | ND | 2.4
Orthophosphate | Grab | EPA 300.0 | 0.1 | mg/L | ND | 2.1
Algal Biomass | Grab | SM10200H | 2 | ug/L | 4 | 3
Surfactants (MBAS) | Grab | SM5540C | 0.1 | mg/L | ND | ND
Surfactants (CTAS) | Grab | SM5540D | 0.2 | mg/L | ND | ND
Chemical Oxygen Demand (COD) | Grab | EPA410.1 | 1 | mg/L | 7.8 | 16.8
Oil and grease | Grab | EPA1664 | 3 | mg/L | ND | ND
Settleable Solids | Grab | SM2540F | 0.1 | mL/L/hr | ND | ND
Suspended Solids | Grab | EPA 160.2 | 5 | mg/L | 0.9 | 0.5
Copper | Grab | EPA 200.8 | 1 | ug/L | 1.4 | 4.7
Mercury | Grab | EPA 245.1 | 0.01 | ug/L | 0.06 | 0.05
Cyanide | Grab | SM4500CN | 5 | ug/L | ND | ND
Bromodichloromethane | Grab | EPA 624 | 0.5 | ug/L | ND | 4.6
Dibromochloromethane | Grab | EPA 624 | 0.5 | ug/L | ND | 2.1
Bis(2-Ethylhexyl)Phthalate | Grab | EPA 625 | 5 | ug/L | ND | ND
4,4'-DDE | Grab | EPA 608 | 0.05 | ug/L | ND | ND
4,4'-DDD | Grab | EPA 608 | 0.05 | ug/L | ND | ND