EFFLUENT AND RECEIVING WATER QUALITY ASSESSMENT

FOR THE

DEER CREEK WASTEWATER TREATMENT PLANT

Prepared for:

Regional Water Quality Control Board

Central Valley Region

On Behalf of:

El Dorado Irrigation District

Prepared by:

February 28, 2003

EFFLUENT AND RECEIVING WATER QUALITY ASSESSMENT

FOR THE

DEER CREEK WASTEWATER TREATMENT PLANT

Prepared for:

Regional Water Quality Control Board

Central Valley Region

3443 Routier Road, Suite A

Sacramento, CA  95827-3003

On Behalf of:

El Dorado Irrigation District

2890 Mosquito Road

Placerville, CA  95667

Prepared by:

9766 Waterman Road, Suite L2

Elk Grove, CA  95624

(916) 714-1801

February 28, 2003

TABLE OF CONTENTS

1	Introduction	1

1.1	Description of Project Area	1

1.2	Statement of Project Need	1

1.3	Previous Related Studies	1

1.4	Project Purpose	2

1.5	Purpose of Report	2

2	Project Approach and Methodologies	3

2.1	Monitoring Schedule	3

2.2	Sampling Methods	3

2.3	Analytical Methods	4

2.4	Sampling Location	4

2.5	Deviations from the QAPP	4

3	Analytical Results	5

3.1	Trace Metals	5

3.1.1	Effluent	5

3.1.2	Deer Creek	6

3.2	Pesticides, Herbicides, and PCBs	6

3.2.1	Effluent	6

3.2.2	Deer Creek	7

3.3	Volatile Organics	16

3.3.1	Effluent	16

3.3.2	Deer Creek	16

3.4	Semi-Volatile Organics	16

3.4.1	Effluent	16

3.4.2	Deer Creek	16

3.5	Dioxins and Furans	25

3.5.1	Effluent	25

3.5.2	Deer Creek	25

3.6	Other Conventional Constituents	26

3.6.1	Effluent	26

3.6.2	Deer Creek	26

4	Deer Creek AND EFFLUENT FLOW	29

5	Summary	30

6	References	31

List of Figures

Figure 1. Dissolved copper concentration versus hardness in the Deer Creek Wastewater Treatment Plant effluent for the period September 2002 through January 2003.	6

LIST OF TABLES

Table 1.  Trace metals concentrations in the Deer Creek Wastewater Treatment Plant effluent for the period February 2002 through January 2003.	8

Table 2.  Trace metals concentrations in Deer Creek for the period February 2002 through January 2003.	10

Table 3.  Pesticides, herbicides, and PCBs concentrations in the Deer Creek Wastewater Treatment Plant effluent for the period February through November 2002.	12

Table 4.  Pesticides, herbicides, and PCBs concentrations in Deer Creek for the period February 2002 and May 2002.	14

Table 5.  Volatile organic compound concentrations in the Deer Creek Wastewater Treatment Plant effluent for the period February 2002 through January 2003.	17

Table 6.  Volatile organic compound concentrations in Deer Creek for the period February 2002 through May 2002.	19

Table 7.  Semi-volatile organic compound concentrations in the Deer Creek Wastewater Treatment Plant effluent for the period February through November 2002.	21

Table 8.  Semi-volatile organic compound concentrations in Deer Creek for the period February and May 2002.	23

Table 9.  Dioxin and furan congener concentrations in the Deer Creek Wastewater Treatment Plant effluent during February and August 2002.	25

Table 10.  Other conventional constituent concentrations in the Deer Creek Wastewater Treatment Plant effluent for the period February 2002 through February 2003.	27

Table 11.  Other conventional constituent concentrations in Deer Creek for the period February 2002 through January 2003.	28

Table 12.  Deer Creek and effluent daily flow rate for the period February 2002 through January 2003.	29

Table 13.  Summary of Deer Creek Wastewater Treatment Plant effluent and receiving water monitoring results for the period February 2002 through February 2003.	30

APPENDICES

Appendix A: 	RWQCB Letters Dated September 10, 2001 and December 27, 2001

Appendix B:	Summary of Analytical Results by Constituent

Appendix C:	Laboratory Contacts

Appendix D:	Laboratory Analytical Reports

ACRONYMS AND ABBREVIATIONS

BHC	hexachlorocyclohexane

CTR	California Toxics Rule

DCWWTP	Deer Creek Wastewater Treatment Plant

DHS	California Department of Health Services

District	El Dorado Irrigation District

MCL	maximum contaminant level

mgd	million gallons per day

mg/l	milligram per liter

N	nitrogen

NPDES	National Pollutant Discharge Elimination System

NTR	National Toxics Rule

QAPP	Quality Assurance Project Plan

PCBs	polychlorinated biphenyls

pg/l	picograms per liter

RWQCB	Regional Water Quality Control Board, Central Valley Region

SIP	Statewide Implementation Plan

SWRCB	State Water Resources Control Board

g/l	micrograms per liter

U.S. EPA	United States Environmental Protection Agency

# Introduction

## Description of Project Area

The El Dorado Irrigation District (District) owns and operates the Deer Creek Wastewater Treatment Plant (DCWWTP).  The DCWWTP provides sewerage service to Cameron Park and the Mother Lode Service Area.  The DCWWTP is located in the Section 16, T9N, R9E, MDB&M, adjacent to Deer Creek.  Treated municipal wastewater is discharged to Deer Creek, a tributary to the Cosumnes River.  The discharges from this facility to Deer Creek are permitted by the Central Valley Regional Water Quality Control Board (RWQCB) for an average dry weather design flow of 2.5 million gallons per day (mgd) under NPDES Permit No. CA0078662, RWQCB Order No. R5-2002-0210, adopted December 6, 2002.

## Statement of Project Need

The RWQCB required the District to perform effluent and receiving water monitoring, pursuant to California Water Code Section 13267, as directed in Section 1.2 of the Policy for Implementation of Toxics Standards for Inland Surface Waters, Enclosed Bays, and Estuaries (SWRCB 2000), also referred to as the Statewide Implementation Plan or “SIP.”  The RWQCB request was made in a letter to the District dated September 10, 2001 and revised on December 27, 2001 (henceforth referred to as the 13267 letter) (Appendix A).  The 13267 letter states:

“In order to prepare appropriate NPDES permits, it is necessary to have adequate characterization of the discharged effluent and the receiving water.”

The Water Code Section 13267 letter requires the District to:

“…submit data sufficient to (1) determine if priority pollutants require effluent limitations (Reasonable Potential Analysis) and (2) calculate water quality-based effluent limitations.”

The RWQCB 13267 letter requested monitoring of priority pollutants and other constituents, including organophosphorus pesticides, drinking water constituents, and conventional constituents, such as pH and hardness, some of which are currently monitored by the District as required by its NPDES permit.

The RWQCB incorporated the effluent and receiving water monitoring requested by the 13267 letter into Provision #2 of the NPDES permit recently adopted for the DCWWTP, with a requirement to complete the study by March 1, 2003, with the exception of dioxins monitoring, which is to be completed by March 1, 2004.  However, the 13267 letter requires the dioxins study to be completed by November 1, 2004.  As stated in the NPDES permit Provision #2, “The technical report [13267 letter] requirements shall take precedence in resolving any conflict.”  Consequently, the applicable completion date for the dioxins study is November 1, 2004.

## Previous Related Studies

In accordance with a previous NPDES permit, RWQCB Order No. 97-211, the District performed a study entitled “Phase II Effluent and Receiving Water Quality Assessment for the El Dorado Irrigation District’s Deer Creek Wastewater Treatment Plant” dated February 12, 1999 (SWRI 1999).  The purpose of this report was to present findings pertaining to contaminant concentrations in the treated, undiluted effluent of the DCWWTP as determined through sampling and analyses.  The study provided a significant amount of data to assist the RWQCB with determining compliance with CTR criteria and other applicable water quality objectives, including data for many constituents required by the RWQCB’s 13267 letter.  However, the RWQCB’s 13267 letter required monitoring of additional constituents not previously monitored under the SWRI (1999) study, and established requirements for reporting limits, some of which were not met in the previous study.  In a meeting on February 11, 2002, the RWQCB NPDES permitting staff agreed to allow the District to conduct a supplemental study that, when combined with applicable data collected from the 1999 monitoring study, would provide the data requested by the 13267 letter.  This was agreed to, because the DCWWTP’s service area has not changed in any significant manner since the time that the SWRI (1999) study was completed; therefore, data from the 1999 study are adequately representative of current effluent quality.  Specifically, it was approved that additional monitoring be conducted for:  (1) constituents not monitored for in the Phase II effluent and receiving water quality assessment completed in 1999; and (2) constituents monitored in 1999 that did not meet the 13276 letter reporting limit requirements.

## Project Purpose

The specific objectives defined for this effluent and receiving water monitoring study are to provide data sufficient for RWQCB NPDES staff to:

- determine pollutants requiring water quality-based effluent limitations based on the analysis in Section 1.3 of the SIP; and

- calculate water quality-based effluent limitations in accordance with Section 1.4 of the SIP.

## Purpose of Report

The purpose of this report is to:

- meet the requirement of the District’s NPDES permit, Provision #2, which requires the District to conduct a study as requested by the RWQCB in its September 10, 2001 letter (i.e., 13267 letter); and

- meet the requirement of the RWQCB’s 13267 letter to conduct effluent and receiving water monitoring (Appendix A).

# Project Approach and Methodologies

## Monitoring Schedule

Effluent and receiving water sampling was conducted between February 2002 and February 2003.  The monitoring conducted in this study supplemented effluent and receiving water quality monitoring conducted requested by the RWQCB and conducted by the District in 1997 and 1998 to characterize the levels of priority pollutants and other conventional constituents in the DCWWTP at that time.  The results of this effluent and receiving water study were presented in a report to the RWQCB titled “Phase II Effluent and Receiving Water Quality Assessment for the El Dorado Irrigation District’s Deer Creek Wastewater Treatment Plant” (SWRI 1999).  The analyses that were completed in 1997 and 1998 that met the requested reporting limits included in the 13267 letter and, therefore, did not require re-monitoring in this study include:

- cyanide (EPA Method 335.2)

- polychlorinated biphenyls (PCBs) (EPA Method 8082)

- mercury (CV-AFS)

- trace metals (ICP/MS):  aluminum, antimony, arsenic, cadmium, chromium, copper, lead, nickel, selenium, silver, thallium, and zinc

Per the Quality Assurance Project Plan (QAPP) prepared for this project (RBI 2002), sampling was to be performed monthly from February 2002 through January 2003.  Effluent samples for trace metals (i.e., barium, beryllium, manganese, and iron), volatile organics, and other conventional constituent analyses were collected monthly.  Per the QAPP, effluent samples for asbestos and tributyltin were to be collected in the months of February, April, June, July, September, October, December, and January only.  Effluent samples for semi-volatile organics and pesticides analyses were collected quarterly.  Effluent samples for dioxins and furans were collected semi-annually.

Receiving water samples for trace metals (i.e., barium, beryllium, manganese, and iron) and conventional constituents were collected monthly.  Receiving water samples for volatile organics were collected the first four months of the study.  Receiving water samples for semi-volatile organics and pesticides were collected in February and May.  Per the QAPP, receiving water samples for asbestos and tributyltin were collected in the months of February and April only.

## Sampling Methods

Two portable composite samplers were used to collect 24-hour, time-weighted composite effluent samples for all contaminant analyses, except the volatile organic constituents, chromium VI, and sulfite analyses.  For the volatile organic constituents, chromium VI, and sulfite analyses, grab samples were collected.  A detailed description of all procedures used for collection and transport of all effluent samples is provided in the QAPP prepared for this study (RBI 2002).  All receiving water samples were grab samples.

## Analytical Methods

The laboratory analytical methods used to quantify the effluent concentrations of all contaminants monitored under the ERWQA study are identified in Appendix B.  Detailed information pertaining to these methods can be acquired by contacting the project representatives at each of the analytical laboratories used for this study.  Name, affiliation, address, and phone number for each laboratory representative are provided in Appendix C.

## Sampling Location

All effluent samples were collected at the effluent monitoring well located in the water quality building immediately prior to the discharge point, after the effluent had been fully treated by the DCWWTP.  Receiving water samples were collected at the NPDES permit R1 monitoring location, which is located in Deer Creek at the gauging station upstream of the point of discharge at the first bridge crossing Deer Creek as part of the access road to the DCWWTP.

## Deviations from the QAPP

This section describes deviations from the QAPP that were necessary to address the 13267 letter requirements and/or resulting from other unforeseen circumstances.

- Effluent and receiving water samples for copper (total recoverable and dissolved) were collected in the months of September 2002 through January 2003 to acquire additional information for a copper water-effect ratio study.

- No effluent samples were collected for asbestos and tributyltin in February 2002.  However, effluent samples for asbestos and tributyltin were collected in February 2003 thereby fulfilling the eight monthly samples specified in the QAPP.

- Effluent and receiving water samples for total recoverable aluminum, antimony, arsenic, cadmium, chromium, copper, lead, nickel, selenium, silver, thallium, and zinc were reported for February 2002, although these were not specified in the QAPP.

- No receiving water samples for dissolved concentrations of barium, beryllium, iron, or manganese were collected in February 2002.

- Effluent and receiving water samples of Aroclor were collected in February 2002, although these were not specified in the QAPP.

# Analytical Results

The following sections summarize the analytical results from the effluent and receiving water monitoring at the DCWWTP.  The major categories of constituents, as defined by the RWQCB’s 13267 letter (Appendix A), are: (1) trace metals; (2) pesticides, herbicides, and PCBs; (3) volatile organics; (4) semi-volatile organics; (5) dioxin and furans; and (6) other conventional constituents.

## Trace Metals

### Effluent

Trace metals concentrations in the undiluted effluent are provided along with the applicable water quality standards in Table 1.  Undiluted effluent trace metals concentrations were below detection limits and/or below applicable water quality standards, with the exception of copper.

The dissolved copper concentrations ranged from 10 to 31 g/l (Table 1).  These concentrations are below the California Department of Health Services (DHS) secondary maximum contaminant level (MCL) for copper of 1,000 g/l and the CTR human health standard, for the consumption of water and organisms, of 1,300 g/l.  However, the dissolved copper concentrations in all samples were greater than the CTR chronic aquatic life standard for copper, when the standard is calculated using the measured effluent hardness (Figure 1).  It should be noted that the DCWWTP’s NPDES permit already contains an effluent limitation for copper based on the CTR standard for the chronic protection of aquatic life and a schedule for compliance with the copper limitation by December 30, 2006.

The District has met with RWQCB NPDES permitting staff and discussed the value of determining the appropriate water-effect-ratio (WER) for copper, as applied to the NPDES permit’s copper limitation.  The District is currently collecting the necessary data, consistent with U.S. EPA guidelines, to determine the applicable site-specific WER to be applied in the NPDES permit copper limitation.  This constitutes an integral component of the District’s ongoing efforts to achieve compliance with the applicable copper limitation for the DCWWTP.

Figure 1. Dissolved copper concentration versus hardness in the Deer Creek Wastewater Treatment Plant effluent for the period September 2002 through January 2003.

### Deer Creek

Trace metals concentrations in Deer Creek are provided along with the applicable water quality standards in Table 2.  Deer Creek’s trace metals concentrations were below detection limits and/or below applicable water quality standards, with the exception of iron and manganese.  Deer Creek’s concentrations of iron (expressed as total recoverable) ranged from 50 g/l in June 2002 to 590 g/l in May 2002.  The samples collected in February, May, July, and December 2002 had total recoverable iron concentrations ranging from 360 to 590 g/l, which are greater than the DHS secondary MCL of 300 g/l.  Concentrations of manganese (expressed as total recoverable) ranged from 3.7 g/l to 260 g/l.  The July 2002 sample had a concentration of 260 g/l, which is greater than the DHS secondary MCL of 50 g/l.  The other 11 samples had concentrations of manganese less than the DHS secondary MCL.

## Pesticides, Herbicides, and PCBs

### Effluent

Concentrations of pesticides, herbicides, and PCBs in the undiluted effluent are provided along with the applicable water quality standards in Table 3.  Undiluted effluent concentrations of pesticides, herbicides, and PCBs were below detection limits and/or below applicable water quality standards, with the exception of dieldrin.

Dieldrin was detected in the August 2002 sample at an estimated concentration of 0.0069 g/l, which is greater than the CTR human health criterion, for the consumption of water and organisms, of 0.00014 g/l.  The dieldrin concentrations were below the DHS action level of 0.05 g/l and the CTR aquatic life criterion of 0.056 g/l.  Dieldrin is an insecticide, so its sources may be industrial or domestic in nature. From the 1950s until 1970, dieldrin was a widely used pesticide for crops such as corn and cotton.  Because of concerns about damage to the environment and potentially to human health, the U.S. EPA banned all uses of dieldrin in 1974, except to control termites. In 1987, the U.S. EPA banned all uses in the United States.

### Deer Creek

Concentrations of pesticides, herbicides, and PCBs in Deer Creek are provided along with the applicable water quality standards in Table 4.  Undiluted effluent concentrations of pesticides, herbicides, and PCBs were all below detection limits and/or below applicable water quality standards.

Table 1.  Trace metals concentrations in the Deer Creek Wastewater Treatment Plant effluent for the period February 2002 through January 2003.

| Constituent | Units | Reporting Limit | Feb-02 | Mar-02 | Apr-02 | May-02 | Jun-02 | Jul-02 | Aug-02 | Sep-02 | Oct-02 | Nov-02 | Dec-02 | Jan-03 | Human Health |  | Aquatic Life |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DHS MCL | CTR/NTR | CTR/NTR |
| Aluminum (Al) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 50 | 39 E | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1,000 (200 ) | -- | -- |
| Dissolved | g/l | 50 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1,000 (200 Error: Reference source not found) | -- | -- |
| Antimony (Sb) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 5.0 | 1.12 E | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 6 | 14 | -- |
| Dissolved | g/l | 5.0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 6 | 14 | -- |
| Arsenic (As) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 1.0 | 0.4 E | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 50 | -- | 150 |
| Dissolved | g/l | 1.0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 50 | -- | 150 |
| Barium (Ba) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 100 | 5.6 E | ND | 4.2 E | 2.4 E | 4.5 E | 4.1 E | 6.9 E | 1.7 E | 2.8 E | 2.8 E | 4.2 E | 5.3 E | 1,000 | -- | -- |
| Dissolved | g/l | 100 | -- | -- | -- | -- | -- | -- | -- | 1.6 E | 20 E | 2.9 E | 5.3 E | 5.8 E | 1,000 | -- | -- |
| Beryllium (Be) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 1.0 | ND | 0.29 E | ND | ND | ND | ND | ND | ND | 0.15 E | ND | ND | ND | 4 | -- | -- |
| Dissolved | g/l | 1.0 | -- | -- | -- | -- | -- | -- | -- | ND | ND | ND | ND | ND | 4 | -- | -- |
| Cadmium (Cd) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 0.25 | ND | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 5 | -- | 2.2 |
| Dissolved | g/l | 0.25 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 5 | -- | 2.2 Error: Reference source not found |
| Chromium (Cr) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 2.0 | 0.34 E | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 50 | -- | 11 Error: Reference source not found |
| Dissolved | g/l | 2.0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 50 | -- | 11 Error: Reference source not found |
| Copper (Cu) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 0.50 | 14 | -- | -- | -- | -- | -- | -- | 21 | 29 | 35 | 13 | 9.9 | 1,000 Error: Reference source not found | 1,300 | 9 Error: Reference source not found |
| Dissolved | g/l | 0.50 | -- | -- | -- | -- | -- | -- | -- | 20 | 28 | 31 | 11 | 10 | 1,000 Error: Reference source not found | 1,300 | 9 Error: Reference source not found |
| Iron (Fe) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 100 | ND | 33 E | 15 E | 21 E | 36 E | 8 E | 130 | 14 E | 23 E | 30 E | 12 E | 23 E | 300 Error: Reference source not found | -- | -- |
| Dissolved | g/l | 100 | -- | -- | -- | -- | -- | -- | -- | 10 E | 25 E | 21 E | 3 E | 30 E | 300 Error: Reference source not found | -- | -- |
| Lead (Pb) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 0.50 | ND | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 15 | -- | 2.5 Error: Reference source not found |
| Dissolved | g/l | 0.50 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 15 | -- | 2.5 Error: Reference source not found |
| Manganese (Mn) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 20 | 0.5 E | ND | ND | ND | ND | 4.1 E | ND | 0.50 E | ND | ND | ND | ND | 50 Error: Reference source not found | -- | -- |
| Dissolved | g/l | 20 | -- | -- | -- | -- | -- | -- | -- | 0.70 E | ND | ND | ND | ND | 50 Error: Reference source not found | -- | -- |
| Nickel (Ni) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 5.0 | 24 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 100 | 610 | 52 Error: Reference source not found |
| Dissolved | g/l | 5.0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 100 | 610 | 52 Error: Reference source not found |

Table 1.  Continued from previous page.

| Constituent | Units | Reporting Limit | Feb-02 | Mar-02 | Apr-02 | May-02 | Jun-02 | Jul-02 | Aug-02 | Sep-02 | Oct-02 | Nov-02 | Dec-02 | Jan-03 | Human Health |  | Aquatic Life |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DHS MCL Error: Reference source not found | CTR/NTR | CTR/NTR |
| Selenium (Se) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 5.0 | 1.1 E | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 50 | -- | 5 |
| Dissolved | g/l | 5.0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 50 | -- | 5 |
| Silver (Ag) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 1.0 | ND | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 100 Error: Reference source not found | -- | -- |
| Dissolved | g/l | 1.0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 100 Error: Reference source not found | -- | -- |
| Thallium (Tl) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 1.0 | ND | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 2 | 1.7 | -- |
| Dissolved | g/l | 1.0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 2 | 1.7 | -- |
| Zinc (Zn) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 10 | 30 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 5,000 Error: Reference source not found | -- | 120 Error: Reference source not found |
| Dissolved | g/l | 10 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 5,000 Error: Reference source not found | -- | 120 Error: Reference source not found |

Table 1 Notes:

E = estimated concentration between laboratory’s method detection limit and reporting limit.

ND = not detected above the laboratory’s method detection limit.

“ – “ = sample not collected this month.

BOLD values are greater than one or more of the water quality standards in the far right three columns of the table.

Table 2.  Trace metals concentrations in Deer Creek for the period February 2002 through January 2003.

| Constituent | Units | Reporting Limit | Feb-02 | Mar-02 | Apr-02 | May-02 | Jun-02 | Jul-02 | Aug-02 | Sep-02 | Oct-02 | Nov-02 | Dec-02 | Jan-03 | Human Health |  | Aquatic Life |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DHS MCL | CTR / NTR | CTR / NTR |
| Aluminum (Al) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 50 | 110 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1,000 (200 ) | -- | -- |
| Dissolved | g/l | 50 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1,000 (200 Error: Reference source not found) | -- | -- |
| Antimony (Sb) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 5.0 | ND | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 6 | 14 | -- |
| Dissolved | g/l | 5.0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 6 | 14 | -- |
| Arsenic (As) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 1.0 | 0.5 E | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 50 | -- | 150 |
| Dissolved | g/l | 1.0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 50 | -- | 150 |
| Barium (Ba) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 100 | 16.6 E | 15.7 E | 16 E | 12.1 E | 15.9 E | 8.3 E | 12 E | 12 E | 13 E | 18.4 E | 17 E | 22 E | 1,000 | -- | -- |
| Dissolved | g/l | 100 | -- | 17 E | 15 E | 12.1 E | 17.3 E | 7.9 E | 11 E | 14 E | 14 E | 16 E | 15 E | 19 E | 1,000 | -- | -- |
| Beryllium (Be) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 1.0 | 0.18 E | 0.39 E | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 4 | -- | -- |
| Dissolved | g/l | 1.0 | -- | 0.48 E | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 4 | -- | -- |
| Cadmium (Cd) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 0.25 | 2.1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 5 | -- | 2.2 |
| Dissolved | g/l | 0.25 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 5 | -- | 2.2 Error: Reference source not found |
| Chromium (Cr) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 2.0 | 0.86 E | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 50 | -- | 11 Error: Reference source not found |
| Dissolved | g/l | 2.0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 50 | -- | 11 Error: Reference source not found |
| Copper (Cu) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 0.50 | 4.5 | -- | -- | -- | -- | -- | -- | 1.3 | 1.3 | 4.2 | 3.5 | 1.4 | 1,000 Error: Reference source not found | 1,300 | 9 Error: Reference source not found |
| Dissolved | g/l | 0.50 | -- | -- | -- | -- | -- | -- | -- | 1.7 | 2.1 | 4.2 | 3.1 | 1.8 | 1,000 Error: Reference source not found | 1,300 | 9 Error: Reference source not found |
| Iron (Fe) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 100 | 520 | 140 | 85 E | 590 | 50 E | 550 | 300 | 67 E | 65 E | 88 E | 360 | 120 | 300 Error: Reference source not found | -- | -- |
| Dissolved | g/l | 100 | -- | 38 E | 50 E | 190 | 79 E | 120 | 190 | 47 E | 39 E | 54 E | 170 | 47 E | 300 Error: Reference source not found | -- | -- |
| Lead (Pb) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 0.50 | ND | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 15 | -- | 2.5 Error: Reference source not found |
| Dissolved | g/l | 0.50 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 15 | -- | 2.5 Error: Reference source not found |
| Manganese (Mn) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 20 | 8.8 E | 3.7 E | 4.5 E | 13.5 E | 6.4 E | 260 | 30 | 13 E | 6.0 E | 10.2 E | 12 E | 7.6 E | 50 Error: Reference source not found | -- | -- |
| Dissolved | g/l | 20 | -- | 2.2 E | 3.1 E | 4.3 E | 3.4 E | 180 | 7.0 E | 10 E | 3.0 E | 7.6 E | ND | 6.3 E | 50 Error: Reference source not found | -- | -- |
| Nickel (Ni) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 5.0 | 35 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 100 | 610 | 52 Error: Reference source not found |
| Dissolved | g/l | 5.0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 100 | 610 | 52 Error: Reference source not found |

Table 2.  Continued from previous page.

| Constituent | Units | Reporting Limit | Feb-02 | Mar-02 | Apr-02 | May-02 | Jun-02 | Jul-02 | Aug-02 | Sep-02 | Oct-02 | Nov-02 | Dec-02 | Jan-03 | Human Health |  | Aquatic Life |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DHS MCL Error: Reference source not found | CTR / NTR | CTR / NTR |
| Selenium (Se) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 5.0 | ND | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 50 | -- | 5 |
| Dissolved | g/l | 5.0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 50 | -- | 5 |
| Silver (Ag) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 1.0 | ND | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 100 Error: Reference source not found | -- | -- |
| Dissolved | g/l | 1.0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 100 Error: Reference source not found | -- | -- |
| Thallium (Tl) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 1.0 | ND | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 2 | 1.7 | -- |
| Dissolved | g/l | 1.0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 2 | 1.7 | -- |
| Zinc (Zn) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Total Recoverable | g/l | 10 | 4 E | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 5,000 Error: Reference source not found | -- | 120 Error: Reference source not found |
| Dissolved | g/l | 10 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 5,000 Error: Reference source not found | -- | 120 Error: Reference source not found |

Table 2 Notes:

E = estimated concentration between laboratory’s method detection limit and reporting limit.

ND = not detected above the laboratory’s method detection limit.

“ – “ = sample not collected this month.

BOLD values are greater than one or more of the water quality standards in the far right three columns of the table.

Table 3.  Pesticides, herbicides, and PCBs concentrations in the Deer Creek Wastewater Treatment Plant effluent for the period February through November 2002.

| Constituent | Units | Reporting Limit | Feb-02 | May-02 | Aug-02 | Nov-02 | Human Health |  | Aquatic Life |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | DHS MCL | CTR/NTR | CTR/NTR |
| 2,4,5-TP (Silvex) | g/l | 1.0-10 | ND | ND | ND | ND | 50 | -- | -- |
| 2,4-D | g/l | 1.0-10 Error: Reference source not found | ND | ND | ND | ND | 70 | -- | -- |
| 4,4’-DDD | g/l | 0.050 | ND | ND | ND | ND | -- | 0.00083 | -- |
| 4,4’-DDE | g/l | 0.050 | ND | ND | ND | ND | -- | 0.00059 | -- |
| 4,4’-DDT | g/l | 0.010 | ND | ND | ND | ND | -- | 0.00059 | 0.001 |
| Alachlor | g/l | 1.0 | ND | ND | ND | ND | 2 | -- | -- |
| Aldrin | g/l | 0.0050 | ND | ND | ND | ND | 0.002 | 0.00013 | -- |
| alpha-BHC | g/l | 0.010 | ND | ND | ND | ND | 0.015 Error: Reference source not found | 0.0039 | -- |
| Aroclor 1016 | g/l | 0.50 | ND | -- | -- | -- | 0.5 | 0.00017 Error: Reference source not found | 0.014 Error: Reference source not found |
| Aroclor 1221 | g/l | 0.50 | ND | -- | -- | -- | 0.5 Error: Reference source not found | 0.00017 Error: Reference source not found | 0.014 Error: Reference source not found |
| Aroclor 1232 | g/l | 0.50 | ND | -- | -- | -- | 0.5 Error: Reference source not found | 0.00017 Error: Reference source not found | 0.014 Error: Reference source not found |
| Aroclor 1242 | g/l | 0.50 | ND | -- | -- | -- | 0.5 Error: Reference source not found | 0.00017 Error: Reference source not found | 0.014 Error: Reference source not found |
| Aroclor 1248 | g/l | 0.50 | ND | -- | -- | -- | 0.5 Error: Reference source not found | 0.00017 Error: Reference source not found | 0.014 Error: Reference source not found |
| Aroclor 1254 | g/l | 0.50 | ND | -- | -- | -- | 0.5 Error: Reference source not found | 0.00017 Error: Reference source not found | 0.014 Error: Reference source not found |
| Aroclor 1260 | g/l | 0.50 | ND | -- | -- | -- | 0.5 Error: Reference source not found | 0.00017 Error: Reference source not found | 0.014 Error: Reference source not found |
| Atrazine | g/l | 1.0 | ND | 2.2 | ND | ND | 3 | -- | -- |
| Bentazon | g/l | 2.0-20 Error: Reference source not found | ND | ND | ND | ND | 18 | -- | -- |
| beta-BHC | g/l | 0.0050 | ND | ND | ND | ND | 0.3 Error: Reference source not found | 0.014 | -- |
| Carbofuran | g/l | 5.0 | ND | ND | ND | ND | 18 | -- | -- |
| Chlordane | g/l | 0.10 | ND | ND | ND | ND | 0.1 | 0.00057 | 0.0043 |
| Chlorpyrifos | g/l | 1.0 | ND | ND | ND | ND | -- | -- | -- |
| Dalapon | g/l | 2.0-20 Error: Reference source not found | ND | ND | ND | ND | 200 | -- | -- |
| delta-BHC | g/l | 0.0050 | ND | ND | ND | ND | -- | -- | -- |
| Di(2-ethylhexyl)adipate | g/l | 5.0 | ND | ND | ND | ND | 400 | -- | -- |
| Diazinon | g/l | 0.25 | ND | ND | ND | ND | -- | -- | -- |
| Dibromochloropropane | g/l | 0.010 | ND | ND | ND | ND | 5 | 4.7 | -- |
| Dieldrin | g/l | 0.010 | ND | ND | 0.0069 E | ND | 0.05 Error: Reference source not found | 0.00014 | 0.056 |
| Dinoseb | g/l | 1.0-10 Error: Reference source not found | ND | ND | ND | ND | 7 | -- | -- |
| Diquat | g/l | 4.0 | ND | ND | ND | ND | 20 | -- | -- |
| Endosulfan I | g/l | 0.020 | ND | ND | ND | ND | -- | 110 | 0.056 |
| Endosulfan II | g/l | 0.010 | ND | ND | ND | ND | -- | 110 | 0.056 |
| Endosulfan sulfate | g/l | 0.050 | ND | ND | ND | ND | -- | 110 | -- |
| Endothall | g/l | 45 | ND | ND | ND | ND | 100 | -- | -- |
| Endrin | g/l | 0.010 | ND | ND | ND | ND | 2 | 0.76 | 0.036 |
| Endrin aldehyde | g/l | 0.010 | ND | ND | ND | ND | -- | 0.76 | -- |
| Ethylene dibromide | g/l | 0.020 | ND | ND | ND | ND | 0.05 | -- | -- |
| gamma-BHC (Lindane) | g/l | 0.020 | ND | ND | 0.015 E | ND | 0.2 | 0.019 | -- |
| Glyphosate | g/l | 25 | ND | ND | ND | ND | 700 | -- | -- |
| Heptachlor | g/l | 0.010 | ND | ND | ND | ND | 0.01 | 0.00021 | 0.0038 |
| Heptachlor epoxide | g/l | 0.010 | ND | ND | ND | ND | 0.01 | 0.0001 | 0.0038 |
| Methoxychlor | g/l | 10 | ND | ND | ND | ND | 40 (30 proposed) | -- | -- |
| Molinate | g/l | 2.0 | ND | 1.4 E | ND | ND | 20 | -- |  |
| Oxamyl | g/l | 20 | ND | ND | ND | ND | 200 | -- | -- |
| Picloram | g/l | 1.0-10 Error: Reference source not found | ND | ND | ND | ND | 500 | -- | -- |
| Simazine | g/l | 4.0 | ND | ND | ND | ND | 4 | -- | -- |
| Thiobencarb | g/l | 1.0 | ND | ND | ND | ND | 70 (1 ) | -- |  |
| Toxaphene | g/l | 0.50 | ND | ND | ND | ND | 3 | 0.00073 | 0.0002 |

Table 3 Notes:

E = estimated concentration between laboratory’s method detection limit and reporting limit.

ND = not detected above the laboratory’s method detection limit.

“ – “ = sample not collected this month.

BOLD values are greater than one or more of the water quality standards in the far right three columns of the table.

Table 4.  Pesticides, herbicides, and PCBs concentrations in Deer Creek for the period February 2002 and May 2002.

| Constituent | Units | Reporting Limit | Feb-02 | May-02 | Human Health |  | Aquatic Life |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | DHS MCL | CTR/NTR | CTR/NTR |
| 2,4,5-TP (Silvex) | g/l | 1.0 | ND | ND | 50 | -- | -- |
| 2,4-D | g/l | 1.0 | ND | ND | 70 | -- | -- |
| 4,4’-DDD | g/l | 0.050 | ND | ND | -- | 0.00083 | -- |
| 4,4’-DDE | g/l | 0.050 | ND | ND | -- | 0.00059 | -- |
| 4,4’-DDT | g/l | 0.010 | ND | ND | -- | 0.00059 | 0.001 |
| Alachlor | g/l | 1.0 | ND | 1.9 | 2 | -- | -- |
| Aldrin | g/l | 0.0050 | ND | ND | 0.002 | 0.00013 | -- |
| alpha-BHC | g/l | 0.010 | ND | ND | 0.015 Error: Reference source not found | 0.0039 | -- |
| Aroclor 1016 | g/l | 0.50 | ND | -- | 0.5 | 0.00017 Error: Reference source not found | 0.014 Error: Reference source not found |
| Aroclor 1221 | g/l | 0.50 | ND | -- | 0.5 Error: Reference source not found | 0.00017 Error: Reference source not found | 0.014 Error: Reference source not found |
| Aroclor 1232 | g/l | 0.50 | ND | -- | 0.5 Error: Reference source not found | 0.00017 Error: Reference source not found | 0.014 Error: Reference source not found |
| Aroclor 1242 | g/l | 0.50 | ND | -- | 0.5 Error: Reference source not found | 0.00017 Error: Reference source not found | 0.014 Error: Reference source not found |
| Aroclor 1248 | g/l | 0.50 | ND | -- | 0.5 Error: Reference source not found | 0.00017 Error: Reference source not found | 0.014 Error: Reference source not found |
| Aroclor 1254 | g/l | 0.50 | ND | -- | 0.5 Error: Reference source not found | 0.00017 Error: Reference source not found | 0.014 Error: Reference source not found |
| Aroclor 1260 | g/l | 0.50 | ND | -- | 0.5 Error: Reference source not found | 0.00017 Error: Reference source not found | 0.014 Error: Reference source not found |
| Atrazine | g/l | 1.0 | ND | 1.2 | 3 | -- | -- |
| Bentazon | g/l | 2.0 | ND | ND | 18 | -- | -- |
| beta-BHC | g/l | 0.0050 | ND | ND | 0.3 Error: Reference source not found | 0.014 | -- |
| Carbofuran | g/l | 5.0 | ND | ND | 18 | -- | -- |
| Chlordane | g/l | 0.10 | ND | ND | 0.1 | 0.00057 | 0.0043 |
| Chlorpyrifos | g/l | 1.0 | ND | ND | -- | -- | -- |
| Dalapon | g/l | 2.0 | ND | ND | 200 | -- | -- |
| delta-BHC | g/l | 0.0050 | ND | ND | -- | -- | -- |
| Di(2-ethylhexyl)adipate | g/l | 5.0 | ND | ND | 400 | -- | -- |
| Diazinon | g/l | 0.25 | ND | ND | -- | -- | -- |
| Dibromochloropropane | g/l | 0.010 | ND | ND | 5 | 4.7 | -- |
| Dieldrin | g/l | 0.010 | ND | ND | 0.05 Error: Reference source not found | 0.00014 | 0.056 |
| Dinoseb | g/l | 1.0 | ND | ND | 7 | -- | -- |
| Diquat | g/l | 4.0 | ND | ND | 20 | -- | -- |
| Endosulfan I | g/l | 0.020 | ND | ND | -- | 110 | 0.056 |
| Endosulfan II | g/l | 0.010 | ND | ND | -- | 110 | 0.056 |
| Endosulfan sulfate | g/l | 0.050 | ND | ND | -- | 110 | -- |
| Endothall | g/l | 45 | ND | ND | 100 | -- | -- |
| Endrin | g/l | 0.010 | ND | ND | 2 | 0.76 | 0.036 |
| Endrin aldehyde | g/l | 0.010 | ND | ND | -- | 0.76 | -- |
| Ethylene dibromide | g/l | 0.020 | ND | ND | 0.05 | -- | -- |
| gamma-BHC (Lindane) | g/l | 0.020 | ND | ND | 0.2 | 0.019 | -- |
| Glyphosate | g/l | 25 | ND | ND | 700 | -- | -- |
| Heptachlor | g/l | 0.010 | ND | ND | 0.01 | 0.00021 | 0.0038 |
| Heptachlor epoxide | g/l | 0.010 | ND | ND | 0.01 | 0.0001 | 0.0038 |
| Methoxychlor | g/l | 10 | ND | ND | 40 (30 proposed) | -- | -- |
| Molinate | g/l | 2.0 | ND | ND | 20 | -- |  |
| Oxamyl | g/l | 20 | ND | ND | 200 | -- | -- |
| Picloram | g/l | 1.0 | ND | ND | 500 | -- | -- |
| Simazine | g/l | 4.0 | ND | ND | 4 | -- | -- |
| Thiobencarb | g/l | 1.0 | ND | ND | 70 (1 ) | -- |  |
| Toxaphene | g/l | 0.50 | ND | ND | 3 | 0.00073 | 0.0002 |

Table 4 Notes:

ND = not detected above the laboratory’s method detection limit.

“ – “ = sample not collected this month.

## Volatile Organics

### Effluent

Concentrations of volatile organic compounds in the undiluted effluent are provided along with the applicable water quality standards in Table 5.  Undiluted effluent concentrations of volatile organics were below detection limits and/or below applicable water quality standards, with the exception of bromodichloromethane, dibromochloromethane, and the sum of total trihalomethanes (i.e., sum of bromodichloromethane, bromoform, chloroform, and dibromochloromethane).

Bromodichloromethane concentrations ranged from 4.8 to 12 g/l, which are greater than the CTR human health standards, for the consumption of water and organisms, of 0.56 g/l.  Detectable effluent concentrations of dibromochloromethane ranged from 0.37 to 1.2 g/l.  Detectable effluent concentrations of dibromochloromethane in February, March, April, May, June, July, September, and October 2002 ranged from 0.50 to 1.2 g/l, which are greater than the CTR human health standards for the consumption of water and organisms of 0.401 g/l.  The sum of the trihalomethanes ranged from 43.1 to 152.61 g/l.  The sum of the trihalomethanes was greater than the DHS primary MCL of 100 g/l in June, August, and September 2002, at concentrations of 152.61 g/l, 105.5 g/l, and 100.2 g/l, respectively.  Bromodichloromethane, chloroform, and dibromochloromethane are likely formed as a by-product when chlorine is added in the effluent treatment process.

It should be noted that the DCWWTP’s NPDES permit already contains effluent limitations for bromodichloromethane (0.56 g/l monthly average), dibromochloromethane (0.41 g/l monthly average), and total trihalomethanes (80 g/l monthly average) and a schedule for compliance with these limitations by December 30, 2006.

### Deer Creek

Concentrations of volatile organic compounds in Deer Creek are provided along with the applicable water quality standards in Table 6.  Concentrations of volatile organic compounds in Deer Creek were below detection limits and/or below applicable water quality standards in all samples.

## Semi-Volatile Organics

### Effluent

Concentrations of semi-volatile organic compounds in the undiluted effluent are provided along with the applicable water quality standards in Table 7.  Undiluted effluent concentrations of semi-volatile organics were below detection limits in all samples.

### Deer Creek

Concentrations of semi-volatile organic compounds in Deer Creek are provided along with the applicable water quality standards in Table 8.  Concentrations of semi-volatile organics in Deer Creek were below detection limits in all samples.

Table 5.  Volatile organic compound concentrations in the Deer Creek Wastewater Treatment Plant effluent for the period February 2002 through January 2003.

| Constituent | Units | Reporting Limit | Feb-02 | Mar-02 | Apr-02 | May-02 | Jun-02 | Jul-02 | Aug-02 | Sep-02 | Oct-02 | Nov-02 | Dec-02 | Jan-03 | Human Health |  | Aquatic Life |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DHS MCL | CTR/NTR | CTR/NTR |
| 1,1,1-Trichloroethane | g/l | 2.0 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 200 | -- | -- |
| 1,1,2,2-Tetrachloroethane | g/l | 0.50 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1 | 0.17 | -- |
| 1,1,2-Trichloro-1,2,2-trifluoroethane | g/l | 10 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1,200 | -- | -- |
| 1,1,2-Trichloroethane | g/l | 0.50 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 5 | 0.6 | -- |
| 1,1-Dichloroethane | g/l | 1.0 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 5 | -- | -- |
| 1,1-Dichloroethene | g/l | 0.50 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 6 | 0.057 | -- |
| 1,2,4-Trichlorobenzene | g/l | 5.0 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 70 (5 proposed) | -- | -- |
| 1,2-Dichlorobenzene | g/l | 2.0 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 600 | 2,700 | -- |
| 1,2-Dichloroethane | g/l | 0.50 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.5 | 0.38 | -- |
| 1,2-Dichloropropane | g/l | 0.50 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 5 | 0.52 | -- |
| 1,3-Dichlorobenzene | g/l | 2.0 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 130 | 400 | -- |
| 1,3-Dichloropropene | g/l | 0.50 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.5 | 10 | -- |
| 1,4-Dichlorobenzene | g/l | 2.0 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 5 | 400 | -- |
| 2-Chloroethyl vinyl ether | g/l | 1.0 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | -- | -- | -- |
| Acrolein | g/l | 5.0 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | -- | 320 | -- |
| Acrylonitrile | g/l | 2.0 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | -- | 0.059 | -- |
| Benzene | g/l | 0.50 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.34 E | ND | 1 | 1.2 | -- |
| Bromodichloromethane | g/l | 0.50 | 5.6 | 7.6 | 9.7 | 8.5 | 12 | 8.6 | 5.5 | 12 | 6.9 | 6.2 | 5.1 | 4.8 | 100 (80 proposed) | 0.56 | -- |
| Bromoform | g/l | 2.0 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 100 (80 proposed) Error: Reference source not found | 4.3 | -- |
| Bromomethane | g/l | 2.0 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | -- | 48 | -- |
| Carbon tetrachloride | g/l | 0.50 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.5 | 0.25 | -- |
| Chlorobenzene | g/l | 2.0 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 70 | 680 | -- |
| Chloroethane | g/l | 2.0 | ND | ND | 0.53 E | ND | ND | ND | ND | ND | ND | ND | ND | ND | -- | -- | -- |
| Chloroform | g/l | 0.50 | 37 | 48 | 61 | 49 | 140 | 71 | 95 | 87 | 42 | 48 | 44 | 51 | 100 (80 proposed) Error: Reference source not found | -- | -- |
| Chloromethane | g/l | 0.50 | ND | ND | 0.45 E | ND | 0.65 | ND | ND | ND | ND | ND | ND | ND | -- | -- | -- |
| cis-1,2-Dichloroethene | g/l | 0.50 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 6 | -- | -- |
| Dibromochloromethane | g/l | 0.50 | 0.50 | 0.65 | 0.83 | 0.68 | 0.61 | 0.59 | ND | 1.2 | 0.57 | 0.37 E | ND | ND | 100 (80 proposed) Error: Reference source not found | 0.401 | -- |

Table 5.  Continued from previous page.

| Constituent | Units | Reporting Limit | Feb-02 | Mar-02 | Apr-02 | May-02 | Jun-02 | Jul-02 | Aug-02 | Sep-02 | Oct-02 | Nov-02 | Dec-02 | Jan-03 | Human Health |  | Aquatic Life |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DHS MCL Error: Reference source not found | CTR/NTR | CTR/NTR |
| Dichloromethane | g/l | 2.0 | 0.31 E | 0.31 E | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 5 | 4.7 | -- |
| Ethylbenzene | g/l | 2.0 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 700 (300 proposed) | 3,100 | -- |
| Hexachlorobutadiene | g/l | 1.0 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | -- | 0.44 | -- |
| Methyl-tert-butyl ether | g/l | 3.0 | 0.45 E | ND | ND | ND | ND | ND | ND | ND | 0.51 E | ND | 1.79 E | ND | 13 (5 ) | -- | -- |
| Naphthalene | g/l | 10 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | -- | -- | -- |
| Styrene | g/l | 0.50 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 100 | -- | -- |
| Tetrachloroethene | g/l | 0.50 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 5 | 0.8 | -- |
| Toluene | g/l | 2.0 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 150 | 6,800 | -- |
| trans-1,2-dichloroethene | g/l | 1.0 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 10 | 700 | -- |
| Trichloroethene | g/l | 2.0 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 5 | 2.7 | -- |
| Trichlorofluoromethane | g/l | 5.0 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 150 | -- |  |
| Vinyl chloride | g/l | 0.50 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.5 | 2 | -- |
| Xylenes | g/l | 0.50 | ND | ND | 13 | ND | ND | ND | ND | ND | ND | ND | ND | ND | 1,750 | -- | -- |

Table 5 Notes:

E = estimated concentration between laboratory’s method detection limit and reporting limit.

ND = not detected above the laboratory’s method detection limit.

BOLD values are greater than one or more of the water quality standards in the far right three columns of the table.

Table 6.  Volatile organic compound concentrations in Deer Creek for the period February 2002 through May 2002.

| Constituent | Units | Reporting Limit | Feb-02 | Mar-02 | Apr-02 | May-02 | Human Health |  | Aquatic Life |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | DHS MCL | CTR/NTR | CTR/NTR |
| 1,1,1-Trichloroethane | g/l | 2.0 | ND | ND | ND | ND | 200 | -- | -- |
| 1,1,2,2-Tetrachloroethane | g/l | 0.50 | ND | ND | ND | ND | 1 | 0.17 | -- |
| 1,1,2-Trichloro-1,2,2-trifluoroethane | g/l | 10 | ND | ND | ND | ND | 1,200 | -- | -- |
| 1,1,2-Trichloroethane | g/l | 0.50 | ND | ND | ND | ND | 5 | 0.6 | -- |
| 1,1-Dichloroethane | g/l | 1.0 | ND | ND | ND | ND | 5 | -- | -- |
| 1,1-Dichloroethene | g/l | 0.50 | ND | ND | ND | ND | 6 | 0.057 | -- |
| 1,2,4-Trichlorobenzene | g/l | 5.0 | ND | ND | ND | ND | 70 (5 proposed) | -- | -- |
| 1,2-Dichlorobenzene | g/l | 2.0 | ND | ND | ND | ND | 600 | 2,700 | -- |
| 1,2-Dichloroethane | g/l | 0.50 | ND | ND | ND | ND | 0.5 | 0.38 | -- |
| 1,2-Dichloropropane | g/l | 0.50 | ND | ND | ND | ND | 5 | 0.52 | -- |
| 1,3-Dichlorobenzene | g/l | 2.0 | ND | ND | ND | ND | 130 | 400 | -- |
| 1,3-Dichloropropene | g/l | 0.50 | ND | ND | ND | ND | 0.5 | 10 | -- |
| 1,4-Dichlorobenzene | g/l | 2.0 | ND | ND | ND | ND | 5 | 400 | -- |
| 2-Chloroethyl vinyl ether | g/l | 1.0 | ND | ND | ND | ND | -- | -- | -- |
| Acrolein | g/l | 5.0 | ND | ND | ND | ND | -- | 320 | -- |
| Acrylonitrile | g/l | 2.0 | ND | ND | ND | ND | -- | 0.059 | -- |
| Benzene | g/l | 0.50 | ND | ND | ND | ND | 1 | 1.2 | -- |
| Bromodichloromethane | g/l | 0.50 | ND | ND | ND | ND | 100 (80 proposed) | 0.56 | -- |
| Bromoform | g/l | 2.0 | ND | ND | ND | ND | 100 (80 proposed) Error: Reference source not found | 4.3 | -- |
| Bromomethane | g/l | 2.0 | ND | ND | ND | ND | -- | 48 | -- |
| Carbon tetrachloride | g/l | 0.50 | ND | ND | ND | ND | 0.5 | 0.25 | -- |
| Chlorobenzene | g/l | 2.0 | ND | ND | ND | ND | 70 | 680 | -- |
| Chloroethane | g/l | 2.0 | ND | ND | ND | ND | -- | -- | -- |
| Chloroform | g/l | 0.50 | ND | ND | ND | 0.39 E | 100 (80 proposed) Error: Reference source not found | -- | -- |
| Chloromethane | g/l | 0.50 | ND | ND | ND | ND | -- | -- | -- |
| cis-1,2-Dichloroethene | g/l | 0.50 | ND | ND | ND | ND | 6 | -- | -- |
| Dibromochloromethane | g/l | 0.50 | ND | ND | ND | ND | 100 (80 proposed) Error: Reference source not found | 0.401 | -- |
| Dichloromethane | g/l | 2.0 | ND | ND | ND | ND | 5 | 4.7 | -- |
| Ethylbenzene | g/l | 2.0 | ND | ND | ND | ND | 700 (300 proposed) | 3,100 | -- |
| Hexachlorobutadiene | g/l | 1.0 | ND | ND | ND | ND | -- | 0.44 | -- |
| Methyl-tert-butyl ether | g/l | 3.0 | ND | ND | ND | ND | 13 (5 ) | -- | -- |
| Naphthalene | g/l | 10 | ND | ND | ND | ND | -- | -- | -- |
| Styrene | g/l | 0.50 | ND | ND | ND | ND | 100 | -- | -- |
| Tetrachloroethene | g/l | 0.50 | ND | ND | ND | ND | 5 | 0.8 | -- |
| Toluene | g/l | 2.0 | ND | ND | ND | ND | 150 | 6,800 | -- |
| trans-1,2-dichloroethene | g/l | 1.0 | ND | ND | ND | ND | 10 | 700 | -- |
| Trichloroethene | g/l | 2.0 | ND | ND | ND | ND | 5 | 2.7 | -- |
| Trichlorofluoromethane | g/l | 5.0 | ND | ND | ND | ND | 150 | -- |  |
| Vinyl chloride | g/l | 0.50 | ND | ND | ND | ND | 0.5 | 2 | -- |
| Xylenes | g/l | 0.50 | ND | ND | ND | ND | 1,750 | -- | -- |

Table 6 Notes:

E = estimated concentration between laboratory’s method detection limit and reporting limit.

ND = not detected above the laboratory’s method detection limit.

Table 7.  Semi-volatile organic compound concentrations in the Deer Creek Wastewater Treatment Plant effluent for the period February through November 2002.

| Constituent | Units | Reporting Limit | Feb-02 | May-02 | Aug-02 | Nov-02 | Human Health |  | Aquatic Life |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | DHS MCL | CTR/NTR | CTR/NTR |
| 1,2-Diphenylhydrazine | g/l | 1.0 | ND | ND | ND | ND | -- | 0.04 | -- |
| 2-Chloronaphthalene | g/l | 10 | ND | ND | ND | ND | -- | 1,700 | -- |
| 2-Chlorophenol | g/l | 2.0 | ND | ND | ND | ND | -- | 120 | -- |
| 2-methyl-4,6-dinitrophenol | g/l | 10 | ND | ND | ND | ND | -- | 13.4 | -- |
| 2,4-Dichlorophenol | g/l | 2.0 | ND | ND | ND | ND | -- | 93 | -- |
| 2,4-Dimethylphenol | g/l | 3.0 | ND | ND | ND | ND | 400 | 540 | -- |
| 2,4-Dinitrophenol | g/l | 5.0 | ND | ND | ND | ND | -- | 70 | -- |
| 2,4-Dinitrotoluene | g/l | 5.0 | ND | ND | ND | ND | -- | 0.11 | -- |
| 2,4,6-Trichlorophenol | g/l | 10 | ND | ND | ND | ND | -- | 2.1 | -- |
| 2,6-Dinitrotoluene | g/l | 5.0 | ND | ND | ND | ND | -- | -- | -- |
| 2-Nitrophenol | g/l | 10 | ND | ND | ND | ND | -- | -- | -- |
| 3,3’-Dichlorobenzidine | g/l | 5.0 | ND | ND | ND | ND | -- | 0.04 | -- |
| 4-Bromophenyl phenyl ether | g/l | 10 | ND | ND | ND | ND | -- | -- | -- |
| 4-Chloro-3-methylphenol | g/l | 5.0 | ND | ND | ND | ND | -- | -- | -- |
| 4-Chlorophenyl phenyl ether | g/l | 5.0 | ND | ND | ND | ND | -- | -- | -- |
| 4-Nitrophenol | g/l | 10 | ND | ND | ND | ND | -- | -- | -- |
| Acenaphthene | g/l | 0.50 | ND | ND | ND | ND | -- | 1,200 | -- |
| Acenaphthylene | g/l | 0.20 | ND | ND | ND | ND | -- | -- | -- |
| Anthracene | g/l | 0.20 | ND | ND | ND | ND | -- | 9,600 | -- |
| Benzidine | g/l | 5.0 | ND | ND | ND | ND | -- | 0.00012 | -- |
| Benzo (a) anthracene | g/l | 0.20 | ND | ND | ND | ND | -- | 0.0044 | -- |
| Benzo (a) pyrene | g/l | 0.10 | ND | ND | ND | ND | 0.2 | 0.0044 | -- |
| Benzo (b) fluoranthene | g/l | 0.20 | ND | ND | ND | ND | -- | 0.0044 | -- |
| Benzo (g,h,i) perylene | g/l | 0.20 | ND | ND | ND | ND | -- | -- | -- |
| Benzo (k) fluoranthene | g/l | 0.20 | ND | ND | ND | ND | -- | 0.0044 | -- |
| Bis (2-chloroethoxy) methane | g/l | 5.0 | ND | ND | ND | ND | -- | -- | -- |
| Bis (2-chloroethyl) ether | g/l | 1.0 | ND | ND | ND | ND | -- | 0.031 | -- |
| Bis (2-chloroisopropyl) ether | g/l | 10 | ND | ND | ND | ND | -- | 1,400 | -- |
| Bis (2-ethylhexyl) phthalate | g/l | 5.0 | ND | ND | ND | ND | 4 | 1.8 | -- |
| Butyl benzyl phthalate | g/l | 10 | ND | ND | ND | ND | -- | 3,000 |  |
| Chrysene | g/l | 0.20 | ND | ND | ND | ND | -- | 0.0044 | -- |
| Dibenzo (a,h) anthracene | g/l | 0.10 | ND | ND | ND | ND | -- | 0.0044 | -- |
| Diethyl phthalate | g/l | 2.0 | ND | ND | ND | ND | -- | 23,000 | -- |
| Dimethyl phthalate | g/l | 2.0 | ND | ND | ND | ND | -- | 313,000 | -- |
| Di-n-butyl phthalate | g/l | 10 | ND | ND | ND | ND | -- | 2,700 | -- |
| Di-n-octyl phthalate | g/l | 10 | ND | ND | ND | ND | -- | -- | -- |
| Fluoranthene | g/l | 0.20 | ND | ND | ND | ND | -- | 300 | -- |
| Fluorene | g/l | 0.20 | ND | ND | ND | ND | -- | 1,300 | -- |
| Hexachlorobenzene | g/l | 1.0 | ND | ND | ND | ND | 1 | 0.00075 | -- |
| Hexachlorobutadiene | g/l | 10 | ND | ND | ND | ND | -- | 0.44 | -- |
| Hexachlorocyclopentadiene | g/l | 5.0 | ND | ND | ND | ND | 50 | 240 | -- |
| Hexachloroethane | g/l | 2.0 | ND | ND | ND | ND | -- | 1.9 | -- |
| Indeno (1,2,3-c,d) pyrene | g/l | 0.050 | ND | ND | ND | ND | -- | 0.0044 | -- |
| Isophorone | g/l | 1.0 | ND | ND | ND | ND | -- | 8.4 | -- |
| Naphthalene | g/l | 0.20 | ND | ND | ND | ND | -- | -- | -- |
| Nitrobenzene | g/l | 10 | ND | ND | ND | ND | -- | 17 | -- |
| N-Nitrosodimethylamine | g/l | 5.0 | ND | ND | ND | ND | -- | 0.00069 | -- |
| N-Nitroso-di-n-propylamine | g/l | 5.0 | ND | ND | ND | ND | -- | 0.005 | -- |
| N-Nitrosodiphenylamine | g/l | 1.0 | ND | ND | ND | ND | -- | 5 | -- |

Table 7.  Continued from previous page.

| Constituent | Units | Reporting Limit | Feb-02 | May-02 | Aug-02 | Nov-02 | Human Health |  | Aquatic Life |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | DHS MCL Error: Reference source not found | CTR/NTR | CTR/NTR |
| Pentachlorophenol | g/l | 1.0-10 | ND | ND | ND | ND | 1 | 0.28 | 6.7 (at pH 7) |
| Phenanthrene | g/l | 0.20 | ND | ND | ND | ND | -- | -- | -- |
| Phenol | g/l | 1.0 | ND | ND | ND | ND | 5 Error: Reference source not found | 21,000 | -- |
| Pyrene | g/l | 0.20 | ND | ND | ND | ND | -- | 960 | -- |

Table 7 Notes:

ND = not detected above the laboratory’s method detection limit.

Table 8.  Semi-volatile organic compound concentrations in Deer Creek for the period February and May 2002.

| Constituent | Units | Reporting Limit | Feb-02 | May-02 | Human Health |  | Aquatic Life |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | DHS MCL | CTR/NTR | CTR/NTR |
| 1,2-Diphenylhydrazine | g/l | 1.0 | ND | ND | -- | 0.04 | -- |
| 2-Chloronaphthalene | g/l | 10 | ND | ND | -- | 1,700 | -- |
| 2-Chlorophenol | g/l | 2.0 | ND | ND | -- | 120 | -- |
| 2-methyl-4,6-dinitrophenol | g/l | 10 | ND | ND | -- | 13.4 | -- |
| 2,4-Dichlorophenol | g/l | 2.0 | ND | ND | -- | 93 | -- |
| 2,4-Dimethylphenol | g/l | 3.0 | ND | ND | 400 | 540 | -- |
| 2,4-Dinitrophenol | g/l | 5.0 | ND | ND | -- | 70 | -- |
| 2,4-Dinitrotoluene | g/l | 5.0 | ND | ND | -- | 0.11 | -- |
| 2,4,6-Trichlorophenol | g/l | 10 | ND | ND | -- | 2.1 | -- |
| 2,6-Dinitrotoluene | g/l | 5.0 | ND | ND | -- | -- | -- |
| 2-Nitrophenol | g/l | 10 | ND | ND | -- | -- | -- |
| 3,3’-Dichlorobenzidine | g/l | 5.0 | ND | ND | -- | 0.04 | -- |
| 4-Bromophenyl phenyl ether | g/l | 10 | ND | ND | -- | -- | -- |
| 4-Chloro-3-methylphenol | g/l | 5.0 | ND | ND | -- | -- | -- |
| 4-Chlorophenyl phenyl ether | g/l | 5.0 | ND | ND | -- | -- | -- |
| 4-Nitrophenol | g/l | 10 | ND | ND | -- | -- | -- |
| Acenaphthene | g/l | 0.50 | ND | ND | -- | 1,200 | -- |
| Acenaphthylene | g/l | 0.20 | ND | ND | -- | -- | -- |
| Anthracene | g/l | 0.20 | ND | ND | -- | 9,600 | -- |
| Benzidine | g/l | 5.0 | ND | ND | -- | 0.00012 | -- |
| Benzo (a) anthracene | g/l | 0.20 | ND | ND | -- | 0.0044 | -- |
| Benzo (a) pyrene | g/l | 0.10 | ND | ND | 0.2 | 0.0044 | -- |
| Benzo (b) fluoranthene | g/l | 0.20 | ND | ND | -- | 0.0044 | -- |
| Benzo (g,h,i) perylene | g/l | 0.20 | ND | ND | -- | -- | -- |
| Benzo (k) fluoranthene | g/l | 0.20 | ND | ND | -- | 0.0044 | -- |
| Bis (2-chloroethoxy) methane | g/l | 5.0 | ND | ND | -- | -- | -- |
| Bis (2-chloroethyl) ether | g/l | 1.0 | ND | ND | -- | 0.031 | -- |
| Bis (2-chloroisopropyl) ether | g/l | 10 | ND | ND | -- | 1,400 | -- |
| Bis (2-ethylhexyl) phthalate | g/l | 5.0 | ND | ND | 4 | 1.8 | -- |
| Butyl benzyl phthalate | g/l | 10 | ND | ND | -- | 3,000 |  |
| Chrysene | g/l | 0.20 | ND | ND | -- | 0.0044 | -- |
| Dibenzo (a,h) anthracene | g/l | 0.10 | ND | ND | -- | 0.0044 | -- |
| Diethyl phthalate | g/l | 2.0 | ND | ND | -- | 23,000 | -- |
| Dimethyl phthalate | g/l | 2.0 | ND | ND | -- | 313,000 | -- |
| Di-n-butyl phthalate | g/l | 10 | ND | ND | -- | 2,700 | -- |
| Di-n-octyl phthalate | g/l | 10 | ND | ND | -- | -- | -- |
| Fluoranthene | g/l | 0.20 | ND | ND | -- | 300 | -- |
| Fluorene | g/l | 0.20 | ND | ND | -- | 1,300 | -- |
| Hexachlorobenzene | g/l | 1.0 | ND | ND | 1 | 0.00075 | -- |
| Hexachlorobutadiene | g/l | 10 | ND | ND | -- | 0.44 | -- |
| Hexachlorocyclopentadiene | g/l | 5.0 | ND | ND | 50 | 240 | -- |
| Hexachloroethane | g/l | 2.0 | ND | ND | -- | 1.9 | -- |
| Indeno (1,2,3-c,d) pyrene | g/l | 0.050 | ND | ND | -- | 0.0044 | -- |
| Isophorone | g/l | 1.0 | ND | ND | -- | 8.4 | -- |
| Naphthalene | g/l | 0.20 | ND | ND | -- | -- | -- |
| Nitrobenzene | g/l | 10 | ND | ND | -- | 17 | -- |
| N-Nitrosodimethylamine | g/l | 5.0 | ND | ND | -- | 0.00069 | -- |
| N-Nitroso-di-n-propylamine | g/l | 5.0 | ND | ND | -- | 0.005 | -- |
| N-Nitrosodiphenylamine | g/l | 1.0 | ND | ND | -- | 5 | -- |

Table 8.  Continued from previous page.

| Constituent | Units | Reporting Limit | Feb-02 | May-02 | Human Health |  | Aquatic Life |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | DHS MCL Error: Reference source not found | CTR/NTR | CTR/NTR |
| Pentachlorophenol | g/l | 1.0 | ND | ND | 1 | 0.28 | 6.7 (at pH 7) |
| Phenanthrene | g/l | 0.20 | ND | ND | -- | -- | -- |
| Phenol | g/l | 1.0 | ND | ND | 5 Error: Reference source not found | 21,000 | -- |
| Pyrene | g/l | 0.20 | ND | ND | -- | 960 | -- |

Table 8 Notes:

ND = not detected above the laboratory’s method detection limit.

## Dioxins and Furans

The CTR includes standards for 2,3,7,8-tetrachlorodibenzo-p-dioxin (2,3,7,8-TCDD).  In addition to this compound, the State is concerned with levels of sixteen other congeners of chlorinated dibenzodioxins and chlorinated dibenzofurans, though no standards have been formally adopted.  The results from sampling for the seventeen dioxin and furan congeners are presented below.

### Effluent

Dioxin and furan congener concentrations were monitored during two months – February and August 2002.  No dioxin or furan congeners were detected in the effluent.  Table 9 summarizes results from the dioxin and furans analyses.

### Deer Creek

Because there is no assimilative capacity for dioxins or furans in the receiving water, it was only necessary to determine whether dioxins and furans are present in the effluent.  Therefore, Deer Creek water was not sampled for dioxin and furans analyses.

Table 9.  Dioxin and furan congener concentrations in the Deer Creek Wastewater Treatment Plant effluent during February and August 2002.

| Constituent | Units | Effluent Concentrations |  | Human Health |  | Aquatic Life |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Feb-02 | Aug-02 | DHS MCL | CTR/NTR | CTR/NTR |
| 2,3,7,8-TCDD | pg/l | < 3.19 | < 1.83 | 30 | 0.013 | -- |
| 1,2,3,7,8-PeCDD | pg/l | < 2.70 | < 2.65 | -- | -- | -- |
| 1,2,3,4,7,8-HxCDD | pg/l | < 1.60 | < 2.83 | -- | -- | -- |
| 1,2,3,6,7,8-HxCDD | pg/l | < 1.79 | < 2.94 | -- | -- | -- |
| 1,2,3,7,8,9-HxCDD | pg/l | < 1.62 | < 2.87 | -- | -- | -- |
| 1,2,3,4,6,7,8-HpCDD | pg/l | < 2.33 | < 2.62 | -- | -- | -- |
| OCDD | pg/l | < 9.70 | < 3.65 | -- | -- | -- |
| 2,3,7,8-TCDF | pg/l | < 1.02 | < 1.18 | -- | -- | -- |
| 1,2,3,7,8-PeCDF | pg/l | < 1.95 | < 2.50 | -- | -- | -- |
| 2,3,4,7,8-PeCDF | pg/l | < 1.58 | < 2.17 | -- | -- | -- |
| 1,2,3,4,7,8-HxCDF | pg/l | < 1.03 | < 0.762 | -- | -- | -- |
| 1,2,3,6,7,8-HxCDF | pg/l | < 1.06 | < 0.775 | -- | -- | -- |
| 2,3,4,6,7,8-HxCDF | pg/l | < 1.01 | < 0.975 | -- | -- | -- |
| 1,2,3,7,8,9-HxCDF | pg/l | < 1.51 | < 1.31 | -- | -- | -- |
| 1,2,3,4,6,7,8-HpCDF | pg/l | < 0.804 | < 1.09 | -- | -- | -- |
| 1,2,3,4,7,8,9-HpCDF | pg/l | < 1.17 | < 1.36 | -- | -- | -- |
| OCDF | pg/l | < 3.82 | < 3.93 | -- | -- | -- |

Table 9 Notes:

## Other Conventional Constituents

### Effluent

Concentrations of other conventional constituents in the undiluted effluent are provided along with the applicable water quality standards in Table 10.  Undiluted effluent concentrations of other conventional constituents were below detection limits and/or below applicable water quality standards, with the exception of nitrate.  Nitrate (as N) concentrations ranged from 10 mg/l to 24 mg/l.  Eleven of twelve samples had concentrations greater than the DHS primary MCL of 10 mg/l.  It should be noted that the DCWWTP’s NPDES permit already contains an effluent limitation for nitrate (10 mg/l monthly average) and a schedule for compliance with the nitrate limitation by December 30, 2006.

In addition to the constituents presented in Table 10, the 13267 letter required monitoring of pH and temperature.  These parameters are required to be monitored in the effluent, per the DCWWTP’s NPDES permit, on a daily basis.  This frequency exceeded that required by the 13267 letter, which was monthly.  Therefore, no additional monitoring for pH and temperature was necessary to meet the pH and temperature data requirements defined by the 13267 letter.  For effluent pH and temperature data, refer to the District’s monthly self-monitoring reports for the DCWWTP.

### Deer Creek

Concentrations of other conventional constituents in Deer Creek are provided along with the applicable water quality standards in Table 11.  Deer Creek’s concentrations of other conventional constituents were below detection limits and/or below applicable water quality standards.

In addition to the constituents presented in Table 10, the 13267 letter required monitoring of pH and temperature.  These parameters are required to be monitored in the creek, per the DCWWTP’s NPDES permit, on a weekly basis.  This frequency exceeded that required by the 13267 letter, which was monthly.  Therefore, no additional monitoring for pH and temperature was conducted beyond that performed to meet the monitoring requirements of the NPDES permit.  For Deer Creek pH and temperature data, refer to the District’s monthly self-monitoring reports for the DCWWTP.

Table 10.  Other conventional constituent concentrations in the Deer Creek Wastewater Treatment Plant effluent for the period February 2002 through February 2003.

| Constituent | Units | Reporting Limit | Feb-02 | Mar-02 | Apr-02 | May-02 | Jun-02 | Jul-02 | Aug-02 | Sep-02 | Oct-02 | Nov-02 | Dec-02 | Jan-03 | Feb-03 | Human Health |  | Aquatic Life |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DHS MCL | CTR/NTR | CTR/NTR |
| Asbestos | mf/l | 0.20 | -- | -- | ND | -- | ND | ND | -- | ND | ND | -- | ND | ND | ND | 7 | 7 | -- |
| Ammonia (as N) | mg/l | 0.10 | 0.22 | 0.81 | 0.27 | 0.81 | 0.18 | 0.18 | 0.22 | 0.27 | 0.17 | 0.24 | 0.18 | 0.23 | -- | -- | -- | -- |
| Chloride | mg/l | 1.0-10 | 55 | 63 | 65 | 65 | 66 | 78 | 69 | 64 | 67 | 64 | 48 | 65 | -- | 250 | -- | -- |
| Chromium VI | g/l | 1.0 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | -- | -- | -- | 11 |
| Fluoride | mg/l | 0.10 | 0.089 E | 0.084 E | 0.19 | 0.20 | 0.25 | 0.22 | 0.22 | 0.29 | 0.29 | ND | ND | 0.41 | -- | 2.0 | -- | -- |
| Hardness (as CaCO3) | mg/l | 1.0 | 92 | 87 | 79 | 130 | 61 | 160 | 190 | 56 | 22 | 66 | 99 | 87 | -- | -- | -- | -- |
| Methylene blue active substances | mg/l | 0.10-0.50 | 0.18 E | 0.19 E | 0.19 E | 0.16 E | 0.11 E | 0.18 E | 0.078 E | 0.13 E | 0.14 E | 0.12 E | 0.15 E | 0.15 | -- | 0.5 Error: Reference source not found | -- | -- |
| Nitrate (as N) | mg/l | 1.0-10 | 14 | 15 | 18 | 19 | 22 | 24 | 13 | 10 | 19 | 24 | 12 | 17 | -- | 10 | -- | -- |
| Nitrite (as N) | mg/l | 0.10-0.40 | ND | ND | ND | ND | ND | ND | ND | ND | 0.15 E | ND | ND | ND | -- | 1 | -- | -- |
| pH | std units | 0.1 | 7.5 | 7.0 | 7.4 | 7.1 | 7.3 | 7.1 | 7.2 | -- | -- | 6.9 | 7.1 | 7.2 | -- |  |  |  |
| Phosphorus, total | mg/l | 0.50-1.0 | 17.9 | 2.2 | 2.9 | 3.2 | 4.1 | 3.6 | 3.2 | 3.7 | 3.3 | 3.3 | 1.9 | 2.6 | -- | -- | -- | -- |
| Specific conductance | mhos/cm | 1.0 | 630 | 730 | 780 | 730 | 820 | 850 | 790 | 710 | 760 | 790 | 570 | 750 | -- | -- | -- | -- |
| Sulfate (as SO4) | mg/l | 1.0-10 | 72 | 84 | 81 | 85 | 85 | 100 | 93 | 78 | 82 | 67 | 71 | 73 | -- | 250 Error: Reference source not found | -- | -- |
| Sulfide (as S) | mg/l | 1.0 | ND | ND | ND | 5.8 | ND | ND | ND | 2.4 | ND | 4.6 | ND | 4.8 | -- | -- | -- | -- |
| Sulfite (as SO3) | mg/l | 5.0 | ND | ND | ND | 17 | 6.0 | ND | ND | 16 | ND | 7.0 | ND | 12 | -- | -- | -- | -- |
| Total dissolved solids | mg/l | 1.0 | 440 | 480 | 530 | 520 | 600 | 550 | 530 | 480 | 460 | 490 | 390 | 480 | -- | 1,000 Error: Reference source not found | -- | -- |
| Tributyltin | g/l | 0.005-10 | ND | -- | ND | -- | ND | ND | -- | ND | ND | -- | ND | ND | ND | -- | -- | -- |

Table 10 Notes:

E = estimated concentration between laboratory’s method detection limit and reporting limit.

ND = not detected above the laboratory’s method detection limit.

“ – “ = sample not collected this month.

Table 11.  Other conventional constituent concentrations in Deer Creek for the period February 2002 through January 2003.

| Constituent | Units | Reporting Limit | Feb-02 | Mar-02 | Apr-02 | May-02 | Jun-02 | Jul-02 | Aug-02 | Sep-02 | Oct-02 | Nov-02 | Dec-02 | Jan-03 | Feb-03 | Human Health |  | Aquatic Life |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | DHS MCL | CTR/NTR | CTR/NTR |
| Asbestos | mf/l | 0.20 | ND | -- | ND | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 7 | 7 | -- |
| Ammonia (as N) | mg/l | 0.10 | 0.18 | 0.73 | 0.18 | 0.55 | 0.21 | 0.34 | 0.20 | 0.21 | 0.13 | 0.15 | 0.18 | 0.26 | -- | -- | -- | -- |
| Chloride | mg/l | 0.50-1.0 | 9.2 | 11 | 11 | 7.4 | 12 | 18 | 18 | 15 | 13 | 14 | 12 | 13 | -- | 250 | -- | -- |
| Chromium VI | g/l | 1.0 | ND | ND | ND | ND | -- | -- | -- | -- | -- | -- | -- | -- | -- |  |  |  |
| Fluoride | mg/l | 0.10 | 0.077 E | 0.094 E | ND | 0.19 | 0.24 | 0.22 | ND | 0.28 | 0.28 | 0.51 | 0.34 | 0.46 | -- | 2.0 | -- | -- |
| Hardness (as CaCO3) | mg/l | 1.0 | 160 | 180 | 220 | 71 | 260 | 190 | 140 | 270 | 250 | 140 | 150 | 230 | -- | -- | -- | -- |
| Methylene blue active substances | mg/l | 0.10-0.50 | 0.047 E | ND | ND | 0.025 E | ND | 0.038 E | ND | 0.024 E | ND | ND | 0.047 E | ND | -- | 0.5 Error: Reference source not found | -- | -- |
| Nitrate (as N) | mg/l | 0.50 | 0.52 | 0.39 E | 0.29 E | 0.46 E | 0.164 E | 0.13 E | 0.14 E | 0.12 E | 0.16 E | 0.36 E | 0.83 | 0.17 | -- | 10 | -- | -- |
| Nitrite (as N) | mg/l | 0.10-0.40 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | 0.13 E | 0.13 | -- | 1 | -- | -- |
| pH | std units | 0.1 | 8.4 | 8.5 | 8.7 | 8.1 | 8.7 | 8.4 | 8.1 | -- | -- | 8.2 | 8.0 | 8.27 | -- |  |  |  |
| Phosphorus, total | mg/l | 0.050 | 0.021 E | ND | ND | 0.064 | ND | 0.062 | ND | ND | ND | 0.16 | 0.035 E | ND | -- | -- | -- | -- |
| Specific conductance | mhos/cm | 1.0 | 280 | 310 | 390 | 230 | 400 | 410 | 280 | 460 | 470 | 480 | 280 | 410 | -- | -- | -- | -- |
| Sulfate (as SO4) | mg/l | 0.50-2.5 | 9.8 | 12 | 14 | 8.3 | 16 | 4.9 | 5.8 | 17 | 19 | 21 | 12 | 17 | -- | 250 Error: Reference source not found | -- | -- |
| Sulfide (as S) | mg/l | 1.0 | ND | ND | ND | ND | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |
| Sulfite (as SO3) | mg/l | 5.0 | ND | 12 | ND | ND | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |
| Total dissolved solids | mg/l | 1.0-10 | 190 | 220 | 260 | 190 | 290 | 230 | 200 | 290 | 290 | 300 | 190 | 280 | -- | 1,000 Error: Reference source not found | -- | -- |
| Tributyltin | g/l | 0.020-10 | ND | -- | ND | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |

Table 11 Notes:

E = estimated concentration between laboratory’s method detection limit and reporting limit.

ND = not detected above the laboratory’s method detection limit.

“ – “ = sample not collected this month.

# Deer Creek AND EFFLUENT FLOW

The District is required to monitor Deer Creek flow and the rate of effluent discharged to the creek, per the DCWWTP’s NPDES permit Monitoring and Reporting Program, when discharging treated effluent to Deer Creek.  The flow rates for the period February 2002 through February 2003, the period during which the monitoring was conducted, are summarized in Table 12.  The results in Table 12 were taken directly from the District’s Discharger Self-Monitoring Reports submitted monthly to the RWQCB.  Because the District monitors flow when discharging to Deer Creek, as required by the NPDES permit, additional flow data are available for other periods that are not reported here, in other Discharger Self-Monitoring Reports.

Table 12.  Deer Creek and effluent daily flow rate for the period February 2002 through January 2003.

| Parameter | Feb 02 | Mar 02 | Apr 02 | May 02 | Jun 02 | Jul 02 | Aug 02 | Sep 02 | Oct 02 | Nov 02 | Dec 02 | Jan 03 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Effluent Flow Rate (million gallons per day) |  |  |  |  |  |  |  |  |  |  |  |  |
| Count | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31 | 31 |
| Average | 3.43 | 3.76 | 2.72 | 1.94 | 1.23 | 1.14 | 1.15 | 1.11 | 1.53 | 2.40 | 3.23 | 2.95 |
| Maximum | 4.91 | 5.82 | 3.31 | 3.40 | 1.56 | 1.24 | 1.81 | 1.77 | 2.54 | 3.44 | 5.20 | 3.56 |
| Minimum | 2.71 | 2.89 | 1.21 | 1.35 | 1.05 | 0.99 | 0.80 | 0.52 | 0.71 | 1.54 | 2.10 | 2.69 |
| Deer Creek Flow Rate (million gallons per day) |  |  |  |  |  |  |  |  |  |  |  |  |
| Count | 28 | 31 | 30 | 31 | 30 | 31 | 31 | 30 | 31 | 30 | 31 | 31 |
| Average | > 24 | > 24 | > 24 | > 24 | > 24 | 14.8 | 16.0 | 1.4 | 2.4 | 3.6 | > 24 | > 24 |
| Maximum | > 24 | > 24 | > 24 | > 24 | > 24 | > 24 | > 24 | 2.0 | 3.5 | > 24 | > 24 | > 24 |
| Minimum | > 24 | > 24 | > 24 | > 24 | 8.0 | 0.9 | 10.0 | 0.8 | 1.2 | 0.0 | 2.8 | > 24 |

# Summary

Effluent and receiving water monitoring was conducted at the DCWWTP from February 2002 through February 2003.  The constituents listed in Table 13 were detected in the undiluted effluent or Deer Creek at concentrations greater than an applicable, or recommended, water quality criterion.  It should be noted that the DCWWTP NPDES permit already contains effluent limitations for all of the constituents listed in Table 13, except for dieldrin.

Table 13.  Summary of Deer Creek Wastewater Treatment Plant effluent and receiving water monitoring results for the period February 2002 through February 2003.

| Constituent Group | Constituent | Units | Lowest CTR Standard | Effluent |  | Deer Creek |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Concentration Range | # Samples > CTR | Concentration Range | # Samples > CTR |
| Trace metals | Copper (dissolved) | g/l | 9 | 10 - 39 | 5 out of 5 | 1.7 – 4.2 | none |
| Pesticides, herbicides, and PCBs | Dieldrin | g/l | 0.00014 | ND – 0.0069 | 1 out of 4 | ND | none |
| Volatile organics | Bromodichloromethane | g/l | 0.56 | 4.8 - 12 | 12 out 12 | ND | none |
|  | Dibromochloromethane | g/l | 0.401 | ND – 1.2 | 8 out of 12 | ND | none |
|  | Trihalomethanes (total) | g/l | 100 , | 43.1 – 152.61 | 3 out of 12 | ND – 0.39 | none |
| Conventional constituents | Nitrate (as N) | mg/l | 10 Error: Reference source not found | 10 - 24 | 11 out of 12 | 0.12 – 0.83 | none |

ND = not detected above the laboratory’s reporting limit.

# References

RBI (Robertson-Bryan, Inc.).  2002.  Effluent and receiving water quality monitoring for Deer Creek Wastewater Treatment Plant.  A quality assurance project plan for the collection and analysis of samples. Prepared for the El Dorado Irrigation District by Robertson-Bryan, Inc.  March.

SWRCB (State Water Resources Control Board).  2000.  Policy for the Implementation of Toxics Standards for Inland Surface Waters, Enclosed Bays, and Estuaries of California (Phase 1 of the Inland Surface Waters Plan and the Enclosed Bays and Estuaries Plan), State Water Resources Control Board.

SWRI 1999.  Phase II Effluent and Receiving Water Quality Assessment for the El Dorado Irrigation District’s Deer Creek Wastewater Treatment Plant.  Prepared for the Central Valley Regional Water Quality Control Board.  February 12, 1999.

APPENDIX A: 	RWQCB Letters Dated September 10, 2001 and December 27, 2001

(APPENDIX A.pdf)

APPENDIX B: 	Summary of Analytical Results by Constituent

Data Qualifiers and Abbreviations

COLOR	colorimetry

CQL	criterion quantitation limit established by the Regional Water Quality Control Board

CV-AFS	cold vapor – atomic fluorescence spectrometry

E	estimated concentration between laboratory’s method detection limit and reporting limit

GC-FPD	gas chromatography-flame photometric detector

HG-AFS	hydride generation – atomic fluorescence spectrometry

ICP-MS	Inductively coupled plasma – mass spectroscopy

MDL	laboratory method detection limit

na	not applicable

ND	not detected above laboratory’s method detection limit

R-1	NPDES permit receiving water monitoring station upstream of the effluent discharge point

RL	laboratory reporting limit

U	constituent also detection in laboratory method blank

Appendix B.DCWWTP.xls

APPENDIX C: 	Analytical Laboratory Contacts

ANALYTICAL LABORATORY CONTACTS

Mr. Raymond Oslowski, Jr.	 or	 Mr. James Liang

Sales/Marketing Manager		Laboratory Director

California Laboratory Services

3249 Fitzgerald Road

Rancho Cordova, CA  95742

(916) 638-7301

Ms. Martha Maier

HRMS Services Coordinator

Alta Analytical Laboratory

5070 Robert J. Mathews Parkway

El Dorado Hills, CA  95762

(916) 933-1640

APPENDIX D: 	Analytical Laboratory Reports

APPENDIX D.pdf

FEBRUARY 2002

MARCH 2002

APRIL 2002

MAY 2002

JUNE 2002

JULY 2002

AUGUST 2002

SEPTEMBER 2002

OCTOBER 2002

NOVEMBER 2002

DECEMBER 2002

JANUARY 2003

FEBRUARY 2003

California Department of Health Services primary maximum contaminant level.

California Department of Health Services secondary maximum contaminant level.

Based on a hardness of 100 mg/l as CaCO3.

California Department of Health Services primary maximum contaminant level.

California Department of Health Services secondary maximum contaminant level.

Based on a hardness of 100 mg/l as CaCO3.

California Department of Health Services primary maximum contaminant level.

August reporting limits were elevated due to matrix interference.

California Department of Health Services action level.

The aquatic life and human health standards apply to the sum of the seven aroclors.

California Department of Health Services secondary maximum contaminant level.

California Department of Health Services primary maximum contaminant level.

California Department of Health Services action level.

The aquatic life and human health standards apply to the sum of the seven aroclors.

California Department of Health Services secondary maximum contaminant level.

California Department of Health Services primary maximum contaminant level.

California Department of Health Services action level.

For total trihalomethanes (sum of bromodichloromethane, bromoform, chloroform, and dibromochloromethane).

California Department of Health Services secondary maximum contaminant level.

California Department of Health Services primary maximum contaminant level.

California Department of Health Services action level.

For total trihalomethanes (sum of bromodichloromethane, bromoform, chloroform, and dibromochloromethane).

California Department of Health Services secondary maximum contaminant level.

California Department of Health Services primary maximum contaminant level.

California Department of Health Services action level.

August reporting limits were elevated due to matrix interference.

California Department of Health Services primary maximum contaminant level.

California Department of Health Services action level.

California Department of Health Services primary maximum contaminant level.

California Department of Health Services primary maximum contaminant level.

Value represents millions of fibers per liter; limited to fibers greater than 10 microns in length.

California Department of Health Services secondary maximum contaminant level.  Range for total dissolved solids is 500 mg/l (recommended) to 1,000 mg/l (upper limit).

California Department of Health Services primary maximum contaminant level.

Value represents millions of fibers per liter; limited to fibers greater than 10 microns in length.

California Department of Health Services secondary maximum contaminant level.  Range for total dissolved solids is 500 mg/l (recommended) to 1,000 mg/l (upper limit).

Based on a hardness of 100 mg/l as CaCO3.

California Department of Health Services primary maximum contaminant level.

Sum of bromodichloromethane, bromoform, chloroform, and dibromochloromethane.