## Sheet1
Sample ID | Analyte | Result | Units
1247-01-8 | TPH-Gasoline | 29 | ug/L
1247-01-1 | TPH-Gasoline | ND
1247-01-1 | Ammonia as N | 0.2 | mg/L
1247-01-5 | Ammonia as N | 0.1 | mg/L
1247-01-7 | Ammonia as N | 0.1 | mg/L
1247-01-6 | Nitrate as N | 0.2 | mg/L
1247-01-1 | Total Phosphorus as P | 0.1 | mg/L
1247-01-5 | Total Phosphorus as P | 0.88 | mg/L
1247-01-7 | Total Phosphorus as P | 0.8 | mg/L
1247-01-2 | TSS | ND
1247-01-3 | TSS | ND
1247-01-4 | TSS | ND
1247-01-2 | TDS | 1350 | mg/L
1247-01-3 | TDS | 21400 | mg/L
1247-01-4 | TDS | 847 | mg/L

## Sheet2
Tracking No. | Regional Board Contact Notified (Name, or "VOICE MAIL", or "FAX") | Date & Time Reported | Reported By | Phone No. | Agency | Start Date & Time | End Date & Time | Total Overflow Volume (Gallons) | Overflow Volume Recovered (Gallons) | SSO Location -- Street Address | SSO Location -- City | SSO County SD, RV, OR | SSO Zip Code | SSO Structure I.D. | No. of Overflows in past 12 months | SSO Cause (Short Description) | SSO Cause (Detailed Description) | SSO Correction and Prevention | Reach Surface Waters? (Y or N) | Entered Storm Drain? (Y or N) | Initial Receiving Waters | Secondary Receiving Waters | Final Sewage Destination | Local Health Services Agency Notified (Y or N) | OES Notified (Y or N) | Warning Signs Posted (Y or N) | No. of Days Signs Posted | Remarks
978001 | N/A | 7/2/97 1200 | Mike Schultz | 760-738-4347 | City of Escondido | 7/1/97 1015 | 7/1/97 1515 | 600 | 0 | La Honda Dr. | Escondido | SD | 92027 | Sewer Atlas PG. 251 MH.1174 | 1 | Vandalism | Vandalism, rocks, sticks,charcoal. | A locking manhole cover was installed. | N | N | N/A | N/A | Ground Absorption | Y | N | N | N/A
978002 | Called and Faxed | 7/8/97 730 | J. Vaught/L. Bishop | 741-4668 | City of Escondido | 7/8/97 730 | 7/8/97 1015 | 22600 | 8600 | 1750 W. El Norte Pkwy. | Escondido | SD | 92026 | 8" Forcemain | 2 | Forcemain break | 10' cracked 8" pipe. | Repair was made with a higher rated pipe. | Y | Y | San Marcos Creek | Lake San Marcos | Pacific Ocean | Y | Y | Y | 7 | Samples were taken.
978003 | Called and Faxed | 7/19/97 1030 | Joe Sanchez | 739-5538 | City of Escondido | 7/19/97 1000 | 7/19/97 1100 | 3000 | 0 | 223 S. Fig st. | Escondido | SD | 92025 | Sewer Atlas PG.368 MH.6470 | 1 | Roots / Grease | Grease, paper, and roots caused stoppage in sewer mainline. | This mainline was put on a three month cleaning schedule. | Y | Y | Escondido Creek | San Elijo Lagoon | Pacific Ocean | Y | Y | Y | 3 | Samples were taken.
978004 | Called and Faxed | 7/24/97 1630 | John Vaught | 738-4323 | City of Escondido | 7/21/97 600 | 7/24/97 1800 | 4300 | 0 | 1433 N. Broadway | Escondido | SD | 92026 | Private cleanout | 1 | Private cleanout | Private system | Private System | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific | Y | Y | Y | 3
978005 | Called and Faxed | 7/30/97 1020 | Lance Lauricha | 741-4668 | City of Escondido | 7/29/97 500 | 7/30/97 1445 | 3300 | 1500 | 1625 E. Grand Ave. | Escondido | SD | 92026 | Private cleanout | 1 | Private cleanout/grease | Large amounts of grease in private cleanout. | Property owner said they would install additional cleanouts to ensure proper cleaning in the future | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | Y | Y | 5 | Samples were taken.
978006 | Called and Faxed | 8/2/97 1330 | Lucky Bishop | 741-4668 | City of Escondido | 8/1/97 1400 | 8/2/97 1400 | 15720 | 6720 | 725 N. Fig St. | Escondido | SD | 92026 | Private cleanout | 1 | Private cleanout | Private system | Asked property to maintain their system. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | Y | Y | 5 | Samples were taken.
978007 | Called and Faxed | 8/18/97 1330 | Mike Schultz | 738-4347 | City of Escondido | 8/16/97 2323 | 8/16/97 2440 | 1750 | 0 | 802 W. 3rd. | Escondido | SD | 92025 | Sewer Atals PG. 387 MH. 6129 | 1 | Debris/Grease | Build up of grease and other debris caused mainline stoppage. | This line segment has been place on the City's capital improvement plan. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | Y | Y | 5 | Samples were taken.
978008 | N/A | 9/2/97 1550 | Mike Schultz | 738-4347 | City of Escondido | 1997-08-29 | 8/29/97 1705 | 120 | 50 | 1605 Hamlton | Escondido | SD | 92025 | Sewer Atlas PG.486 Airvac. | 1 | Air release valve malfunctioned. | Malfunctioning air release value. | Remove unit cleaned, inspected. then reinstalled. | N | N | N/A | N/A | N/A | Y | N | N | N/A
978009 | N/A | 9/2/97 1350 | Mike Schultz | 738-4347 | City of Escondido | 8/30/97 915 | 8/30/97 1020 | 195 | 50 | 1141 E. Washington | Escondido | SD | 92025 | Private Cleanout | 1 | Private Cleanout | Private cleanout | Elia's Restraunt, possible grease problem. Will be forwarded to Pretreatment Inspector. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | N | N | N/A
978010 | N/A | 9/3/97 1115 | Mike Schultz | 738-4347 | City of Escondido | 8/30/97 ? | 8/31/97 ? | 400 Estimated | 100 | 1629 E. Valley Pkwy. | Escondido | SD | 92027 | Private cleanout | 1 | Private cleanout/Grease | Grease trap which was not being maintained was the cause of the overflow. | The Golden Sun Restaurant was warned by our Pretreatment Inspector/Industrial Waste Inspector of the importance of maintaining his grease trap. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | N | N | N/A
978011 | N/A | 9/18/1997 1430 | Mike Schultz | 738-4347 | City of Escondido | 9/18/97 845 | 9/18/97 930 | 90 | 0 | W. El Norte Pkwy. at Rees Rd. | Escondido | SD | 92026 | Airvac. Sewer Atlas PG. 264 | 2 | Airvac Malfunction | Air release valve malfunctioned allowing wastewater to trickle. | The valve was removed and clean, inspected, then reinstalled. | Y | Y | San Marcos Creek | Lake San Marcos | N/A | Y | N | N | N/A
978012 | N/A | 9/24/97 800 | Lance Lauricha | 738-4323 | City of Escondido | 9/24/97 800 | 9/24/97 1045 | 247.5 | 45 | 330 W. Felicita | Escondido | SD | 92027 | Private Cleanout | 1 | Private cleanout | Unknown | Private cleanout, Plumber cleared blockage. | Y | Y | Dead Horse Creek | Lake Hodges | N/A | Y | N | N | N/A
978001 | quarterly report | n/a | Orv Salisbury | 760-744-0460 | V.W.D. | 7-10-97 1830 | 7-10-97 1915 | 800 | none | 1510 Via Brisa Del Lago | San Marcos | S.D. | 92069 | sewer clean out | 1 | grease | grease blockage in a gravity 8" sewer line | new piping and a new pump station is under const. | y | y | Lake San Marcos | none | Lake San Marcos | y | n | y | 4+ | no body contact in the lake
978002 | quarterly report | n/a | Orv Salisbury | 760-744-0460 | V.W.D. | 7-16-97 2000 | 7-16-97 2200 | 1800 | 1000 | Liberty St. | San Marcos | S.D. | 92069 | sewer manhole | 1 | grease | heavy grease from low income apartments | we will include this site on our trouble spot list | y | y | Storm drain | S.M. Creek | open channel | y | n | y | 4 | spill was contained and recovered
978003 | Pam Jackson | 9-25-97 1750 | Orv Salisbury | 760-744-0460 | V.W.D. | 9-25-97 1630 | 9-26-97 0600 | 1500000 | none | easment | Carlsbad | S.D. | 92009 | 24" outfall line | 1 | broken pipe | steel pipe was possibly crushed when installed | engeneering dept is investigating the cause | n | n | canyon | irrigation ponds | La Costa Resort | y | y | y | 14+ | spill was contained
978004 | voice mail | 9-26-97 1000 | Orv Salisbury | 760-744-0460 | V.W.D. | 9-26-97 0900 | 9-26-97 1430 | 942000 | none | easment | Carlsbad | S.D. | 92009 | 24" outfall line | 2 | broken pipe | steel pipe was possibly crushed when installed | engeneering dept is investigating the cause | n | n | canyon | irrigation ponds | La Costa Resort | y | y | y | 14+ | spill was contained
978001 | Quarterly Report | 07/17/97; 14:30 | Richard Andrews | 619 755-3294 | City of Del Mar | 07/15/97; 20:22 | 07/16/97; 08:30 | 50 gallons | 0 | 119 11th Street | Del Mar | SD | 92014 | City Manhole No. 13 | 0 | Construction Defect | Incorrect connection lateral to main allowed leakage when lateral pressurized by basement ejector pump. | Rodded main which was clear. Contacted contractor ID fix connection. | N | N | N/A | N/A | dissipated @ road edge & storm drain system | Y | NA | N | NA | NA
978002 | Quarterly Report | 07/27/97; 17:15 | Richard Andrews | 619 755-3294 | City of Del Mar | 07/25/97; 16:50 | 07/25/97; 18:00 | 350 gallons | 0 | 200 Block Stratford Court, West Bluff | Del Mar | SD | 92014 | City Manhole No. 4 | 0 | Roots and Debris | Roots, Debris, and paper | Rodded Main to Clear Blockage | N | Y | N/A | N/A | Dirt next to manhole and dirt east of RR | Y | NA | N | NA | NA
978003 | Quarterly Report | 07/28/97; 13:45 | Richard Andrews | 619 755-3294 | City of Del Mar | 07/27/97; 15:30 | 07/28/97; 09:30 | 600 gallons | 0 | 390 Stratford Court | Del Mar | SD | 92014 | Private Lateral Clean Out | 0 | Roots | Roots in private lateral caused backup and overflow from residents cleanout. | Plumber contracted by owner and cleared. | N | Y | N/A | N/A | Ran down street leached into ground at bluff drainage swale est of RR | Y | NA | N | NA | Resident called PW answering machine (Sunday PM) to report a water leak at meter box. Did not call emergency number given in message. PW investigation Monday morning revealed private sewer company.
978004 | Quarterly Report | 08/12/97; 13:30 | Richard Andrews | 619 755-3294 | City of Del Mar | 08/12/97; 10:30 | 08/12/97; 11:45 | 900 gallons | 0 | 12th Street and Maiden Lane | Del Mar | SD | 92014 | Manholes grid B8 81, 17, 18 | 0 | Roots | Roots blocking 8" sewer main. | Rodded main to clear roots. Continue preventative rodding. | Y | Y | Ocean | N/A |  | Y | NA | Y | 1 | Two signs posted north and 2 south 50 yards either side of spill.
978005 | Quarterly Report | 10/02/97; 14:00 | Richard Andrews | 619 755-3294 | City of Del Mar | 09/27/97; 10:37 | 09/27/97; 11:50 | 146 gallons | 0 | 310 La Amatista Road | Del Mar | SD | 92014 | City Manhole Grid B 10 17 | 0 | Roots | Plumber clearing private lateral pushed roots into City main caused the blockage and overflow. | Rodded main to clear blockage. Continue preventative rodding. | N | Y | N/A | N/A | Road edge, gutter and drain. | Y | NA | N | NA | NA
978001 | none | none | D.Catone |  | L.G.Sanitation Dist. | 09/12/97 09:00 | 1997-09-12 13:00 | 2400 GA | 2400 GA | Lemon Grove Ave between Canton and Viewcrest | Lemon Grove | San Diego | 91945 | 8" main | 0 | line break to roots in main | line break due to tree roots in main | Repaired pipe | NO | NO | N/A | N/A | some soaked in to surrounding soil. Most was contained with dam & pumped back into system. Line was pumped on bypass during repair. | N | N/A | N | 0 | breakage was on side of main traveled way.
977001 | Voice Mail | 7/10/97 1330 PM | Mike M. Calvert | 9096764101 | Rancho California Water District | 7/10/97 0700 AM | 7/10/97 0745 AM | 2250 | 0 | Washington & Brown | Murrieta | RV | 92562 | 24" CML-CMC pipe | 1 | Vandalism | A new 12" valve was put on a 24" line and during the night vandals opened the line.
978001 | KATHY STONE-FAX | 7/14/97-2:00P | PAT GUEVARA | 438-2722 X134 | CARLSBAD MWD | 7/14/97-8:30A | 7/14/97-9:30 A | 60 | 30 | SHUTTLE RD/FINCH/KINGFISHER | CARLSBAD | SD | 92009 | MANHOLE | 2 | ROCKS/DEBRIS/BLOCKAGE |  | ROUTINELY CHECK MANHOLES IN AREA DURING CONSTRUCTION PERIOD | N | N |  |  | 1/2 WAS VACTORED UP, REMAINING FLOWED TO DIRT PILES | Y | N | N | N/A | DISINFECTED AREA. AREA STILL UNDER CONSTRUCTION.
978002 | N/A | N/A | N/A | N/A | PRIVATE | 7/22/97-12:00 P | 7/22/97-2:00 P | 1 TO 5 | 0 | 3180 CANYON | CARLSBAD | SD | 92008 | CLEANOUT | 1 | UNKNOWN BLOCKAGE |  |  | N | N |  |  | SEWER CLEANOUT AREA | N | N | N | N/A | DISINFECTED AREA.
978003 | KATHY STONE-FAX | 8/5/97-11:03 A | PAT GUEVARA | 438-2722 X134 | CARLSBAD MWD | 8/2/97-11:30 A | 8/2/97-1:15 P | 150-250 | 0 | MEDFORD CT. | CARLSBAD | SD | 92008 | SEWER MAIN DEAD-END CLEANOUT | 1 | UNKNOWN BLOCKAGE |  | USED VACTOR TO JET ROD PLUGGED SEWER MAIN. RAN JET RODDER THRU PROBLEM AREA SEVERAL TIMES TO INSURE BLOCKAGE WAS COMPLETELY CLEARED | Y | Y | POWER LINE EASEMENT, CALAVERA HILLS (NATURAL DRAINAGE BASIN) |  |  | Y | N | N | N/A | CHECKED DRAIN AREA AT CHESTNUT CROSSING POINT, FOUND NO EVIDENCE OF WASTEWATER AT THAT POINT.
978004 | N/A | N/A | N/A | N/A | PRIVATE | 8/11/97-8:00 A | 8/11/97-9:00A | 1 TO 5 | 0 | 7260 MIMOSA DR. | CARLSBAD | SD | 92009 | CLEANOUT | 3 | UNKNOWN BLOCKAGE |  | USED RODDING MACHINE TO CLEAR STOPPAGE. T.V. INSPECTED LATERAL. WILL SCHEDULE FOR LATERAL REPLACEMENT | N | N |  |  | SEWER CLEANOUT AREA | N | N | N | N/A | DISINFECTED AREA.
978005 | N/A | N/A | N/A | N/A | PRIVATE | 8/13/97-7:00 P | 8/13/97-9:30 P | 5 TO 10 | 0 | 3883 WOODVALE | CARLSBAD | SD | 92008 | CLEANOUT | 1 | ROOTS & HAIR |  | USED RODDING MACHINE TO CLEAR STOPPAGE | N | N |  |  | SEWER CLEANOUT AREA | N | N | N | N/A | DISINFECTED AREA.
978006 | N/A | N/A | N/A | N/A | PRIVATE | 8/19/97-4:40 P | 8/19/97-6:15 P | 2 | 0 | 330 REDWOOD | CARLSBAD | SD | 92008 | CLEANOUT | 1 | UNKNOWN BLOCKAGE |  | USED DRAIN KING TO CLEAR STOPPAGE | N | N |  |  | SEWER CLEANOUT AREA | N | N | N | N/A | DISINFECTED AREA
978007 | N/A | N/A | N/A | N/A | PRIVATE | 9/16/97-8:15 P | 9/16/97-10:00P | 1 TO 2 | 0 | 2074 AVE OF THE TREES | CARLSBAD | SD | 92008 | CLEANOUT | 1 | UNKNOWN BLOCKAGE |  | USED RODDING MACHINE TO CLEAR STOPPAGE | N | N |  |  | SEWER CLEANOUT AREA | N | N | N | N/A | DISINFECTED AREA
978001 | VOICE MAIL | 7/07/97 11:00AM | ROBERT BRAUN | (619) 874-4087 | COUNTY OF SAN DIEGO | 7/04/97 4:15PM | 7/4/97 5:00PM | 300 | NONE | 604 GALAPAGO ST. | SPRING VALLEY | SD | 91977 | MANHOLE COVER | 0 | GREASE | GREASE BUILDED UP IN 8 INCH. SEWER MAIN CAUSING SEWER TO BACK UP IN MANHOLE | SEWER LINE WILL GO ON SPECIAL MAINTENANCE - RODDED 4 TIMES A YEAR | N | Y |  | SWEETWATER RIVER | OCEAN | Y | N | N | NONE | LINE NOW ON SPECIAL MAINTENANCE 4 TIMES YEAR
978002 | VOICE MAIL | 8/23/97 930A | ROBERT BRAUN | (619) 874-4082 | CO OF SAN DIEGO | 8/23/97 0930 | 8/23/97 1015A | 750 | NONE | 4306 VISTA WAY | SP VALLEY | SD | 91977 | MANHOLE COVER | 0 | ROOTS | ROOTS BLOCKING OUTLET SIDE OF MANHOLE | SPECIAL MAINTENANCE, CLEAN 4 TIMES YEARLY | N | N |  |  | DRY CREEK | Y | N | N | NONE | SPECIAL MAINITENANCE
978001 | Left Message | 1997-07-03 08:14 | Jim Gusman | (760)726-1340ext1665 | City of Vista | 1997-07-02 18:45 | 1997-07-02 19:15 | 7500 | 0 | Eucalypus Ave. 300' west of Escondido Ave. | Vista | SD | 92083 | Basin V.22, SMH 96, AP 175-29 | Zero | Grease | Grease Blockage | Cleaned the line downstream two blocks and upstream to the next manhole. | Y | N | Branch of Buena Vista Creek | Buena Vista Creek |  | Y | N | Y | 3 | Washed the area of the spill with 1800 gal of fresh water.
978001 | fax | 1997-09-11 13:00 | Denis Pollak | 7607530155 | Leucadia County Water District | 9-11-97 700 | 9-11-97 830 | 3600 | 2500 | 50 yards south of 6200 Avenida Encinas | Carlsbad | SD | 92009 | 16" DIP failsafe pipeline | 0 | leak in DIP pipeline | corrosion of pip material | Spot repair of pipline, inspection of condition and extent of corrosion to pipe material | y | y | Storm channel | marsh area | Marsh area | y | n | n | n/a | Spill was of highly treated secondary effluent not raw sewage.
978001 | VOICE MAIL | 21:00 | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 07/06/97 | 15:40 | 25000 | 19200 | Carnes Road | SD | 920555008 | MANHOLE 13Y28 | 2 | BLOCKAGE | solids and debris in line caused overflow from manhole. | cleared sewer line with jet-TRUCK. | Y | Y | STP #13 OXIDATION/PERC. POND | Santa Margarita River |  | Y | Y | Y | 3 |  | SPILL TRAVELED 1/2 MILE FROM MANHOLE-ACROSS ROAD TO CANYON ALONG CARNES RD UNDER ASH RD TO VANDERGRIFT INTO CULVERT TO STP #13 TWIN LAKES TREATED EFFLUENT POND TO PERCOLATE ADJACENT SANTA MARGARITA RIVER.
978002 | ELECTRONIC QTLY RPT |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 07/13/97 | 15:30 | 150 | 0 | 205 ABeyta, Sierra Mesa | SD | 920555008 | 2Y152 | 1 | BLOCKAGE | Chunks of grease and soap caused blockage which resulted in overflow from manhole | cleared with jetter. | Y | N | Pilgrim Creek | San Luis Rey River |  | Y | NA | N | 0 |  | SPILL FLOWED FROM MANHOLE 30' TO CANYON THEN 10' INTO CANYON AND PERCOLATED. NOT IN AN AREA OF EXPECTED PUBLIC CONTACT
978003 | ELECTRONIC QTLY RPT |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 07/15/97 | 16:25 | 25 | 10 | Bldg 520450 | SD | 920555008 | cleanout | 4 | ROOTS | paper towels and roots in manhole | replaced broken pipe. | Y | N | San Onofre Creek | Pacific Ocean |  | N | NA | N | 0 |  | SPILL FLOWED 15' INTO A DRY GRASS AREA. NOT IN AN AREA OF EXPECTED PUBLIC CONTACT.
978004 | ELECTRONIC QTLY RPT |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 07/29/97 | 15:00 | 600 | 0 | Bldg 51096, Burger King | SD | 920555008 | Grease Trap | 1 | GREASE | Grease trap exit pipe backed up due to grease and debris | notified tenant to have grease trap cleaned. Used ramjet to clear line | Y | Y | San Onofre Creek/ESTUARY | none (see remarks) |  | Y | NA | Y | 3 |  | FLOWED 60' OVER PARKING LOT TO STORM DRAIN, 300' UNDER PARKING LOT TO EDGE OF CANYON, 400' TO SAN ONOFRE CREEK. CREEK IS NOT FLOWING BUT HAS WATER POOLED UNDER FREEWAY. ESTUARY MOUTH BLOCKED BY SANDBAR.
978005 | ELECTRONIC QTLY RPT |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 08/01/97 | 18:00 | 30 | 10 | Bldg 62520 | SD | 920555008 | cleanout on main line | 1 | ROOTS | roots and towels caused blockage resulting in sewage overflowing from cleanout | used jetter to clear stoppage | Y | N | San Mateo Creek | Pacific Ocean |  | N | NA | N | 0 |  | SPILLED FLOWED 5' FROM CLEANOUT OVER SIDEWALK 30' INTO GRASSY AREA
978006 | ELECTRONIC QTRLY RPT |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 08/09/97 | 18:00 | 300 | 175 | Bldg 43535, BEQ | SD | 920555008 | cleanout AT BLDG 43535 | 2 | BLOCKAGE | paper towels and roots caused blockage causing overflow from cleanout | Used jetter to clear blockage. Informed duty to tell tenants to stop flushing paper towels into sewer. | N | N | n/a | n/a | ponded around cleanout | Y | NA | N | 0 |  | SPILL OVERFLOWED FROM CLEANOUT AND PONDED INTO A POOL 10 FT ACROSS.
978007 | ELECTRONIC QRTLY RPT |  | KARL VOGEL | 6197259762 | MCB, CAMP PENDLETON | 08/15/97 | 18:30 | 500 | 150 | BLDG 43402 | SD | 920555008 | Grease TRAP MESS HALL | 3 | GREASE | Grease trap stopped up WITH GREASE causing OVERFLOW of cleanout | contact food services, advised to check grease trap enzyme program for proper application. cleaned out trap. | Y | Y | Las Flores Creek | Pacific Ocean |  | Y | NA | N | 0 |  | SPILL FLOWED 200' ACROSS A PARKING LOT INTO STORM DRAIN, 100' DOWN CEMENT LINED DITCH, SOAKED INTO DIRT AND WEEDS IN BOTTOM OF DITCH.
978008 | ELECTRONIC QTRLY RPT |  | KARL VOGEL | 6197259762 | MCB, CAMP PENDLETON | 08/17/97 | 10:30 | 30 | 0 | BLDG 43402 | SD | 920555008 | Grease Trap Mess Hall | 4 | GREASE | grease trap STOPPED UP WITH GREASE resulted in overflow | Ramjet used to clear line, will notify food services to treat. Check enzyme program for proper application | Y | Y | Las Flores Creek | Pacific Ocean |  | Y | NA | N | 0 |  | SPILL FLOWED 200 FT DOWN STREET AND 50 FT INTO STORM DRAIN. PERCOLATED IN CEMENT LINED DITCH THAT HAS DIRT AND WEEDS IN BOTTOM.
978009 | ELECTRONIC QTRLY RPT |  | KARL VOGEL | 6197259762 | MCB, CAMP PENDLETON | 08/26/97 | 17:30 | 950 | 0 | LIFT STATIONS 51050 & 51054 BASILONE RD | SD | 920555008 | MH FOR 51050 WET WELL AND MH FOR 51054 WET WELL | 1 | OTHER | POWER SECURED AT 51050, TO REPAIR AIR-VAC VALVE ON FORCE MAIN TO STP 11. FLOW WENT FROM 51050 TO 51054- ADDITIONAL FLOW TO 51054 CAUSED FLOW OUT MAN HOLES AT BOTH STATIONS WHEN 51054 COULD NOT KEEP UP |  | Y | Y | SAN ONOFRE CREEK | PACIFIC OCEAN |  | Y | NA | N | 0 |  | SPILL FLOWED FROM BOTH MH51050=110 FT AND MH51054=55FT INTO STORM DRAIN, FLOW TRAVELLED APPROX 1/4 MILE TO UNDEVELOPED FIELD AN PERCOLATED INTO SOIL.NOT IN AN AREA OF EXPECTED PUBLIC CONTACT.
97810 | ELECTRONIC QTRLY RPT |  | KARL VOGEL | 6197259762 | MCB, CAMP PENDLETON | 08/26/97 | 14:00 | 900 | 0 | BasIlone Rd. | SD | 920555008 | Air-Vac on forced main | 2 | OTHER | Air-Vac jammed open, venting to atmosphere | Secured PUMP STATION 51050 TO SECURE Air-Vac and installed new one. | Y | Y | San Onofre Creek | Pacific Ocean |  | Y | NA | N | 0 |  | SPILL FLOWED 30 FT DOWN ROAD INTO CULVERT, 20 FT UNDER ROAD, PERCOLATED IN SAND 10 FT FROM END OF CULVERT. TOTAL OF 60 FT. SPILL OCCURED IN SEMI-WILDERNESS, NOT EXPECTED TO HAVE PUBLIC CONTACT.
978011 | ELECTRONIC QTLY RPT |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 09/04/97 | 11:30 | 800 | 0 | Bldg 1795 | SD | 920555008 | Z-Y-128 Officers Club | 1 | ROOTS | roots caused a blockage which caused sewage to overflow from manhole | used cutting head to cut out roots | Y | N | Pilgrim Creek | San Luis Rey River |  | Y | NA | N | 0 |  | SPILL FLOWED APPROX. 880' FROM MANHOLE INTO DITCH AND PERCOLATED INTO THE GROUND. SLOW LEAK WAS NOT CALLED IN TO MAINTENANCE UNTIL THE DAY AFTER IT STARTED.
987012 | QTLY RPT TO RWQCB |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 09/16/97 | 20:30 | 200 | 50 | Bldg 520450 | SD | 920555008 | C/O main | 12 | OTHER | manhole overflowed due to jetting equipment when clearing roots from the sewer line. | Preventative maintenance program of clearing roots from the lines | Y | Y | San Onofre Creek (dry) | Pacific Ocean |  | N | NA | N | 0 |  | SPILL FLOWED FROM MANHOLE 150 FT INTO STORM DRAIN ON BASILONE RD THEN INTO SAN ONOFRE CREEK (DRY). TOTAL DISTANCE 530 FT
978013 | G. FULTON VOICEMAIL | 13:45 | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 09/16/97 | 17:30 | 1800 | 1000 | Intersection of Eliason and Angel | SD | 920555008 | MANHOLE | 1 | GREASE | Grease caused blockage which caused overflow from manhole | Ramjetted blockage. Recovered 1000 gallons with Super Vac truck | Y | Y | Santa Margarita | Pacific Ocean |  | Y | Y | N | 0 |  | Spill flowed 65' from manhole to storm drain on Eliason THEN INTO CANYON. TOTAL DISTANCE 650 FT INTO THE CANYON. SPILL FLOWED TO AREA OF NO EXPECTED PUBLIC CONTACT
978014 | CAROL TAMAKI | 12:00 | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 09/28/97 | 19:30 | 09/29/97 | 16,000 | 1,000 | Behind 243 Holt Court (SERRA MESA HOUSING AREA) | SD | 920555008 | M/H 2Y112, 2Y113 | 1 | VANDALISM | Bowling ball size rocks in bottom of manhole causED pipe blockage. DURING THE CLEARING PROCESS ONE OF THE ROCKS ROLLED DOWN THE PIPE AND CAUSED A BREAKAGE. | Ramjetted manhole and recovered large rocks. One of the rocks slipped through line and caused a breakage near m/h 2Y110. Repaired line and pumped 1,000 gallons back into m/h 2Y110. | Y | N | Pilgrim Creek | San Luis Rey River |  | Y | Y | Y | 3 | SPILL FLOWED OUT OF M/H 500' TO PILGRIM CREEK THEN APPROX 1 MILE AND PERCOLATED IN CREEK BED
978001 | SIRT (FAX) | 1997-07-30 08:45 | James E. Smith | 714-448-4053 | Moulton Niguel Water | 1997-07-30 20:45 | 1997-07-30 21:30 | 1000 | 0 | Moulton Parkway, 300' south of Aliso Creek Road | Laguna Niguel | OR | 92677 | 8" rEcycled water main | 1 | Broken 8" pipeline | An 8-inch recycled water pipeline broke due to corrosion. | The broken pipeline was dug up and replaced. | Y | N | Aliso Creek | Pacific Ocean at Aliso Beach | N/A | Y | N | N | N/A | N/A
978002 | SIRT (FAX) | 1997-08-23 10:00 | James E. Smith | 714-448-4053 | Moulton Niguel Water | 1997-08-23 10:00 | 1997-08-23 11:30 | 500 | 0 | Southwing Lift Station | Aliso Viejo | OR | 92656 | Lift Station | 1 | Automatic reset failed after power outage | Automatic reset device failed after a power outage at the lift station. | An uninterruptible power supply (UPS) has been installed at the lift station. | Y | N | Aliso Creek | Pacific Ocean | N/A | Y | N | N | N/A | N/A
978001 | N/A | N/A | N/A | N/A | N/A | 7-20-97, 10:50 | 7-20-97, 11:45 | 25 GALLONS | 25 GALLONS | 420 ADELLA LANE | CORONADO | SD | 92118 | SEWER LINE |  | ROOTS | ROOTS IN SEWER LINE | CLEARED WITH VACTOR/RODDER | N | N | NONE | NONE | SEWER LINE | N | N/A | N | N
978002 | N/A | N/A | N/A | N/A | N/A | 8-3-97, 2:20 | 8-3-97, 2:00 | 25 GALLONS | 25 GALLONS | 10TH/I-J ALLEY | CORONADO | SD | 92118 | SEWER LINE |  | ROOTS | FOREIGN MATTER IN ROOTS | CLEARED WITH VACTOR/RODDER | N | N | NONE | NONE | SEWER LINE | N | N/A | N | N
978003 | N/A | N/A | N/A | N/A | N/A | 8-8-97, 9:30 | 8-8-97, 11:00 | 250 GALLONS | 250 GALLONS | VENT VAULT, SR 75 | CORONADO | SD | 92118 | SEWER LINE |  | VENT VALVE FAILURE | VENT VALVE ON FORCE MAIN FAILED | REPLACED VENT VALVE | N | N | NONE | NONE | SEWER LINE | N | N/A | N | N
978004 | N/A | N/A | N/A | N/A | N/A | 8-13-97, 1:30 | 8-13-97, 2:30 | 30 GALLONS | 30 GALLONS | FIRST/G-H ALLEY | CORONADO | SD | 92118 | SEWER LINE |  | GREASE | GREASE BUILD-UP IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N/A | N | N
978005 | N/A | N/A | N/A | N/A | N/A | 9-2-97, 8:00 | 9-2-97, 9:00 | 25 GALLONS | 25 GALLONS | 555 D AVENUE | CORONADO | SD | 92118 | SEWER LINE |  | FOREIGN MATTER | PLASTIC MATERIAL IN SEWER | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N/A | N | N
978006 | N/A | N/A | N/A | N/A | N/A | 9-2-97, 9:30 | 9-2-97, 10:30 | 150 GALLONS | 150 GALLONS | 340 B AVENUE | CORONADO | SD | 92118 | SEWER LINE |  | ROOTS | ROOTS IN SEWER LINE | CLEARED WITH VACTOR/RODDER | N | N | NONE | NONE | SEWER LINE | N | N/A | N | N
978007 | N/A | N/A | N/A | N/A | N/A | 9-4-97,12:30 | 9-4-97, 1:30 | 40 GALLONS | 40 GALLONS | A AND ORANGE | CORONADO | SD | 92118 | SEWER LINE |  | GREASE | MASSIVE AMOUNT OF GREASE IN SEWER | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N/A | N | N
989001 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 07-08-97 | 07-08-97 |  | 0 | 2121 Monument Road | San Diego | SD | 92154 | Smuggler Gulch | 1 | other | overload of collection system |  | Y | N | Smuggler Gulch | None |  | N | N | N
989002 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 07-08-97 | 07-08-97 |  | not known | International Border | San Diego | SD | 92154 | Laureles System | 1 | Line Break |  | spill pumped by City of SD MWWD | Y | N | Goat Creek | None |  | Y | N | N
989003 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 07-09-97 | 07-09-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 2 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989004 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 07-10-97 | 07-10-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 3 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989005 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 07-24-97 | 07-24-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 4 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989006 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-07-97 | 08-07-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 5 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989007 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-08-97 | 08-08-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 6 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989008 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-11-97 | 08-11-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 7 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989009 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-12-97 | 08-12-97 |  | 0 | 2121 Monument Road | San Diego | SD | 92154 | Smuggler Gulch | 2 | other | overload of collection system |  | Y | N | Smuggler Gulch | None |  | N | N | N
989010 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-12-97 | 08-12-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 8 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989011 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-13-97 | 08-13-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 9 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989012 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-14-97 | 08-14-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 10 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989013 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-15-97 | 08-15-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 11 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989014 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-16-97 | 08-16-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 12 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989015 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-17-97 | 08-17-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 13 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989016 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-18-97 | 08-18-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 14 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989017 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-19-97 | 08-19-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 15 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989018 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-20-97 | 08-20-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 16 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989019 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-21-97 | 08-21-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 17 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989020 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-22-97 | 08-22-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 18 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989021 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-27-97 | 08-27-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 1 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989022 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-30-97 | 08-30-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 2 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989023 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-31-97 | 08-31-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 3 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989024 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-04-97 | 09-04-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 4 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989025 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-05-97 | 09-05-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 5 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989026 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-06-97 | 09-06-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 6 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989027 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-07-97 | 09-07-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 7 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989028 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-08-97 | 09-08-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 19 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989029 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-10-97 | 09-10-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 8 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989030 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-11-97 | 09-11-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 20 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989031 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-12-97 | 09-12-97 |  | 0 | 2121 Monument Road | San Diego | SD | 92154 | Smuggler Gulch | 3 | other | overload of collection system |  | Y | N | Smuggler Gulch | None |  | N | N | N
989032 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-12-97 | 09-12-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 21 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989033 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-12-97 | 09-12-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 9 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989034 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-13-97 | 09-13-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 10 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989035 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-14-97 | 09-14-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 11 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989036 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-15-97 | 09-15-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 22 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989037 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-15-97 | 09-15-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 12 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989038 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-16-97 | 09-16-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 13 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989039 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-17-97 | 09-17-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 23 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989040 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-17-97 | 09-17-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 14 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989041 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-18-97 | 09-18-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 24 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989042 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-18-97 | 09-18-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 15 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989043 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-19-97 | 09-19-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 25 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989044 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-19-97 | 09-19-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 16 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989045 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-20-97 | 09-20-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 17 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989046 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-25-97 | 09-25-97 |  | 0 | 5000 Monument Road | San Diego | SD | 92173 | Stewarts Drain | 1 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989047 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-25-97 | 09-25-97 |  | 0 | International Border | San Diego | SD | 92154 | Silva Drain | 1 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989048 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-25-97 | 09-25-97 |  | 0 | International Border | San Diego | SD | 92154 | Canyon del Sol | 1 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989049 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-25-97 | 09-25-97 |  | 0 | 2121 Monument Road | San Diego | SD | 92154 | Smuggler Gulch | 4 | other | overload of collection system |  | Y | N | Smuggler Gulch | None |  | N | N | N
989050 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-25-97 | 09-25-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 26 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989051 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-25-97 | 09-25-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 18 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989052 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-26-97 | 09-26-97 |  | 0 | 5000 Monument Road | San Diego | SD | 92173 | Stewarts Drain | 2 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989053 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-26-97 | 09-26-97 |  | 0 | International Border | San Diego | SD | 92154 | Canyon del Sol | 2 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989054 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-26-97 | 09-26-97 |  | 0 | 2121 Monument Road | San Diego | SD | 92154 | Smuggler Gulch | 5 | other | overload of collection system |  | Y | N | Smuggler Gulch | None |  | N | N | N
989055 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-26-97 | 09-26-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 27 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989056 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-26-97 | 09-26-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 19 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989057 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-27-97 | 09-27-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 20 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989058 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-28-97 | 09-28-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 21 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989059 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-29-97 | 09-29-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 28 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
989060 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-29-97 | 09-29-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 22 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
989061 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-30-97 | 09-30-97 |  | 0 | International Border | San Diego | SD | 92154 | Canyon del Sol | 3 | other | overload of collection system |  | N | N | None | None |  | N | N | N
931472 | Fax 571-6972 | 07/01/97 10:31 | Gensler | 6544160 | City of San Diego | 07/01/97 07:40 | 07/01/97 09:05 | 170 | 0 | Calamar Dr. & Inverno Dr. | San Diego | SD | 92124 | 8" vc main | 1 | Roots | Root blockage | Rodded/flushed 2 sections | n | n |  |  | dissipated in storm drain | y | n | n
931567 | Fax 571-6972 | 07/02/97 03:59 | Whelan | 6544160 | City of San Diego | 07/01/97 14:33 | 07/01/97 20:30 | 714 | 180 | 1552 Tarbox St. | San Diego | SD | 92114 | 8" vc main | 1 | Grease | Grease blockage | Rodded, vacuumed overflow | n | n |  |  | dried in gutter | y | n | n
931583 | Fax 571-6972 | 07/02/97 03:57 | Whelan | 6544160 | City of San Diego | 07/01/97 16:09 | 07/01/97 17:09 | 120 | 0 | 1712 Gateway Dr. | San Diego | SD | 92105 | 8" vc main | 1 | Roots | Root blockage | Rodded main, ref for MH location | n | n |  |  | dried in gutter | y | n
931620 | Fax 571-6972 | 07/03/97 03:53 | Whelan | 6544160 | City of San Diego | 07/02/97 15:50 | 07/02/97 16:30 | 24500 | 7000 | 3296 Talbot St. | San Diego | SD | 92106 | 8" cp main | 2 | Grvty Mn Brk | Gravity Main Break | Rodded main, ref for televising | n | n |  |  | back into manhole | y | n
931702 | Fax 571-6972 | 07/02/97 16:12 | Gensler | 6544160 | City of San Diego | 07/02/97 12:26 | 07/02/97 14:26 | 60 | 0 | 6218 Calle Empinada Dr. | San Diego | SD | 92120 | 8" vc main | 1 | Roots | Root stop in MH #138 | Rodded/flushed to relieve stop | y | y |  | Pacific Ocean | dried in storm drain | y | n
931705 | Fax 571-6972 | 07/02/97 15:00 | Richardson | 6544160 | City of San Diego | 07/02/97 13:29 | 07/02/97 14:20 | 51 | 20 | 3312 Madison Av. | San Diego | SD | 92116 | 6" vc main | 1 | Construction | So-Cal Constr. broke off 200' of PVC in main | Flushed to relieve, retrieve pipe | n | n |  |  | dried at curb | y | n
931793 | Fax 571-6972 | 07/03/97 03:30 | Whelan | 6544160 | City of San Diego | 07/02/97 18:57 | 07/02/97 20:30 | 490 | 0 | Florida St. & Lincoln Av. | San Diego | SD | 92104 | 8" vc main | 1 | Grease | Grease caused blockage | Flushed to relieve stop | y | y |  | Pacific Ocean | dried in storm drain | y | n
931991 | Fax 571-6972 | 07/03/97 12:40 | Harris,L | 6544160 | City of San Diego | 07/03/97 06:00 | 07/03/97 11:00 | 150 | 40 | 3762 Main St. | San Diego | SD | 92136 | 8" vc main | 1 | Other | Heavy sludge | Rodded main w/4" screw | y | n | San Diego Bay | Pacific Ocean | soaked into ground @ MH | y | n
932274 | Fax 571-6972 | 07/05/97 23:30 | Oropeza | 6544160 | City of San Diego | 07/05/97 18:01 | 07/05/97 19:45 | 105 | 0 | 2404 Loring St. | San Diego | SD | 92037 | 8" vc main | 1 | Grvty Mn Brk | Broken main | Dig out/repair main | y | y | Mission Bay | Pacific Ocean | soil ditch/Pico & Garnet | y | n
932333 | Fax 571-6972 | 07/07/97 13:15 | Richardson | 6544160 | City of San Diego | 07/07/97 09:46 | 07/07/97 10:21 | 35 | 0 | Banillo Dr. & Malcolm Dr. | San Diego | SD | 92115 | 6" cp main | 1 | Grease | Grease build-up | Rodded 2 sec. upstream/downstream | y | y | Chollas Creek | San Diego Bay | soaked into creek bed | y | n
932428 | Fax 571-6972 | 07/08/97 14:15 | Finch | 6544160 | City of San Diego | 07/07/97 16:29 | 07/08/97 12:00 | 585 | 45 | 3144 Quimby St. | San Diego | SD | 92106 | 6" cp main | 1 | Roots | Partial root stop | Rodded up/downstream w/root cutter | y | y | San Diego Bay | Pacific Ocean | San Diego Bay | y | n | n
932762 | Fax 571-6972 | 07/11/97 07:15 | Finch | 6544160 | City of San Diego | 07/08/97 21:31 | 07/09/97 09:09 | 115 | 0 | 30th St. & Olive St. | San Diego | SD | 92104 | 6" cp main | 1 | Roots | Root blockage | Machine rodded to relieve stop | y | n | San Diego Bay | Pacific Ocean | Soaked into ground | y | n
933103 | Fax 571-6972 | 07/10/97 14:20 | Galinzoga | 6544160 | City of San Diego | 07/10/97 10:57 | 07/10/97 11:22 | 250 | 0 | 8540 Camino Santa Fe** | San Diego | SD | 92121 | 10" pvc main | 1 | Other | Bubbler failure @ P.S. #51 | Repaired failed bubbler on PS #51 | y | y |  | Pacific Ocean | Dissipated in storm drain | y | n
933396 | Fax 571-6972 | 07/11/97 19:25 | Branco | 6544160 | City of San Diego | 07/11/97 11:54 | 07/11/97 17:30 | 6720 | 0 | 5980 Mission Center Rd. | San Diego | SD | 92123 | 8" vc main | 1 | Debris | Broken screws/hand rod | Removed broken hand-rod screw, debris from 8" vc main | y | y | San Diego River | Pacific Ocean |  | y | y | y | unk
933451 | Fax 571-6972 | 07/11/97 21:21 | Branco | 6544160 | City of San Diego | 07/11/97 17:38 | 07/11/97 19:02 | 252 | 0 | 3676 Orange Av. | San Diego | SD | 92105 | 6" vc main | 1 | Grease | Grease and debris | Rodded 6" vc main | y | y | Chollas Creek | San Diego Bay |  | y | n
933575 | Fax 571-6972 | 07/12/97 09:35 | Kelly | 6544160 | City of San Diego | 07/11/97 21:28 | 07/12/97 00:00 | 46 | 0 | 6526 Lanston St. | San Diego | SD | 92111 | 8" vc main | 1 | Debris | Wastepaper | Rodded 8" vc main to relieve stop, ref. to sup. for eval. | y | y | E. Mission Bay | Pacific Ocean |  | y | n
933615 | Fax 571-6972 | 07/13/97 13:44 | Branco | 6544160 | City of San Diego | 07/13/97 08:24 | 07/13/97 11:15 | 855 | 0 | 1307 Upas St./canyon | San Diego | SD | 92103 | 6" cp main | 1 | Roots | Root blockage | Rodded 6" cp main | y | n | canyon floor | San Diego Bay |  | y | n
933617 | Fax 571-6972 | 07/13/97 13:52 | Branco | 6544160 | City of San Diego | 07/13/97 09:10 | 07/13/97 11:45 | 465 | 0 | 4910 Pacifica Dr. | San Diego | SD | 92109 | 8" vc main | 1 | Roots | Heavy roots caused blockage | Machine rodded 8" vc main to remove heavy roots | n | y |  |  | Interceptor V760 | y | n
932271 | Fax 571-6972 | 07/15/97 14:45 | Gensler | 6544160 | City of San Diego | 07/05/97 17:10 | 07/14/97 19:20 | 36000 | 0 | Mobley St. & Winen Wy./canyon | San Diego | SD | 92123 | 8" vc main | 1 | Roots | Roots, rags, paper towels | Used hand rods, scoop to clear stop | y | n | canyon floor | Pacific Ocean |  | y | y | n
934093 | Fax 571-6972 | 07/16/97 13:10 | Richardson | 6544160 | City of San Diego | 07/16/97 08:15 | 07/16/97 08:55 | 20 | 20 | 1752 Adams Av. | San Diego | SD | 92116 | 6" cp main | 1 | Roots | Root blockage | Flushed/used root saw on 6" cp main | y | n | Chollas Creek | n/a | returned to syst via MH #382 | y | n | n
934500 | Fax 571-6972 | 07/21/97 14:30 | Payne | 6544160 | City of San Diego | 07/14/97 12:00 | 07/18/97 16:30 | 975 | 82 | I-163 North & Laurel Street (El Prado Bridge) | San Diego | SD | 92101 | 8" cp main | 1 | Grvty Mn Brk | Deterioration of cp main | Remv'd blockage from 8" vc main, recovered 106 gallons | y | y | San Diego Bay | Pacific Ocean |  | y | y | n
934851 | Fax 571-6972 | 07/18/97 20:22 | Branco | 6544160 | City of San Diego | 07/18/97 18:05 | 07/18/97 18:56 | 510 | 0 | 1301 Dellcrest Ln. | San Diego | SD | 92037 | 8" vc main | 1 | Roots | Root blockage | Machine rodded 8" vc main | y | n | canyon floor | Pacific Ocean |  | y | n | n
934967 | Fax 571-6972 | 07/19/97 10:58 | Branco | 6544160 | City of San Diego | 07/19/97 08:55 | 07/19/97 09:55 | 60 | 0 | 1502 Minden Dr. | San Diego | SD | 92111 | 8" vc main | 1 | Roots | Root blockage | Machine rodded 8" vc main | y | n | San Diego River | Pacific Ocean |  | y | n | n
935540 | Fax 571-6972 | 07/24/97 13:30 | Parker | 6544160 | City of San Diego | 07/22/97 20:11 | 07/22/97 21:41 | 1165 | 350 | 3510 Auburndale St. | San Diego | SD | 92111 | 8" vc main | 1 | Roots | Heavy roots | Rodded 267' of 8" vc main | y | y | Tecolote Creek | Mission Bay |  | y | y | n
936081 | Fax 571-6972 | 07/24/97 00:00 | Whelan | 6544160 | City of San Diego | 07/23/97 19:36 | 07/23/97 20:50 | 296 | 36 | 4671 Terrace Dr. | San Diego | SD | 92116 | 8" pvc main | 2 | Grease | Grease blockage | Rodded 8" pvc main, vacuumed 36 gallons of spill | y | y | San Diego River | Pacific Ocean |  | y | n | n
907174 | Fax 571-6972 | 07/25/97 16:02 | Harris | 6544160 | City of San Diego | 07/25/97 11:30 | 07/25/97 13:31 | 121 | 0 | 1248 Hayes St. | San Diego | SD | 92103 | 4" unmarked main | 2 | Roots | Roots and debris | Hand rodded 4" unmarked main | y | n | canyon floor | San Diego Bay |  | y | n | n
936410 | Fax 571-6972 | 07/26/97 08:00 | Mickelson | 6544160 | City of San Diego | 07/25/97 11:00 | 07/25/97 17:00 | 90 | 0 | 3205 Edith Ln. | San Diego | SD | 92106 | 6" cp main | 1 | Roots | Root blockage | Vacuumed manhole on 6" cp main | n | n |  |  | soaked into ground | y | n | n
936631 | Fax 571-6972 | 07/26/97 15:51 | Branco | 6544160 | City of San Diego | 07/26/97 09:38 | 07/26/97 12:30 | 86 | 0 | 6102 La Pintura Dr. | San Diego | SD | 92037 | 8" vc main | 1 | Roots | Root blockage | Machine rodded 8" vc main | y | n | Van Nuys canyon | Pacific Ocean |  | y | n | n
936661 | Fax 571-6972 | 07/27/97 12:55 | Branco | 6544160 | City of San Diego | 07/27/97 09:49 | 07/27/97 10:39 | 500 | 0 | 10035 Rue Chantemar | San Diego | SD | 92131 | 8" pvc main | 1 | Grease | Grease blockage | Machine rodded 8" pvc main | y | y | San Diego River | Pacific Ocean |  | y | n | n
937041 | Fax 571-6972 | 07/29/97 03:58 | Whelan | 6544160 | City of San Diego | 07/27/97 13:00 | 07/28/97 20:50 | 5730 | 200 | 7258 Romero Dr. | San Diego | SD | 92037 | 8" vc main | 1 | Roots | Root blockage | Rodded 8" vc main | y | y |  | Pacific Ocean | storm drain | y | y | n
937419 | Fax 571-6972 | 07/31/97 09:45 | Parker | 6544160 | City of San Diego | 07/29/97 21:40 | 07/29/97 23:02 | 852 | 0 | 6434 Camto. Listo | San Diego | SD | 92111 | 8" pvc main | 1 | Grease | Grease blockage | Relieved stop, ref. for stepped-up PM, ref. for TV | y | y | Tecolote Creek | Mission Bay | soaked into hillside | y | n | n
937620 | Fax 571-6972 | 07/31/97 02:05 | Whelan | 6544160 | City of San Diego | 07/30/97 22:25 | 07/30/97 23:02 | 925 | 0 | 4600 Collwood Ln. | San Diego | SD | 92115 | 12" vc main | 1 | Roots | Root blockage | Rodded 12" vc main to relieve stop | y | y | San Diego River | Pacific Ocean |  | y | y | n
937668 | Fax 571-6972 | 08/01/97 10:05 | Payne | 6544160 | City of San Diego | 07/31/97 06:00 | 07/31/97 10:30 | 5400 | 2000 | 11600 Flintkote Av. | San Diego | SD | 92121 | 6" ci main | 1 | Force Mn Brk | Break on 6" return line from surge tank | Repaired 6" ci main | n | n |  |  | holding pond | y | y | n
938376 | Fax 571-6972 | 08/02/97 20:35 | Branco | 6544160 | City of San Diego | 08/02/97 18:33 | 08/02/97 19:30 | 570 | 0 | 5450 University Av. | San Diego | SD | 92105 | 8" vc main | 1 | Roots | Root blockage | Flushed line to relieve stop | y | y | San Diego Bay | Pacific Ocean | storm drain | y | n | n
938414 | Fax 571-6972 | 08/04/97 11:30 | Richardson | 6544160 | City of San Diego | 08/04/97 07:00 | 08/08/97 09:02 | 6100 | 4000 | 51st St. & Hilltop Dr. | San Diego | SD | 92114 | 21" vc main | 1 | Construction | Rocks in main from construction | Flushed main, vacuumed spill | y | n | Chollas Creek | Pacific Ocean | storm channel/recovered | y | y | n
939326 | Fax 571-6972 | 08/11/97 12:00 | Senior | 6544160 | City of San Diego | 08/07/97 13:21 | 08/07/97 19:30 | 730 | 650 | I-163 North & Laurel Street (El Prado Bridge) | San Diego | SD | 92101 | 8" cp main | 2 | Grvty Mn Brk | Concrete main deterioration | Replace main from MH 17 to MH 16 | y | y | San Diego Bay | Pacific Ocean |  | y | n | n
939877 | Fax 571-6972 | 08/09/97 16:11 | Branco | 6544160 | City of San Diego | 08/09/97 12:20 | 08/09/97 14:50 | 300 | 0 | 6161 Alvarado Rd. | San Diego | SD | 92120 | 8" vc main | 1 | Roots | Root blockage | Machine rodded to clear | y | y | canyon floor | San Diego River | soaked into canyon floor | y | n | n
939907 | Fax 571-6972 | 08/10/97 18:27 | Branco | 6544160 | City of San Diego | 08/10/97 15:55 | 08/10/97 17:20 | 85 | 0 | 6292 Lolly Ln. | San Diego | SD | 92114 | 8" pvc main | 1 | Grease | Grease blockage | Machine rodded 8" pvc main | y | y | San Diego Bay | Pacific Ocean |  | y | n | n
939925 | Fax 571-6972 | 08/11/97 15:00 | Davis,L | 6544160 | City of San Diego | 08/11/97 08:00 | 08/11/97 10:30 | 300 | 0 | Bernardo Center Dr. & Bernardo Center Ct. | San Diego | SD | 92128 | 8" vc main | 1 | Roots | Roots and grease in main | Rodded 8" vc main | y | y |  | Pacific Ocean | dried in storm drain | y | n | n
940089 | Fax 571-6972 | 08/11/97 18:05 | Whelan | 6544160 | City of San Diego | 08/11/97 13:30 | 08/11/97 14:00 | 60 | 0 | I-163 North & Laurel Street (El Prado Bridge) | San Diego | SD | 92101 | 8" vc main | 3 | Construction | Stoppage following main repair | Machine rodded; found pieces of broken main | y | n | canyon floor | Pacific Ocean | dried in canyon | y | n | n
940367 | Fax 571-6972 | 08/13/97 05:23 | Whelan | 6544160 | City of San Diego | 08/12/97 15:38 | 08/13/97 00:30 | 978 | 90 | 5366 Santa Margarita St. | San Diego | SD | 92114 | 8" vc main | 1 | Grease | Grease blockage | Rodded 8" vc main | y | y | Market St. Creek | San Diego Bay |  | y | y | n
940375 | Fax 571-6972 | 08/13/97 06:19 | Whelan | 6544160 | City of San Diego | 08/12/97 16:18 | 08/12/97 17:45 | 720 | 50 | 60th St. & Fulmar St. | San Diego | SD | 92114 | 8" vc main | 1 | Roots | Heavy roots | Set up pump, vacuumed heavy roots | y | n | creek bed | Pacific Ocean | dried in canyon | y | n | n
940384 | Fax 571-6972 | 08/13/97 06:15 | Whelan | 6544160 | City of San Diego | 08/12/97 17:40 | 08/12/97 18:25 | 90 | 80 | 4540 51st St. | San Diego | SD | 92115 | 6" cp main | 2 | Grease | Grease blockage | Rodded main to relieve stop, recovered most of spill | n | n |  |  | vacuumed some, rest soaked into ground | y | n | n
940386 | Fax 571-6972 | 08/20/97 07:45 | Richardson | 6544160 | City of San Diego | 08/12/97 18:12 | 08/12/97 22:52 | 220 | 0 | Altadena Av. & Sterling Ct. | San Diego | SD | 92105 | 8" vc main | 1 | Vandalism | 1' x 1' x 1' concrete block | Removed debris (concrete block) from main | y | n | canyon floor | Pacific Ocean | dried in canyon | y | n | n
940534 | Fax 571-6972 | 08/14/97 15:00 | Richardson | 6544160 | City of San Diego | 08/13/97 10:03 | 08/13/97 03:20 | 25925 | 19200 | 7120 Bullock Dr. | San Diego | SD | 92114 | 10" vc main | 1 | Rocks | Rocks, grease, debris | Rodded 10" vc main to relieve stop, recovered portion of spill | y | n | creek bed | Pacific Ocean | soaked into canyon florr | y | y | n
940894 | Fax 571-6972 | 08/15/97 04:46 | Whelan | 6544160 | City of San Diego | 08/14/97 15:13 | 08/14/97 16:32 | 79 | 0 | 54th St. & Montezuma Rd. | San Diego | SD | 92115 | 8" vc main | 1 | Grvty Mn Brk | main break or offset joint | Rodded 8" vc main to relieve stop | y | y | Montezuma Creek | Pacific Ocean | dissipated in drainage ditch | y | n | n
942266 | Fax 571-6972 | 08/15/97 04:49 | Whelan | 6544160 | City of San Diego | 08/14/97 16:35 | 08/14/97 16:45 | 100 | 0 | 54th St. & Baja Dr. | San Diego | SD | 92115 | 8" vc main | 2 | Roots | secondary spill as a result of clearing the above spill | Ovrflw subsided after post-stoppage removal surcharge | y | y | Montezuma Creek | Pacific Ocean | dissipated in drainage ditch | y | n | n
941305 | Fax 571-6972 | 08/16/97 15:26 | Branco | 6544160 | City of San Diego | 08/16/97 13:22 | 08/16/97 14:10 | 24 | 0 | S. Crown Pt. Park & Corona Orente Rd. | San Diego | SD | 92109 | 8" vc main | 1 | Roots | Root blockage | Machine rodded 8" vc main | y | n | Mission Bay | Pacific Ocean | soaked into ground around MH | y | n | n
941552 | Fax 571-6972 | 08/19/97 01:52 | Whelan | 6544160 | City of San Diego | 08/18/97 19:20 | 08/18/97 21:00 | 300 | 0 | 7003 Saranac St. | San Diego | SD | 92115 | 6" vc main | 1 | Roots | Roots in main | Flushed, used root saw to clear main | y | y | Alvarado Creek | San Diego River |  | y | n | n
941783 | Fax 571-6972 | 08/21/97 04:25 | Whelan | 6544160 | City of San Diego | 08/20/97 17:58 | 08/20/97 19:35 | 388 | 0 | Palm Av. & 18th St. | San Diego | SD | 92154 | 8" vc main | 1 | Grease | Grease accumulation | Rodded 8" vc main | y | y | San Diego Bay | Pacific Ocean |  | y | n | n
941809 | Fax 571-6972 | 08/21/97 04:30 | Whelan | 6544160 | City of San Diego | 08/20/97 15:14 | 08/20/97 18:33 | 50 | 0 | 2504 San Marcos St. | San Diego | SD | 92104 | 6" cp main | 1 | Roots | Roots in main | Hand rodded 6" cp main | n | n |  |  | soaked into ground | y | n | n
941872 | Fax 571-6972 | 08/21/97 13:30 | Parker | 6544160 | City of San Diego | 08/21/97 08:29 | 08/21/97 10:10 | 101 | 101 | 3954 Hains St./alley | San Diego | SD | 92109 | 8" vc main | 1 | Roots | Root stoppage | Rodded main by machine/spill captured by interceptor | y | y | Mission Bay | Pacific Ocean |  | y | n | n
942010 | Fax 571-6972 | 08/22/97 05:25 | Whelan | 6544160 | City of San Diego | 08/21/97 22:51 | 08/22/97 01:13 | 2130 | 2130 | 1820 Midway Dr. | San Diego | SD | 92110 | 6" vc main | 1 | Grease | Grease stoppage | Flushed/vacuumed spill/rest captured by interceptor | y | y |  |  | Interceptor #10 | y | n | n
942030 | Fax 571-6972 | 08/22/97 14:00 | Finch | 6544160 | City of San Diego | 08/22/97 08:41 | 08/22/97 10:15 | 10 | 0 | Del Mar Av. & Guizott St. | San Diego | SD | 92107 | 6" cp main | 1 | Roots | Light roots | Removed stop (main scheduled for Group Job Replacement) | n | n |  |  | dried at curb | y | n | n
942041 | Fax 571-6972 | 08/22/97 12:30 | Parker | 6544160 | City of San Diego | 08/22/97 09:40 | 08/22/97 10:00 | 500 | 0 | Bonair St. & Tyrian St. | San Diego | SD | 92037 | 21" vc main | 1 | Construction | Contractor caused/bypass pumping | Washed street, posted signs, notified lifeguard | y | y |  | Pacific Ocean |  | y | n | n
942198 | Fax 571-6972 | 08/23/97 14:38 | Branco | 6544160 | City of San Diego | 08/23/97 09:27 | 08/23/97 11:00 | 50 | 0 | 1843 Bancroft St. | San Diego | SD | 92102 | 6" cp main | 1 | Roots | Root blockage | Removed roots from manhole | y | n | canyon floor | San Diego Bay | soaked into canyon floor | y | n | n
942208 | Fax 571-6972 | 08/23/97 18:04 | Branco | 6544160 | City of San Diego | 08/23/97 12:10 | 08/23/97 15:30 | 800 | 0 | 330 Willie James Jones St. | San Diego | SD | 92102 | 6" vc main | 1 | Roots | Root blockage | Machine rodded to relieve stop | y | n | Chollas Creek | San Diego Bay | soaked into canyon floor | y | n | n
942213 | Fax 571-6972 | 08/23/97 17:58 | Branco | 6544160 | City of San Diego | 08/23/97 13:34 | 08/23/97 16:24 | 340 | 210 | 6600 Navajo Rd. | San Diego | SD | 92120 | 8" vc main | 1 | Roots | Root blockage | Rodded to relieve stop, vacuumed portion of spill | y | n | canyon floor | San Diego Bay | soaked into canyon floor | y | n | n
942225 | Fax 571-6972 | 08/24/97 14:08 | Branco | 6544160 | City of San Diego | 08/24/97 10:15 | 08/24/97 12:30 | 135 | 0 | 2619 Montclair St./canyon | San Diego | SD | 92104 | 6" cp main | 1 | Rocks | Rock blockage | Machine rodded, ref. for PM scheduling | y | n | Chollas Creek | San Diego Bay | soaked into canyon floor | y | n | n
942229 | Fax 571-6972 | 08/24/97 20:26 | Branco | 6544160 | City of San Diego | 08/24/97 17:02 | 08/24/97 19:20 | 690 | 0 | 4942 Lantana Dr. | San Diego | SD | 92105 | 6" vc main | 1 | Roots | Root blockage | Machine rodded 6" vc main, ref. for PM scheduling | y | n | Chollas Creek | San Diego Bay | soaked into canyon floor | y | n | n
943106 | Fax 571-6972 | 08/28/97 11:00 | Bauer | 6544160 | City of San Diego | 08/28/97 09:04 | 08/28/97 09:48 | 440 | 0 | 15603 Caldas de Reyes | San Diego | SD | 92128 | 8" pvc main | 1 | Grease | Grease blockage | Flushed 8" pvc main | y | y | Los Penasquitos Cnyn | Cypress Creek | dried in storm drain | y | n | n
943215 | Fax 571-6972 | 08/29/97 06:10 | Whelan | 6544160 | City of San Diego | 08/28/97 17:55 | 08/28/97 19:18 | 9 | 9 | 4146 33rd St. | San Diego | SD | 92104 | 8" vc main | 1 | Grease | Grease blockage | Rodded 8" vc main to relieve blockage | n | n |  |  | recovered from around manhole | y | n | n
944639 | Fax 571-6972 | 08/31/97 15:30 | Neel | 6544160 | City of San Diego | 08/31/97 11:50 | 08/31/97 13:30 | 100 | 0 | 18535 Bernardo Trails Dr. | San Diego | SD | 92128 | 8" vc main | 1 | Roots | Root blockage | Machine rodded 8" vc main/ref. to area supv. | y | n | canyon floor | Lake Hodges |  | y | n | n
944658 | Fax 571-6972 | 09/01/97 14:00 | Kelly | 6544160 | City of San Diego | 09/01/97 08:26 | 09/01/97 10:42 | 680 | 0 | Romero Dr. & Romero Ct. | San Diego | SD | 92037 | 8" vc main | 3 | Roots | Root blockage | Rodded 8" vc main | y | n | storm channel | Pacific Ocean |  | y | n | n
944680 | Fax 571-6972 | 09/08/97 09:50 | Richardson | 6544160 | City of San Diego | 09/02/97 11:15 | 09/02/97 13:15 | 6000 | 0 | 4290 Polk Av. | San Diego | SD | 92105 | 8" vc main | 1 | Grease | Grease blockage | Rodded 8" vc main, stopped resident from pumping into strm drn | y | y | Lexington Cyn. storm channel | Pacific Ocean | Dried in storm channel | y | y | n
944931 | Fax 571-6972 | 09/03/97 14:00 | Parker | 6544160 | City of San Diego | 09/03/97 10:05 | 09/03/97 11:35 | 180 | 0 | Tecolote Canyon Park 1/2 mi. e. of gate | San Diego | SD | 92109 | 10" vc main | 1 | Roots | Root blockage | Cleared stop, ref. for poss. MC site | y | n | Tecolote Creek | Mission Bay |  | y | n | n
945143 | Fax 571-6972 | 09/04/97 15:30 | Parker | 6544160 | City of San Diego | 09/04/97 12:48 | 09/04/97 14:10 | 82 | 0 | Cobb Dr. & Cobb Pl./canyon | San Diego | SD | 92117 | 8" vc main | 1 | Roots | Root blockage | Cleared stop on 8" vc main | y | y | Rose Creek | Mission Bay |  | y | n | n
945280 | Fax 571-6972 | 09/05/97 15:06 | Richardson | 6544160 | City of San Diego | 09/05/97 07:47 | 09/05/97 10:40 | 685 | 0 | 3679 Collier Av. | San Diego | SD | 92116 | 8" vc main | 2 | Roots | Root blockage | Relieved stop by rodding/flushing 8" vc main | y | n | canyon floor | Pacific Ocean | soaked into canyon floor | y | n | n
946547 | Fax 571-6972 | 09/11/97 16:45 | Finch | 6544160 | City of San Diego | 08/11/97 12:00 | 09/10/97 16:00 | 217200 | 0 | 10th Av. & A St. | San Diego | SD | 92101 | 6" vc main | 1 | Grease | Grease blockage caused backup thru abandoned lateral | Flushed to relieve stop, plugged abandoned lateral | y | y | San Diego Bay | Pacific Ocean |  | y | y | n
946908 | Fax 571-6972 | 09/12/97 15:00 | Sackett | 6544160 | City of San Diego | 09/12/97 10:38 | 09/12/97 12:01 | 180 | 0 | I-163 & Laurel St. /under bridge | San Diego | SD | 92101 | 6" cp main | 2 | Debris | debris, deteriorating main | Cleared stop; this main scheduled for Group Job repl. | n | n |  |  | soaked into ground | y | n | n
946659 | Fax 571-6972 | 09/11/97 15:10 | Finch | 6544160 | City of San Diego | 09/11/97 09:28 | 09/11/97 11:28 | 240 | 0 | 4445 Logan Av. | San Diego | SD | 92113 | 6" vc main | 1 | Grease | Heavy grease | Cleared stop, ref. to FEWD | n | n |  |  | soaked into ground in dirt lot | y | n | n
946873 | Fax 571-6972 | 09/12/97 15:00 | Finch | 6544160 | City of San Diego | 09/12/97 09:09 | 09/12/97 11:20 | 615 | 0 | Canon St. & Evergreen St. | San Diego | SD | 92106 | 6" cp main | 1 | Grease | Grease and rocks | Cleared stop, ref. to FEWD | y | y | San Diego Bay | Pacific Ocean |  | y | n | n
947198 | Fax 571-6972 | 09/13/97 13:29 | Branco | 6544160 | City of San Diego | 09/13/97 07:30 | 09/13/97 08:50 | 80 | 0 | 14004 Rue St. Raphael | San Diego | SD | 92014 | 8" vc main | 1 | Roots | Root blockage | Machine rodded 8" vc main, ref. for MC site | y | y |  | Pacific Ocean |  | y | n | n
947203 | Fax 571-6972 | 09/13/97 14:31 | Branco | 6544160 | City of San Diego | 09/13/97 08:45 | 09/13/97 10:40 | 230 | 0 | 2997 Marquette St. | San Diego | SD | 92110 | 8" vc main | 1 | Roots | Root blockage | Machine rodded 8" vc main, ref. for MC site | y | y | San Diego Bay | Pacific Ocean |  | y | n | n
947242 | Fax 571-6972 | 09/14/97 20:16 | Branco | 6544160 | City of San Diego | 09/14/97 15:53 | 09/14/97 18:30 | 314 | 314 | 3769 Promontory St. | San Diego | SD | 92109 | 8" vc main | 1 | Grease | Grease, plastic bags | Rodded to clear stop; spill captured by interceptor V70 | n | y |  |  | Interceptor V-70 | y | n | n
946895 | Fax 571-6972 | 09/18/97 08:50 | Finch | 6544160 | City of San Diego | 09/12/97 10:12 | 09/17/97 17:58 | 3948 | 0 | 2431 Willow St./canyon | San Diego | SD | 92106 | 6" cp main | 1 | Roots | Heavy roots | Cleared stop, TV'd for integrity, ref. for Group Job repl. | n | n | San Diego Bay | Pacific Ocean |  | y | y | y | unk
948096 | Fax 571-6972 | 09/19/97 02:55 | Whelan | 6544160 | City of San Diego | 09/18/97 16:34 | 09/18/97 18:15 | 101 | 0 | 5211 Joan Ct. | San Diego | SD | 92115 | 8" vc main | 1 | Roots | Root blockage | Rodded 8" vc main w/screw to clear stop | y | y | canyon floor | Pacific Ocean | dried in canyon | y | n | n
948220 | Fax 571-6972 | 09/19/97 14:00 | Finch | 6544160 | City of San Diego | 09/19/97 09:51 | 09/19/97 11:05 | 2220 | 1110 | Canon St. & Evergreen St. | San Diego | SD | 92135 | 6" pvc main | 2 | Grease | Grease and roots | Cleared stop, ref to be TV'd for pipe integrity | y | y | San Diego Bay | Pacific Ocean |  | y | y | y | 3
948225 | Fax 571-6972 | 09/19/97 15:25 | Finch | 6544160 | City of San Diego | 09/19/97 09:54 | 09/19/97 10:34 | 80 | 60 | 4000 Santa Cruz Av. | San Diego | SD | 92107 | 6" cp main | 1 | Roots | Root blockage | Machine rodded to clear, recovered 60 gal. | n | n |  |  | dried in street | n | n
948287 | Fax 571-6972 | 09/19/97 19:49 | Branco | 6544160 | City of San Diego | 09/19/97 12:25 | 09/19/97 17:24 | 50 | 0 | 5620 Trinidad Wy. | San Diego | SD | 92114 | 6" cp main | 1 | Roots | Root blockage | Machine rodded 6" cp main, deodorize, ref. for MC site | n | n |  |  | soaked into ground | y | n | n
948570 | Fax 571-6972 | 09/20/97 15:26 | Branco | 6544160 | City of San Diego | 09/20/97 09:04 | 09/20/97 11:28 | 72 | 0 | 4421 New Hampshire St. | San Diego | SD | 92108 | 6" cp main | 1 | Roots | Roots, grease | Machine rodded 6" cp main, ref for MC site | y | y | canyon floor | Pacific Ocean | dried in canyon | y | n | n
948574 | Fax 571-6972 | 09/20/97 16:51 | Branco | 6544160 | City of San Diego | 09/20/97 11:09 | 09/20/97 16:30 | 963 | 0 | 2685 Montclair St. | San Diego | SD | 92104 | 10" vc main | 1 | Vandalism | debris dumped in manhole | Ref. to conf. space team to remove rocks, barricades; ref for bucket | y | n | canyon floor | San Diego Bay | dried in canyon | y | n | n
948590 | Fax 571-6972 | 09/20/97 19:23 | Branco | 6544160 | City of San Diego | 09/20/97 15:52 | 09/20/97 18:08 | 260 | 0 | 6320 Potomac St. | San Diego | SD | 92139 | 8" vc main | 1 | Grease | Grease blockage | Vacuumed/flushed 8" vc main, ref for MC site | y | y | Sweetwater River | San Diego Bay | dried in storm drain | y | n | n
948742 | Fax 571-6972 | 09/23/97 02:48 | Parker | 6544160 | City of San Diego | 09/22/97 16:13 | 09/22/97 17:52 | 990 | 0 | 4735 Boxwood Dr./easement behind | San Diego | SD | 92117 | 10" vc main | 1 | Roots | Root blockage | Rodded to relieve stop | n | n |  |  | dried around manhole | y | y | n
948633 | Fax 571-6972 | 09/22/97 13:25 | Harris,L | 6544160 | City of San Diego | 09/22/97 09:35 | 09/22/97 11:05 | 45 | 45 | 2778 Treat St. | San Diego | SD | 92102 | 6" cp main | 3 | Grease | Grease blockage - heavy | Cleared stop on 6" cp main | y | y |  | Pacific Ocean | recovered from storm drain | y | n | n
949716 | Fax 571-6972 | 09/25/97 23:35 | Whelan | 6544160 | City of San Diego | 09/25/97 15:55 | 09/25/97 17:04 | 690 | 0 | 8353 Menkar Rd. | San Diego | SD | 92126 | 8" vc main | 1 | Grease | Grease blockage | Rodded 8" vc main to relieve stop | y | y |  | Pacific Ocean |  | y | n | n
949948 | Fax 571-6972 | 09/26/97 19:48 | Branco | 6544160 | City of San Diego | 09/26/97 15:35 | 09/26/97 18:30 | 875 | 0 | 6528 Bougainvillea Rd. | San Diego | SD | 92139 | 8" vc main | 1 | Grease | Grease blockage | Machine rodded 8" vc main | y | y | Sweetwater River | San Diego Bay |  | y | n | n
950111 | Fax 571-6972 | 09/27/97 12:39 | Branco | 6544160 | City of San Diego | 09/27/97 07:44 | 09/27/97 09:30 | 10600 | 0 | Market St. & Merlin St./under trolley tracks | San Diego | SD | 92114 | 15" vc main | 1 | Rocks | Rock blockage | Machine rod, ref for bucketing to remove add'l rocks | y | y | Chollas Creek | San Diego Bay |  | y | y | n
950558 | Fax 571-6972 | 09/30/97 18:50 | Davis | 6544160 | City of San Diego | 09/29/97 09:00 | 09/30/97 13:30 | 17100 | 1000 | 9770 Carroll Centre Rd. | San Diego | SD | 92145 | 10" vc main | 1 | Grvty Main Brk | Blockage downstrm from main brk | Flushed 407' of 10" vc main | y | y |  | private pond |  | y | y | n
97001 | N/A | N/A | N/A |  | City of Poway | 01/07/97 - 0730 | 01/07/97 - 0810 | 40 | 0 | 17924 St. Andrews Drive | Poway | San Diego | 92064 | Collection System | 1 | Roots in main | 0730-Notified by residents manhole in front of home bubbling sewage. Dispatched Vactor crew to site at 0732. Vactor crew and Utilities Operations Supervisor met at site at 0747. Sewage was bubbling from manhole access in front of residence. Found 8" m | Placed this section of the collection system in the quarterly maintenance file. A video inspection has been scheduled to determine extent of root infiltration. | No | No | N/A | N/A | Cleaned up | No | No | No | N/A | None
978001 | quarterly report | n/a | Orv Salisbury | 760-744-0460 | V.W.D. | 7-10-97 1830 | 7-10-97 1915 | 800 | none | 1510 Via Brisa Del Lago | San Marcos | S.D. | 92069 | sewer clean out | 1 | grease | grease blockage in a gravity 8" sewer line | new piping and a new pump station is under const. | y | y | Lake San Marcos | none | Lake San Marcos | y | n | y | 4+ | no body contact in the lake
978002 | quarterly report | n/a | Orv Salisbury | 760-744-0460 | V.W.D. | 7-16-97 2000 | 7-16-97 2200 | 1800 | 1000 | Liberty St. | San Marcos | S.D. | 92069 | sewer manhole | 1 | grease | heavy grease from low income apartments | we will include this site on our trouble spot list | y | y | Storm drain | S.M. Creek | open channel | y | n | y | 4 | spill was contained and recovered
978003 | Pam Jackson | 9-25-97 1750 | Orv Salisbury | 760-744-0460 | V.W.D. | 9-25-97 1630 | 9-26-97 0600 | 1500000 | none | easment | Carlsbad | S.D. | 92009 | 24" outfall line | 1 | broken pipe | steel pipe was possibly crushed when installed | engeneering dept is investigating the cause | n | n | canyon | irrigation ponds | La Costa Resort | y | y | y | 14+ | spill was contained
978004 | voice mail | 9-26-97 1000 | Orv Salisbury | 760-744-0460 | V.W.D. | 9-26-97 0900 | 9-26-97 1430 | 942000 | none | easment | Carlsbad | S.D. | 92009 | 24" outfall line | 2 | broken pipe | steel pipe was possibly crushed when installed | engeneering dept is investigating the cause | n | n | canyon | irrigation ponds | La Costa Resort | y | y | y | 14+ | spill was contained
829971 |  |  |  |  | City of San Clemente | 8/29/97, 10:05 | 8/29/97, 10:25 | 50 gal | 0 | 110 Balboa | San Clemente | OR | 92672 | SMHD6624 | 0 | Roots |  |  | N | Y |  |  | Absorbed in Canyon Floor | N | N | N | NA
978001 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 07/06/97 1730 | 07/06/97 1830 | 150 | 0 | 4200 Via Rancho Road & Cassanna Way | Oceanside | SD | 92056 | Manhole | 0 | Debris | Eight inch "screw plug" stuck in mouth of channel. | Removed it. | N | Y | Storm Drain | N/A | Dried up quickly. | N | N/A | N | N/A
978002 |  |  | Ira Black | 7609667868 | Water Utilities Dept. City of Oceanside | 07/14/97 0945 | 07/14/97 1030 | 500 | 0 | 2861 Turnbull Street Easement | Oceanside | SD | 92054 | Manhole | 0 | Vandalism. | Fence poles, sand, boards, and rocks. | Put a "lock down" lid on the manhole and check it once a week. | N | Y | Storm Drain | N/A | `Storm Drain | Y | N/A | Y | 2 | Did not go to surface water, but we'll sign anyway.
978003 | FAX | 07/21/97 1045 | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 07/20/97 0910 | 07/20/97 1030 | 600 | 0 | Street in front of 2121 Oceanside Blvd. | Oceanside | SD | 92054 | Manhole | 0 | Blockage. | Easement line off Oc'side Blvd. Blocked with sticks, roots, grease, rocks, etc. | Cleaned street with Fire hydrant. | Y | Y | Loma Alta Creek | Loma Alta Slough | N/A | Y | N/A | Y | 2 | Loma Alta Creek is blocked off @ Bucc. Beach. Slough is being pumped into La Salina WWTP for treatment.
978004 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 07/27/97 1445 | 07/27/97 1500 | 50 | 0 | Mission & Frontier | Oceanside | SD | 92054 | Manhole | 9 | Line Break. | CalTrans contractor crushed lateral. | CalTrans will order repairs when they get around to it. | N | N | N/A | N/A | Soaked into soil. | N | N/A | N | N/A | Ongoing problem. Needs to be fixed, ASAP!
978005 | Tape Recorder | 07/29/97 2353 | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 07/29/97 2000 | 07/29/97 2240 | 15000 | 0 | 5565 Old Ranch Road | Oceanside | SD | 92054 | Manhole | 0 | Debris. | Grease and Rags and Construction Wood. | Put a "lock down" lid on the manhole and check it once a week. | Y | Y | Storm Drain | Storm Drain Channel | Storm Drain Channel | Y | Y | Y | 5 | "Spill" did not reach Guajome Lake, as previously reported. All soaked into the sides and bottom of channel.
978006 |  |  | Ira Black | 7609667868 | Water Utilities Dept. City of Oceanside | 07/29/97 1330 | 07/29/97 1345 | 15 | 0 | 710 Neptune | Oceanside | SD | 92054 | Cleanout | 1 | Roots. | Roots in the City Main. | "Rod " manhole every 30 days. | N | N | N/A | N/A | Soaked into soil. | N | N/A | N | N/A
978007 |  |  | Ira Black | 7609667868 | Water Utilities Dept. City of Oceanside | 07/31/97 1250 | 07/31/97 1300 | 50 | 0 | Lynn Court & Henie Hills | Oceanside | SD | 92054 | Manhole | 2 | Roots. | Roots in the City Main. | "Rod " manhole every 30 days. | N | Y | Storm Drain | N/A | Soaked into soil. | N | N/A | N | N/A
978008 |  |  | Jeremy Kemp | (760)966-7868 | Water Utilities Dept. City of Oceanside | 08/03/97 1150 | 08/03/97 1220 | 40 | 0 | Mission & Frontier | Oceanside | SD | 92054 | Manhole | 10 | Line Break. | CalTrans contractor crushed lateral. | CalTrans will order repairs when they get around to it. | N | N | N/A | N/A | Soaked into soil. | N | N/A | N | N/A | Ongoing problem. Needs to be fixed, ASAP!
978009 |  |  | Steve | (760)966-7868 | Water Utilities Dept. City of Oceanside | 08/10/97 0745 | 08/10/97 0755 | 100 | 0 | Mission & Frontier | Oceanside | SD | 92054 | Manhole | 11 | Line Break. | CalTrans contractor crushed lateral. | CalTrans will order repairs when they get around to it. | N | N | N/A | N/A | Soaked into soil. | N | N/A | N | N/A | Ongoing problem. Needs to be fixed, ASAP!
978010 |  |  | Norm Crum | 7609667868 | Water Utilities Dept. City of Oceanside | 08/14/97 0830 | 08/14/97 0930 | 500 | 0 | Behind 725 Los Arbolitos | Oceanside | SD | 92056 | Air Relief Valve | 0 | Leaky Valve | Tapping Valve on 24 inch force main would not close completely, during time it took to clean grease and debris from air valve. | valve to be placed on air vent riser pipe, prior to the air vent itself. | N | N | N/A | N/A | Soaked into soil. | N | N/A | N | N/A | Repairs will be made A.S.A.P!
978011 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 08/17/97 1218 | 08/17/97 1250 | 300 | 0 | Mission & Frontier | Oceanside | SD | 92054 | Manhole | 12 | Line Break. | CalTrans contractor crushed lateral. | CalTrans will order repairs when they get around to it. | N | N | N/A | N/A | Soaked into soil. | N | N/A | N | N/A | Ongoing problem. Needs to be fixed, ASAP!
978012 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 08/24/97 0800 | 08/24/97 0810 | 25 | 0 | Mission & Frontier | Oceanside | SD | 92054 | Manhole | 13 | Line Break. | CalTrans contractor crushed lateral. | We are "vactoring" out of the manhole three (3) times a day. | N | N | N/A | N/A | Soaked into soil. | N | N/A | N | N/A | Ongoing problem. Needs to be fixed, ASAP!
978013 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 08/26/97 1232 | 08/26/97 1250 | 25 | 0 | 1400 Pacific Street | Oceanside | SD | 92054 | Manhole | 0 | Grease. | Grease plugged City Main. | Dropped 100 lbs. Of Chlorine in sewer main to eat grease. | Y | Y | Storm Drain | Loma Alta Slough | N/A | N | N/A | N | N/A
978014 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 09/07/97 1200 | 09/07/97 1230 | 100 | 0 | Mission & Frontier | Oceanside | SD | 92054 | Manhole | 14 | Line Break. | CalTrans contractor crushed lateral. | CalTrans will order repairs when they get around to it. | N | N | N/A | N/A | Soaked into soil. | N | N/A | N | N/A | Vactor is down for repairs. Scavenger not keeping up w/flow. Called out "Atlas" 3000 Gal. Tanker.
978015 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 09/14/97 1415 | 09/14/97 1440 | 70 | 0 | Mission & Frontier | Oceanside | SD | 92054 | Manhole | 15 | Line Break. | CalTrans contractor crushed lateral. | CalTrans will order repairs when they get around to it. | N | N | N/A | N/A | Soaked into soil. | N | N/A | N | N/A | Ongoing problem. Needs to be fixed, ASAP!
978016 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 09/14/97 2020 | Ongoing | 5-75 GPM | 0 | 515 Greenbrier | Oceanside | SD | 92054 | Private Cleanouts | 0 | Blockage. | Unknown. Private plumbing problem inside building. | Could not contact manager of complex, until 15/0930. | Y | Y | Storm Drain | Loma Alta Slough | Pacific Ocean | Y | N/A | N | N/A | "Cartage Apts." owned by Clifton Warren Investments of Hermosa Beach, CA. (310)372-5774.
978017 |  |  | Mike Teem | 7609667868 | Water Utilities Dept. City of Oceanside | 09/23/97 ?? | Ongoing | 1-2 GPM | 0 | 814 Missouri | Oceanside | SD | 92054 | Private Cleanouts | 1 | Blockage. | Unknown. Private plumbing problem inside building. | Notified Fran Banks (Chamberlain Prop. Manage.) @ 24/1100Sep97. | N | N | Storm Drain | N/A | Soaked into soil. | N | N/A | N | N/A | Peppertree Apts. Owned by Jdames F. Weber of 580 Beech Street, Carlsbad.
4 | GLORIA FULTON | 09/22/97 07:30 | MIKE DUNBAR | (714) 499-4555 | SOUTH COAST WATER DISTRICT | 09/22/97 07:30 | 09/22/97 08:30 | 4000 | 0 | VALIDO WAY & TOTO LOMA LANE | LAGUNA BEACH | OR | 92977 | MANHOLE | 0 | ROOTS / DEBRIS / BLOCKAGE | MANHOLE PLUGGED UP WITH ROOTS AND RAGS | CLEANED MANHOLE | N | Y | NONE | NONE | SAND | Y | N/A | N | N/A
978001 |  |  | Joel Holt | (760) 723-5640 | Fallbrook Public Utility District | 1997-07-02 11:50 | 1997-07-02 12:20 | 25 | 0 | 645 Minnesota | Fallbrook | SD | 92028 | 6" VCP | 1 | Roots | Eucaplyptus Roots | Rodded with small rodder and opened 15' into 6" lateral. Problem area will be replaced. | N | N | N/A | N/A | Ice Plant on bank. | N | N | N | N/A | No overflow was recovered due to ground cover (Ice Plant), debris was picked up.
978002 |  |  | Joel Holt | (760) 723-5640 | Fallbrook Public Utility District | 1997-07-02 18:30 | 7/2/97 1900 | 30 | 5 | 410 E. Fallbrook St. | Fallbrook | SD | 92028 | 6" VCP | 4 | Grease Blockage | Grease & baby wipes. | Flushed lines, ran 6" cutter in cleanout all the way to main. Recovered solids toilet paper, baby wipes, string and other foreign materials. | N | N | N/A | N/A | Around cleanout on grass & asphalt. | N | N | N | N/A | Did not reach storm drain. Cleaned up all debris.
978003 |  |  | Joel Holt | (760) 723-5640 | Fallbrook Public Utility District | 1997-07-18 11:20 | 1997-07-18 11:45 | 5 | 0 | 131 W. Beech St. | Fallbrook | SD | 92028 | 4" Clay Pipe | 1 | Other | Unknown. | Rodded lateral until water went down. Main line needs to be flushed. | N | N | N/A | N/A | Dirt around cleanout. | N | N | N | N/A
978004 |  |  | Joel Holt | (760) 723-5640 | Fallbrook Public Utility District | 1997-07-20 08:30 | 1997-07-20 09:00 | 250 | 0 | 700 Block of Shady Lane | Fallbrook | SD | 92028 | Lift Station | 1 | Power Failure | Power failure. Generator didn't start. | Posted area. Covered area with dirt, and made sure lift station was operational. | N | N | N/A | N/A | Empty/open field that is fenced on all four sides. | N | N | Y | 3
978005 | (619) 571-6972 | 1997-07-28 09:00 | Kyle Drake | (760) 728-1125 | Fallbrook Public Utility District | 1997-07-27 20:00 | 1997-07-27 21:30 | 1300 | 5 | 406 Potter St. | Fallbrook | SD | 92028 | 4" Clay Cleanout | 1 | Grease | Grease, paper, and grit build up in main line. | Rodded from cleanout to main line. Recovered grease, paper, and other objects. Flushed main line. | Y | Y | Fallbrook Creek | Lake O'Neil | N/A | Y | Y | Y | 3 | OES Control # 97-2937.
978006 | (619) 571-6972 | 1997-08-01 09:45 | Joel Holt | (760) 723-5640 | Fallbrook Public Utility District | 1997-07-28 13:00 | 7/28/97 16:30 | 1050 | 0 | 2141 S. Mission | Fallbrook | SD | 92028 | 18" Recycled Water Line | 1 | Line Break | Small break in the recycled water main line. | N/A | N | N | N/A | N/A | Absorbed into the ground just adjascent to an approved recycled water user. | Y | N | N | N/A | Spill was Title 22, recycled water.
978007 | (619) 571-6972 | 1997-07-30 10:30 | Patti Page | (760) 723-5640 | Fallbrook Public Utility District | 1997-07-29 12:30 | 1997-07-29 13:00 | 1800 | 50 | 532 E. Fallbrook St. | Fallbrook | SD | 92028 | Cleanout | 1 | Grease | Grease, paper, and grit build-up in main. | Flushed main line. | Y | Y | Fallbrook Creek | Lake O'Neil | N/A | Y | Y | Y | 3 | OES Control # 97-2980. 50 gallons used in wash down. Posted all public access areas along Fallbrook Creek from 532 E. Fallbrook St. to Mission Rd. Attempted to notify Camp Pendleton (no answer for 3 days).
978008 |  |  | Joel Holt | (760) 723-5640 | Fallbrook Public Utility District | 1997-08-10 20:41 | 1997-08-10 21:10 | 1 | 0 | 229 W. Alavarado | Fallbrook | SD | 92028 | Cleanout | 2 | Roots | Roots possibly offset joint in lateral. Also clogged with toilet paper. | Rodded lateral from open cleanout. Check on monthly basis and rod with root cutter. | N | N | N/A | N/A | Inside cleanout - only 1 gallon overflowed. | N | N | N | N/A
978009 |  |  | Joel Holt | (760) 723-5640 | Fallbrook Public Utility District | 1997-08-11 09:00 | 1997-08-11 09:25 | 20 | 10 | 1062 Via Unidos | Fallbrook | SD | 92028 | 4" Clay Cleanout | 1 | Roots | Roots in main line. | Flushed main line and rodded cleanout to main. Recovered roots, solids, and toilet paper. Removed contaminated soil around cleanout box and replaced with clean soil. | N | N | N/A | N/A | Dirt around cleanout. | N | N | N | N/A
978010 | (619) 571-6972 | 1997-08-17 11:30 | Mitch Pierson | (760) 723-5640 | Fallbrook Public Utility District | 1997-08-16 23:00 | 1997-08-17 01:00 | 195000 | 0 | 2575 Olive Hill Rd. | Fallbrook | SD | 92028 | 6" Pipeline @ Meter | 1 | Line break. | Truck hit 6" recycled water meter pipeline. | Pipeline was valved off until the repair is complete. | Y | N | Ostrich Creek | San Luis Rey River | N/A | Y | Y | N | N/A | Signs were not posted as per OES, David Cammal. Spill was Title 22, recycled water.
978011 |  |  | Joel Holt | (760) 723-5640 | Fallbrook Public Utility District | 1997-08-18 08:30 | 1997-08-19 14:00 | 50 | 40 | 550 Industrial Way | Fallbrook | SD | 92028 | 6" Clay Pipe | 1 | Line break | Pipe was broken by backhoe operator. | Section was in 6" piece of pipe. Removed approximately 2 yards of contaminated soil around pipe. | N | N | N/A | N/A | Recovered spill by vactor truck from bell hole ditch. | N | N | N | N/A
978012 | (619) 467-2952 | 1997-09-29 11:45 | Joel Holt | (760) 723-5640 | Fallbrook Public Utility District | 1997-09-29 05:00 | 1997-09-29 09:30 | 62330 | 0 | Overland Trail | Fallbrook | SD | 92028 | Effluent Line - Plant 2 | 1 | Line Break | Break in pressure line, effluent from Plant 2. | Secured pumps and repaired line. | Y | N | Ostrich Creek | San Luis Rey River | N/A | Y | Y | Y | 3 | Spill was secondary effluent.
978001 | 619 571-6972 | 970801 0800 | City of Laguna Beach | 714 497-0765 | Laguna Beach | 970801 0800 | 970801 0830 | 1000 | 1000 gals. | Temple Hills Drive | Laguna Beach | Orange | 92651 | Temple Hills Drive Manhole #69 | 1 | Roots/Rocks | Main Line was blocked with debris | Main Line jetted/vacuumed to remove | No | No | Temple Hills Dr./Storm Drain | None | Temple Hills Drive | No | No | No |  | The main was jetted/vacuumed to remove all debris and a T.V.
978002 | 619 571-6972 | 970831 1030 | City of Laguna Beach | 714 497-0765 | Laguna Beach | 970831 0930 | 970831 1100 | 40000 | None | 412 N. Coast Hwy | Laguna Beach | Orange | 92651 | 412 N. Coast Hwy. Bathrooms | 1 | Paper/Rags/roots | 8" Sewer Main Line was plugged up | Jetter machine used to open up the | Yes | Yes | Rockpile Beach | None | Rockpile Beach | Yes | No | Yes | 4 | Posting was done by Laguna Beach Lifeguards at the small coves
978003 | 619 571-6972 | 970918 1020 | City of Laguna Beach | 714 497-0765 | Laguna Beach | 970918 1020 | 970918 1040 | 100 | None | 647 S. Coast Hwy | Laguna Beach | Orange | 92651 | 647 S. Coast Hwy | 1 | Grease | 8" Sewer Main Line on Sleepy Hollow | Jetter machine used to open up the | Yes | No | Pacific Ocean / Sleepy Hollow | None | Same | Yes | No | Yes | 4 | Posting was done by Orange County Health Dept. Beach closed from
97002 | N/A | N/A | N/A |  | City of Poway | 09/07/97 - 1400 | 09/07/97 - 1445 | 40 | 16 | 12957 Sagewood Drive | Poway | San Diego | 92064 | Collection System | 1 | Roots in main | 1400 - Resident called in report of overflow. Dispatched Vactor crew to site. Found 8" main partially blocked with tree roots. Cleared roots from pipe and performed clean up procedures. Approximate loss of 40 gallons calculated. | Placed section of collection system in PM database. | No | No | N/A | N/A | Cleaned up | No | No | No | N/A | None
OCT-DEC '97
978002 | NO |  |  |  | City of Vista | 1997-10-06 16:00 | 1997-10-06 16:00 | <200 | 0 | 2525 Lupine Hills Drive | Vista | SD | 92083 | Shadowridge Water Reclamation Plant | Zero | Inadvertent valve closure | While draining the splitter box the surface drain valve was mistakenly closed discharging partially treated wastewater down the storm water drainage system | [10 empty] | The total area affected was less than square feet. It absorbed into the ground within minutes. | bar: N; Y to N
978003 | Carol Tomaki | 1997-10-09 14:00 | Jim Gusman | (760) 726-1340ext1665 | City of Vista | 1997-10-09 12:00 | 1997-10-09 13:30 | 1800 | 500 | 605 W. Vista Way | Vista | SD | 92083 | Private lateral and grease trap | Zero | Grease | Grease trap overflowed across the sidewalk, it also caused a blockage in the lateral which also overflowed across the sidewalk. Both spills followed the gutter about 100' to a catch basin, about 350'-400' north of Buena Vista Creek. | Sewer main was jetted for partial blockage from grease. Sand bags were used to capture still flowing cleanout lateral and grease trap. Vacuum truck captured some of the flow and then a back flush and vacuum of the storm drain was done. | Y | Y | Buena Vista Creek | Buena Vista Lagoon |  | Y | Y | N |  | Washed down the public sidewalk area with fresh water.
978005 | Greg Peters | 10-06-97 1030 | Ted Powell | 760-744-0460 | V.W.D. | 10-6-97 0810 | 10-6-97 0850 | 2000 | none | Discovery St. | San Marcos | S.D. | 92069 | S4C-Q15-M6 | 1 | grease | grease blockage in the 8" sewer line | we will include this on the trouble spot list | y | n | S.M. creek | Lake San Marcos | n/a | y | y | y | 5 | area posted as per health dept. no body contact in lake.
978006 | fax | 11-13-97 1400 | Cheryl Brandstrom | 760-744-0460 | V.W.D. | 11-10-97 1045 | 11-11-97 1230 | 1500000 | none | easment | Carlsbad | S.D. | 92009 | 24" outfall line | 3 | broken pipe | steel pipe was possibly crushed when installed | in process of replacing bad pipe | n | n | canyon | irrigation ponds | La Costa Resort | y | y | y | 14+ | spill was contained
978001 | FAX | 1997-12-20 | Dave Seymour | 714 459-6540 | SMWD | 12/20/97 10:00am | 1997-12-20 17:00 | 900 gal | 0 | Seacountry Lane | Rancho Santa Margarita | OR | 92688 | Manhole | 0 | Construction debri | Construction debri, rocks, wood and mud blocked downstream of manhole causing spill | Removed debri, vactored solids and cleaned section of line effected by blockage | y | y | Trabuco Creek |  |  | Y | Y | N |  | Contained spill upon arrival, washed down area with chlorine solution and vactored remaining spill
978002 | FAX | 12/17/97 6:50AM | KRIS HANBERG | 714/858-4979 | TCWD | 12/17/97 6:50AM | 12/17/97 7:15AM | 6000 | 0 | BARNBURG | TRABUCO CANYON | OR | 92679 | BARNEBURG LIFT STATION | 2 | PUMP STATION FAILURE | COMPUTER THAT CONTROLS STATION LOCKED UP | REBOOTED COMPUTER | Y | Y | BELL CANYON CREEK | SAN JUAN CREEK |  | Y | N | N | 0 | NONE
978003 | Kathy Stone | 12/9/97 8am | Bill Wiltse | 6198744082 | SD County | 11/08/97 2030 | 11/08/97 2210 | 300 | 0 | 10105 Toledo | Spring Valley | SD | 91977 | 501-180-198T | 0 | Roots | Roots caused paper and grease to block line | Special Maintenance Line, Clean every 3 months | N | N | none | none | Perc into meadow | Y | Y | N | 0 | Televised line, good condition
978013 | 619-467-2952 | 1997-10-13 14:00 | Joel Holt | 7607235640 | Fallbrook Public Utility District | 1997-10-13 04:00 | 1997-10-13 08:00 | 4000 | 0 | 2800 Overland Trail | Fallbrook | SD | 92028 | Effluent Line-Plant2 | 2 | Line Break | Pressure line sustained a hole. | Secured pumps and repaired the line. | Y | N | Ostrich Creek | San Luis Rey River | NA | Y | Y | Y | 3 | Secondary Effluent
978014 |  |  | Joel Holt | 7607235640 | Fallbrook Public Utility District | 1997-11-14 13:42 | 1997-11-14 14:05 | 50 | 5 | 2613 Buena Rosa | Fallbrook | SD | 92028 | Cleanout | 1 | Blockage | Toilet paper and foreign material. | Rodded line until it was clear. Picked up solids and other objects. | N | N | NA | NA | Lawn and sidewalk. | N | N | N | NA | None.
978015 |  |  | Joel Holt | 7607235640 | Fallbrook Public Utility District | 1997-11-17 14:00 | 1997-11-17 14:35 | 5 | 5 | 800 E. Porter | Fallbrook | SD | 92028 | Cleanout | 1 | Roots | Roots in cleanout. | Rodded line with bullet and 4" cutter. Recovered 5 gallons of paper, roots, and solids. | N | N | NA | NA | Ground around cleanout. | N | N | N | NA | None.
978016 |  |  | Joel Holt | 7607235640 | Fallbrook Public Utility District | 1997-11-20 16:15 | 1997-11-20 16:30 | 15 | 0 | 500 Ammunition Rd. | Fallbrook | SD | 92028 | Manhole | 1 | Grease | Grease plugging line. | Flushed line. | N | N | NA | NA | Gutter and street. | N | N | N | NA | None.
978017 |  |  | Joel Holt | 7607235640 | Fallbrook Public Utility District | 1997-11-23 02:23 | 1997-11-23 02:50 | 50 | 0 | 400 Block W. Aviation | Fallbrook | SD | 92028 | Manhole | 1 | Grease | There was alot grease in the line. | Flushed line twice. | N | N | NA | NA | On blacktop and cement driveway (about 200 ft.). | N | N | N | NA | Unable to get access to location due to locked gate, which made initial recovery of spill difficult.
978018 | SDCnty - K. Stone | 1997-12-06 10:00 | Joe Polzin | 7607235640 | Fallbrook Public Utility District | 1997-12-05 17:00 | 1997-12-06 08:00 | 27000 | 0 | 700 Block Shady Lane | Fallbrook | SD | 92028 | Lift Station | 2 | Pump Station Failure | Both pumps at the Lift Station tripped out. | Reset both breakers. Cleaned the bubbler tube and watched it run through several cycles. | N | N | NA | NA | Ran into open field with no public access. | Y | N | Y | 3 | Unable to recover any of spill - quicly ran into open field and percolated into ground.
978019 | SDCnty - K. Stone | 1997-12-08 12:40 | Patti Page | 7607235640 | Fallbrook Public Utility District | 1997-12-07 14:00 | 1997-12-07 14:45 | 300 | 0 | 990 E. Mission | Fallbrook | SD | 92028 | Manhole | 1 | Blockage | Stick and mud in manhole. | Flushed and recovered paper and ground cover. Replaced ground cover of surrounding area and posted sign. | Y | Y | Ostrich Creek | San Luis Rey River | NA | Y | N | Y | 3 | Picked up a yard of ground cover for replacement at spill location. Spill ran along side of road and into storm drain to Ostrich Creek.
978020 | (619) 467-2952 | 1997-12-09 14:30 | Joel Holt | 7607235640 | Fallbrook Public Utility District | 1997-12-09 04:00 | 1997-12-09 06:00 | 846 | 0 | 1425 S. Alturas | Fallbrook | SD | 92028 | Lift Station #5 | 1 | Pump Station Failure | Pump control system failed. | Reset pump controler. | Y | Y | Fallbrook Creek | Lake O'Neil | NA | Y | N | N | NA
978021 |  |  | Joel Holt | 7607235640 | Fallbrook Public Utility District | 1997-10-21 08:50 | 1997-10-21 11:00 | 240 | 200 | Beech Street | Fallbrook | SD | 92028 | 8" Mainline | 1 | Roots | Roots in mainline. | Dug up line, replaced line and installed 6" cleanout. Removed contaminated soil (approx. 1 yd.). | N | N | NA | NA | Percolated into ground. | N | N | N | NA | Sequential Tracking # does not correspond to dating sequence, due to the fact that this report was not forwarded to appropriate personnel in proper sequence.
978022 |  |  | Joel Holt | 7607235640 | Fallbrook Public Utility District | 1997-12-09 12:00 | 1997-12-09 12:30 | 15 | 10 | 445 Linden Lane | Fallbrook | SD | 92028 | Cleanout | 1 | Other | Paper towels obstruction in off-set joint of mainline. | Cleaned up site and flushed mainline to open blockage. | N | N | NA | NA | Percolated into ground around cleanout. | N | N | N | NA
978023 |  |  | Joel Holt | 7607235640 | Fallbrook Public Utility District | 1997-12-17 18:35 | 1997-12-17 19:00 | 15 | 0 | 232 E. Kalmia | Fallbrook | SD | 92028 | Cleanout | 1 | Blockage | Unknown blockage - possibly roots or grease. | Ran cutter through 4" cleanout and flushed easement main line. | N | N | NA | NA | Dried up along cement driveway and in Kalmia Street. | N | N | N | NA
978026 | SWRCB | 1998-01-07 14:45 | Joel Holt | 7607265640 | Fallbrook Public Utility District | 12/24/97 *a.m. | 1998-01-06 15:30 | 5600 | 500 | 433 Fallbrook Street | Fallbrook | SD | 92028 | Lateral | 1 | Line Break | Contractor broke lateral accidentally. They were not aware of it. FPUD discovered sewage in the downstream storm water system. | Repaired line, vacuumed wastewater collected, covered with 2 inches of soil. | Y | Y | Fallbrook Creek | Lake O'Neil | NA | Y | N | Y | 3 | County Health Representatives Kathy Stone and Steven Durham assessed the site. Removed 1/2 yd. of soil that was contaminated and covered spill with 2 inches of soil. FPUD sand bagged creek and recovered as much as possible.
978027 |  |  | Joel Holt | 7607235640 | Fallbrook Public Utility District | 1997-12-11 11:00 | 1997-12-11 11:05 | 40 | 0 | 1425 S. Alturas | Fallbrook | SD | 92028 | Sludge Bed | 1 | Blockage | While cleaning up sludge spill, catch basin overflowed. While staff was hosing down and cleaning up. |  | N | * | NA | NA | * Spill went partially into Plant contained storm drain (returned to headworks) & remainder percolated into soil on Naval Weapons Station Property in an isolated area. | N | N | N | NA | Sequential Tracking # does not correspond to dating sequence, due to the fact that this report was not forwarded to appropriate personnel in proper sequence.
97003 | N/A | N/A | N/A |  | City of Poway | 11/27/97 - 0930 | 11/27/97 - 0950 | 45 | 15 | 13441 Sagewood Drive | Poway | San Diego | 92064 | Collection System | 1 | Partial main blockage | 0900 - Resident called water treatment plant to report sewer bubbling out of clean-out. Water Utilities crews called in. Cleared partial blockage in the 8" sewer main caused by grease build up. Used Vactor to vacuum 15 gallons of spill; disinfected and | Video inspection scheduled to determine maintenance needs; placed in cardfile. | No | No | N/A | N/A | Disinfected and spread topsoil | No | No | No | N/A | None
978001 | FAX | 11/21/97 @ 18:45 | Cheryl Neal | 619-423-8311 | City of Imperial Beach | 11/21/97 @ 15:33 | 11/21/97 @ 16:00 | <50 | 0 | 542 Elm Avenue | Imperial Beach | SD | 91932 | MH #85 | 0 | Blockage in main | Blockage in main line. | Cleaned up w/vactor but <50 gallons went into stormdrain. Check main line regularly. | Y | Y | Tijuana Estuary | N/A | Tijuana Estuary | Y | N | N | N/A
978008 | FAX | 10-6-97, 1402 | D. WOODWARD | 619-522-7380 | CITY OF CORONADO | 10-6-97, 1110 | 10-6-97, 1125 | 350 GAL | 80 GAL | 200 BLOCK A/B ALLEY | CORONADO | SD | 92118 | SEWER LINE | 0 | ROOTS | ROOTS AND DEBRIS IN SEWER LINE | CLEARED WITH VACTOR | N | Y | SAN DIEGO BAY | PACIFIC OCEAN | SEWER LINE | Y | N | Y | 3
978009 | N/A | N/A | N/A | N/A | N/A | 10-6-97, 1200 | 10-6-97, 1315 | 50 GAL | 50 GAL | 203 SIXTH STREET | CORONADO | SD | 92118 | SEWER LINE | 0 | FOREIGN OBJECT | ROOTS AND OBJECT IN SEWER LINE | CLEARED WITH RODDER | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978010 | N/A | N/A | N/A | N/A | N/A | 10-9-97, 1015 | 10-9-97, 1130 | 25 GAL | 25 GAL | 100 BLOCK D ALLEY | CORONADO | SD | 92118 | SEWER LINE | 2 | GREASE | GREASE IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978011 | N/A | N/A | N/A | N/A | N/A | 10-14-97, 1345 | 10-14-97, 1415 | 25 GAL | 25 GAL | 945 I AVENUE | CORONADO | SD | 92118 | SEWER LINE | 1 | ROOTS | ROOTS IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978012 | N/A | N/A | N/A | N/A | N/A | 10-17-97, 911 | 10-17-97, 1100 | 25 GAL | 25 GAL | 600 BLOCK J ALLEY | CORONADO | SD | 92118 | SEWER LINE | 0 | ROOTS | ROOTS IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978013 | N/A | N/A | N/A | N/A | N/A | 10-21-97, 1400 | 10-21-97, 1500 | 50 GAL | 50 GAL | 500 BLOCK B/C ALLEY | CORONADO | SD | 92118 | SEWER LINE | 1 | GREASE | GREASE IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978014 | N/A | N/A | N/A | N/A | N/A | 10-27-97, 2030 | 10-27-97, 2130 | 25 GAL | 25 GAL | 750 COUNTRY CLUB LANE | CORONADO | SD | 92118 | SEWER LINE | 0 | DEBRIS | FOREIGN DEBRIS IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978015 | N/A | N/A | N/A | N/A | N/A | 10-29-97, 1750 | 10-29-97, 2000 | 80 GAL | 80 GAL | 600 BLOCK E/F ALLEY | CORONADO | SD | 92118 | SEWER LINE | 0 | SAND | SAND IN SEWER | CLEARED WITH RODDER | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978016 | N/A | N/A | N/A | N/A | N/A | 10-30-97, 1030 | 10-30-97, 1430 | 25 GAL | 25 GAL | 205 SIXTH STREET | CORONADO | SD | 92118 | SEWER LINE | 1 | ROOTS | FOREIGN ROOTS IN SEWER | CLEARED WITH RODDER | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978017 | N/A | N/A | N/A | N/A | N/A | 11-1-97, 1015 | 11-1-97, 1145 | 50 GAL | 50 GAL | FOURTH, BET H/I | CORONADO | SD | 92118 | SEWER LINE | 3 | GREASE | GREASE IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978018 | N/A | N/A | N/A | N/A | N/A | 11-17-97, 945 | 11-17-97,1130 | 50 GAL | 50 GAL | 820 ADELLA AVENUE | CORONADO | SD | 92118 | SEWER LINE | 1 | ROOTS | ROOTS IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978019 | N/A | N/A | N/A | N/A | N/A | 11-27-97, 1015 | 11-27-97, 1130 | 25 GAL | 25 GAL | 200 BLOCK A/B ALLEY | CORONADO | SD | 92118 | SEWER LINE | 2 | ROOTS | ROOTS IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978020 | N/A | N/A | N/A | N/A | N/A | 11-27-97, 1402 | 11-27-97, 1515 | 25 GAL | 25 GAL | 500 BLOCK G/H ALLEY | CORONADO | SD | 92118 | SEWER LINE | 1 | ROOTS | ROOTS AND GREASE IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978021 | N/A | N/A | N/A | N/A | N/A | 12-31-97, 2050 | 12-31-97, 2145 | 25 GAL | 25 GAL | 417 EIGHTH STREET | CORONADO | SD | 92118 | SEWER LINE | 0 | FOREIGN OBJECT | FOREIGN OBJECTS (PLASTIC MATERIAL) IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
966434 | Fax 571-6972 | 12/17/97 13:15 | Parker | 6544160 | City of San Diego | 12/07/97 00:00 | 12/14/97 18:00 | 60911 | 5950 | 3055 Erie St./canyon | San Diego | SD | 92117 | 8" VC | 3 | Grvty Mn Brk | Line break | Built berm, diverted flow back into broken pipe, ref to constr crew | Y | Y | Canyon floor |  | Mission Bay | Y | Y | Y
953700 | Fax 571-6972 | 10/16/97 15:15 | Finch | 6544160 | City of San Diego | 10/15/97 08:20 | 10/16/97 10:50 | 31800 | 20300 | 3617 Curlew St. | San Diego | SD | 92103 | 6" CP | 1 | Roots | Root Ball | Rodded/cleaned main, ref. for TV | Y | Y | Storm Drain | San Diego Bay |  | Y | Y | Y | Unknown
968260 | Fax 571-6972 | 12/26/97 16:41 | Hernandez | 6544160 | City of San Diego | 12/22/97 10:30 | 12/26/97 12:15 | 29325 | 100 | 3066 Elm St./from private cleanout | San Diego | SD | 92102 | 8" VC clean out | 1 | Roots | Roots | Hand rodded to remove roots from main causing overflow from c/o | Y | Y | 33rd and E St | San Diego Bay/Pacific Ocean |  | Y | Y | Y | Unknown
951096 | Fax 571-6972 | 10/02/97 04:10 | McPherson | 6544160 | City of San Diego | 09/30/97 13:12 | 10/02/97 20:00 | 25200 | 0 | Bessemer St. & Scott St. | San Diego | SD |  | 18" VC Sewer Main | 1 | Grvty Mn Break | Hole in 18" VC Sewer Pipe | Repaired 18" vc main | Y | N | San Diego Bay | Pacific Ocean |  | Y | Y | Y
967514 | Fax 571-6972 | 12/29/97 14:00 | McPherson | 6544160 | City of San Diego | 12/19/97 15:16 | 12/21/97 14:00 | 11662 | 3000 | 4409 New Hampshire St. | San Diego | SD |  | 6" CP | 1 | Grvty Mn Brk | Line break | Made temporary main repairs, ref. for contractor for perm. rprs. | N | N | Soaked into canyon | Hoffman Canyon |  | Y | Y | N
957754 | Fax 571-6972 | 11/06/97 11:00 | Davis | 6544160 | City of San Diego | 11/05/97 18:55 | 11/05/97 19:55 | 6000 | 1500 | 10674 Rancho Carmel Dr. | San Diego | SD | 92128 | 10" PVC | 1 | Roots | Rocks and construction debris | Rodded to relieve stop | Y | Y | Chicarita Creek | Los Penasquitos Creek | Canyon | Y | Y | Y
959555 | Fax 571-6972 | 11/16/97 | McPherson | 6544160 | City of San Diego | 11/16/97 21:31 | 11/16/97 23:45 | 4690 | 0 | Renaissance Av. & Towne Centre Dr. | San Diego | SD |  | 8" VC | 1 | Grease | Grease | Flushed 8" vc main | Y | Y | Storm drain |  | Rose Canyon/Dried in dirt | Y | Y | N
967589 | Fax 571-6972 | 12/21/97 18:38 | Branco | 6544160 | City of San Diego | 12/19/97 20:58 | 12/20/97 11:15 | 4285 | 3525 | Albatross St. & Brant St. | San Diego | SD | 92103 | 8" VC | 1 | Other | Unknown | Relieved unknown blockage, recovered 3,525 gals. of overflow | Y | N | Canyon floor | San Diego Bay/Pacific Ocean |  | Y | N/A | N
958286 | Fax 571-6972 | 11/09/97 21:24 | Branco | 6544160 | City of San Diego | 11/09/97 14:57 | 11/09/97 18:26 | 4180 | 500 | Carmel Valley Rd. w. of I-5/on hillside | San Diego | SD | 92014 | 8" VC | 1 | Roots | Roots | Machine rodded to relieve stop | Y | Y | Storm drain | Soledad Creek/Pacific Ocean |  | Y | Y | N
963844 | Fax 571-6972 | 12/05/97 13:00 | Richardson | 6544160 | City of San Diego | 12/03/97 11:35 | 12/03/97 12:50 | 3750 | 3000 | 2181 Avnda. del Mexico | San Diego | SD | 91911 | 12" VC | 1 | Grease | Grease | Flushed 12" vc main to relieve stop | Y | N | Storm channel | San Diego Bay | Storm channel | Y | Y | Y | 3
955539 | Fax 571-6972 | 10/30/97 05:15 | Whelan | 6544160 | City of San Diego | 10/27/97 09:16 | 10/29/96 16:30 | 3315 | 0 | 3606 Pennsylvania Av. | San Diego | SD | 92103 | 8" VC | 1 | Roots | Roots | Removed stop, ref. for re-evaluation of cleaning freq. | N | N | San Diego Bay | Pacific Ocean | Ground in canyon | Y | Y | N
957073 | Fax 571-6972 | 11/03/97 11:46 | Kelly | 6544160 | City of San Diego | 11/02/97 22:12 | 11/02/97 23:20 | 2720 | 0 | 4356 30th St./alley | San Diego | SD | 92116 | 10" VC | 1 | Grease | Grease | Flushed 10" vc main to relieve stop | N | Y | Storm drain | San Diego Bay | Soaked in canyon | Y | Y | N
951690 | Fax 571-6972 | 10/05/97 16:18 | Branco | 6544160 | City of San Diego | 10/05/97 13:38 | 10/05/97 14:03 | 2500 | 0 | I-163 south of Robinson Av. exit | San Diego | SD | 92103 | 12" VC | 1 | Roots | Roots | Flushed to relieve root stop | Y | Y | Storm Drain | Drainage Channel |  | Y | Y | N
953596 | Fax 571-6972 | 10/14/97 23:55 | Whelan | 6544160 | City of San Diego | 10/14/97 16:09 | 10/14/97 18:16 | 1905 | 1200 | 1333 Hotel Circle S. | San Diego | SD | 92108 | 12" VC Main | 1 | Roots | Roots | Vacuumed overflow, hand rodded main to relieve stop | Y | Y | Storm Drain |  | Soaked into ground | Y | Y | N
953167 | Fax 571-6972 | 10/13/97 12:30 | Davis | 6544160 | City of San Diego | 10/13/97 09:40 | 10/13/97 11:00 | 1600 | 900 | 12760 Rancho Penasquitos Bl. | San Diego | SD | 92129 | 12" VC | 1 | Grease | Grease | Cleaned extensively to remove grease | Y | Y | None | None | Canyon | Y |  | N
965108 | Fax 571-6972 | 12/09/97 11:44 | Burton | 6544160 | City of San Diego | 12/09/97 07:07 | 12/09/97 08:07 | 1500 | 0 | 49th St. & Logan Av. | San Diego | SD | 92114 | 10" VC | 1 | Grease | Grease | Machine rodded 10" vc main | Y | Y | Storm drain | San Diego Bay | Dried up in canyon | Y | Y | N
963088 | Fax 571-6972 | 11/30/97 11:57 | Branco | 6544160 | City of San Diego | 11/29/97 09:37 | 11/30/97 10:25 | 1488 | 0 | 4311 Hortensia St. | San Diego | SD | 92103 | 6" CP | 1 | Roots | Roots | Machine rodded to clear stop; ref for possible MC site | Y | Y | Storm drain | San Diego Bay/Pacific Ocean |  | Y | Y | N
960214 | Fax 571-6972 | 11/09/97 00:02 | Whelan | 6544160 | City of San Diego | 11/08/97 15:35 | 11/08/97 17:55 | 1400 | 1000 | 347 S. Royal Oak Dr. | San Diego | SD | 92114 | 8" VC | 1 | Grease | Grease | Rodded main to relieve stop | Y | Y | Storm drain | Storm drain | Storm drain | Y | N | N
960881 | Fax 571-6972 | 11/20/97 11:40 | Finch | 6544160 | City of San Diego | 11/20/97 06:25 | 11/20/97 09:05 | 1050 | 0 | 3174 Falcon St. | San Diego | SD | 92101 | 6" CP | 1 | Roots | Roots | Removed root stoppage, ref for televising | Y | Y | Storm drain | San Diego Bay |  | Y | Y | Y | 1
967053 | Fax 571-6972 | 12/17/97 15:30 | Parker | 6544160 | City of San Diego | 12/17/97 07:13 | 12/17/97 10:42 | 1050 | 0 | 3078 Mercer Ln. | San Diego | SD | 92122 | 8" VC | 1 | Debris | Debris | Rodded to relieve stop, ref. for poss. PM site | Y | Y | Curb/storm drain/San Clemente canyon/interc 1 | Mission Bay/Pacific Ocean |  | Y | Y | N
968824 | Fax 571-6972 | 12/31/97 12:00 | Whelan | 6544160 | City of San Diego | 12/30/97 17:00 | 12/31/97 09:15 | 975 | 0 | Cedar St. & Gregory St./canyon | San Diego | SD | 92102 | 6" CP easement main | 1 | Roots | Roots | Hand rodded, ref for TV to determine extent of root blockage | N | N | Soaked into canyon |  |  | Y | N | N
963237 | Fax 571-6972 | 12/01/97 15:40 | Parker | 6544160 | City of San Diego | 12/01/97 13:50 | 12/01/97 15:10 | 800 | 200 | 4258 Robbins St. | San Diego | SD | 92122 | 8" VC | 1 | Roots | Roots | Cleared roots on 8" vc main | Y | Y | Rose Canyon Creek/Interc 1/M.Bay |  |  | Y | N/A | N
967474 | Fax 571-6972 | 12/20/97 17:29 | Branco | 6544160 | City of San Diego | 12/19/97 11:32 | 12/20/97 10:30 | 689 | 0 | 6394 Elmhurst Dr. | San Diego | SD | 92120 | 8" VC | 1 | Roots | Roots | Hand rodded easement main to remove roots | Y | Y | Storm drain | San Diego River/Pacific Ocean |  | Y | N/A | N
954415 | Fax 571-6972 | 10/18/97 13:55 | Branco | 6544160 | City of San Diego | 10/18/97 10:28 | 10/18/97 11:30 | 620 | 0 | 3705 Albatross St./canyon | San Diego | SD | 92103 | 6" CP | 1 | Roots | Roots | Machine rodded to relieve stop | Y | N | Soaked into Canyon Floor | SD Bay/Pacific Ocean |  | Y | N/A | N
951223 | Fax 571-6972 | 10/02/97 15:30 | Davis | 6544160 | City of San Diego | 10/02/97 12:12 | 10/02/97 13:15 | 600 | 260 | 7751 Mission Gorge Rd./drainage ditch n. | San Diego | SD | 92120 | 8" VC Sewer Main | 1 | Roots | Tree Roots | Rodded 8" vc main | N | Y | Storm Drain North of Mission Gorge | San Diego River | Storm Drain and Drainage Ditch | Y | N/A | N
957874 | Fax 571-6972 | 11/06/97 13:55 | Bauer | 6544160 | City of San Diego | 11/06/97 09:46 | 11/06/97 11:50 | 580 | 0 | 7564 Rainswept Ln. | San Diego | SD | 92119 | 8" PVC | 1 | Roots | Roots | Flushed/cleaned main with root cutter | N | N | N/A | Storm drain/SD River | Ground around manhole | Y | N/A | N
958251 | Fax 571-6972 | 11/08/97 16:27 | Branco | 6544160 | City of San Diego | 11/08/97 11:12 | 11/08/97 12:10 | 580 | 0 | 2330 F St. | San Diego | SD | 92102 | 8" PVC | 1 | Construction | Collapsed pipe | Rodded to clear line, ref for repairs | Y | Y | Storm drain | SD Bay/Pacific Ocean |  | Y | N/A | N
965699 | Fax 571-6972 | 12/11/97 12:20 | Finch | 6544160 | City of San Diego | 12/11/97 08:45 | 12/11/97 09:40 | 550 | 525 | Chatsworth Bl. & James St. | San Diego | SD | 92106 | 8" CP | 1 | Roots | Roots | Relieved stop, placed main on PM schedule | Y | Y | Storm drain | San Diego Bay | Dried in storm drain | Y | N/A | N
962335 | Fax 571-6972 | 11/26/97 07:30 | Parker | 6544160 | City of San Diego | 11/25/97 19:11 | 11/25/97 21:55 | 492 | 300 | 3124 Carnegie Ct. | San Diego | SD | 92122 | 8" VC | 2 | Rocks | Roots | Removed roots from MH, ref for consideration as MC site | Y | Y | Storm drain | San Clemente Canyon/Rose Canyon/Mission Bay |  | Y | N | N
965109 | Fax 571-6972 | 12/09/97 11:30 | Parker | 6544160 | City of San Diego | 12/09/97 07:00 | 12/09/97 11:10 | 450 | 300 | Playa del Sur & Neptune Pl. | San Diego | SD | 92037 | 4" hi-line | 1 | Other | Break in hi-line | Contained majority of overflow, contractor switched to new frc main | Y | Y | Storm drain | Pacific Ocean |  | Y | N/A | Y | Unknown
968516 | Fax 571-6972 | 12/29/97 12:30 | Parker | 6544160 | City of San Diego | 12/29/97 10:35 | 12/29/97 11:06 | 395 | 0 | 5972 Kantor St. | San Diego | SD | 92122 | 8" VC | 1 | Roots | Roots | Rodded 8" vc main to relieve stop | Y | Y | San Clemente Canyon/Highway 52 | Creek/Mission Bay/Pacific Ocean |  | Y | N/A | N
956226 | Fax 571-6972 | 10/29/97 15:30 | Parker | 6544160 | City of San Diego | 10/29/97 10:47 | 10/29/97 13:47 | 360 | 0 | 5895 Camto. Empressa | San Diego | SD | 92109 | 8" VC | 1 | Grease | Grease | Relieved stop, consider for PM site | Y | Y | Storm drain | Pacific Ocean |  | Y | N | N
957066 | Fax 571-6972 | 11/02/97 18:21 | Branco | 6544160 | City of San Diego | 11/02/97 12:46 | 11/02/97 13:55 | 345 | 0 | 7422 Conestoga Wy. | San Diego | SD | 92120 | 12" VC | 1 | Roots | Roots | Machine rodded 12" vc main | Y | Y | Storm drain | SD River/Pacific Ocean |  | Y | N/A | N
962653 | Fax 571-6972 | 11/27/97 20:15 | Finch | 6544160 | City of San Diego | 11/27/97 15:02 | 11/27/97 18:32 | 315 | 0 | 8587 Parkbrook St. | San Diego | SD | 92114 | 8" VC | 1 | Roots | Roots | Removed stop, ref to area sprvsr for re-clean, televising | N | N | Curb | San Diego Bay | 8587 & 8589 Parkbrook/yard | Y | N/A | N
967646 | Fax 571-6972 | 01/05/98 09:30 | Richardson | 6544160 | City of San Diego | 12/22/97 08:10 | 12/22/97 09:12 | 310 | 0 | 5474 Reservoir Dr. | San Diego | SD | 92120 | 10" VC | 1 | Roots | Roots | Rodded main to relieve stop | Y | N | Storm channel | Alvarado Creek | Pacific Ocean |  | N/A | N
963459 | Fax 571-6972 | 12/03/97 10:45 | Davis | 6544160 | City of San Diego | 12/02/97 09:05 | 12/02/97 09:55 | 250 | 0 | 18535 Bernardo Trails Dr. | San Diego | SD |  | Storm Culvert/canyon | 1 | Roots | Roots | Machine rodded main | Y | N | Canyon |  | Canyon | Y | N | N
955318 | Fax 571-6972 | 10/24/97 06:25 | Whelan | 6544160 | City of San Diego | 10/23/97 21:29 | 10/23/97 22:10 | 246 | 0 | 5227 University Av. | San Diego | SD | 92105 | 8" VC | 1 | Grease | Grease | Rodded 8" vc main to relieve stop | Y | Y | Storm Drain | Storm Drain system |  | Y | N | N
968496 | Fax 571-6972 | 12/28/97 21:22 | Branco | 6544160 | City of San Diego | 12/28/97 15:45 | 12/28/97 19:40 | 235 | 0 | 242 Prospect St. | San Diego | SD | 92037 | 6" VC | 1 | Other | Faulty pipe | Faulty slipline pipe connection pried open | Y | Y | Pacific Ocean |  | Pacific Ocean | Y | N/A | Y
952126 | Fax 571-6972 | 10/07/97 19:10 | Finch | 6544160 | City of San Diego | 10/07/97 09:24 | 10/07/97 10:34 | 210 | 0 | 3019 Olive St./canyon | San Diego | SD | 92104 | 8" VC Sewer Main | 1 | Rocks | Rocks in Main | Machine rodded 8" vc main | Y | N | Canyon Surface/Soaked into Ground |  | Soaked into the ground |  | N/A | N
968481 | Fax 571-6972 | 12/28/97 15:36 | Branco | 6544160 | City of San Diego | 12/28/97 10:52 | 12/28/97 12:00 | 204 | 100 | 4920 Imperial Av. | San Diego | SD | 92102 | 6" VC | 1 | Grease | Grease | Flushed main | N | N | Canyon |  | Canyon | Y | N/A | N
968808 | Fax 571-6972 | 12/31/97 06:15 | Whelan | 6544160 | City of San Diego | 12/30/97 16:18 | 12/30/97 16:18 | 190 | 0 | 2255 Camino del Rio So. | San Diego | SD | 92108 | 8" VC sewer main | 1 | Roots | Roots | Rodded 8" vc main to relieve stop | Y | Y | Soaked into ground |  |  | Y | N | N
958333 | Fax 571-6972 | 11/10/97 14:10 | Hoyer | 6544160 | City of San Diego | 11/10/97 11:18 | 11/10/97 11:50 | 184 | 0 | Hillside Dr. & Torrey Pines Rd. | San Diego | SD | 92037 | 8" CI | 1 | Roots | Roots | Rodded main to remove roots | Y | Y | Storm drain | Pacific Ocean |  | Y | N/A | N
969415 | Fax 571-6972 | 12/22/97 11:20 | Galinzoga | 6544160 | City of San Diego | 12/22/97 08:50 | 12/22/97 09:15 | 175 | 0 | 18695 Pomerado Rd.** | San Diego | SD |  | Bldg # 1329 | 1 | Debris | Rocks & debris in suction line | Removed debris/rocks from suction line to pumps in PS #76 | Y | N | N/A | N/A | Station grounds | Y | N/A | Y
963288 | Fax 571-6972 | 12/01/97 20:47 | Wilder | 6544160 | City of San Diego | 12/01/97 15:32 | 12/01/97 16:30 | 174 | 100 | Copley Av. & Oregon St. | San Diego | SD | 92116 | 6" VC | 1 | Grvty Mn Brk | Line break | Repair 6" vc main | Y | Y | Storm drain | Canyon |  | Y | N/A | N
953151 | Fax 571-6972 | 10/12/97 15:52 | Branco | 6544160 | City of San Diego | 10/12/97 13:17 | 10/12/97 14:32 | 150 | 0 | Paradise Valley Rd. & Woodman St. | San Diego | SD | 92114 | 8" PVC | 1 | Grease | Grease | Flushed to relieve grease blockage | Y | Y | Storm Drain | Sweetwater River/SD Bay |  | Y | N/A | N
963985 | Fax 571-6972 | 12/04/97 05:00 | Whelan | 6544160 | City of San Diego | 12/03/97 17:06 | 12/03/97 19:36 | 150 | 10 | 6401 Linda Vista Rd. | San Diego | SD | 92111 | 8" VC sewer main | 1 | Grease | Grease | Rodded 8" vc main | Y | Y | Storm drain |  |  | Y | N | N/A
961705 | Fax 571-6972 | 11/22/97 17:13 | Branco | 6544160 | City of San Diego | 11/22/97 10:41 | 11/22/97 15:27 | 143 | 0 | 47th St. & Quince St. | San Diego | SD | 92105 | 8" PVC | 1 | Roots | Roots | Machine rodded 8" pvc main, ref for MC site | Y | Y | Storm drain | Chollas Creek/San Diego Bay |  | Y | N/A | N
963161 | Fax 571-6972 | 12/01/97 12:15 | Finch | 6544160 | City of San Diego | 12/01/97 09:25 | 12/01/97 10:10 | 135 | 0 | 2748 30th St./alley west | San Diego | SD | 92104 | 6" VC | 1 | Grease | Grease | Flushed 6" vc main | Y | Y | Storm drain | San Diego Bay | Dried & soaked in ground | Y | N/A | N
968185 | Fax 571-6972 | 12/25/97 02:57 | Whelan | 6544160 | City of San Diego | 12/24/97 14:16 | 12/24/97 16:24 | 128 | 0 | 7068 Everglades Av. | San Diego | SD | 92119 | 8" VC sewer main | 1 | Roots | Roots | Rodded main to relieve stop | N | N | Soaked in ground in backyard |  | Soaked into ground in backyard | Y | N | N
954438 | Fax 571-6972 | 10/19/97 13:04 | Branco | 6544160 | City of San Diego | 10/19/97 09:51 | 10/19/97 10:15 | 120 | 0 | 1735 Midvale Dr. | San Diego | SD | 92105 | 8" VC | 1 | Roots | Roots | Machine rodded to relieve root stop | Y | Y | Storm Drain | Chollas Creek/SD Bay |  | Y | N/A | N
951700 | Fax 571-6972 | 10/05/97 22:29 | Branco | 6544160 | City of San Diego | 10/05/97 20:49 | 10/05/97 21:45 | 112 | 0 | 11381 Turtleback Ln. | San Diego | SD | 92127 | 8" PVC | 1 | Grease | Grease | Flushed to relieve stop, ref. for PM | Y | Y | Storm Drain | Lusardi Creek/SD River |  | Y | N/A | N
951051 | Fax 571-6972 | 10/01/97 14:44 | Graham | 6544160 | City of San Diego | 10/01/97 09:15 | 10/01/97 09:25 | 100 | 50 | 2799 Carleton St. | San Diego | SD |  | MH # 71 | 1 | Grease | Grease Blockage in 27" Main | Relieved grease stop, vacuumed sewage from street, flushed lines | Y | Y | Storm Drain/SD harbor |  |  | Y | N/A | Y
968918 | Fax 571-6972 | 12/31/97 13:00 | Richardson | 6544160 | City of San Diego | 12/31/97 10:10 | 12/31/97 11:00 | 100 | 100 | 3450 College Av. | San Diego | SD | 92115 | 8" VC | 1 | Grease | Grease | Rodded 8" vc main, recovered total volume of spill | N | N | Service Tunnel under the mall |  | Sewer recovered | Y | N/A | N
955643 | Fax 571-6972 | 10/28/97 08:40 | Finch | 6544160 | City of San Diego | 10/27/97 15:58 | 10/27/97 16:45 | 94 | 0 | Newton Av. & S. 16th St. | San Diego | SD | 92113 | 6" CP Sewer Main | 1 | Grease | Grease | Hand rodded 29' of 6" cp main | Y | Y | Storm Drain | San Diego Bay | Storm drain system | N | N/A | N
956452 | Fax 571-6972 | 10/30/97 15:20 | Finch | 6544160 | City of San Diego | 10/30/97 09:59 | 10/30/97 12:59 | 90 | 0 | 2600 Golf Course Dr. (hole #4) | San Diego | SD | 92102 | 6" CP | 1 | Grvty Mn Brk | Break in line | Relieved root blockage in broken main, ref. to constr. crew | N | N |  | San Diego Bay | Settle in canyon area | Y | N/A | N
955900 | Fax 571-6972 | 10/28/97 12:30 | Richardson | 6544160 | City of San Diego | 10/28/97 09:32 | 10/28/97 10:16 | 88 | 20 | 4536 Craigie St | San Diego | SD | 92102 | Clean out | 1 | Grease | Grease | Flushed to relieve stop | Y | N | 4536 Craigie St - backyard |  | Ground and street | Y | N/A | N
958090 | Fax 571-6972 | 11/07/97 15:00 | Finch | 6544160 | City of San Diego | 11/07/97 11:45 | 11/07/97 12:30 | 80 | 0 | 21st St. & F St. | San Diego | SD | 92102 | 6" VC | 1 | Construction | Bricks, rocks, concrete | Removed debris, put area on MC site | Y | Y | Storm drain | Dried in storm drain | dried in storm drain | Y | N/A | N
968519 | Fax 571-6972 | 12/29/97 14:45 | Hernandez | 6544160 | City of San Diego | 12/29/97 10:08 | 12/29/97 11:35 | 80 | 0 | Brighton Av. & Long Branch Av./alley | San Diego | SD |  | 6" VC | 1 | Roots | Roots | Relieved stop on 6" vc main | N: Y; NONE: Surface street/curb; NONE: Pacific Ocean; Y: Y; N: N
956158 | Fax 571-6972 | 10/29/97 06:25 | Whelan | 6544160 | City of San Diego | 10/28/97 15:00 | 10/28/97 20:00 | 75 | 0 | 5959 Cornerstone Ct. | San Diego | SD | 92121 | 10" PVC sewer main | 1 | Roots | Roots | Removed roots, rodded main | Y | Y | Storm drain in parking lot |  | Dried up in storm drain | Y | N | N
954887 | Fax 571-6972 | 10/22/97 12:10 | Finch | 6544160 | City of San Diego | 10/22/97 07:11 | 10/22/97 08:50 | 74 | 0 | 3300 Redwood St. | San Diego | SD | 92104 | 6" CP | 1 | Roots | Roots and Debris | Cleaned main, ref. to TV crew for poss. group job referral | Y | N | Dried along curb and street | San Diego Bay |  | Y | N/A | N
966385 | Fax 571-6972 | 12/13/97 14:18 | Branco | 6544160 | City of San Diego | 12/13/97 10:32 | 12/13/97 11:00 | 56 | 50 | 5800 Santa Fe St. | San Diego | SD | 92109 | 8" VC | 1 | Grease | Grease, rocks and dirt | Flushed line to relieve stop | N | Y | Storm drain | N/A | Interceptor I | Y | N/A | N
967944 | Fax 571-6972 | 12/23/97 06:45 | Whelan | 6544160 | City of San Diego | 12/23/97 24:30 | 12/23/97 24:30 | 50 | 0 | 4422 Kansas St. | San Diego | SD | 92104 | 8" VC | 1 | Other | Vactor surcharge | Surcharge from full drain cleaner subsided | Y | N | Dried up in street |  |  | Y | N | N
967533 | Fax 571-6972 | 12/19/97 19:59 | Branco | 6544160 | City of San Diego | 12/19/97 17:02 | 12/19/97 18:30 | 44 | 0 | 2545 G St. | San Diego | SD | 92102 | 6" CP | 1 | Grease | Grease | Flushed main to relieve stop | Y | Y | Storm drain | San Diego Bay/Pacific Ocean |  | Y | N/A | N
954284 | Fax 571-6972 | 10/17/97 13:08 | Finch | 6544160 | City of San Diego | 10/17/97 13:08 | 10/17/97 14:30 | 41 | 0 | 944 Crosby St. | San Diego | SD | 92113 | 6" VC | 1 | Grease | Heavy Grease | Removed stop, placed on PM schedule | Y | Y | Dried in Storm Drain | San Diego Bay |  | Y | N/A | N
956156 | Fax 571-6972 | 10/29/97 06:40 | Whelan | 6544160 | City of San Diego | 10/29/97 01:00 | 10/29/97 01:00 | 40 | 0 | 5511 Yerba Anita Dr. | San Diego | SD | 92115 | 8" VC sewer main | 1 | Roots | Roots | Surge from stoppage clearing overflowed briefly, receded | Y | N | 5511 Yerba Anita Dr |  | Dried up in street | Y | N | N
954461 | Fax 571-6972 | 10/20/97 14:15 | Richardson | 6544160 | City of San Diego | 10/20/97 11:30 | 10/20/97 12:00 | 30 | 0 | 1935 Leatherwood St. | San Diego | SD | 92154 | 8" PVC | 1 | Grease | Grease | Flushed main to relieve stop | Y | Y | At Curb | Storm Drain | Storm Drain System | Y | N/A | N
954416 | Fax 571-6972 | 10/18/97 13:47 | Branco | 6544160 | City of San Diego | 10/18/97 10:34 | 10/18/97 11:30 | 28 | 0 | Ingraham St. & La Cima St. | San Diego | SD | 92109 | 5" SL | 2 | Roots | Roots | Machine rodded to relieve stop | Y | N | Dried up at curb | Pacific Ocean |  | Y | N/A | N
952610 | Fax 571-6972 | 10/09/97 05:45 | Whelan | 6544160 | City of San Diego | 10/08/97 23:05 | 10/08/97 23:39 | 25 | 0 | 3511 Oliphant St. | San Diego | SD | 92106 | 6" CP | 1 | Other | Unknown | Unknown cause, self-clearing stop, main 10-34 upon arrival | Y | Y | Storm Drain |  | Storm Drain | Y | N/A | N
951361 | Fax 571-6972 | 10/03/97 06:32 | Whelan | 6544160 | City of San Diego | 10/02/97 21:58 | 10/02/97 23:31 | 23 | 0 | 907 Court Wy. | San Diego | SD | 92103 | 6" CP | 1 | Roots | Roots in Manhole | Hand rod/vacuum/machine rod 6" cp main | Y | Y | Canyon through Storm Drain | San Diego River | Soaked into ground in canyon | Y |  | N
957953 | Fax 571-6972 | 11/06/97 | West | 6544160 | City of San Diego | 11/06/97 14:15 | 11/06/97 15:00 | 23 |  | 989 Sunset Cliffs Bl.** | San Diego | SD |  |  | 1 | Surcharge | Main break | Discontinued bypass pumping into collapsed manhole | Y | N |  |  | Sand and dirt | Y | N | N
957136 | Fax 571-6972 | 11/03/97 10:45 | Richardson | 6544160 | City of San Diego | 11/03/97 09:30 | 11/03/97 09:50 | 20 | 0 | 5940 University Av. | San Diego | SD | 92115 | 6" VC | 1 | Roots | Roots and grease | Rodded to relieve stop | Y | N | Street | N/A | Dried in the street | Y | N/A | N
968920 | Fax 571-6972 | 12/31/97 13:00 | Richardson | 6544160 | City of San Diego | 12/31/97 09:15 | 12/31/97 09:35 | 20 | 20 | 893 Leppert St. | San Diego | SD | 92113 | 8" VC | 1 | Roots | Roots | Rodded 8" pvc main, recovered total volume of spill | Y | N | Street and curb |  | Dried up in the street | Y | N/A | N
978008 | N/A | N/A | N/A | N/A | PRIVATE | 10/2/97-3:15 P | 10/2/97-4:30 P | LESS THAN 1 | 0 | 3190 CANYON | CARLSBAD | SD | 92008 | CLEANOUT | 1 | UNKNOWN |  | RODDED LATERAL TO CLEAR STOPPAGE | N | N |  |  | CLEANOUT | N | N | N | N/A | DISINFECTED AREA
978009 | N/A | N/A | N/A | N/A | CARLSBAD MWD | 10/6/97-12:30 P | 10/6/97-2:00 P | 10 | 10 | 2410 BUENA VISTA CR | CARLSBAD | SD | 92008 | DEAD-END CLEANOUT | 1 | UNKNOWN |  | CLEARED SEWER MAIN WITH VACTOR. | N | N |  |  | STREET SURFACE | N | N | N | N/A | DISINFECTED AREA
978010 | N/A | N/A | N/A | N/A | PRIVATE | 10/13/97-5:35 P | 10/13/97-7:10 P | 3 TO 5 | 0 | 2598 JEFFERSON | CARLSBAD | SD | 92008 | CLEANOUT | 1 | UNKNOWN |  | RODDED LATERAL TO CLEAR STOPPAGE | N | N |  |  | CLEANOUT | N | N | N | N/A | DISINFECTED AREA
978011 | N/A | N/A | N/A | N/A | CARLSBAD MWD | 11/6/97-3:11 P | 11/6/97-4:15 P | 1 TO 5 | 0 | PIO PICO,N OF TAMARACK | CARLSBAD | SD | 92008 | MANHOLE | 1 | GREASE |  | CLEARED SEWER MAIN WITH VACTOR. | N | N |  |  | STREET SURFACE | N | N | N | N/A | DISINFECTED AREA
978012 | N/A | N/A | N/A | N/A | CARLSBAD MWD | 11/7/97-2:49 P | 11/7/97-4:15 P | 1 TO 5 | 0 | 260 NORMANDIE | CARLSBAD | SD | 92008 | CLEANOUT | 2 | GREASE |  | RODDED MAIN LINE TO CLEAR STOPPAGE. MAIN LINE TOO SMALL FOR VACTOR. | N | N |  |  | STREET SURFACE | N | N | N | N/A | DISINFECTED AREA
978013 | N/A | N/A | N/A | N/A | CARLSBAD MWD | 11/8/97-2:30 P | 11/8/97-3:00 P | 20 | 0 | 5192 CARLSBAD BLVD. | CARLSBAD | SD | 92008 | MANHOLE | 1 | ROOTS/PLASTIC BAGS |  | CLEARED SEWER MAIN WITH VACTOR. | N | N |  |  | STREET SURFACE | N | N | N | N/A | DISINFECTED AREA
978014 | KATHY STONE-FAX | 11/18/97-4:30 P | PAT GUEVARA | 438-2722 X132 | CARLSBAD MWD | 11/16/97-10:30 A | 11/16/97-1:00 P | 120 | 0 | 3183 JEFFERSON | CARLSBAD | SD | 92008 | CLEANOUT | 1 | UNKNOWN |  | CLEARED SEWER MAIN WITH VACTOR. FLAT AREA IN MAIN LINE. WILL SCHEDULE TO CLEAN THIS LINE EVERY 6 MONTHS. | N | N |  |  | INSIDE APT. UNITS AND WALKWAY IN FRONT OF APTS. | Y | N | N | N/A | DISINFECTED AREA
978015 | N/A | N/A | N/A | N/A | PRIVATE | 11/24/97-8:30 A | 11/24/97-10:30 A | 1 TO 5 | 0 | 1271 TAMARACK | CARLSBAD | SD | 92008 | CLEANOUT | 1 | UNKNOWN |  | RODDED LATERAL TO CLEAR STOPPAGE | N | N |  |  | CLEANOUT | N | N | N | N/A | DISINFECTED AREA
978016 | KATHY STONE-FAX | 12/2/97-? | PAT GUEVARA | 438-2722 X132 | CARLSBAD MWD | 11/28/97-9:45 A | 11/28/97-11:15 A | 50 | 40 | TYLER & PINE | CARLSBAD | SD | 92008 | CLEANOUT | 1 | POSSIBLY GREASE |  | CLEARED SEWER MAIN WITH VACTOR. | N | N |  |  | EMPTY LOT ON TYLER | Y | N | N | N/A | DISINFECTED AREA
978017 | N/A | N/A | N/A | N/A | PRIVATE | 12/6/97-1:30 P | 12/6/97-1:55 P | 20 | 15 | 4205 CLEARVIEW | CARLSBAD | SD | 92008 | BATHROOMS INSIDE HOUSE | 2 | ROOTS |  | CLEARED LATERAL WITH RODDING MACHINE | N | N |  |  | BATHROOMS IN HOUSE | N | N | N | N/A | CUSTOMER CLEANED UP INSIDE HOUSE.
978018 | N/A | N/A | N/A | N/A | PRIVATE | 12/13/97-5:55 P | 12/13/97-7:35 P | 1 TO 5 | 0 | 1123 CAMEO DEL SOL | CARLSBAD | SD | 92008 | CLEANOUT | 1 | ROOTS |  | CLEARED LATERAL WITH RODDING MACHINE | N | N |  |  | CLEANOUT | N | N | N | N/A | DISINFECTED AREA
97019 | N/A | N/A | N/A | N/A | CARLSBAD MWD | 12/23/97-1:15 P | 12/23/97-2:30 P | 5 TO 10 | 0 | 237 NORMANDIE | CARLSBAD | SD | 92008 | CLEANOUT | 3 | BROKEN CUTTER |  | CLEARED MAIN LINE W/RODDING MACHINE | N | N |  |  | STREET SURFACE | N | N | N | N/A | DISINFECTED AREA
987006 | QUARTERLY REPORT | 10-2-97; 14:30 | RICHARD ANDREWS | 6197553294 | CITY OF DEL MAR | 10-2-97; 10:15 | 10-2-97;13:45 | 840 | 0 | 1247 CAMINO DEL MAR | DEL MAR | SD | 92014 | CLEANOUT | 0 | GREASE |  | ADVISED OWNER TO HAVE LATERAL CLEAN SEMIANNUALLY | Y | Y | PACIFIC |  |  | Y | N | Y | 1 | NA
978007 | QUARTERLY REPORT | 11-17-97;16:02 | RICHARD ANDREWS | 6197553294 | CITY OF DEL MAR | 10-27-97:13:00 | 11-16-97; 13:00 | 6400 | 0 | 2900 CAMINO DEL MAR | DEL MAR | SD | 92014 | PUMP DISCHARGE | 0 | CONSTRUCTION |  | TOLD CONTRACTOR TO POTHOLE UTILITIES BEFORE BORING | Y | Y | SAN DIEGUITO RIVER | PACIFIC |  | Y | Y | N | N/A | NA
978005 | Greg Peters | 10-06-97 1030 | Ted Powell | 760-744-0460 | V.W.D. | 10-6-97 0810 | 10-6-97 0850 | 2000 | none | Discovery St. | San Marcos | S.D. | 92069 | S4C-Q15-M6 | 1 | grease | grease blockage in the 8" sewer line | we will include this on the trouble spot list | y | n | S.M. creek | Lake San Marcos | n/a | y | y | y | 5 | area posted as per health dept. no body contact in lake.
978006 | fax | 11-13-97 1400 | Cheryl Brandstrom | 760-744-0460 | V.W.D. | 11-10-97 1045 | 11-11-97 1230 | 1500000 | none | easment | Carlsbad | S.D. | 92009 | 24" outfall line | 3 | broken pipe | steel pipe was possibly crushed when installed | in process of replacing bad pipe | n | n | canyon | irrigation ponds | La Costa Resort | y | y | y | 14+ | spill was contained
978015 | VOICE MAIL | 10/04/97,1400 | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 10/04/97,0840 | 10/04/97,1230 | 9000 | 000 | 509 Parker (Stuart Mesa Housing) | CAMP PENDLETON | SD | 920555008 | unknown manhole | 1 | PUMP STATION FAILURE | BREAKER ON SEWAGE LIFT STATION PUMP TRIPPED. THIS CAUSED THE PUMP TO FAIL AND SEWAGE TO OVERFLOW FROM MANHOLE | REPAIRED ELECTRICAL SYSTEM AT LIFT STATION. WASTEWATER SHOP IS MONITORING LIFT STATION TO AVERT POSSIBLE SPILL. TWO WARNING SIGNS POSTED ALONG PARKER STREET. | Y | Y | SANTA MARGARITA RIVER | PACIFIC OCEAN |  | Y | Y | Y | 3 | SPILL FLOWED 60' FROM MANHOLE ACROSS STREET DOWN GUTTER INTO STORM DRAIN THEN 600' TO CANYON AND PERCOLATED INTO THE GROUND. POTENTIAL PUBLIC CONTACT IN STUART MESA HOUSING AREA.
978016 | ELECTRONIC QTLY RPT |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 10/07/97,1420 | 10/07/97,1500 | 25 | 3 | Wire Mountain elementary school | CAMP PENDLETON | SD | 920555008 | c/o | 1 | BLOCKAGE | blockage in lateral caused cleanout to backup | adviced school faculty to ensure students only put toilet paper into toilets. | Y | N | SANTA MARGARITA RIVER | PACIFIC OCEAN |  | N | NA | N | 0 | SPILL OCCURED IN FACULTY PARKING LOT. NOT IN PLAY AREA.
978017 | DAT QUACH VOICEMAIL | 11/18/97,1345 | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 11/18/97,0800 | 11/18/97,1545 | 10,400 | 7,000 | PIPE NEXT TO Twin Lakes. ALSO LIFT ST. 31220 | CAMP PENDLETON | SD | 920555008 | PIPE PRIOR TO STP 13. ALSO M/H AT LIFT ST. 31220. | 1 | CONSTRUCTION | Contractor backhoe punched hole in pipe. | Prevented additional spillage by turnING off WATER SUPPLY AND lift stations 31220 and 31227. PUMPER TRUCKS PUMPED OUT WET WELL AT LIFT STATION 31227. COLIFORM SAMPLING TAKEN AT S.M. RIVER AND BEACH | Y | N | Santa Margarita River | Pacific Ocean |  | Y | Y | N | 0 | 9,500 gallons spilled from hole in pipe, of which 7,000 gallons was recovered. THIS SPILL FLOWED INTO TWIN LAKES (OUTFALL TO SAN. MARG. RIVER). 900 gallons spilled from manhole at lift station 31220 AND FLOWED INTO NEWTON CANYON POND (NO
| SIRT (Attn: Gloria Fulton) | 1997-10-01 11:00 | James E. Smith | 714-448-4053 | Moulton Niguel Water | 1997-10-01 10:30 | 1997-10-01 10:32 | 100-200 | 100-200 | End of Alipaz | San Juan Capistrano | OR | 92675 | 3A Effluent Pipeline | 1 | Construction | Grading contractor for Pepper Tree Estates hit the buried 20" effluent pipeline that transports secondary effluent to the Chiquita Land outfall. The 3A plant was processing only recycled water, so the only water in the pipeline was residual effluent. | What water that escaped from the pipeline percolated into the ground. | N | N | N/A | NA | Ground | Y | N | N | N/A
| SIRT (Attn:Gloria Fulton) | 1997-10-03 16:45 | James E. Smith | 714-448-4053 | Moulton Niguel Water | 1997-10-03 11:00 | 1997-10-03 14:00 | 32000 | 0 | End of Alipaz | San Juan Capistrano | OR | 92675 | 3A Effluent Pipeline | 1 | Construction | Grading contractor for Pepper Tree Estates hit the effluent pipeline that transports secondary effluent to the Chiquita Land Outfall. The pipeline fracture was on the side of the pipe, causing a hole 3" wide X 6" long. | Effluent was contained on the site, however, the majority escaped to Trabuco Creek. | Y | N | Trabuco Creek | San Juan Creek | NA | Y | N | N | N/A
| SIRT (Attn: Gloria Fulton) | 1997-12-10 12:00 | James E. Smith | 714-448-4053 | Moulton Niguel Water | 1997-12-06 10:45 | 1997-12-06 11:00 | 3000 | 0 | Niguel Road, near Club House Drive | Laguna Niguel | OR | 92677 | Upper Salada Lift Station | 1 | Infiltration | This particular lift station has two force mains leading from the station. The rains on Saturday morning were very heavy, and we had only one force main in operation. Approx. 3,000 gallaons spilled while we were opening the 2nd force main. | Both force mains will remain open during the winter months. | Y | Y | Salt Creek | Pacific Ocean |  | Y | N | N | N/A
| SIRT (Attn: Gloria Fulton) | 1997-12-10 16:45 | James E. Smith | 714-448-4053 | Moulton Niguel Water | 1997-12-07 01:00 | 1997-12-07 06:00 | 248000 | 0 | One mile south of Del Obispo & Camino Capistrano | San Juan Capistrano | OR | 92713 | 20" effluent line | 1 | Line break | Contractor dropped rip rap on our outfall line during emergency repairs to the San Juan Creek channel. The contractor was doing the emergency work for the County of Orange. The effluent was secondary treated effluent, not chlorinated. | The plant and the valves were shut down prior to breaking the effluent line, however, line is a gravaity line with the high point near Oso Road. The portion of the line from Oso Road to the break drains by gravity. | Y | N | San Juan Creek | Pacific Ocean | N/A | Y | Y | Y | N/A
| SIRT (Attn: Gloria Fulton) | 1997-12-16 10:45 | Property Manager | 714-448-0061 | Moulton Niguel Water | 1997-12-16 10:00 | 1997-12-16 11:00 | 300 | 0 | 23932 Aliso Creek Rd. | Laguna Niguel | OR | 92677 | Sectional map E-19, MH #2 | 1 | Grease | Cause is unknown. Sewer is from business park only. Partial blockage | Sewer lines were jetted and will be videoed in the next few days. | Y | N | N/A | Pacific Ocean | N/A | Y | N | N | N/A | The pipelines leading from the commercial area will be videoed to see if there is a problem with the sewer or manholes.
978014 | none | na | na | 738-4323 | City of Escondido | 10-22-97 900 | 10-22-97 1730 | 50 | 30 | 2500 S. Esc. Blvd. | Escondido | SD | 92025 | Private Grease Trap | 1 | Grease | Private grease trap overflow | Grease trap cleaned and reported to out pretreatment inspector | y | y | Storm Drain | Deadhorse Creek | Lake Hodges | n | n | n | na
978015 | called / faxed | 11-21-97 1115 | Jim Miller | 741-4668 | City of Escondido | 11-21-97 715 | 11-21-97 754 | 1950 | 0 | N. Centre City Pkwy. @ Country Club Ln. | Escondido | SD | 92026 | MH 245, Sewer atlas p. 245 | 0 | Grease | Grease and rags | Line was placed on 3-month cleaning schedule | y | y | Storm Drain | Reidy Creek | Esc. Creek | y | y | y | 3 | samples were taken
978016 | called / faxed | 11-25-97 1330 | Lance Lauricha | 738-4347 | City of Escondido | 11-18-97 700 | 11-25-97 1300 | 1890 | 0 | 1032 N. Gamble | Escondido | SD | 92026 | Private Cleanout | 0 | Private cleanout / Broken | Contractor broke sewer line | A plumber opened stoppage while city inspector scheduled the contractor to make repairs | y | y | Storm Drain | Esc. Creek | San Elijo Lagoon | y | y | y | 4 | samples were taken
978017 | county health | 12-9-97 945 | Lance Lauricha | 738-4348 | City of Escondido | 12-9-97 915 | 12-9-97 1115 | 100 | 100 | 1203 S. Maple | Escondido | SD | 92026 | Private Cleanout | 0 | Private Cleanout / unknown | unknown | Plumber cleared blockage | n | n | na | na | na | y | n | n | na
978018 | called / faxed | 12-14-97 1320 | Lance Lauricha | 738-4349 | City of Escondido | 12-7-97 ? | 12-14-97 1415 | 3150 | 0 | 610 E. Washington | Escondido | SD | 92026 | Private Cleanout | 0 | Private Cleanout | Plastic bags | Private system | y | y | Storm Drain | Esc. Creek | San Elijo Lagoon | y | y | n | na
978019 | county health | 12-16-97 745 | Lance Lauricha | 738-4350 | City of Escondido | 12-15-97 1330 | 12-15-97 1600 | 750 | 400 | 1960 W. Mission | Escondido | SD | 92025 | Private Cleanout | 0 | Private Cleanout / unknown | Unknown | Plumber cleared blockage | y | y | Storm Drain | Esc. Creek | San Elijo Lagoon | y | n | n | na
978020 | called / faxed | 12-19-97 1530 | Lance Lauricha | 738-4351 | City of Escondido | 12-18-97 700 | 12-19-97 1200 | 6300 | 500 | 1670 El Norte Pkwy | Escondido | SD | 92027 | Private Cleanout | 0 | Private Cleanout / unknown | Rags | Plumber cleared blockage | y | y | Storm Drain | Esc. Creek | San Elijo Lagoon | y | y | y | 3 | samples were taken
978021 | county health | 12-23-97 1300 | Lance Lauricha | 738-4352 | City of Escondido | 12-23-97 900 | 12-23-97 1230 | 420 | 50 | 204 E. Second Ave. | Escondido | SD | 92026 | Private Cleanout | 2 | Private Cleanout | Paper towels | Plumber cleared blockage | y | y | Storm Drain | Esc. Creek | San Elijo Lagoon | y | n | n | na
978022 | none | na | na | 738-4353 | City of Escondido | 12-25-97 900 | 12-25-97 1130 | 100 | 100 | 1103 E. 5th. | Escondido | SD | 92025 | MH 3684, Sewer atlas 369 | 0 | Roots | Roots | Cleared stoppage and put manhole on scheduled root inspection. | bar: N to N/A
978003 | No, spill totalled 50 gallons. Kathy Stone, County of San Diego contacted via fax. | October 29, 1997; 11:00 am | DENNIS K. QUILLEN | -541 | RAMONA WATER DISTRICT | October 29, 1997; 11:00 am | October 29, 1997; 11:05 am | 50 | 0 | Barona Mesa Road | RAMONA | SD | 92065 | Lift Station no. 2 | 0 | Electrician failed to shut-down lift station 1 while performing mainternance on pump station no. 2 | Pump station no. 1 operated on auto, and began pumping into station no. 2. Sewage spilled onto ground surface while pump station no. 1 was being shut-off. | Electrician instructed to shut-down lift station no. 1 anytime pump station no. 2 is being maintained. | NO | No | None | None | No solids, all liquid waste which was diluted with water | Yes | NA | NO | N/A | All liquid waste, diluted with water
967- 001 | Whitney Ghoram | 8/12/96 8:20 | Renzo Marin | (714) 837-7050 | El Toro Water District | 8/10/96 17:45 | 8/10/96 18:05 | 600 GAL. | 0 GAL. | 25011 El Toro Rd. | Laguna Hills | OR | 92630 | Oso Sta. Wet Well | 1 | State Wide Power Outage and failure of the Transfer Switch. | The Automatic Transfer Switch "Power Sensing Relay" was wired incorrectly, it did not allow the switch to transfer the pumps to the Emergency Power source, leaving the station pumps inoperable. | Rewired "Power Sensing Relay" to prevent failure of the ATS control system. | Y | Y | Storm drain | Aliso creek | OCEAN | Y | N | Y | ? | OCHD placed the warning signs and monitored water quality.
967- 002 | Susan Pease | 2/7/97 13:30 | Renzo Marin | (714) 837-7050 | El Toro Water District | 2/7/97 11:20 | 2/7/97 11:45 | 500 GAL. | 0 GAL. | B - 607 U Avenida Sevilla | Laguna Hills | OR | 92630 | ETWD Atlas page ME-497, MH 14 | 2 | Sticks and rocks. | Sticks and rocks blockage in 6" gravity main line. | Used the Hydrocleaner to break stoppage. Clean up spill and washed down with 4,000 gallons of potable water. Relayed to maintenance crew for routine inspection. | Y | Y | Storm drain | Aliso creek | OCEAN | Y | N | N | N/A | Notified all responsible agencies and mailed discharge report.
967-003 | Laurie Walsh | 1997-12-04 11:15 | Renzo Marin | (714) 837-7050 | El Toro Water District | 1997-12-03 22:34 | 1997-12-03 22:41 | 350 GAL. | 0 GAL. | 25121 Charlinda | Mission Viejo | OR | 92691 | ETWD Freeway Lift station | 3 | Controller power accidentally shut off. | Pumps Controller power circuit was accidentally turned off by contractor. | Reactivated Controller and pumps. Replaced panel key lock. Requested contractor to obtain district approval prior to entering any district facilities. | Y | Y | Aliso Creek | Aliso Creek | OCEAN | Y | N | N | N/A | Notified all responsible agencies and mailed discharge report.
967 -004 | Whitney Ghoram | 1997-12-13 11:55 | Renzo Marin | (714) 837-7050 | El Toro Water District | 1997-12-13 09:15 | 1997-12-13 16:55 | 225,660 GAL. | 94,660 GAL. | 24206 Twig st. and 25121 Charlinda | Mission Viejo | OR | 92691 | 12” Force main and Freeway Sta. MH-5 | 4 | 12” Force main break. | 12" Freeway force main was cracked by tree roots growing around the pipeline. | Performed permanent repairs of pipeline break. Built containment area for sewage spill and recovery. Diluted spill with potable water. Cleaned and wash down area. | Y | Y | Storm drain and Aliso creek | Aliso creek | OCEAN | Y | Y | Y | N/A | Notified all responsible agencies and mailed discharge report.
978018 |  |  | Mike Teem | 7609667868 | Water Utilities Dept. City of Oceanside | 10/13/97 1010 | 10/13/97 1115 | 650 | 0 | 200 Blk. Of Avenida Margarita | Oceanside | SD | 92057 | Manhole | 0 | Grease | Grease & rags in City main caused overflow from manhole. | Vactor truck jet cleaned main. | N | Y | Drainage Ditch | N/A | Soaked into dirt drainage ditch. | Y | N/A | N | N/A | Spill washed down by Vactor truck and paper debris was picked up.
978019 |  |  | Norman Crum | 7609667868 | Water Utilities Dept. City of Oceanside | 10/16/97 1700 | 10/16/97 1730 | 100 | 0 | 3207 Roymar Road | Oceanside | SD | 92056 | Manhole | 0 | Grease | Build up of grease in city main. | Main was "jet rodded". | N | Y | N/A | N/A | Soaked into dirt drainage ditch. | Y | N/A | N | N/A | No "solids" escaped manhole. No "public contact" was evident, or likely.
978020 |  |  | Mike Teem | 7609667868 | Water Utilities Dept. City of Oceanside | 10/27/97 0715 | 10/27/97 0815 | 275 | 0 | 4221 Thomas Street | Oceanside | SD | 92054 | Manhole | 0 | Grease | Heavy blockage of grease in city main. | Line was "jet rodded" after breaking up stoppage, also chlorine will be dropped in the line to dissolve grease. | N | Y | Storm Drain | N/A | Storm Drain. | N | N/A | N | N/A | Spill area was washed down with water.
978021 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 11/02/97 0930 | 11/02/97 1000 | 80 | 0 | Mission & Frontier | Oceanside | SD | 92056 | Manhole | 14 | Line Break | Sewer Lateral was crushed by contractor for CalTrans while working on #76. | CalTrans will fix it, when they get around to it. | N | N | N/A | N/A | Soaked into dirt drainage ditch. | N | N/A | N | N/A | Atlas was hired to remove 3,800 gallons.
978022 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 11/09/97 0840 | 11/09/97 0905 | 100 | 0 | Mission & Frontier | Oceanside | SD | 92056 | Manhole | 15 | Line Break | Sewer Lateral was crushed by contractor for CalTrans while working on #76. | CalTrans will fix it, when they get around to it. | N | N | N/A | N/A | Soaked into dirt drainage ditch. | Y | N/A | N/A | N/A | Flow is also coming out of a CalTrans "pull" box for traffic signals, etc.
978023 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 11/16/97 1250 | 11/16/97 1320 | 80 | 0 | Mission & Frontier | Oceanside | SD | 92056 | Manhole | 16 | Line Break | Sewer Lateral was crushed by contractor for CalTrans while working on #76. | CalTrans will fix it, when they get around to it. | N | N | N/A | N/A | Soaked into dirt drainage ditch. | Y | N/A | N/A | N/A | Flow is also coming out of a CalTrans "pull" box for traffic signals, etc.
978024 |  |  | Ed Calhoun | 7609667868 | Water Utilities Dept. City of Oceanside | 11/21/97 1430 | 11/21/97 1500 | 100 | 0 | 1200 North Harbor | Oceanside | SD | 92054 | Manhole | 0 | Roots | Sewer Lateral belonging to Oceanside Marina Towers became "root bound" by their trees. | Management of "Towers" was requested to keep their lateral free of roots. | Y | Y | Oceanside Harbor | Pacific Ocean | N/A | Y | N/A | Y | 2
978025 |  |  | Ira Black | 7609667868 | Water Utilities Dept. City of Oceanside | 12/18/97 0930 | 12/18/97 1030 | 200 | 150 | 2209 Valley Road | Oceanside | SD | 92056 | Private Cleanout | 0 | Roots | Sewer Lateral "backed up" because of root bound City Main. | City Main put on monthly "Rodding" schedule. | N | N | N/A | N/A | Front Yard | Y | N/A | N/A | N/A | Property has yard drain illegally hooked to sewer lateral.
978026 |  |  | Ed Calhoun | 7609667868 | Water Utilities Dept. City of Oceanside | 12/26/97 0830 | 12/26/97 1530 | 50 | 0 | 143 Harrison Street | Oceanside | SD | 92057 | Private Cleanout | 0 | Blockage | City Main "running free". Private lateral has blockage. | Advised renter to call plumber. | N | N | N/A | N/A | Front Yard | N | N/A | N/A | N/A
1110971 | VM/FAX | 11/10/97, 13:20 | Jay Elston | 714 366-1553 | CITY OF SAN CLEMENTE | 11/10/97, 10:30 | 11/10/97, 11:10 | 900 gal | 0 | Cascadita / Montego | San Clemente | OR | 92672 | SMHB5434 | 0 | Roots |  |  | Y | Y | Ocean |  | Pacific Ocean | Y | N | Y | 2 Days | Roots caused blockage at intersection of Cascadita / montego. Area not root problem. Blockage may be a result of homeowner cleaning house lateral. County posted beaches and sampled.
1124971 | Rebecca Stewart | 1997-11-24 | A J Howard | 714 366-1553 | CITY OF SAN CLEMENTE | 11/21/97, 12:00 | 11/22/97, 16:00 | 2300 gal | 0 | 380 Ave Pico | San Clemente | OR | 92672 | RWW Yard Pipe | 0 | Corroded Line |  |  | Y | Y | Ocean |  | Pacific Ocean | Y | N | N | NA | Reclaimed water line for irrigation corroded. Leak initially thought to be domestic fire service line. Crews ID line as RWW and repairs began next day. A new line is being installed.
5 | GLORIA FULTON | 10/06/97 15:00 | MIKE DUNBAR | (714) 499-4555 | SOUTH COAST WATER DISTRICT | 10/06/97 14:00 | 10/06/97 15:30 | 500-1000 | 0 | LINKS GOLF COURSE | DANA POINT | OR | 92629 | FORCE MAIN | 0 | CONSTRUCTION | CONTRACTOR HIT AIR LINE HOOKED UP TO FORCE MAIN (BROKE FITTING) | 500-1000 GALLONS CONTAINED IN DITCH (SEEPING INTO GROUND) 50 GALLONS WENT INTO OCEAN | Y | Y | SALT CREEK | PACIFIC OCEAN | N/A | Y |  | Y | 3 DAYS | POSTED AT MOUTH OF CREEK
6 | GLORIA FULTON | 10/15/97 07:30 | MIKE DUNBAR | (714) 499-4555 | SOUTH COAST WATER DISTRICT | 10/13/97 12:15 | 10/13/97 12:30 | 100 | 80 | PACIFIC COAST HWY & RITZ COVE DR | DANA POINT | OR | 92629 | 6" DIP FORCE MAIN | 1 | CONSTRUCTION | CONTRACTOR SNAGGED 6" DIP FORCE MAIN WHILE TRENCHING FOR NEW 12" PVC LINE | 80% OF DISCHARGE WAS DIVERTED BACK INTO NEW PIPELINE ALREADY IN PLACE, REPAIR CLAMP PLACED ON 6" DIP LINE, HTH SPRINKLED IN TRENCH AND ON SOIL REMOVED | N | N | NONE | NONE | 8' DEEP TRENCH WITH ROCK BASE | Y | N/A | N | N/A
7 | 6195716972 (FULTON) | 10/16/97 08:20 | MIKE DUNBAR | (714) 499-4555 | SOUTH COAST WATER DISTRICT | 10/15/97 16:30 | 10/15/97 17:15 | 500 | 0 | 31672 SCENIC DR | LAGUNA BEACH | OR | 92677 | MAIN LINE | 0 | ROOTS | BLOCKAGE AT MAINLINE CAME OUT OF CUSTOMER CLEAN-OUT, ROOTS WERE THE CAUSE | CLEANED OUT MAIN LINE WITH RODDING MACHINE | N | Y | NONE | NONE | SAND | Y | N/A | N | N/A
8 | 6195716972 (FULTON) | 11/10/97 10:20 | MIKE DUNBAR | (714) 499-4555 | SOUTH COAST WATER DISTRICT | 11/09/97 09:00 | 10/09/97 10:00 | 100 | 0 | 21651 WESLEY DRIVE | LAGUNA BEACH | OR | 92651 | MANHOLE | 0 | ROOTS | ROOTS BLOCKED LINE | REMOVED ROOTS AND CLEANED LINE | Y | Y | ALISO CREEK | PACIFIC OCEAN | N/A | Y | N/A | Y AS OF 1:16 PM 11/10/97 |  | CREEK MOUTH ALWAYS POSTED, COUNTY REMOVED BERM ALLOWING FLOW TO OCEAN AT 1:16 PM 11/10/97
9 | 6195716972 (FULTON) | 12/08/97 12:30 | MIKE DUNBAR | (714) 499-4555 | SOUTH COAST WATER DISTRICT | 12/06/97 12:43 | 12/06/97 14:00 | 130000-150000 | 0 | ALISO CREEK | LAGUNA BEACH | OR | 92651 | SEWAGE LIFT STATION | 0 | INFILTRATION | INFILTRATION OF SURFACT FLOOD WATER COMING FROM ALISO CREEK PUMPS COULD NOT HANDLE VOLUME | FLOWS DIVERTED INTO ABANDONED OUTFALL LINE PUMPS WERE BACK ON LINE AS SOON AS MANHOLE COVERS COULD BE REACHED AND PLACED BACK IN POSITION | Y | N | PACIFIC OCEAN | NONE | N/A | Y | Y | Y | UNKNOWN AT THIS TIME | ALISO CREEK IMPACTED BY HEAVY SURFACE RUNOFF ORIGINATING INLAND
978003 | GLORIA FULTON FAX | 1997-09-05 | BRIAN WALTHER | 691-5027 | CITY OF CHULA VISTA | 1997-09-05 10:00 | 1997-09-05 11:00 | 1500 | 0 | SOUTH END OF HUNTE PARKWAY | CITY OF CHULA VISTA | SD | 91910 | ORANGE AVENUE FORCE MAIN CLEANOUT | 0 | FORCEMAIN CLEANOUT FAILED | FORCEMAIN CLEANOUT FAILED DUE TO IMPROPER INSTALLATION AT TIME OF CONSTRUCTION | CHECKED OTHER FORCEMAIN CLEANOUTS AND FOUND HALF TO HAVE BEEN IMPROPERLY CONSTRUCTED. ORIGINAL CONTRACTOR REPAIRED ALL OTHERS | Y | Y | SALT CREEK | NONE | UPPER REACH OF SALT CREEK | Y | N | N | 0 | THE AREA WHERE THE SEWEAGE FLOWED INTO SALT CREEK IS IN ACCESSESSIBLE. THERE WAS NO VISABLE FLOW IN THE CREEK AT THE TIME
978004 | GLORIA FULTON FAX | 1997-09-09 13:00 | EASTLAKE PROPERTY MANAGER | 421-0127 | CITY OF CHULA VISTA | 1997-09-09 13:00 | 1997-09-09 14:00 | 800 | 0 | HUNTE PARKWAY APPROXIMATELY 1000 FEETSOUTH OF OTAY LAKES ROAD | CITY OF CHULA VISTA | SD | 91910 | MANHOLE | 0 | CONTRACTOR HIT MANHOLE COVER | DIRT FELL INTO MANHOLE AFTER COVER HIT AND PLUGGED THE LINE | USED OUR VACCON AND REMOVED DIRT AND DEBRIS FROM THE MANHOLE AND MAIN. RARE OCCURRENCE, NO PREVENTATIVE MEASURES REQUIRED. | N | Y | SALT CREEK | N/A | UPPER REACH OF SALT CREEK | Y | N | N | 0 | THE AREA WHERE THE SEWEAGE FLOWED INTO SALT CREEK IS IN ACCESSESSIBLE. THERE WAS NO VISABLE FLOW IN THE CREEK AT THE TIME
978004 | 619 571-6972 | 971212 0700 | City of Laguna Beach | 714 497-0765 | Laguna Beach | 971211 1055 | 971211 1120 | 250 | None | 100 Blk. S. Coast Hwy | Laguna Beach | Orange | 92651 | 100 Blk. S. Coast Hwy Manhole #3 | 1 | Grease | Grease build-up caused the flow to | Broke stoppage using the Jetter. Need | Yes | Yes | Pacific Ocean/Main Beach | None | Same | Yes | No | Yes | 4 | Signs were still up from previous spill on 12/6
97003 | N/A | N/A | N/A |  | City of Poway | 11/27/97 - 0930 | 11/27/97 - 0950 | 45 | 15 | 13441 Sagewood Drive | Poway | San Diego | 92064 | Collection System | 1 | Partial main blockage | 0900 - Resident called water treatment plant to report sewer bubbling out of clean-out. Water Utilities crews called in. Cleared partial blockage in the 8" sewer main caused by grease build up. Used Vactor to vacuum 15 gallons of spill; disinfected and | Video inspection scheduled to determine maintenance needs; placed in cardfile. | No | No | N/A | N/A | Disinfected and spread topsoil | No | No | No | N/A | None
JAN-MAR '98
| SIRT (FAX) | 1998-02-14 15:00 | Brad Bruington | 714-425-3514 | Moulton Niguel Water | 1998-02-14 10:50 | 1998-02-14 11:15 | 500 | 0 | Upper Salada Pump Station, Niguel Rd. | Laguna Niguel | OR | 92677 | Upper Salada Pump Station | 2 | Pump Station Failure | Heavy rains calling on all pumps. One pump check valve stuck open, returning flow to wet well. | Check valve cleaned and repaired | Y | N | Salt Creek | Pacific Ocean | N/A | Y | N/A | Y | TBD | O.C. Health Dept. posted beaches
| SIRT (FAX) | 1998-02-18 15:00 | Brad Bruington | 714-425-3514 | Moulton Niguel Water | 1998-02-16 11:30 | 1998-02-16 15:30 | 3600 | 0 | Camino Capistrano | Laguna Niguel | OR | 92677 | 30" steel line | 1 | Line break | Ground sliding into river cracked 30" steel secondary effluent outfall line, plant off, drained line. | Line repaired by welder. Tested with flow. | Y | N | Oso Creek | Pacific Ocean | NA | Y | N | Y | TBD | O.C. Health Dept. posted beaches
| SIRT (FAX) | 1998-02-18 15:00 | Brad Bruington | 714-425-3514 | Moulton Niguel Water | 1998-02-18 12:00 | 1998-02-18 17:00 | 1200 | 0 | Camino Capistrano | Laguna Niguel | OR | 92677 | pipeline | 2 | Line break | Second break at land slide area. | Drain and weld line. | Y | N | Oso Creek | Pacific Ocean | N/A | Y | N | Y | TBD | O.C. Health Dept. posted beaches
| SIRT (FAX) | 1998-02-25 | Brad Bruington | 714-425-3514 | Moulton Niguel Water | 1998-02-24 08:00 | 1998-02-25 12:30 | 3000000 | 0 | Camino Capistrano/Junipero Serra | San Juan Capistrano | OR | 92675 | 39" pipeline | 1 | Line break | Trabuco Creek broke 39" concrete-encased sewer line under creek | Bypass pipe and put pumps in place. Was in place and operational by 2/25/98 14:00 hours | Y | N | Trabuco Creek | Pacific Ocean | N/A | Y | Y | Y | TBD | O.C. Health Dept. is sampling and posting beaches.
| SIRT (FAX) | 1998-02-26 10:00 | Brad Bruington | 714-425-3514 | Moulton Niguel Water | 1998-02-25 20:30 | 1998-02-25 23:30 | 3500 | 0 | 400 yds. south of Del Obispo (San Juan River) | San Juan Capistrano | OR | 92675 | 21" secondary effluent outfall line | 1 | Line break | Contractor placing rip rap on San Juan Creek punctured 21" secondary effluent outfall line. | Crew repaired punctured area. | Y | N | San Juan Creek | Pacific Ocean | N/A | Y | N | Y | TBD | O.C. Health Dept. posted beaches.
10 | 6195716972 (FULTON) | 02/17/98 10:30 | MIKE DUNBAR | (714) 499-4555 | SOUTH COAST WATER DISTRICT | 02/17/98 05:15 | 02/17/98 08:40 | 11286 | 0 | ALISO PKWY & AWMA ROAD | LAGUNA NIGUEL | OR | 92677 | EAST EXPORT SLUDGE BARREL | 0 | LINE BREAK | CREEK EROSION DUE TO HEAVY STORM RUNOFF CAUSED EMBANKMENT FAILURE | FIX LINE BREAK | Y | N | PACIFIC OCEAN | NONE | N/A | Y | Y | Y |  | SIGNS ALREADY POSTED DUE TO SPILL FROM TRABUCO CANYON WATER DISTRICT
978001 | Kristin Schwall | 1998-02-09 11:00 | Gary Masters | (760)753-6203 | San Elijo Joint Powers Authority | 1998-02-06 16:00 | 1998-02-06 16:05 | <250 gallons | 0 gallons | 2695 Manchester Avenue | Cardiff | SD | 92007 | Plant Headworks | 0 | Infiltration | Heavy rain caused infiltration at the Olivenhain Pump Station and the Solana Beach Pump Station. The momentary high peak flow caused the spill an the plant's headworks. | Infiltration at both pump stations will be investigated. | Y | Y | San Elijo Lagoon | Pacific Ocean |  | Y | NA | N | NA
978004 | Voicemail | 1998-02-24 02:00 | Jim Gusman | (760)-726-1340ext1665 | City of Vista | 1998-02-24 00:15 | 1998-02-24 01:30 | 7500 | 0 | Buena Sanitation Trunk Line Easement | Vista | SD | 92083 | B1-2 #101 | 0 | Flood Damage due to rains, Infiltration | High flows at the Buena Pump Station due to very heavy rains. The lowest upstream manhole spilled effluent because the pump station couldn't keep up with the high flows. | All three pumps at the pump station were at high speed,it took over an hour for the pump station to catch up. | Y | N | Aqua Hedionda Creek | Aqua Hedionda Lagoon, Pacific Ocean |  | Y | Y | Y | 10 | Signs posted in the A.M., due to heavy rains and easement access none of the spill was captured. The beach is 8-10 miles from the spill, there was heavy dilution due to the rains. Signs posted on the easement 2 miles downstream.
978005 | Voicemail | 1998-02-24 10:00 | Jim Gusman | (760)-726-1340ext1665 | City of Vista | 1998-02-24 07:50 | 1998-02-24 09:50 | 10500 | 0 | Buena Sanitation Trunk Line Easement | Vista | SD | 92083 | B1-2 #101 | 0 | Flood Damage due to rains, Infiltration | High flows at the Buena Pump Station due to very heavy rains. The lowest upstream manhole spilled effluent because the pump station couldn't keep up with the high flows. | All three pumps at the pump station were at high speed,it took over an hour for the pump station to catch up. | Y | N | Aqua Hedionda Creek | Aqua Hedionda Lagoon, Pacific Ocean |  | Y | Y | Y | 10 | Signs posted in the A.M., due to heavy rains and easement access none of the spill was captured. The beach is 8-10 miles from the spill, there was heavy dilution due to the rains. Signs posted on the easement 2 miles downstream.
978003 | VOICE MAIL-PAUL RICHTOR, FAX | 2/16/98 9:00AM | KRIS HANBERG | 714/858-4979 | TCWD | 2/15/98 5:00AM | 2/16/98 9:00AM | 480000 | 0 | EL TORO/PORTOLA | TRABUCO CANYON | OR | 92679 | EL TORO LIFT STATION | 1 | POWER FAILURE | LOW VOLTAGE RELAY FAILED AND FUSE | LOOKING INTO REDESIGN | Y | Y | ALISO CREEK | OCEAN |  | Y | N | Y | 96 HRS | NONE
978020 | N/A | N/A | N/A | N/A | CARLSBAD MWD | 1/2/98-9:08 A | 1/2/98-12:30 P | 5 TO 10 | 5 TO 10 | 260 NORMANDIE | CARLSBAD | SD | 92008 | CLEANOUT | 4 |  | PIECE OF RODDING MACHINE BROKE OFF IN MAIN | CLEARED OBSTRUCTION AND WILL INCREASE PREVENTATIVE MAINTENANCE IN THIS AREA DUE TO GREASE PROBLEMS | N | N |  |  | STREET SURFACE | N | N | N | N/A | VACUUMED UP WATER THAT SPILLED AND DISINFECTED AREA.
978021 | N/A | N/A | N/A | N/A | CARLSBAD MWD | 1/10/98-11:30 A | 1/10/98-11:50 A | 5 | 0 | 1113 CAMINO DEL SOL CIRCLE | CARLSBAD | SD | 92008 | CLEANOUT | 1 | TREE ROOTS |  | RODDED LATERAL WITH RODDING MACHINE, CLEARED LINE. | N | N |  |  | AREA AROUND CLEANOUT | N | N | N | N/A | DISINFECTED AREA AROUND CLEANOUT
978022 | KATHY STONE-FAX | 1/15/98-A.M. | DON WASKO | 760-438-2722 | CARLSBAD MWD | 1/14/98-7:00A | 1/14/98-8:00A | 50 | 50 | 1275 YOURELL | CARLSBAD | SD | 92008 | INSIDE HOUSE | 1 | TREE ROOTS |  | RODDED LATERAL WITH RODDING MACHINE, CLEARED LINE. | N | N |  |  | FAMILY ROOM INSIDE HOUSE | N | N | N | N/A | RESIDENT CLEANED UP SEWAGE
978023 | N/A | N/A | N/A | N/A | CARLSBAD MWD | 1/14/98-8:00A | 1/14/98-9:30A | 30 | 30 | IMPALA @ PALMER WAY | CARLSBAD | SD | 92008 | PRIVATE PUMP STATION | 2 |  | POWER FAILURE, PUMP STATION FAILURE AT PRIVATE PUMP STATION LOCATED ON PROPERTY. | REITERATED TO MANAGEMENT COMPANY (MULLER CO.) THE IMPORTANCE OF PREVENTATIVE MAINTENANCE ON PUMP STATION | N | N |  |  | STREET SURFACE | N | N | N | N/A | VACUUMED UP WATER THAT SPILLED AND DISINFECTED AREA.
978024 | KATHY STONE-FAX | 1/19/98-A.M. | PAT GUEVARA | 760-438-2722 | CARLSBAD MWD | 1/17/98-10:30 A | 1/17/98-11:30 A | 100 | 100 | 2445 PIO PICO | CARLSBAD | SD | 92008 | INSIDE HOUSE | 1 |  | SEWER MAIN STOPPAGE ON PIO PICO, BETWEEN BUENA VISTA WAY & KNOWLES | CLEARED OBSTRUCTION IN SEWER MAIN WITH VACTOR | N | N |  |  | INSIDE HOUSE | N | N | N | N/A | RESIDENT HIRED CONTRACTOR TO CLEAN UP SEWAGE
978025 | N/A | N/A | N/A | N/A | CARLSBAD MWD | 1/21/98-3:00P | 1/21/98-4:00P | 20 | 0 | 7201 TANAGER | CARLSBAD | SD | 92009 | MANHOLE | 1 |  | PIPE OBSTRUCTION AT MANHOLE (DEBRIS) | CLEARED BLOCKAGE WITH VACTOR | N | N |  |  | AREA AROUND MANHOLE | N | N | N | N/A | DISINFECTED AREA AROUND MANHOLE
978026 | N/A | N/A | N/A | N/A | CARLSBAD MWD | 1/23/98-9:04 A | 1/23/98-11:30 A | 1 TO 5 | 0 | 3898 WESTHAVEN | CARLSBAD | SD | 92008 | CLEANOUT | 1 | TREE ROOTS |  | RODDED LATERAL WITH RODDING MACHINE, CLEARED LINE. | N | N |  |  | AREA AROUND CLEANOUT | N | N | N | N/A | DISINFECTED AREA AROUND CLEANOUT
978027 | KATHY STONE-FAX AND CRWQCB | 3/12/98-P.M. | PAT GUEVARA | 760-438-2722 | CARLSBAD MWD | 3/11/98-7:45P | 3/11/98-7:52P | 2000 | 0 | 2700 BLOCK OF AVENIDA DE ANITA | CARLSBAD | SD | 92008 | MANHOLE | 1 | GREASE | GREASE BLOCKAGE UPSTREAM CAME LOOSE AND FORCED @ 2,000 GAL. OUT OF MANHOLE INSTANTANEOUSLY | BLOCKAGE CLEARED ITSELF. THIS AREA IS CURRENTLY ON OUR PREVENTATIVE MAINTENANCE HIGH PRIORITY LIST. | Y | Y | DESILTING BASIN BEHIND VON'S SHOPPING CTR. | BUENA VISTA CREEK AT EL CAMINO REAL | BUENA VISTA LAGOON | Y | Y | N | N/A | ADVISED KATHY STONE ON VOICE MAIL OF OUR FOLLOW UP & INVESTIGATION
967-001 | Kristin Schwall | 1997-04-25 10:00 | Shawn Atherton | 753-5018 | City of Encinitas | 1997-01-25 14:15 | 1997-01-25 15:15 | 400 | 0 | 801 Birmingham (Cardiff) | Encinitas | SD | 92024 | Crdf 16 mh121 | 0 | Tree Roots | Nearby tree roots growing into side of m.h. and down into the waters, causing blockage in the channel of the m.h. | Nearby trees were removed from the easement by the property owner. | n | y |  |  | Ocean (4 miles from source) | y | n | n | n/a | It was raining at the time of the blocakge. We also flushed additional 1,000 gal. of water into storm drain. Sewage was well diluted by the time it reached the ocean.
978-001 | Kristin Schwall | 1998-02-15 11:15 | City of Encinitas Lifeguard | (760)753-6203 | City of Encinitas | 1998-02-15 11:15 | 1998-02-15 12:45 | 85000 | 0 | 301 Third Street | Encinitas | SD | 92024 | Moonlight Beach Pump Station | 0 | Infiltration/ Pump Station Failure | Inflow exceeded pump capacity and submerged level sensor which gave inaccurate level data. Caused eratic pump operation and failure to match flow. All data was lost. Pumps shut down causing spill. High wetwell alarm went unreported. | Manually started pumps, cleaned level sensor and reset system. Notified alarm company. Clean-up initiated. Spill and debris completely cleaned using vaccon. | y | y | Pacific Ocean/ Moonlight Beach |  |  | y | n | y | n/a
978027 |  |  | Norm Crum | 760/966-7868 | Water Utilities Dept. City of Oceanside | 01/03/98 2245 | 01/03/98 2330 | 350+ | 0 | 1999 So. El Camino Real | Oceanside | SD | 92054 | 4" Air Release Valve | 0 | Vandalism | Motor Vehicle crashed into Air Release Valve, over Forse Main from Buena Vista Lift Station. | Repaired Valve. Steel pipe posts will be installed to prevent damage from another crash. | Y | Y | Loma Alta Creek | Loma Alta Slough | Pacific Ocean | Y | N/A | Y | 2 | Spill occurred during storm. Creek running full, anyway!.
978028 |  |  | Ira Black | 760/966-7868 | Water Utilities Dept. City of Oceanside | 01/06/98 1030 | 01/06/98 1100 | 150 | 0 | 3685 Vista Campana North & "W" | Oceanside | SD | 92056 | Manhole | 0 | Roots | Roots in City Main. | Rodded City Main and washed down. | N | N | N/A | N/A | Street & Gutters | Y | N/A | N | N/A
978029 |  |  | Jacob DeLa Rosa | 760/966-7868 | Water Utilities Dept. City of Oceanside | 01/06/98 1013 | 01/06/98 1340 | 500 | 0 | 1900 Block of Palmer Drive | Oceanside | SD | 92056 | Manhole | 0 | Roots | Roots in City Main. | Rodded city Main and will monitor quarterly. | Y | Y | Buena Vista Creek | Buena Vista Lagoon | N/A | Y | N/A | N | N/A | Domestic W/W had no solids. Half mile of city gutters before Creek. Public restricted from entering Creek.
978030 |  |  | Ed Calhoun | 760/966-7868 | Water Utilities Dept. City of Oceanside | 01/07/98 0845 | 01/07/98 0930 | 200 | 0 | 1619 Loretta Street | Oceanside | SD | 92054 | Manhole | 0 | Debris | Found paper towels & rags & grease plugging the City Main. | Routine Rodding Schedule. | N | Y | N/A | N/A | Street & Gutters | N | N/A | N | N/A | Aprox. 1/4 of mile from storm system.
978031 |  |  | Gary K. Orr | 760/966-4854 | Water Utilities Dept. City of Oceanside | 1998-01-05 | 01/08/98 1515 | 200 | 0 | 217 North Tremont Street | Oceanside | SD | 92054 | Private lateral | 0 | Other | Lateral has blockage & break. Every time commercial washer pumps out, the effluent comes up through cracks in the parking lot in fron of Bell's Liquor Store. |  | N | Y | Gutter | Storm Drain | N/A | N | N/A | N | N/A | Notified landowner (Partners ARO @ 1015 Chestnut Avenue,#A3 @ Carlsbad 92008.
978032 |  |  | Ed Calhoun | 760/966-7868 | Water Utilities Dept. City of Oceanside | 1/15/98 0730 | `01/15/98 0800 | 100 | 0 | 1968 College Blvd.,#163 | Oceanside | SD | 92056 | Manhole | 1 | Debris | Found paper towels & rags & grease plugging the City Main. | Routine Rodding Schedule. | N | Y | N/A | N/A | Street & Gutters | N | N/A | N | N/A
978033 |  |  | Ed Calhoun | 760/966-7868 | Water Utilities Dept. City of Oceanside | 1/17/98 1130 | 1/17/998 1200 | 200 | 0 | 1217 Holly Street | Oceanside | SD | 92054 | Private lateral | 0 | Other | City opened "cleanout" in house lateral to relieve pressure on downstairs area from flooding further. | City Main ;has been cleared and is on a monthly "Jetter" schedule. | N | N | N/A | N/A | Private Property | N | N/A | N | N/A
978034 |  |  | Norm Crum | 760/966-7868 | Water Utilities Dept. City of Oceanside | 1/29/98 1915 | 1/29/98 2015 | 150 | 0 | 2209 Valley Road | Oceanside | SD | 92054 | Yard Drain | 2 | Blockage in City Main | Owner should receive letter requesting them to install a backwater valve in their lateral. |  | N | N | N/A | N/A | Front & Side Yards | N | N/A | N | N/A | Orr to order their yard drain disconnected from lateral.
978035 |  |  | Norm Crum | 760/966-7868 | Water Utilities Dept. City of Oceanside | 2/11/98 1720 | 2/11/98 1830 | 55 | 0 | 2434 Vista Way | Oceanside | SD | 92054 | Manhole | 0 | Grease | Grease build up in City Main. | Preventative Maint. Scheduleing for Jetter" | N | Y | N/A | N/A | Unknown | N | N/A | N | N/A
978036 |  |  | Jeremy Kemp | 760/966-7868 | Water Utilities Dept. City of Oceanside | 02/15/98 1250 | 02/15/98 2110 | 800 | 2000 | 2861 Turnbull (easement line) | Oceanside | SD | 92056 | Manhole | 0 | Grease | Grease build up in line through the easement. | Drop chlorine into line for grease prevention. WE NEED A NEW ROAD INTO THE EASEMENT. | N | Y | Flood Control Ditch | Corps of Engineers Detention Pond | N/A | N | N/A | N | N/A
978037 | Voice Mail | 02/24/98 0430 | Paul Hojo | 760/966-4870 | Water Utilities Dept. City of Oceanside | 02/24/98 0030 | 02/24/98 0330 | 7500 | 0 | 1330 South Tait Street (La Salina WWTP) | Oceanside | SD | 92054 | Load Equalization Tank | 0 | Infiltration | Heavy rain infiltration caused increased raw sewage flow into headworks. LET exceeded max. level of 10 Ft. to 10.5 Ft. Flow spilled fm two gaps in concrete wall. | Fill in the two gaps with concrete. | Y | Y | Loma Alta Creek | Pacific Ocean | N/A | Y | Y | Y | 2 | Extremely heavy rain fm 2000 to 0230.
978038 |  |  | Gary K. Orr | 760/966-4854 | Water Utilities Dept. City of Oceanside | 02/26/98 0800 | 02/26/98 0830 | 3000 | 0 | 1330 South Tait Street (La Salina WWTP) | Oceanside | SD | 92054 | Force Main | 0 | Equipment Failure | Fitting broke or seperated underground. | Replace fitting and fill hole. | Y | Y | Loma Alta Creek | Pacific Ocean | N/A | Y | Y | Y | 2 | Occurred during high tide. No chance of public contact.
978039 |  |  | Mark Levine | 760/966-7868 | Water Utilities Dept. City of Oceanside | 03/18/98 0715 | 03/18/98 0740 | 50 | 0 | 3100 Block of Alto Street | Oceanside | SD | 92054 | Manhole | 0 | Roots | Roots in City Main. | Rodded line with large cutter blade. | N | N | N/A | N/A | Gutter | N | N/A | N | N/A
978024 | Quarterly |  | Joel V. Holt | (760) 723-5640 | Fallbrook Public Utility District | 1998-01-05 09:15 | 1998-01-05 10:30 | 20 | 20 | Fallbrook & Elbrook Streets | Fallbrook | SD | 92028 | 8" Main Line | 1 | Construction | Contractor broke the pipe with backhoe. | Vacuumed 20 gallons of wastewater from along pipe. Also hauled away 3/4 yards of contaminated dirt. | N | N | NA | NA | Ditch beside pipeline | N | N | N | NA
978025 | (619) 571-6972 | 1998-01-06 08:44 | Patti S. Page | (760) 723-5640 | Fallbrook Public Utility District | 1998-01-05 19:30 | 1998-01-06 00:30 | 1500 | 0 | 1400 Block Mission Rd. | Fallbrook | SD | 92028 | Manhole | 1 | Roots & Grease | Roots and grease plugged line. | Cleaned line, checked all downstream manholes and cleaned lines as needed. | Y | N | Earthen Creek | Fallbrook Creek | NA | Y | N | Y | 3 | Spill percolated quickly into earthen creek bed (dirt culvert) and did not reach Fallbrook Creek.
978029 | Quarterly |  | Joel V. Holt | (760) 723-5640 | Fallbrook Public Utility District | 1998-01-25 14:45 | 1998-01-25 15:00 | 60 | 50 | 1309 Via Del Oro | Fallbrook | SD | 92028 | 4" Cleanout | 1 | Blockage | Unknown blockage. | Flushed main line and unblocked. | N | N | NA | NA | Percolated into ground. | N | N | N | NA | Main line was draining slowly and that is why it wasn't overflowing when crew arrived on site.
978031 | Quarterly |  | Joel V. Holt | (760) 723-5640 | Fallbrook Public Utility District | 1998-02-07 12:00 | 1998-02-07 13:00 | 40 | 0 | 314 Calle de la Paloma | Fallbrook | SD | 92028 | Cleanout | 1 | Grease | Grease and grit blockage. | Flushed line from Fallbrook Street. Need to raise manholes under blacktop. | N | N | NA | NA | Percolated into gravel area. | N | N | N | NA | Washed down gravel area.
978034 | County SD | 1998-03-23 10:45 | Patti S. Page | (760) 723-5640 | Fallbrook Public Utility District | 1998-03-17 13:30 | 1998-03-17 14:30 | 40 | 5 | 904 S. Main St. | Fallbrook | SD | 92028 | Cleanout | 1 | Grease | Cleanout plug full of grease. | Rodded line all the way to main. Flushed main line. | Y | Y | Ostrich Creek | San Luis Rey River | NA | N | N | N | NA | Washed down and disinfected immediate area around cleanout.
978035 | Quarterly |  | Joel V. Holt | (760) 723-5640 | Fallbrook Public Utility District | 1998-03-20 09:20 | 1998-03-20 10:00 | 15 | 5 | 2537 Buena Rosa | Fallbrook | SD | 92028 | Cleanout | 1 | Other | Foreign paper products clogging line. | Rodded line until open, about 20 feet. | N | N | NA | NA | Around cleanout box | N | N | N | NA
978036 | Quarterly |  | Joel V. Holt | (760) 723-5640 | Fallbrook Public Utility District | 1998-03-21 15:01 | 1998-03-21 16:00 | 15 | 7 | 2355 S. Stagecoach | Fallbrook | SD | 92028 | 4" Cleanout | 1 | Other | Foreign paper products clogging line. | Rodded 4" cleanout and unplugged stoppage. Primary male resident informed others in household not to flush "problem" items down toilet any more. | N | N | NA | NA | Around cleanout box | N | N | N | NA
978037 | Quarterly |  | Joel V. Holt | (760) 723-5640 | Fallbrook Public Utility District | 1998-03-23 09:47 | 1998-03-23 10:35 | 30 | 0 | 1708 E. Mission Rd. | Fallbrook | SD | 92028 | 4" Cleanout | 1 | Roots | Roots primary problem. Foreign paper products secondary problem. | Rodded line 3 times and removed all roots. Should be dug up and replaced with new pipe in near future. | N | N | NA | NA | Dried up on roadway (100 ft.). | N | N | N | NA
978038 | County SD | 1998-03-30 10:55 | Patti S. Page | (760) 723-5640 | Fallbrook Public Utility District | 1998-03-29 16:00 | 1998-03-29 17:30 | 1400 | 0 | 529 Debby Street - Pump Station | Fallbrook | SD | 92028 | Lift Station | 1 | Pump Station Failure | Pump Failure. | Removed and repaired pumps. | N | N | NA | NA | Empty field - fenced with restricted access. | Y | N | Y | 3
978039 | Quarterly |  | Joel V. Holt | (760) 723-5640 | Fallbrook Public Utility District | 1998-03-29 13:30 | 1998-03-29 15:00 | 5 | 0 | 1338 E. Fallbrook St. | Fallbrook | SD | 92028 | 4" Cleanout | 1 | Blockage | Roots or offset pipe, can't tell with out digging up. | Homeowner is going to remove trees. | N | N | NA | NA | Percolated into ground around cleanout | N | N | N | NA
1109801 | R.Stewart | 1/10/1998; 17:30 | A J Howard | 714 366-1553 | CSC | 1/10/1998; 900 | 1/10/1998; 1400 | 6000 | 0 | 100 Ave Rosa/Alley | San Clemente | OR | 92691 | SMHD721 | 0 | Contractor Trench collapse displaced sewer line | Contractor Trench collapse displaced sewer line |  | Y | Y | Pacific Ocean |  | Pacific Ocean | Y | N | Y | 5 | Contractor cited by City Inspector to protect all utilities before proceeding. City inspector to continue to monitor contractor.
1309801 | SiRT | 1/30/1998; 17:00 | Jay Elston | 714 366-1553 | CSC | 1/30/1998; 1605 | 1/30/1998; 1715 | 7,500 Gal | 0 | Avenida Califia | San Clemente | OR | 92691 | SMHD725 | 0 | Grease/Roots | Grease/Roots |  | Y | Y | Pacific Ocean |  | Pacific Ocean | Y | N | Y | 4
2269801 | R. Stewart | 2/26/1998; 17:30 | A J Howard | 714 366-1553 | CSC | 2/26/1998; 800 | 2/26/1998; 1730 | 50000 | 0 | Esplanade/Trafalgar | San Clemente | OR | 92691 | RWW Beach | 0 | High Tide/Storm; Surf condition eroded 6ft. soil | High Tide/Storm; Surf condition eroded 6ft. soil |  | Y | Y | Pacific Ocean |  | Pacific Ocean | Y | N | Y | 1 | Combination of high tide and extremely heavy storm surf conditions eroded beach up to the RR tracks exposing and undermining RWW line. Line was isolated at plant on 25 Feb 98 and pumped until loss of suction.
3199801 | N/A |  |  |  |  | 3/19/1998; 815 | 3/19/1998; 930 | <500 Gallons | 0 | Esplanade/Trafalgar | San Clemente | OR | 92691 | RWW Beach | 0 | Line out of service; line plug leaking | Line out of service; line plug leaking |  | Y | Y | Pacific Ocean |  | Pacific Ocean | Y | N | Y | 0 | Off duty operator observed RWW line leaking<3gpm at 08:15; Monica Mazur, OC DOHS also reported at 900; Spoke w/ Monica advise crew was resetting plug at plant; Crew pumped down sump and hard pipe air line to pulg; EST lost < 500 gallons RWW soaked in sand
3259801 | Craig | 3/25/1998; 1310 | Jay Elston | 714 366-1553 | CSC | 3/25/1998; 1210 | 3/25/1998; 1313 | 200Gallons | 0 | Victoria/Del Mar | San Clemente | OR | 92691 | SMHC708 | 0 | 3" Rainfall in less than 3 hrs. Trunk line under 8ft water upstream | 3" Rainfall in less than 3 hrs. Trunk line under 8ft water upstream |  | Y | Y | Pacific Ocean |  | Pacific Ocean | Y | N | Y |  | Unusually high level of precipitation in short period time flooded beach trunk line south of Pier. Inflows Subsided within 30 minutes, pump stations recovered within 90 minutes.
3259802 | Craig | 3/25/1998; 1310 | Jay Elston | 714 366-1553 | CSC | 3/25/1998; 1330 | 3/25/1998; 1410 | 1,200 Gallons | 0 | Boca De La Playa | San Clemente | OR | 92691 | SMHD8713 | 0 | 3" Rainfall in less than 3 hrs. Trunk line under 8ft water upstream | 3" Rainfall in less than 3 hrs. Trunk line under 8ft water upstream |  | Y | Y | Pacific Ocean |  | Pacific Ocean | Y | N | Y |  | Unusually high level of precipitation in short period time flooded beach trunk line south of Pier. Inflows Subsided within 30 minutes, pump stations recovered within 90 minutes.
978007 | Greg Peters | 02-07-98 1100 | Cheryl Brandstrom | 760-744-0460 | V.W.D. | 02-06-98 1730 | 02-07-98 1400 | 2000000 | none | easement | Carlsbad | S.D. | 92069 | 24" outfall line | 4 | broken pipe | steel pipe was possibly crushed when installed | in process of replacing bad pipe | y | n | canyon | irrigation ponds | La Costa Resort | y | y | y | 14+ | spilled into Batiquitos lagoon Carlsbad
978008 | Quarterly Report | 02-18-98 1200 | Ted Powell | 760-744-0460 | V.W.D. | 02-17-98 1430 | 02-17-98 1445 | 950 | none | Field | San Marcos | S.D. | 92009 | 8" line | 1 | surcharging | surcharging due to heavy rains | cut back on pumping to Treatment plant in heavy rains | n | n | none | none | n/a | y | n | n | 0 | absorbed into ground at m/h
978009 | Greg Peters | 02-24-98 0930 | Cheryl Brandstrom | 760-744-0460 | V.W.D. | 02-24-98 0700 | 02-25-98 1800 | 5 to 7 mg | none | easement | Carlsbad | S.D. | 92069 | 30" Line | 5 | broken pipe | steel pipe was possibly crushed when installed | in process of replacing bad pipe | y | n | Canyon De Las Encinas Ponds, and stream on golf course. | Batiquitos lagoon | pacific ocean | y | y | y | 14+ | area posted as per health dept.
978010A | Quarterly Report | 03-03-98 0800 | Ted Powell | 760-744-0460 | V.W.D. | 03-02-98 1100 | 03-02-98 1130 | 450 | none | Lake San Marcos Golf Course | San Marcos | S.D. | 92069 | 8" line | 1 | roots | Roots in line due to large tree next to line. | engineering will talk to golf course about tree removal. | n | n | n/a | n/a | n/a | y | n | n | 0 | spill was contained
978010B | Voice mail | 03-21-98 1325 | Cheryl Brandstrom | 760-744-0460 | V.W.D. | 03-21-98 1000 | 03-21-98 1200 | 239000 | none | Canyon Easement SE of El Camino Real & Palomar Airport Rd. | Carlsbad | S.D. | 92009 | 24" line | 6 | broken pipe | Steel pipe was possibly crushed when installed. | In process of replacing bad pipe. | n | n | Pond on golf course | n/a | Series of ponds on golf course | y | y | y | 14+ | area posted as per health dept.
978005 | 619 571-6972 | 080224 1500 | City of Laguna Beach | 714 497-0765 | Laguna Beach | 980223 1800 | 980224 1430 | 200000 | None | 2556 Temple Hills Drive | Laguna Beach | Orange | 92651 | 2556 Temple Hills/Swr Easement | 1 | Heavy Rain | Due to extremely heavy rain, the hillside gave way | City Crew replaced the missing pipe with pvc | Yes | Yes | Pacific Ocean/Cleo Street Beach | None | Same | Yes | No | Yes | On Going | Due to storm water and sewer spill, all of our beaches were contaminated.
978006 | 619 571-6972 | 980317 0905 | City of Laguna Beach | 714 497-0765 | Laguna Beach | 980317 0900 | 980317 1030 | 10000 | None | Fairview Street | Laguna Beach | Orange | 92651 | Fairview Street Pump Station | 1 | Force Main Break | Failure of 6" Force Main just outside the pump station. This force main is 40 yrs old. | Repaired with a clamp, pipe has a 4" long crack. This main wil be replace by May 98. | Yes | Yes | Pacific Ocean/Shaws Cove Bch | No | Pacific Ocean | Yes | No | Yes | 5 | Number of posted days are estimates
97-98-01 | Mailed Report | Jan22,7:40am | Marc Avila | 714 248-3940 | CBWD | Jan21,2:35pm | Jan21,3:00pm | 75 | 0 | Camino De Los Mares | Capistrano Beach | OR | 92624 | Manhole | 0 | Grease | Grease in upstream manhole,flow caused bubbling at manhole. | Vactor jetted line clear, scheduled to do follow up and is cleaned on regular P&M schedule | no | yes | None | None | Curb and Gutter | Yes | N | No | N/A | Reported to Monica Mazur OCHD
97-98-03 | Faxed | Feb 15,9:00pm | Chris Goodchild | 714 487-1097 | CBWD | Feb 14,1:00pm | Feb14,4:00pm | 4500 | 0 | Pacific Coas Hwy | Capistrano Beach | OR | 92624 | Manhole | 1 | OTHER | Heavy rainstorm event caused hydraulic surcharge on our system.PCH stormdrain on hillside broken also. | Storm finally stopped, jetted lines as precaution due to tremendous amount of surface water infiltration | no | yes | Pacific Ocean | none | Ocean | yes |  | yes | OCH | Reported to OCHD
97-98-02 | Faxed | Feb 2,10:30am | Larry Fregin | 714496-1324 | CBWD | Feb 3,10:30am | Feb 3,11:30am | 6750 | 0 | Pacific Coast Hwy | Capistrano Beach | OR | 92624 | Manhole | 0 | OTHER | Heavy rainstorm event caused hydraulic surcharge on our system. | Follow up inspection, El Nino storm event | no | yes | Pacific Ocean | none | Ocean | yes |  | yes | OCH | Larry Honeyborne was in area,showed up to location
97-98-04 | Faxed | Feb22,5:30pm | Geoffrey Cook | 714 487-1097 | CBWD | Feb22,3:45pm | Feb 22,4:05pm | 500 | 0 | Pacific Coast Hwy | Capistrano Beach | OR | 92624 | Manhole | 2 | OTHER | Continuous storm events continue to cause hydraulic overloads on system. | Continue to monitor system | no | yes | Pacific Ocean | none | Ocean | yes |  | yes | OCH | El Nino heavy rain, causing us surcharge.005-
97-98-05 | Faxed | March14,9:30am | Chris Goodchild | 714 487-1097 | CBWD | March14,NA | Mar14,11:30am | 75 | 0 | Pacific Coast Hwy | Capistrano Beach | OR | 92624 | service lateral | 1 | OTHER | Heavy rainstorm event caused hillside to slide and break line. | Contractor repaired line | no | no | none | none | soil | yes |  | no | N/A | Approx. 50 gallons entered storm drain of the 300
97-98-06 | Faxed | Mar.18,9:15pm | Geoffrey Cook | 714-487-1097 | CBWD | Mar.18,9:15pm | Mar.18,10:10pm | 300 | 0 | Calle Paloma | Capistrano Beach | OR | 92624 | Manhole | 1 | Grease | Grease in upstream manhole,flow caused bubbling at manhole. | Jetted line clear, schedule follow up and review next scheduled cleaning on regular scheduled cleaning. | no | yes | storm drain | none | storm drain | yes |  | no | N/A
978018 | ELECTRONIC QTLY RPT |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 01/28/98, 1200 | 02/05/98, 1000 | 200 | 0 | BUILDING 2378 | CAMP PENDLETON | SD | 920555008 | SEWER LATERAL FROM BUILDING | 1 | CONSTRUCTION | EXISTING SEWER LATERALS FROM BUILDING WERE NOT CONNECTED TO NEW SEWER MAIN BEFORE EXISTING SEWER MAIN WAS DEMOLISHED |  | N | N | NONE | NONE | PERCOLATION SITE AROUND PIPE. | N | NA | N | N/A | SPILL OCCURRED AT CONSTRUCTION SITE. NOT IN AN AREA OF EXPECTED PUBLIC CONTACT.
978019 | PETERS (VOICE MAIL) | 02/13/98, 1420 | Karl Vogel | 6197259762 | MCB, CAMP PENDLETON | 02/11/98, 1800 | 02/11/98, 1915 | 2000 | 0 | 2250 Lift Station | CAMP PENDLETON | SD | 920555008 | 3Y174 | 1 | PUMP STATION FAILURE | Booster pumps not operational, excess flow from bldg 2252 to wet well. | Pumper utilized while booster pumps are being repaired. Cause of excess flow from bldg 2252 repaired. | Y | Y | SANTA MARGARITA RIVER | PACIFIC OCEAN |  | Y | Y | N | 0
978020 | PETERS, VOICE MAIL | 02/13/98, 1505 | KARL VOGEL | 6197259762 | MCB, CAMP PENDLETON | 02/13/98, 1000 | 02/13/98, 1300 | 1800 | 0 | Bldg 140210 | CAMP PENDLETON | SD | 920555008 | 1 Y 14 | 1 | BLOCKAGE | Manhole cover found in adjacent manhole in combination with heavy grease and wood causing blockage. This manhole did not overflow. | Remove cover from manhole and repair /reset ring with cover. | Y | Y | Santa Margarita River | Pacific Ocean |  | Y | Y | N | 0 | Only paper solids had to be disposed of
978021 | GREG PETERS | 02/13/98, 1510 | KARL VOGEL | 6197259762 | MCB, CAMP PENDLETON | 02/13/98, 1130 | 02/14/98, 1730 | 22,800 | 7,800 | South of Stuart Mesa Bridge | CAMP PENDLETON | SD | 920555008 | 6" Force Sewer Main | 1 | CONSTRUCTION | Contractor nicked 6" Force Sewer Main when paving the road. Additional overflow to adjacent wetlands occured when repairs effected. | When leak began an Earthen impound was dug to capture the flow while broken sewer line was repaired. | Y | N | Santa Margarita River | Pacific Ocean |  | Y | Y | Y | 8 | No public access to wetlands. Signs posted at Del Mar Beach (3/4 of a mile south of San. Mar. River) will remain up until sampling results confirm acceptable coliform levels.
978022 | GREG PETERS | 02/13/98, 1510 | Karl Vogel | 6197259762 | MCB, CAMP PENDLETON | 02/13/98, 1445 | 02/14/98, 1730 | 90,000 | 0 | East of Stuart Mesa road, North of San. Mar. River | CAMP PENDLETON | SD | 920555008 | Lift Station # 31-220 | 1 | LINE BREAK | Lift Station secured to prevent further damage to 6" Force Main until repairs effected. |  | N | N |  |  | Abandoned sewage lagoon. | Y | Y | N | 0
978023 | ELECTRONIC QTLY RPT |  | Karl Vogel | 6197259762 | MCB, CAMP PENDLETON | 02/18/98, 0400 | 02/18/98, 0900 | 900 | 850 | LCAC area, ajacent Fire station | CAMP PENDLETON | SD | 920555008 | Lift station # 31-0924 | No | LINE BREAK | Cause undetermined | Discharge line repaired will monitor for any sign of problems. | N | N |  |  | Grass adjacent Lift station. | Y | NA | N | 0 | Area is grassy and level. Spill spead 20" around station percolated/ponded and was pumped. Reached no surface waters.
978024 | RICHTER (VOICE MAIL) | 03/03/98, 1720 | SSgt Duke | 6197259762 | MCB, CAMP PENDLETON | 03/03/98, 1440 | 03/03/98, 1630 | 2000 | 0 | 1.5 miles East of Water Well 41618 Las Pulgas Rd | CAMP PENDLETON | SD | 920555008 | Las Flores Creek | 1 | LINE BREAK | Sewer Force main crossing Las Flores Creek from 41300 Lift Station to STP #9 broke because of high flows in creek. | Shut down 41300 Lift Station. Used Pumper trucks to keep wet well pumped down. Short term action - divert creek & repair line. Long term preventative measures - bore line under creek or suspend line over creek. | Y | N | Las Flores Creek | Pacific Ocean | Red Beach | Y | Y | N | 0 | Red Beach is military training area. No bodily contact occurs. No public access.
978025 | ELECTRONIC QTLY RPT |  | SSgt Duke | 6197259762 | MCB, CAMP PENDLETON | 03/11/98, 1930 | 03/11/98, 2230 | 150 | 0 | 702 Erskine San Onofre I Housing | CAMP PENDLETON | SD | 920555008 | Man Hole HY-184 | 1 | GREASE | Animal fat build up, broom handle and sticks FOUND IN MANHOLE | Put GREASE cutter head on jetter and PM'D lines on Erskine to Torrey. REMOVED Animal fat CLUMPS AND sticks FOR DISPOSAL. | Y | Y | San Mateo Creek | Pacific Ocean |  | Y | NA | N | 0 | NO DISINFECTION OF STREET BUT HOSED DOWN AREA OF CONTACT. SPILL Did not ACTUALLY reach surface waterS. Went 424 DOWN STREET GUTTER,500' down storm drain, 50' DOWN EARTHEN DITCH BY 61 AREA AG FIELD AND Percolated into SOIL.
978026 | ELECTRONIC QTLY RPT |  | KARL VOGEL | 6197259762 | MCB, CAMP PENDLETON | 03/23/98, 0730 | 03/23/98, 1000 | 500 | 0 | F STREET, AT MESSHALL BLDG 14036 | CAMP PENDLETON | SD | 920555008 | Grease Trap | 1 | GREASE | animal fat BUILD UP CAUSED BLOCKAGE IN OUTLET PIPES OF GREASE TRAP DUE TO MISSING SANITARY TEE'S (FOUND IN BOTTOM OF TANK). |  | y | Y | PILGRAM CREEK | SAN LUIS REY RIVER | Earthen diTCH ADJACENT F Street and Messhall. | Y | NA | N | 0 | FLOW TRAVELLED: CONCRETE SWALE (30FT) EARTHEN DITCH (250FT) AND PERCOLATED AFTER MINOR PONDING. NO EXPECTED PUBLIC CONTACT IN AREA OF OVERFLOW. HOT WATER AND DEGREASER USED TO CLEAN/DISINFECT AREA ADJACENT THE MESSHALL.
978022 | N/A | N/A | N/A | N/A | City of Coronado | 1-2-98, 8:45 | 1-2-98, 10:30 | 50 gal | 50 gal | 100 block F/G alley | Coronado | SD | 92118 | Sewer line | 2 | Roots | Roots and debris in sewer line | Cleared with Vactor | N | N | None | None | Sewer line | N | N | N | N/A
978023 | N/A | N/A | N/A | N/A | City of Coronado | 1-10-98, 10:30 | 1-10-98, 12:00 | 60 gal | 60 gal | Third and Orange | Coronado | SD | 92118 | Sewer line | 1 | Debris | Plastic debris in sewer line | Cleared with Vactor | N | N | None | None | Sewer line | N | N | N | N/A
978024 | Fax | 1-5-98, 7:15 am | Woodward | 619-522-7380 | City of Coronado | 1-13-98, 12:00 | 1-14-98, 15:45 | 6,000 gal | 200 gal | Tenth and Glorietta | Coronado | SD | 92118 | Sewer line | 0 | Pipe break | Sewer line collapsed into storm drain | Replaced sewer line over storm drain | N | Y | Glorietta Bay | Pacific Ocean | Sewer line | Y | N | Y | 3
978025 | N/A | N/A | N/A | N/A | City of Coronado | 1-20-98, 21:35 | 1-20-98, 23:00 | 50 gal | 50 gal | 8th and I/J alley | Coronado | SD | 92118 | Sewer line | 1 | Roots | Roots and debris in sewer line | Cleared with Vactor | N | N | None | None | Sewer line | N | N | N | N/A
978026 | N/A | N/A | N/A | N/A | City of Coronado | 1-23-98, 19:00 | 1-23-98, 22:00 | 100 gal | 100 gal | 555 D Avenue | Coronado | SD | 92118 | Sewer line | 2 | Debris/grease | Debris and grease in sewer line | Cleared with Vactor | N | N | None | None | Sewer line | N | N | N | N/A
978027 | N/A | N/A | N/A | N/A | City of Coronado | 2-16-98, 9:15 | 2-16-98, 12:00 | 75 gal | 75 gal | Ninth and B | Coronado | SD | 92118 | Sewer line | 0 | Roots | Roots and debris in sewer line | Cleared with Vactor | N | N | None | None | Sewer line | N | N | N | N/A
978008 | Quarterly Report | 1998-02-02 12:30 | Richard Andrews | 619 755-3294 | City of Del Mar | 02/02/98; 09:00 | 02/02/98; 09:50 | 500 gallons | 250 gallons | 600 Blk Camino Del Mar, East side | Del Mar | SD | 92014 | City Manhole No. 15 sewer block map b-10 | 0 | Roots / Blockage | Roots and Paper | Ran 388' of rod from 600 block of Stratford. Found roots and paper. Travel Vac used to catch overflow and returned. | n | y | n/a | n/a | Retrieved back to system 50%, other soaked into dirt drainage ditches next to railroad tracks. | y | n/a | n | n/a | Sewage caught before reaching ocean, all streets cleaned.
978009 | Quarterly Report | 1998-03-04 18:00 | Richard Andrews | 619 755-3294 | City of Del Mar | 1998-03-04 14:30 | 3/4/1998; 14:30 | 300 gallons | none | Carmel Valley @ Portofino | San Diego | SD | 92014 | Force Main | 0 | Construction | Contractor excavating at south edge Carmel Valley @ intersection w/ Portofino, struck and damaged force main. |  | n | n | n/a | n/a | Road edge weeds and bushes at edge | y | n/a | n | n/a | none
978006 | Voice Mail | 1998-02-24 | Steve Polzin | (909)676-4101 | R.C.W.D. | 02/24/98 0035 | 02/24/98 1226 | 1800000 | 0 | 26266 Washington | Murrieta | RV | 92562 | Secondary Effluent Equalization Basin | none | Vandalism Manhole | Manhole Cover Removed | Raised Manhole Cover and Locking Lid Installed | Y | Yes | Murrieta Creek | Santa Margarita River | Santa Margarita River | Yes | No | No | N/A
978007 | Voice Mail | 1998-03-09 | Bob Olds | (909)676-4101 | R.C.W.D. | 03/07/98 1824 | 03/08/98 0630 | 1000000 | 0 | 26266 Washington | Murrieta | RV | 92562 | Secondary Effluent Equalization Basin | One | Operator Error | Alarm Reset Error | New Alarms Installed | Y | Yes | Murrieta Creek | Santa Margarita River | Santa Margarita River | Yes | No | No | N/A
| BOB BAKER | 1/19/98 1300 | MIKE CALVERT | (909)676-4101 | R.C.W.D. | 1/18/98 2100 | 1/19/98 0900 | 675000 | 0 | 31008 RANCHO CA. ROAD | TEMECULA | RV | 92591 | 12" Reclaimed Reservoir Overflow Line | 0 | TELEMETRY CALIBRATION ERROR | RESERVOIR OVERFLOWED DUE TO THE LEVEL CALIBRATION WAS OFF BY 2' & THE ALTITUDE VALVE SETTING WAS OFF BY 2' | RECALIBRATED LEVEL | N | Yes | EMPIRE CREEK | N/A | EMPIRE CREEK | Yes | No | No | N/A | Spill Contents were fully disinfected Title 22 Effluent
978002 | NO | n/a | n/a | 619-464-6934 | Lemon Grove | 112797*10:30 | 112797*14:30 | 20-25 gal | 0 | 7923 Nichals St | Lemon Grove | San Diego | 91945 | Rear easement | 0 | roots,grease | combination of roots & grease constricted flow | 6" line jetted,stoppage removed/area sanitized | N | N | N/A | N/A | Small amount around manhole, rear easement, area sanitized | N | N | N | N/A | none
978003 | NO | n/a | b/a | 619-464-6934 | Lemon Grove | 022498*2:30 | 022498*6:30 | backup into home | all | 1758 Colfax St | Lemon Grove | San Diego | 91945 | Into residence | 0 | backup into home | No problem in main located | Installed p/l backflow. Home sanitized | N | N | N/A | N/A | Private property. Sewer system | N | N | N | N/A | none
978004 | NO | n/a | n/a | 619-464-6934 | Lemon Grove | 033198*19:00 | 033198*23:00 | 2 to 4 gal | all | 1467 Madera | Lemon Grove | San Diego | 91945 | none | 0 | line blockage | not determined | jetted line. Small spill swept back into sewer | N | N | N/A | N/A | Small amt swept back into sewer | N | N | N | N/A | none
1 | PAM | 2/17/98, 23:30 | HENRY MONROE | 728-1178 | RAINBOW MWD | 1998-02-17 10:45 | 2/17/98, 22:00 | 4500 | 0 | OLD RIVER, GOPHER | BONSALL | S.D. | 92008 | M.H. 3P2161 | 0 | POWER FAILURE | BACKUP GENERATOR FAILED TO TURN ON | REPAIR GENERATOR | Y | Y | CREEK | SAN LUIS REY RIVER | PACIFIC OCEAN | Y | Y | N | N/A | NONE
969183 | Fax 571-6972 | 01/01/98 14:00 | J.Grable | 6544160 | City of San Diego | 01/01/98 10:30 | 01/01/98 13:00 | 750 | 0 | Falcon Fire Wy. & Jacmar Av. | San Diego | SD | 92114 | 8" VC | One | Grease | Grease | Rodded main/refer for pm and grease treatment schedule | N | Y | Storm Drain | Pacific Ocean | Soaked into ground | Y | N | N
969365 | Fax 571-6972 | 01/03/98 14:24 | D.Branco | 6544160 | City of San Diego | 01/03/98 09:36 | 01/03/98 11:00 | 168 | 0 | 3996 Hatton St. | San Diego | SD | 92111 | 8" VC | One | Debris | Roots/Heavy paper buildup | Machine rodded/referred to area supervisor for scheduled PM | Y | Y | Storm Drain | Mission Bay/Pacific Ocean |  | Y | N | N
969380 | Fax 571-6972 | 01/03/98 22:50 | D.Branco | 6544160 | City of San Diego | 01/03/98 20:52 | 01/03/98 22:05 | 730 | 0 | 2331 Galveston St. | San Diego | SD | 92110 | 8" VC | One | Roots | Roots | Machine rodded/referred to area supervisor for scheduled PM | Y | Y | Storm Drain |  | Mission Bay/Pacific Ocean | Y | N | Y | Unknown
969664 | Fax 571-6972 | 01/06/98 14:50 | L.Finch | 6544160 | City of San Diego | 01/06/98 10:35 | 01/06/98 12:45 | 260 | 0 | 3091 Elm St./canyon | San Diego | SD | 92102 | 8" VC | One | Roots | Roots | Hand rod/refer to TV for pipe integrity | N | N | Canyon bed | Chollas Creek/SD Bay/Pacific Ocean | Contained in canyon | Y | N | N
969976 | Fax 571-6972 | 01/08/98 12:30 | G.Richardson | 6544160 | City of San Diego | 01/07/98 18:31 | 01/07/98 19:05 | 150 | 75 | Imperial Av. & Woodman St./Wideman Park | San Diego | SD | 92114 | 6" VC | One | Roots | Roots | Rodded main/vactored approximately 75 gallons from spill site | N | N | Ground at spill site/manhole #138 |  | Soaked into ground | Y | N | Y | One
970299 | Fax 571-6972 | 01/09/98 06:35 | M.Whelan | 6544160 | City of San Diego | 01/08/98 19:08 | 01/08/98 21:38 | 150 | 15 | 1180 S. Valencia Py. | San Diego | SD | 92114 | 8" VC | One | Grease | Grease | Rod main/cleaned and vacuumed manhole/vacuumed puddle | Y | Y | Storm Drain | Dissipated in storm drain system |  | Y | N | N
970317 | Fax 571-6972 | 01/09/98 15:15 | L.Finch | 6544160 | City of San Diego | 01/09/98 08:59 | 01/09/98 12:30 | 2110 | 2110 | 1600 Upas St. | San Diego | SD | 92103 | 6" VC | One | Construction | Contractor's temporary hook-up | Replace 4" hookup with 6" until made permanent when new main laid | Y | N | Curb line on Upas and Herbert | San Diego Bay | Recovered by city crews | N | Y | N
970541 | Fax 571-6972 | 01/11/98 14:42 | D.Branco | 6544160 | City of San Diego | 01/11/98 11:14 | 01/11/98 12:30 | 38 | 0 | 65th St. & Imperial Av. | San Diego | SD | 92114 | 8" VC | One | Roots | Roots | Machine rodded/referred to area supervisor for scheduled PM | N | N | Ground around manhole |  | Dried into ground | Y | N | N
970674 | Fax 571-6972 | 01/13/98 05:05 | M.Whelan | 6544160 | City of San Diego | 01/12/98 15:45 | 01/12/98 16:45 | 300 | 250 | 40th St. 1800' n. of Adams Av. | San Diego | SD | 92116 | 8" VC | Three | Vandalism | Rocks and debris buildup from vandalism | Rocks removed from manhole/cleaned manhole | Y | Y | Pumped overflow into manhole | Storm drain/San Diego River |  | Y | N | N
971178 | Fax 571-6972 | 01/15/98 01:02 | M.Whelan | 6544160 | City of San Diego | 01/14/98 16:21 | 01/14/98 17:38 | 77 | 34 | 5203 S. Thorn St. | San Diego | SD | 92105 | 6" VC | One | Roots | Roots | Rodded main/checked easement manhole; referred to be strapped | Y | Y | Soaked into canyon |  |  | Y | N | N
971258 | Fax 571-6972 | 01/15/98 01:00 | M.Whelan | 6544160 | City of San Diego | 01/14/98 19:38 | 01/14/98 22:08 | 450 | 0 | 6474 El Cajon Bl. | San Diego | SD | 92115 | 8" VC | One | Roots | Roots | Rod main/trace out overflow | Y | Y | Storm Drain | Dissipated in storm drain |  | Y | N | N
971580 | Fax 571-6972 | 01/16/98 19:00 | J.McPherson | 6544160 | City of San Diego | 01/16/98 13:30 | 01/16/98 14:15 | 450 | 0 | Roselle St. & Sorrento Valley Bl.** | San Diego | SD | 92121 | 24" Plug | One | Force Main Brk | Leak on 24" plug at end of force main | Shut off force main/pumping through new #65 Station | Y | Y | Torrey Pines State Reserve | Pacific Ocean |  | Y | N | N
971662 | Fax 571-6972 | 01/17/98 17:12 | D.Branco | 6544160 | City of San Diego | 01/17/98 09:01 | 01/17/98 10:30 | 455 | 0 | 4575 Arizona St. | San Diego | SD | 92104 | 8" VC | One | Grease | Grease | Machine Rodded/referred to area supervisor for scheduled PM | Y | Y | Storm Drain | San Diego Bay/Pacific Ocean |  | Y | N | N
971668 | Fax 571-6972 | 01/17/98 17:06 | D.Branco | 6544160 | City of San Diego | 01/17/98 10:06 | 01/17/98 11:07 | 122 | 0 | El Amigo & Nob Av. | San Diego | SD | 92014 | 8" VC | One | Roots | Roots | Flushed main to relieve stop/refer to area supervisor for scheduled PM | Y | Y | Storm Drain | Pacific Ocean |  | Y | N | N
971701 | Fax 571-6972 | 01/17/98 23:55 | J.McPherson | 6544160 | City of San Diego | 01/17/98 20:52 | 01/17/98 23:00 | 68 | 2 | 1018 Bangor St. | San Diego | SD | 92106 | 6" CP | One | Roots | Roots | Rodded easement line to remove blockage | Y | Y | Storm Drain | Pacific Ocean |  | Y | N | N
971737 | Fax 571-6972 | 01/19/98 15:00 | J.McPherson | 6544160 | City of San Diego | 01/19/98 12:33 | 01/19/98 14:33 | 600 | 0 | 168 Kenyatta Dr. | San Diego | SD | 92114 | 8" VC | One | Grease | Heavy grease | Referred to area supervisor for main cleaning schedule | Y | Y | Storm Drain | Chollas Creek |  | Y | N | N
971748 | Fax 571-6972 | 01/19/98 20:30 | J.McPherson | 6544160 | City of San Diego | 01/19/98 16:04 | 01/19/98 17:00 | 56 | 0 | 4432 Pacific Hy. | San Diego | SD | 92140 | 8" VC | One | Debris | Rags in main | Added to cleaning schedule | Y | Y | Storm Drain | San Diego Bay | Dried in storm drain | Y | N | N
971823 | Fax 571-6972 | 01/21/98 01:27 | M.Whelan | 6544160 | City of San Diego | 01/20/98 13:37 | 01/20/98 17:05 | 1040 | 400 | Calle Cristobal & Corley Ct. | San Diego | SD | 92126 | 8" VC | One | Grease | Heavy grease mixed with roots | Flushed main/cleaned manholes | Y | Y | Storm Drain | None | Dried in canyon | Y | Y | N
971852 | Fax 571-6972 | 01/21/98 01:30 | M.Whelan | 6544160 | City of San Diego | 01/20/98 15:24 | 01/20/98 20:24 | 300 | 100 | 3206 47th St. | San Diego | SD | 92105 | 8" VC | One | Roots | Heavy roots and grease | Cleaned manhole to remove roots, grease and flushed main | Y | N | Canyon | None | Canyon | Y | N | N
972348 | Fax 571-6972 | 01/22/98 19:55 | M.Whelan | 6544160 | City of San Diego | 01/22/98 13:48 | 01/22/98 15:03 | 150 | 74 | 5005 Texas St. | San Diego | SD | 92108 | 8" VC | One | Roots | Heavy roots and heavy grease | Machine rodded main/cleaned out manhole of very heavy roots | Y | Y | Storm Drain | Soaked into ground in drainage ditch |  | Y | N | N
972521 | Fax 571-6972 | 01/23/98 10:10 | G.Richardson | 6544160 | City of San Diego | 01/22/98 19:09 | 01/22/98 21:15 | 504 | 288 | 4125 58th St. | San Diego | SD | 92115 | 8" VC | One | Grvty Main Brk | Break in main | Directed overflow back into manhole/referred to construction crew | Y | Y | Break site between manholes 85 and 86 | Storm Drain | Dissipated into storm drain | Y | N | N
972712 | Fax 571-6972 | 01/24/98 12:00 | D.Branco | 6544160 | City of San Diego | 01/24/98 08:40 | 01/24/98 09:17 | 74 | 0 | 40th St. & T St. | San Diego | SD | 92113 | 8" VC | One | Grease | Grease | Flushed main/referred to area supervisor for scheduled PM | Y | Y | Storm Drain | San Diego Bay/Pacific Ocean |  | Y | N | Y
972745 | Fax 571-6972 | 01/25/98 02:15 | L.Finch | 6544160 | City of San Diego | 01/24/98 22:14 | 01/25/98 00:20 | 630 | 0 | Swift Av. & Wightman St./alley east | San Diego | SD | 92104 | 6" VC | One | Debris | Vandalism/manhole deterioration | Refer to area supervisor for maintenance scheduling | Y | Y | Storm Drain | San Diego Bay/Pacific Ocean |  | Y | N | N
972765 | Fax 571-6972 | 01/25/98 21:12 | D.Branco | 6544160 | City of San Diego | 01/25/98 12:41 | 01/25/98 18:10 | 1645 | 0 | 4310 Mt. Elbrus Ct. | San Diego | SD | 92117 | 8" VC | One | Roots | Roots | Hand rodded main/refer to area supervisor for scheduled PM | Y | N | Tecolate Canyon | Mission Bay/Pacific Ocean | Canyon Floor | Y | Y | N
975021 | Fax 571-6972 | 01/25/98 22:20 | L.Finch | 6544160 | City of San Diego | 01/25/98 16:00 | 01/25/98 20:20 | 260 | 0 | 5005 Texas St. | San Diego | SD | 92108 | 8" VC | Two | Grease | Heavy grease | Clean and TV main for evaluation for shorter maintenance site | Y | Y | Storm Drain | Soaked into ground |  | Y | N | N
972858 | Fax 571-6972 | 01/26/98 16:10 | L.Finch | 6544160 | City of San Diego | 01/26/98 12:40 | 01/26/98 13:30 | 150 | 100 | 1694 Main St. | San Diego | SD | 92113 | 6" CP | One | Rocks | Rocks | Clean area and re-evaluate cleaning schedule | Y | N | Vactored street | San Diego Bay |  | Y | N | N
973179 | Fax 571-6972 | 01/27/98 15:30 | L.Finch | 6544160 | City of San Diego | 01/27/98 13:56 | 01/27/98 14:40 | 88 | 0 | 21st St. & F St. | San Diego | SD | 92102 | 6" CP | Two | Debris | Rags and paper | Re-evaluation main and MC site | Y | Y | Storm Drain | San Diego Bay | Dissipated in storm drain | Y | N | N
973995 | Fax 571-6972 | 01/30/98 10:15 | L.Davis | 6544160 | City of San Diego | 01/30/98 07:15 | 01/30/98 07:30 | 60 | 0 | Mercury Ct. & Mercury Dr.** | San Diego | SD | 92111 | Manhole | One | Other | Pump station failure | Referred to an electrician for repairs | Y | Y | San Clemente Canyon | Rose Creek |  | Y | N | N
974119 | Fax 571-6972 | 01/31/98 09:05 | M.Bedard | 6544160 | City of San Diego | 01/30/98 18:45 | 01/31/98 01:00 | 2505 | 480 | Roselle St. & Sorrento Valley Bl.** | San Diego | SD | 92121 | SPS 65 force main | Two | Construction | Sewer plug lost seal causing leak | Vactor flow/shut down SPS 65 | Y | Y | Storm Drain | Pacific Ocean |  | Y | Y | N
974463 | Fax 571-6972 | 02/01/98 17:39 | D.Branco | 6544160 | City of San Diego | 02/01/98 09:29 | 02/01/98 12:55 | 412 | 0 | 2757 K St. | San Diego | SD | 92102 | 6" CP | One | Grease | Grease | Machine rodded/referred to area supervisor for scheduled PM | Y | Y | Storm Drain | San Diego Bay/Pacific Ocean |  | Y | N | N
974710 | Fax 571-6972 | 02/02/98 22:34 | J.Wilder | 6544160 | City of San Diego | 02/02/98 15:20 | 02/02/98 16:55 | 380 | 0 | 5884 Madra Av. | San Diego | SD | 92120 | 8" VC | One | Roots | Roots | Rodded main to clean section | N | N | Soaked into hillside | N/A | Soaked into hillside | Y | N | N
975031 | Fax 571-6972 | 02/03/98 19:07 | J.Wilder | 6544160 | City of San Diego | 02/03/98 15:17 | 02/03/98 16:44 | 44 | 10 | 4120 Hillandale Rd. | San Diego | SD | 92116 | 8" VC | One | Roots | Roots | Rodded main/refer for further cleaning | Y | Y | Backyard | N/A | Backyard & vacuumed at gutter | Y | N | N
975210 | Fax 571-6972 | 02/04/98 15:30 | G.Richardson | 6544160 | City of San Diego | 02/04/98 10:00 | 02/04/98 11:00 | 12 | 0 | Baja Dr. & Tierra Baja Wy. | San Diego | SD | 92115 | 6" CP | One | Roots | Roots | Rodded to relieve stop | Y | N | Canyon | Pacific Ocean | Dissipated in canyon | Y | N | N
975167 | Fax 571-6972 | 02/04/98 14:00 | L.Finch | 6544160 | City of San Diego | 02/04/98 08:11 | 02/04/98 09:10 | 680 | 500 | Rosecrans St. & Zola St. | San Diego | SD | 92133 | 8" CP | One | Debris | Paper towels and other debris | Machine rodded main/adding to MC site | Y | Y | Storm Drain | San Diego Bay/Pacific Ocean |  | Y | N | Y | Three
975544 | Fax 571-6972 | 02/06/98 04:53 | M.Whelan | 6544160 | City of San Diego | 02/05/98 18:07 | 02/05/98 20:15 | 6400 | 3800 | 8228 San Vicente St. | San Diego | SD | 92114 | 10" VC | Two | Roots | Roots and grease in main | Rod main and flushed section | Y | Y | Canyon | Jamacha Creek bed |  | Y | Y | N
975844 | Fax 571-6972 | 02/07/98 15:38 | D.Branco | 6544160 | City of San Diego | 02/07/98 13:28 | 02/07/98 14:35 | 34 | 0 | 3912 Lomaland Dr. | San Diego | SD | 92106 | 8" VC | One | Roots | Roots | Machine rod/refer to area supervisor for scheduled maintenance | N | N | Seepage around manhole |  | Dried up around manhole | Y | N | N
975987 | Fax 571-6972 | 02/10/98 04:59 | M.Whelan | 6544160 | City of San Diego | 02/09/98 17:22 | 02/09/98 19:00 | 980 | 800 | 1010 W. San Ysidro Bl. | San Diego | SD | 92173 | 8" VC | One | Grease | Grease | Flush main to remove grease | N | N | None | None | Soaked up along I-5 | Y | Y | N
978151 | Fax 571-6972 | 02/10/98 14:45 | G.Himaka | 6544160 | City of San Diego | 02/07/98 15:00 | 02/09/98 14:15 | 950 | 0 | 5240 Convoy St. (Metro Biosolids Center) | San Diego | SD | 92123 | 4" blow-off valve | One | Construction | 4" blow-off valve left open | Closed valve/initiating clean up | Y | N | San Clemente Canyon | N/A | Canyon floor | Y | N | N
975913 | Fax 571-6972 | 02/09/98 15:30 | W.Payne | 6544160 | City of San Diego | 02/09/98 10:34 | 02/09/98 10:39 | 250 | 0 | 4605 Huron Av./canyon | San Diego | SD | 92117 | 8" VC | Two | Grvty Mn Brk | Major flooding of dirt storm channel | Replace VC pipe with PVC pipe | Y | Y | Mission Bay | Pacific Ocean |  | Y | N | Y | Unknown
975957 | Fax 571-6972 | 02/09/98 13:00 | J.McPherson | 6544160 | City of San Diego | 02/08/98 12:00 | 02/09/98 08:00 | 1200 | 0 | 11388 Sorrento Valley Rd. | San Diego | SD | 92121 | 2" air valve | One | Debris | Debris | Put air valve on regular maintenance program | Y | Y | Penasquitos Lagoon | Pacific Ocean |  | Y | Y | N
976079 | Fax 571-6972 | 02/10/98 13:30 | L.Finch | 6544160 | City of San Diego | 02/10/98 05:44 | 02/10/98 09:00 | 3920 | 0 | 2648 E St./alley north | San Diego | SD | 92102 | 6" CP | One | Construction | Construction debris | Cleaned main/advised contractor to trap better & keep traps clean | Y | Y | Storm Drain | San Diego Bay |  | Y | Y | N
976074 | Fax 571-6972 | 02/10/98 04:30 | M.Bedard | 6544160 | City of San Diego | 02/09/98 21:15 | 02/10/98 03:10 | 17750 | 0 | Murray Ridge Rd. & Fireside Av./canyon | San Diego | SD | 92123 | 10" VC | One | Other | Rain washed out manhole cone/rocks in main | Hand rod main/cleaned base of manhole/rebuild manhole | Y | N | Murray Canyon Creek | San Diego River | Pacific Ocean at Dog Beach | Y | Y | N
975877 | Fax 571-6972 | 02/11/98 14:00 | J.McPherson | 6544160 | City of San Diego | 02/08/98 15:25 | 02/10/98 09:00 | 24955 | 0 | I-805 & Railroad Tracks @ Rose Canyon | San Diego | SD | 92122 | 15" VC | One | Surcharge | Line surcharge | Will investigate to find out problem & correct | Y | Y | Rose Canyon/Mission Bay | Pacific Ocean |  | Y | Y | N
976068 | Fax 571-6972 | 02/17/98 08:00 | W.Payne | 6544160 | City of San Diego | 02/09/98 20:10 | 02/10/98 12:00 | 23500 | 0 | 1000 Van Nuys St./canyon | San Diego | SD | 92109 | 8" VC | One | Grvty Mn Brk | Rains washed out pipe causing rocks in main | Repaired main/pumped & cleaned ponded areas back into system | Y | Y | Van Nuys Canyon | Storm Drain | Pacific Ocean | Y | Y | N
978158 | Fax 571-6972 | 02/14/98 19:33 | M.Bedard | 6544160 | City of San Diego | 02/14/98 15:00 | 02/14/98 15:10 | 50 | 50 | 2211 Avenida de la Playa** | San Diego | SD | 92037 | SPS 27 | One | Power Outage | Power outage caused by storm | Power returned and spill vacuumed up; area hosed & cleaned | N | N | Parking garage | Tennis Club |  | Y | N | N
977247 | Fax 571-6972 | 02/17/98 15:05 | W.Graham | 6544160 | City of San Diego | 02/17/98 07:30 | 02/17/98 08:00 | 150 | 0 | 18700 W. Bernardo Dr.** | San Diego | SD | 92128 | SPS 77 | One | Other | Station shut down per Hale Treatment Plant | Turn station back on | Y | N | Creek | Lake Hodges |  | Y | N | Y | Unknown
977424 | Fax 571-6972 | 02/19/98 09:30 | G.Richardson | 6544160 | City of San Diego | 02/18/98 13:41 | 02/18/98 14:10 | 10 | 10 | 4121 Camino del Rio S. | San Diego | SD | 92115 | 8" VC | One | Debris | Debris | Flushed to relieve stop. Flushed main for city protection | Y | N | Pavement at manhole 231 | N/A | Recovered by Vactor | Y | N | N
977344 | Fax 571-6972 | 02/18/98 07:30 | M.Bedard | 6544160 | City of San Diego | 02/17/98 15:09 | 02/18/98 04:30 | 120150 | 0 | 9255 Camino Santa Fe | San Diego | SD | 92121 | 21" CI & VC | Two | Grvty Mn Brk | Deteriorated 21" CI pipe caused rocks in line | Contain overflow/make repairs/line previously submitted for repairs | Y | N | Creek | Penasquitos Lagoon | Pacific Ocean | Y | Y | N
977532 | Fax 571-6972 | 02/19/98 10:15 | M.Whelan | 6544160 | City of San Diego | 02/18/98 17:28 | 02/18/98 18:58 | 900 | 0 | Herbert Pl. & Pennsylvania Av. | San Diego | SD | 92103 | 8" VC | One | Roots | Roots growing into manhole 593 | Hand rod main/cleaned channels in manhole/refer to manhole crew | Y | N | Canyon | Unknown |  | Y | Y | N
977660 | Fax 571-6972 | 02/25/98 09:00 | W.Payne | 6544160 | City of San Diego | 02/16/98 22:00 | 02/18/98 10:05 | 43300 | 0 | 4605 Huron Av./canyon | San Diego | SD | 92117 | 8" VC/PVC | Three | Grvty Mn Brk | Flood damage due to heavy rains | Re-connect 8" PVC to 8" VC main/sandbag to protect until rains stop. | Y | Y | Mission Bay | Pacific Ocean |  | Y | Y | N
977272 | Fax 571-6972 | 02/19/98 10:00 | R.Parker | 6544160 | City of San Diego | 02/17/98 17:34 | 02/18/98 16:04 | 27000 | 3600 | 1000 Van Nuys St./canyon | San Diego | SD | 92109 | 8" VC | Two | Grvty Mn Brk | Line washed away causing rocks in pipe | Rodded main and made repairs | Y | Y | Van Nuys Canyon creek/Storm Drain | Pacific Ocean |  | Y | Y | Y | Unknown
977216 | Fax 571-6972 | 02/19/98 09:00 | R.Parker | 6544160 | City of San Diego | 02/17/98 08:00 | 02/18/98 08:00 | 36000 | 0 | I-805 & Railroad Tracks @ Rose Canyon | San Diego | SD | 92122 | 15" VC | Two | Surcharge | Infiltration inside 15" VC sewer main | Find points of infiltration and plug | Y | Y | Rose Creek & I-805 to Mission Bay | Mission Bay/Pacific Ocean |  | Y | Y | Y | Unknown
978353 | Fax 571-6972 | 02/24/98 12:00 | R.Parker | 6544160 | City of San Diego | 02/20/98 10:30 | 02/20/98 17:30 | 10500 | 0 | I-805 & Railroad Tracks @ Rose Canyon | San Diego | SD | 92122 | 15" VC | Three | Surcharge | Infiltration inside 15" VC sewer main | Find points of infiltration and flow to stop inflow | Y | Y | Rose Creek to Mission Bay | Mission Bay/Pacific Ocean |  | Y | Y | Y | Unknown
977994 | Fax 571-6972 | 02/21/98 13:00 | J.Oropeza | 6544160 | City of San Diego | 02/21/98 10:28 | 02/21/98 11:50 | 82 | 0 | 7590 Windy Ridge Rd. | San Diego | SD | 92126 | 8" PVC | One | Other | Sand & Rocks | Refer to area supervisor to possibly add to PM schedule | N | Y | Storm drain | Los Penasquitos Canyon Preserve | Soaked into canyon | Y | N | N
978008 | Fax 571-6972 | 02/21/98 17:35 | J.Oropeza | 6544160 | City of San Diego | 02/21/98 14:40 | 02/21/98 16:00 | 80 | 30 | 3504 La Cima Dr. | San Diego | SD | 92109 | 8" VC | One | Roots | Heavy grease and roots | Refer to area supervisor to add to PM site | Y | Y | Storm drain | Mission Bay | Mission Bay/Storm Drain | Y | N | Y | Unknown
978363 | Fax 571-6972 | 02/24/98 14:00 | R.Parker | 6544160 | City of San Diego | 02/24/98 08:30 | 02/25/98 08:00 | 35250 | 0 | I-805 & Railroad Tracks @ Rose Canyon | San Diego | SD | 92122 | 15" VC | Four | Surcharge | Infiltration inside 15" VC | Find points of infiltration and repair to stop inflow | Y | Y | Rose Creek to Mission Bay | Mission Bay to Pacific Ocean |  | Y | Y | Y | Unknown
978992 | Fax 571-6972 | 02/27/98 10:19 | M.Dawson | 6544160 | City of San Diego | 02/27/98 07:26 | 02/27/98 08:56 | 90 | 0 | Chamoune Av. & Dwight St. | San Diego | SD | 92105 | 6" CP | One | Grease | Grease | Flushed to relieve stop/referred to FEWD | N | Y | Storm Drain | Chollas Creek | San Diego Bay | Y | N | N
979415 | Fax 571-6972 | 02/28/98 13:56 | D.Branco | 6544160 | City of San Diego | 02/28/98 10:29 | 02/28/98 14:21 | 116 | 0 | 4236 Venus St. | San Diego | SD | 92110 | 8" VC | One | Grvty Mn Brk | Main collapsed cuasing system to back-up | Repaired collapsed main | Y | Y | Storm Drain | San Diego River/Pacific Ocean |  | Y | N | N
979557 | Fax 571-6972 | 03/02/98 14:00 | G.Richardson | 6544160 | City of San Diego | 03/02/98 12:46 | 03/02/98 13:03 | 85 | 0 | Altadena Av. & Wightman St. | San Diego | SD | 92105 | 8" VC | One | Grease | Grease | Rodded main to relieve stop | Y | Y | Storm Drain | Chollas Creek | San Diego Bay | Y | N | N
979589 | Fax 571-6972 | 03/03/98 05:55 | M.Whelan | 6544160 | City of San Diego | 03/02/98 14:31 | 03/02/98 19:30 | 224 | 0 | 6471 Norman Ln. | San Diego | SD | 92120 | 8" VC | One | Roots | Roots | Clean main to clear roots | N | N | None | Soaked into hillside |  | Y | N | N
979598 | Fax 571-6972 | 03/03/98 09:00 | G.Richardson | 6544160 | City of San Diego | 03/02/98 15:31 | 03/02/98 17:31 | 120 | 0 | 1137 31st St. | San Diego | SD | 92102 | 8" VC | One | Roots | Roots, grease and debris in main | Rodded to relieve stop | Y | N | Ground at spill site | N/A | Soaked into dirt at site | Y | N | N
979929 | Fax 571-6972 | 03/04/98 15:00 | L.Davis | 6544160 | City of San Diego | 03/04/98 06:59 | 03/04/98 08:30 | 4500 | 1500 | 6449 Bell Bluff Av. | San Diego | SD | 92123 | 12" VC | One | Roots | Roots and rocks in the main | Bucketing main to remove rocks/putting main on 36 month PM schedule | Y | Y | Storm Drain | Pond area | Pond area | Y | Y | Y | Unknown
980102 | Fax 571-6972 | 03/05/98 15:15 | G.Richardson | 6544160 | City of San Diego | 03/04/98 10:49 | 03/04/98 17:50 | 432000 | 9000 | Kostner Av. & Marge Wy. | San Diego | SD | 91911 | 8" VC | One | Grvty Mn Brk | Storm Drain failure | Referred to construction for repairs | Y | Y | Storm Drain | Tijuana River | Pacific Ocean | Y | N | Y | One
980448 | Fax 571-6972 | 03/06/98 06:00 | M.Whelan | 6544160 | City of San Diego | 03/05/98 18:34 | 03/05/98 22:04 | 315 | 0 | 4036 S. Hampstead Cir. | San Diego | SD | 92116 | 6" CP | One | Grease | Grease | Rod section to relieve stop. Rod to clean section | Y | Y | Storm Drain | Soaked into ground in canyon |  | Y | N | N
980624 | Fax 571-6972 | 03/07/98 13:11 | D.Branco | 6544160 | City of San Diego | 03/07/98 10:38 | 03/07/98 11:19 | 20 | 0 | 4400 Del Monte Av. | San Diego | SD | 92107 | 6" CP | One | Grease | Grease | Flushed main/referred to area supervisor for scheduled maintenance | N | N | Dried up in street | N/A | Dried up in street | Y | N | N
980652 | Fax 571-6972 | 03/07/98 18:55 | D.Branco | 6544160 | City of San Diego | 03/07/98 16:46 | 03/07/98 17:40 | 108 | 0 | 6170 Dunant St. | San Diego | SD | 92122 | 8" VC | One | Grease | Grease | Flushed main/referred to area supervisor for scheduled maintenance | Y | Y | Storm Drain | Rose Canyon/Mission Bay |  | Y | N | N
980700 | Fax 571-6972 | 03/09/98 11:30 | R.Parker | 6544160 | City of San Diego | 03/09/98 06:07 | 03/09/98 09:00 | 865 | 0 | David St. & Ulric St./on Ulric s/o David | San Diego | SD | 92111 | 18" VC | One | Other | Sludge build-up caused back-up | Flushed main/possibly place on scheduled maintenance | Y | Y | Storm Drain | San Diego River/Pacific Ocean |  | Y | N | Y | Unknown
980706 | Fax 571-6972 | 03/09/98 07:51 | L.Davis | 6544160 | City of San Diego | 03/09/98 07:44 | 03/09/98 09:00 | 380 | 100 | Lake Murray Bl. & Lynn Haven Ln. | San Diego | SD | 92119 | 8" VC | One | Roots | Roots and grease | Machine flushed, cleaned up spill site | Y | Y | Storm Drain | Trench in canyon | Soaked into open trench | Y | N | N
980722 | Fax 571-6972 | 03/11/98 09:00 | W.Payne | 6544160 | City of San Diego | 03/09/98 12:00 | 03/09/98 12:36 | 3600 | 3400 | 4177 Mt Ashmun Dr. | San Diego | SD | 92111 | 15"VC | One | Grvty Mn Brk | Soil erosion caused rocks to break main | Pipe repaired and backfilled | Y | N | Tecolote Creek |  |  | Y | Y | N
981292 | Fax 571-6972 | 03/12/98 08:40 | L.Finch | 6544160 | City of San Diego | 03/11/98 09:16 | 03/11/98 15:00 | 516 | 450 | 4279 Pacific Hy./RR tracks east | San Diego | SD | 92110 | 8" VC | One | Grease | Grease | Add to 36 month cleaning schedule | N | N | San Diego Bay | Pacific Ocean | Soaked into ground | Y | N | N
981068 | Fax 571-6972 | 03/12/98 14:15 | R.Parker | 6544160 | City of San Diego | 03/05/98 09:00 | 03/12/98 12:35 | 122360 | 21840 | 7970 Sevan Ct./canyon | San Diego | SD | 92123 | 8" VC | One | Grvty Mn Brk | Heavy rains exposed pipe/heavy rocks falling | Rodded and repaired main | Y | Y | Storm Drain | Murray Canyon/ San Diego River/ Pacific Ocean |  | Y | Y | Y | Unknown
981490 | Fax 571-6972 | 03/12/98 13:10 | G.Richardson | 6544160 | City of San Diego | 03/12/98 10:55 | 03/12/98 12:02 | 134 | 0 | 2282 Leighton Ct. | San Diego | SD | 92139 | 8" VC | One | Roots | Roots and grease | Rodded main to relieve stop | Y | Y | Storm Drain | N/A | Dissipated in Storm Drain | Y | N | N
981601 | Fax 571-6972 | 03/13/98 05:48 | M.Whelan | 6544160 | City of San Diego | 03/12/98 18:39 | 03/12/98 21:39 | 540 | 300 | 4403 Cynthia Pl. | San Diego | SD | 92105 | 8" VC | One | Grvty Mn Brk | Main break caused by roots in main | Flushed and rodded main/need to repair pipe | Y | Y | Drainage ditch | Storm channel |  | Y | N | N
981687 | Fax 571-6972 | 03/13/98 11:20 | L.Davis | 6544160 | City of San Diego | 03/13/98 08:50 | 03/13/98 09:15 | 300 | 0 | 10265 Pinetree Dr. | San Diego | SD | 92131 | 8" VC | One | Roots | Root build-up | Cleaned manhole and easement/place on scheduled maintenance | Y | Y | Storm Drain | Drainage Ditch |  | Y | N | Y | Unknown
981702 | Fax 571-6972 | 03/14/98 17:45 | M.Bedard | 6544160 | City of San Diego | 03/13/98 08:39 | 03/13/98 20:30 | 4838 | 0 | Cottontail Ln. & Deer Hill Ct./canyon rear | San Diego | SD | 92037 | 8" VC | One | Grvty Mn Brk | Landslides caused section of pipe to break | Replace broken sections | Y | Y | Canyon | Storm Drain | Pacific Ocean | Y | Y | Y | Unknown
982004 | Fax 571-6972 | 03/15/98 15:00 | D.Branco | 6544160 | City of San Diego | 03/14/98 22:55 | 03/15/98 12:30 | 8150 | 0 | 7970 Sevan Ct./canyon | San Diego | SD | 92123 | 8" VC | Two | Grvty Mn Brk | Rocks, roots and debris in main | Flushed and rodded main/refer to construction and TV section | Y | Y | San Diego River/Pacific Ocean |  |  | Y | Y | Y | Unknown
982018 | Fax 571-6972 | 03/16/98 02:39 | M.Bedard | 6544160 | City of San Diego | 03/15/98 18:37 | 03/16/98 01:00 | 19150 | 0 | 3455 Landis St. | San Diego | SD | 92104 | 15" VC | One | Vandalism | Vandalism-rocks, debris, mattress in manhole | Removed debris/lock down and seal manholes in area | Y | Y | Chollas Creek | San Diego Bay |  | Y | Y | N
982022 | Fax 571-6972 | 03/16/98 14:30 | G.Richardson | 6544160 | City of San Diego | 03/16/98 06:32 | 03/16/98 10:32 | 240 | 0 | 35th St. & Landis St. | San Diego | SD | 92104 | 8" CP | One | Roots | Roots | Rodded main to relieve stop | Y | N | Ground at spil site | N/A | Soaked into canyon | Y | N | N
982116 | Fax 571-6972 | 03/16/98 14:55 | M.Bedard | 6544160 | City of San Diego | 03/16/98 08:00 | 03/16/98 08:32 | 450 | 450 | Cottontail Ln. & Deer Hill Ct./canyon rear | San Diego | SD | 92037 | 8" VC | One | Other | Bypass pumping temporarily failed | Set up additional measures to by-pass pump | Y | Y | Storm Drain | Canyon Creek | Storm Drain/open manhole | Y | N | N
982375 | Fax 571-6972 | 03/17/98 15:00 | L.Davis | 6544160 | City of San Diego | 03/17/98 09:45 | 03/17/98 13:30 | 113 | 0 | 8355 Aero Dr. | San Diego | SD | 92123 | MH 151 on 8" VC | One | Roots | Roots | Area will be added to MC site | Y | N | Canyon | Soaked into canyon |  | N | N | N
983574 | Fax 571-6972 | 03/20/98 21:53 | D.Branco | 6544160 | City of San Diego | 03/20/98 16:11 | 03/20/98 20:41 | 1350 | 0 | 3300 Euclid Av. | San Diego | SD | 92105 | 8" VC | One | Roots | Roots | Hand rodded main/refer to area supervisor for PM maintenance | Y | N | Soaked into canyon floor | San Diego Bay/Pacific Ocean |  | Y | Y | N
983589 | Fax 571-6972 | 03/20/98 21:57 | D.Branco | 6544160 | City of San Diego | 30/20/98 18:04 | 30/20/98 20:15 | 131 | 0 | 2362 Hartford St. | San Diego | SD | 92110 | 8" VC | One | Roots | Roots | Flushed main/refer to area supervisor for scheduled PM maintenance | N | Y | Storm Drain | Interceptor I-2 |  | Y | N | N
983739 | Fax 571-6972 | 03/22/98 11:10 | D.Branco | 6544160 | City of San Diego | 03/22/98 08:38 | 03/22/98 09:33 | 550 | 0 | College Av. & Lance St. | San Diego | SD | 92120 | 8" VC | One | Roots | Roots | Rodded main/refer to area supervisor to review cleaning schedule | Y | Y | Storm Drain | San Diego River/Pacific Ocean |  | Y | N | N
983776 | Fax 571-6972 | 03/31/98 11:00 | G.Richardson | 6544160 | City of San Diego | 03/23/98 10:18 | 03/23/98 16:35 | 3770 | 0 | 2915 39th St. | San Diego | SD | 92105 | 8" VC | One | Other | Possible main break/rocks & dirt in main | Rodded to relieve overflow/refer to construction and TV sections. | Y | N | Canyon | Chollas Creek | San Diego Bay | Y | Y | Y | Three
983849 | Fax 571-6972 | 03/23/98 10:30 | E.Semo | 6544160 | City of San Diego | 03/23/98 09:18 | 03/23/98 10:12 | 112 | 0 | 4836 Mt. Frissell Dr. | San Diego | SD | 92117 | 8" VC | One | Grease | Grease | Rod main/add to flush PM schedule | Y | Y | Storm Drain | Pacific Ocean |  | Y | N | N
984173 | Fax 571-6972 | 03/25/98 04:37 | M.Whelan | 6544160 | City of San Diego | 03/24/98 16:47 | 03/24/98 17:52 | 33 | 0 | 1740 Midvale Dr. | San Diego | SD | 92105 | 8" VC | One | Debris | Debris | Rodded and flushed main/vacummed overflow | Y | Y | Storm Drain | Storm Drain |  | Y | N | N
984850 | Fax 571-6972 | 03/29/98 16:31 | D.Branco | 6544160 | City of San Diego | 03/29/98 13:33 | 03/29/98 14:20 | 470 | 0 | 65th St. & Benson Av. | San Diego | SD | 92114 | 8" VC | One | Grease | Grease | Machine rodded/refer to area supervisor for scheduled PM maintenance | Y | Y | Storm Drain | San Diego Bay/Pacific Ocean |  | Y | N | N
985129 | Fax 571-6972 | 03/31/98 11:00 | G.Richardson | 6544160 | City of San Diego | 03/31/98 08:39 | 03/31/98 09:51 | 3600 | 0 | 555 Cadman St. | San Diego | SD | 92114 | 8" VC | One | Other | Possible main break | Rodded main/refer to construction and TV sections | Y | N | Creek in canyon | Chollas Creek | San Diego Bay | Y | Y | Y | One
985240 | Fax 571-6972 | 03/31/98 20:50 | R.Parker | 6544160 | City of San Diego | 03/31/98 14:30 | 03/31/98 18:38 | 248 | 0 | Paseo Bonita & Rutgers Rd./canyon | San Diego | SD | 92037 | 8" VC | One | Roots | Roots | Hand rodded manhole to relieve stop | Y | Y | Van Nuys Canyon | Storm Drain/Pacific Ocean |  | Y | N | N
978023 | Faxed | 1/2/1998 1545 | Lance Lauricha | 738-4347 | City of Escondido | 1998-01-02 08:00 | 1/2/98 1500 | 480 gallons | 30 gallons | 1026 E. 5th. Ave. | Escondido | SD | 92026 | Private cleanout | 0 | Unknown | Unknown-Private clean-out | Sewer Dept. cleared the stoppage and installed a cap. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | N | N | N/A | No samples taken.
978024 | Quarterly Report only | N/A | Don Keifer | 741-4668 | City of Escondido | 1/11/98 1400 | 1/11/98 1600 | 120 Gallons | 120 Gallons | 701 E. 7th. Ave. | Escondido | SD | 92025 | Private cleanout | Unknown | Unknown | Unknown-Private clean-out | Property owner cleared stoppage. City sewer crew cleared the area of wastewater debris. | N | N | N/A | N/A | Recovered | N | N | N | N/A | No samples taken.
978025 | Quarterly Report only | N/A | Don Keifer | 741-4668 | City of Escondido | 1/12/98 930 | 1/12/98 1000 | 30 Gallons | 0 | Aldergrove Pl. and Andreason St. | Escondido | SD | 92025 | Manhole, Sewer Atlas Page 384 MH. 4300 | 0 | Roots | Roots in manhole caused stoppage. | Manhole was put on a root inspection schedule. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | N | N | N | N/A | No samples taken.
978026 | Quarterly Report only County Health was notified. | 1/17/98 1130 | Todd Anderson | 741-4668 | City of Escondido | 1/16/98 2100 | 1/17/98 900 | 760 Gallons | 25 Gallons | Jesmondene Park | Escondido | SD | 92025 | Waste water storage tank | 0 | Tank overflowed due to stuck urinal valve. | Same as short description. | Valve was repaired, effected area was vacuumed and disinfected. Signs were posted. | N | N/A | N/A | N/A | Grass area | Y | N | Y | Two | No samples taken.
978027 | Faxed and Called | 1/20/98 1045 | Todd Anderson | 738-4347 | City of Escondido | 1/20/98 735 | 1/20/98 835 | 12,000 Gallons | 200 Gallons | 1800 Block Citricado Pkwy. | Escondido | SD | 92025 | Manhole, Sewer Atlas Page 444 MH. 3977 | 0 | Roots and Grease | Roots and grease formed stoppage in main line causing it to back-up and overflow. | This is an easement line and has been recommended for replacement. | Y | Y | Did not reach surface waters. | N/A | Open field | Y | Y | Y | Two | No samples taken.
978028 | Quarterly Report only County Health was notified. | 1/30/98 1055 | Todd Anderson | 741-4854 | City of Escondido | 1/30/98 1050 | 1/30/98 1055 | 125 Gallons | 50 Gallons | 1564 Tanglewood | Escondido | SD | 92025 | Manhole, Sewer Atlas Page 426 MH. 5803 | 1 | Roots | Stoppage could have formed due to roots in main line and manhole. | Roots were removed and main lines were cleaned. Televising of main revealed no major structural problem. | Y | Y | Open culvert then to soil. | N/A | N/A | Y | N | Y | Two | No samples taken.
978029 | Quarterly Report only County Health was notified. | 2/11/98 800 | Lance Lauricha | 738-4347 | City of Escondido | 2/7/98 800 | 2/10/98 1700 | 625 Gallons | 25 Gallons | 520 W. Grand Ave. | Escondido | SD | 92025 | Private cleanout | 0 | Unknown | Unknown-Private clean-out | Plumber cleared private blockage. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | N | N | N/A | No samples taken.
978030 | Quarterly Report only County Health was notified. | 2/13/98 930 | Todd Anderson | 738-4347 | City of Escondido | 2/13/98 930 | 2/13/98 1000 | 30 Gallons | 0 | Amarillo and Brotherton | Escondido | SD | 92025 | Manhole, Sewer Atlas Page 468 MH. 4617 | 0 | Grease | Grease blockage in main line. | Continue routine maintenance. | Y | Y | Storm system | Felectia Creek | Lake Hodges | Y | N | N | N/A | No samples taken.
978031 | Quarterly Report only County Health was notified. | 2/14/98 1930 | Julius Turner | 741-4854 | City of Escondido | 2/14/98 1215 | 2/14/98 1630 | 1,275 Gallons | 1,000 Gallons | 729 Chestnut St. | Escondido | SD | 92029 | Overflowing from private clean-out | 0 | Debris | Debris in main line caused waste water to backup into private system resulting in an overflow. | Cleaned main line and continue routine maintenance. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | N | N | N/A | No samples taken.
978032 | Quarterly Report only County Health was notified. | 2/18/98 1430 | John Vaught | 738-4323 | City of Escondido | 2/18/98 700 | 2/18/98 745 | 90 Gallons | 0 | 1564 Tanglewood | Escondido | SD | 92025 | Manhole, Sewer Atlas Page 426 MH. 5803 | 2 | Construction Debris | Some how sand and mud entered the system causing system to back-up. | Cleared blockage, cleaned effected lines as well as C.C.T.V. inspection. The Field inspector was notified. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | N | Y | Three | No samples taken.
978033 | Quarterly Report only County Health was notified. | 3/4/98 1430 | Todd Anderson | 741-4854 | City of Escondido | 3/4/98 1215 | 3/4/98 1223 | 375 Gallons | 0 | 1564 Tanglewood | Escondido | SD | 92025 | Manhole, Sewer Atlas Page 426 MH. 5803 | 3 | Unknown | We suspect that a contractor discharged a large amount of waste water in to our system over taxing it. The Field Inspector was notified and is conducting the investigation. Once again the main lines were televised. No problems were found. | The contractor is being watched! We are also keeping a close eye on this manhole and main line. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | N | Y | two | No samples taken.
978034 | Quarterly Report only County Health was notified. | 3/9/98 945 | Lance Lauricha | 839-4347 | City of Escondido | 3/9/98 807 | 3/9/98 900 | 300 Gallons | 25 Gallons | 1050 Rocksprings | Escondido | SD | 92025 | Private cleanout | 0 | Grease | Grease blockage in apartment service lateral. | Property owner is having a plumbing firm clean all their service laterals. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | N | Y | two | Samples were taken.
978035 | Quarterly Report only | 3/12/98 1315 | Lance Lauricha | 839-4347 | City of Escondido | 3/12/98 1300 | 3/12/89 1530 | 25 Gallons | 0 | 112 S. Grape St. | Escondido | SD | 92026 | Private cleanout | 0 | Roots | Service lateral blocked with roots. | Private system. | N | N | N/A | N/A | N/A | N | N | N | N/A | No samples taken.
978036 | Called and Faxed | 3/17/98 1500 | Lance Lauricha | 839-4347 | City of Escondido | 3/16/98 700 | 3/17/98 1230 | 1,860 Gallons | 500 Gallons | 1236 (A and B) Simpson Way | Escondido | SD | 92025 | Private cleanout | 0 | Rags and toilet paper | Same as short description. | We advised them to clean their system once a year. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | Y | Y | Three | Samples were taken.
978037 | Called and Faxed | 3/18/98 1834 | Lance Lauricha | 839-4347 | City of Escondido | 3/18/98 1834 | 3/18/98 2040 | 1,800 Gallons | 0 | 222Green Ave. | Escondido | SD | 92029 | Manhole, Sewer Atlas Page 449 MH. 5142 | 0 | Grease | Grease blocked main line. | City crew removed stoppage. Will continue routine maintenance. | Y | Y | Kit Carson or Dead Horse Creek | Lake Hodges | Pacific Ocean | Y | Y | Y | Five | Samples were taken.
978038 | Called and Faxed | 3/28/98 1235 | Lance Lauricha | 839-4347 | City of Escondido | 3/28/98 1215 | 3/28/98 1340 | 3,150 Gallons | 0 | Lincoln Ave. | Escondido | SD | 92026 | Manhole, Sewer Atlas Page 308 MH.3077 | 0 | Grease | Grease blocked main line. | City crew removed stoppage. Will continue routine maintenance. Pretreatment Inspector was notified concerning the grease problem. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | Y | Y | Three | Samples were taken.
978039 | Quarterly Report only | 3/30/98 1848 | Jim Miller | 839-4347 | City of Escondido | 3/30/1998 1848 | 3/30/98 2040 | 40 Gallons | 20 Gallons | Mission at Centre City Pkwy. | Escondido | SD | 92026 | Private cleanout | 0 | Roots and Grease | Private system. | Advised property manager to perform preventive maintenance. | N | N | N/A | N/A | N/A | N | N | N/A | N/A | No samples taken.
967- 001 | Whitney Ghoram | 1996-08-12 08:20 | Renzo Marin | (714) 837-7050 | El Toro Water District | 1996-08-10 17:45 | 1996-08-10 18:05 | 600 GAL. | 0 GAL. | 25011 El Toro Rd. | Laguna Hills | OR | 92630 | Oso Sta. Wet Well | 1 | State Wide Power Outage and failure of the Transfer Switch. | The Automatic Transfer Switch "Power Sensing Relay" was wired incorrectly, it did not allow the switch to transfer the pumps to the Emergency Power source, leaving the station pumps inoperable. | Rewired "Power Sensing Relay" to prevent failure of the ATS control system. | Y | Y | Storm drain | Aliso creek | OCEAN | Y | N | Y | ? | OCHD placed the warning signs and monitored water quality.
967- 002 | Susan Pease | 1997-02-07 13:30 | Renzo Marin | (714) 837-7050 | El Toro Water District | 1997-02-07 11:20 | 1997-02-07 11:45 | 500 GAL. | 0 GAL. | B - 607 U Avenida Sevilla | Laguna Hills | OR | 92630 | ETWD Atlas page ME-497, MH 14 | 2 | Sticks and rocks. | Sticks and rocks blockage in 6" gravity main line. | Used the Hydrocleaner to break stoppage. Clean up spill and washed down with 4,000 gallons of potable water. Relayed to maintenance crew for routine inspection. | Y | Y | Storm drain | Aliso creek | OCEAN | Y | N | N | N/A | Notified all responsible agencies and mailed discharge report.
967-003 | Laurie Walsh | 1997-12-04 11:15 | Renzo Marin | (714) 837-7050 | El Toro Water District | 1997-12-03 22:34 | 1997-12-03 22:41 | 350 GAL. | 0 GAL. | 25121 Charlinda | Mission Viejo | OR | 92691 | ETWD Freeway Lift station | 3 | Controller power accidentally shut off. | Pumps Controller power circuit was accidentally turned off by contractor. | Reactivated Controller and pumps. Replaced panel key lock. Requested contractor to obtain district approval prior to entering any district facilities. | Y | Y | Aliso Creek | Aliso Creek | OCEAN | Y | N | N | N/A | Notified all responsible agencies and mailed discharge report.
967 -004 | Whitney Ghoram | 1997-12-13 11:55 | Renzo Marin | (714) 837-7050 | El Toro Water District | 1997-12-13 09:15 | 1997-12-13 16:55 | 225,660 GAL. | 94,660 GAL. | 24206 Twig st. and 25121 Charlinda | Mission Viejo | OR | 92691 | 12” Force main and Freeway Sta. MH-5 | 4 | 12” Force main break. | 12" Freeway force main was cracked by tree roots growing around the pipeline. | Performed permanent repairs of pipeline break. Built containment area for sewage spill and recovery. Diluted spill with potable water. Cleaned and wash down area. | Y | Y | Storm drain and Aliso creek | Aliso creek | OCEAN | Y | Y | Y | N/A | Notified all responsible agencies and mailed discharge report.
967 -005 | Paul Richter | 1998-02-23 14:35 | Renzo Marin | (714)837-7050 x217 | El Toro Water District | 1998-02-21 16:00 | 02/22098 | 2525 GAL. | 0 GAL. | Avenida Sevilla Bldg. # 643 (Leisure World) | Laguna Hills | OR | 92630 | ETWD Atlas page MD-498, MH 20 | 4 | Tree roots blockage | Tree roots blockage in 6" line. Roots broke pipeline. | Built spill containment area with sand bags. Used Hydrocleaner to break stoppage. Assessed line condition with TV. Exposed and repaired line break. | Y | Y | Aliso Creek | Aliso creek | OCEAN | Y | N | N | N/A | Notified all responsible agencies and mailed discharge report.
01-978 | No | N/A | N/A | N/A | City of El Cajon | 3/15/98 1245 | 3/15/98 1345 | 35 | 0 | 253 CUYMACA ST. | RUSSEL RD. |  | 92020 | HOUSE/GARAGE | 1 | ROOTS | ROOTS PARTIALLY BLOCKED LINE. | PLACED ON CLEANING SCHEDULE. |  | NO | NO | NO | HOUSE OR GARAGE | NO | NO | NO | N/A | FIRST PROBLEM AT THIS LOCATION
978001 | LINDA PARDY, VOICE MAIL | 1/24/97 0930 | CUSTOMER | NO PHONE | TCWD | 9/24/97 0915 | 1/24/97 1000 | 8000 | 0 | PLANO/ SANTA MARGRETTA | TRABUCO CANYON | OR | 92679 |  | 1 | BLOCKAGE | BLOCKAGE IN BYPASS TO SMWD | UNCLOGGED BLOCKAGE | Y | Y | TRABUCO CREEK | SAN JUAN CREEK | OCEAN | Y | N | Y | 2 HOURS | NONE
978003 | VOICE MAIL-PAUL RICHTOR, FAX | 2/16/98 9:00AM | KRIS HANBERG | 714/858-4979 | TCWD | 2/15/98 5:00AM | 2/16/98 9:00AM | 480000 | 0 | EL TORO/PORTOLA | TRABUCO CANYON | OR | 92679 | EL TORO LIFT STATION | 1 | POWER FAILURE | LOW VOLTAGE RELAY FAILED AND FUSE | LOOKING INTO REDESIGN | Y | Y | ALISO CREEK | OCEAN |  | Y | N | Y | 96 HRS | NONE
APR-JUN, '98
978040 |  |  | Mark Patnode | 760/966-7868 | Water Utilities Dept. City of Oceanside | 04/13/98 0000 | 04/13/98 1645 | 200 | 160 | 3000 Guajome Lake Road | Oceanside | SD | 92057 | Sewer Lateral | 0 | Line Break | "CalTras" Contractor hit 8" private lateral while breaking up the surface of the road. | Spoke with the contractor. They repaired the break. | N | N | N/A | N/A | Contained within the trench line. | N | N | N | N/A | I notified the Park Ranger @ 14/1100Apr98.
978041 |  |  | E.C. Calhoun | 760/966-7868 | Water Utilities Dept. City of Oceanside | 04/15/98 1035 | 04/15/98 1059 | 150 | 0 | 2900 Blk of Fire Mountain Road | Oceanside | SD | 92054 | Manhole | 0 | Roots | Roots, paper towels and wire caught in manhole. | Quarterly rodding schedule | N | Y | N/A | N/A | Soaked into mud & debris in basin. | N | N/A | N | N/A | Was overdue on the rodding schedule. Heavy workload.
978042 |  |  | Jeremy Kemp | 760/966-7868 | Water Utilities Dept. City of Oceanside | 04/21/98 1912 | 04/21/98 2030 | 600 | 0 | 1905 Comanche | Oceanside | SD | 92056 | Manhole | 2 | Grease | Grease built up in the line through the easement. | We have been dropping chlorine in this area to control the grease problem. | N | Y | Storm Drain | Loma Alta Creek | N/A | Y | N/A | N | N/A | Diluted spill with 500 Gallons of fresh water.
978043 | Voice Mail | 04/26/98 1535 | Jeremy Kemp | 760/966-7868 | Water Utilities Dept. City of Oceanside | 04/26/98 1105 | 04/26/98 1240 | 2300 | 0 | Capistrano & San Jose Easement | Oceanside | SD | 92054 | Manhole | 0 | Blockage | Lots of rags in line. | This easement is rodded on quarterly basis. | Y | Y | Storm Drain | San Luis Rey River | N/A | Y | Y | N | N/A | Easement was due next month for quarterly rodding.
978044 |  |  | Jeremy Kemp | 760/966-7868 | Water Utilities Dept. City of Oceanside | 04/26/98 1330 | 04/26/98 1400 | 50 | 0 | Mission & Frontier | Oceanside | SD | 92056 | Manhole | 17 | Line Break | "CalTrans" Contractor broke Drive-Inn Theater lateral last year, and has not gotten around to fixing it. | We use Vactor to remove contents of line every Friday, Saturday, Sunday, & Monday. | N | N | N/A | N/A | Soaked into the ground @ site. | N | N/A | N | N/A | `
978045 |  |  | Jeremy Kemp | 760/966-7868 | Water Utilities Dept. City of Oceanside | 05/17/98 1140 | 05/17/98 1200 | 250 | 0 | Mission & Frontier | Oceanside | SD | 92056 | Manhole | 18 | Line Break | "CalTrans" Contractor broke Drive-Inn Theater lateral last year, and has not gotten around to fixing it. | We use Vactor to remove contents of line every Friday, Saturday, Sunday, & Monday. | N | N | N/A | N/A | Soaked into the ground @ site. | N | N/A | N | N/A | Needs to be fixed, please.
978046 | Voice Mail | 05/31/98 1950 | Jeremy Kemp | 760/966-7868 | Water Utilities Dept. City of Oceanside | 05/31/98 1147 | 05/31/98 1830 | 18000 | 4000 | 770 Capistrano Drive | Oceanside | SD | 92054 | Manholes | 0 | Vandalism | "kids" or "homeless" removed manhole cover and dropped 5 buckets of rocks into the channel. Manhole is in remote easement, down by river. | Supervisor is ordering "locking" manhole covers to be installed, ASAP. | Y | Y | Storm Drain. | San Luis Rey River | N/A | Y | Y | Y | 2 | Posted temporary signs at river mouth. Additional samples were ordered from Lab.
978047 |  |  | Jeremy Kemp | 760/966-7868 | Water Utilities Dept. City of Oceanside | 06/07/98 1300 | 06/07/98 1345 | 300 | 0 | Mission & Frontier | Oceanside | SD | 92054 | Manhole | 20 | Line Break | "CalTrans" Contractor broke Drive-Inn Theater lateral last year, and has not gotten around to fixing it. | We use Vactor to remove contents of line every Friday, Saturday, Sunday, & Monday. | N | N | N/A | N/A | Soaked into the ground @ site. | N | N/A | N | N/A | …Also, yesterday there was a heavy gasoline smell and oil residue in the hole.
978048 |  |  | Norm Crum | 760/966-7868 | Water Utilities Dept. City of Oceanside | 06/18/98 1830 | 06/18-98 1930 | 100 | 0 | 1015 Eucalyptus | Oceanside | SD | 92054 | Manhole | 0 | Grease | Grease build up in City Main. | Site will be ckecked periodically for two weeks. | N | Y | N/A | N/A | Debris in Storm Drain. | N | N/A | N | N/A
02-978 | yes | 6/16/98 1233 | E. Donnelly | 441-1658 | City of El Cajon | 6/15/98 2030 | 6/15/98 2130 | 500 | 0 | 355 S. WESTWIND | EL CAJON | SD | 92020 | CLEANOUT | 1 | ROOTS | ROOT INFILTRATION CAUSED BLOCKAGE | PLACED ON CLEANING SCHEDULE. | NO | NO | NO | NO | ABSORBED IN | YES | NO | NO | N/A | FIRST PROBLEM AT
978011 | Quarterly Report | 05-18-98 1400 | Ted Powell | 760-744-0460 | V.W.D. | 05-18-98 0920 | 05-18-98 0930 | 900 | none | Rancho Santa Fe Rd. | San Marcos | S.D. | 92069 | 8" line | 2 | surcharging | To much flow for in line | Cut flow back to handle peak flows during the day. | n | n | none | none | n/a | y | n | n | 0 | absorbed into ground at M/H
978012 | Quarterly Report | 05-27-98 0830 | Corey Harrell | 760-744-0460 | V.W.D. | 05-23-98 1030 | 05-23-98 1330 | 900 | none | and Broken Rock | San Marcos | S.D. | 92069 | 8" line | 0 | Roots | Roots in line caused overflow | Have added to our trouble spot list. | n | y | Lake San Marcos | none | Stromdrain | y | n | n | 0 | Contained in Strom drain box
| Mr. Chang | 1998-05-06 10:00 | Anne Briggs | (909) 928-3777 | E.M.W.D. | 1998-05-06 08:03 | 1998-05-06 08:26 | 4025 | None | Overland Trail & Redhawk Parkway | Temecula | Riverside | 92590 | Manhole | 3 | Obstruction | Construction Debris - Plastic Sheeting in Pipe | Remove debris from line and will perform inspections of the area to determine source of construction debris | Y | Y | Temecula Creek | Santa Margarita River |  | Y | N | N | N/A | All solids were picked up
978002 | Fax | 1998-04-22 12:00 | Dave Seymour | 9494596540 | Santa Margarita Water District | 1998-04-21 12:00 | 1998-04-21 12:00 | 3000 | 0 | South Bend Road | Coto de Caza | OR | 92679 | Wetwell | 1 | Construction | Contractor illegally pumped out wet well and dumped it onto nearby ground. Found wet area and signs of sewage (plastics and rubber goods). Cleaned up the site. Questioning of employees and pump truck driver failed to reveal who performed the dumping. |  | N | N | None | None | N/A | Y | Y | N | N/A
978003 | Fax | 1998-05-04 11:00 | Dave Seymour | 9494596540 | Santa Margarita Water District | 1998-05-04 06:00 | 1998-05-04 07:45 | 600 | 150 | Seacountry Lane | Rancho Santa Margarita | OR | 92688 | Manhole | 2 | Construction | Construction debris plugged line. |  | Y | Y | Trabuco Creek | None | N/A | Y | Y | N | N/A
978004 | Mail | 1998-05-12 09:00 | Steve Francis | 9494596540 | Santa Margarita Water District | 1998-05-11 16:00 | 1998-05-11 17:00 | 600 | 0 | Vista del Lago | Mission Viejo | OR | 92690 | Manhole | 1 | Roots | Root intrusion into 8" VCP sewer line. | Cut out root ball and removed from sewer line. Area was disinfected with chlorine and washed into manhole. | Y | Y | Storm Drain | Los Alisos Creek | Aliso Beach | Y | Y | N | N/A
978005 | Fax | 1998-06-27 14:00 | Steve Francis | 9494596539 | Santa Margarita Water District | 1998-06-27 12:30 | 1998-06-27 12:50 | 300 | 0 | Puerte de Luz | Mission Viejo | OR | 92691 | Manhole | 1 | Power Failure | Power Failure caused wetwell to fill and overflow before crew could arrive with Vactor. |  | Y | Y | Storm Drain | Los Alisos Creek | Aliso Beach | Y | N | N | N/A
978028 | KATHY STONE-FAX | 4/21/98-3:45 P | PAT GUEVARA | 760-438-2722 | CARLSBAD | 4/17/98-1:00 P | 4/17/98-1:35 P | 100 | 100 | 1860 MARRON RD. | CARLSBAD | SD | 92008 | PRIV. MANHOLE | 1 | GREASE | GREASE TRAP POSSIBLY NOT SERVICED ADEQUATELY | GREASE TRAPS SHOULD BE CHECKED ONCE A WEEK BY RESPONSIBLE PARTY | Y | Y | STORM DRAIN/CULVERT | NONE | VACTOR TRUCK RECOVERED | Y | N | N | N | DISINFECTED AREA.
978029 | N/A | N/A | N/A | N/A | CARLSBAD | 6/8/98-9:45 A | 6/8/98-10:30 A | 5 TO 10 | 5 TO 10 | 380 CHRISTIANSEN | CARLSBAD | SD | 92008 | PRIV. CLEANOUT | 1 | ROOTS |  |  | N | N |  |  |  | N | N | N/A | N/A | DISINFECTED AREA.
978030 | CLAY CLIFTON-PHONE & FAX | 6/10/98-11:15 A | DON WASKO/PAT GUEVARA | 760-438-2722 | CARLSBAD MWD | 6/10/98-9:20 A | 6/10/98-10:10 A | 1500 | 0 | 2805 OCEAN ST. | CARLSBAD | SD | 92008 | 4" SEWER CLEANOUT (2) | 1 | CONSTRUCTION DEBRIS | MAJOR CONSTRUCTION OCCURING ACROSS THE STREET FROM 2805 OCEAN ST.. DEBRIS INCLUDED SOIL, BRICK PIECES, PIPE SCRAPS. | VACTOR TRUCK USED TO CLEAR SEWER MAIN. ENSURE CONSTRUCTION DEBRIS NEVER ENTERS SEWER SYSTEM. | Y | Y | STORM DRAIN | PACIFIC OCEAN | PACIFIC OCEAN/BEACH AREA | Y | Y | Y | 2 | NANCY ANSON W/ENCINA WWA DISPATCHED JEFF PARKS (ENCINA) TO TAKE WATER SAMPLES. SAMPLES PROVED NEGATIVE. SIGNS WERE THEN REMOVED FROM BEACH AREA.
978-013 | SIRT (FAX) | 1998-04-04 | Brad Bruington | 949-831-1070 | Moulton Niguel Water | 1998-04-04 10:00 | 1998-04-04 13:00 | 75000 | 0 | Camino Capistrano/Juniper Serra | San Juan Capistrano | OR | 92675 |  | 2 | Line break/flood damage | Unknown pump or increased sewer flow problem at temporary pump station at Trabuco Creek sewer line break. | More flow diverted above pump station and all pumps checked for proper operation. | Y | N | Trabuco Creek | Pacific Ocan | N/A | Y | Y | Y |  | O.C. Health Dept. handles this
978-014 | SIRT (FAX) | 1998-05-11 11:50 | Brad Bruington | 949-831-1070 | Moulton Niguel Water | 1998-05-11 09:15 | 1998-05-11 10:00 | 40000 | ongoing | Oso Pkwy. & Moulton Pkwy. | Laguna Niguel | OR | 92677 |  | 1 | Construction | Contractor hit/broke a 20" abandoned sewer force main that was full of stagnant water. Stagnant water filled trench and went down flood control catch basin. | Line drained and stagnant water vacuumed up and put into sewer. Line will be repaired. | Y | Y | Aliso Creek | None | N/A | Y | Y | Y |  | O.C. Health Dept. handles this
978-015 | SIRT (FAX) | 1998-05-14 13:00 | Brad Bruington | 949-831-1070 | Moulton Niguel Water | 1998-05-14 09:15 | 1998-05-14 09:30 | 100 | 0 | David Phillips Buick - 24888 Alicia Parkway | Laguna Hills | OR | 92653 | 6" gravity sewer | 1 | Debris, grease, blockage | heavy grease build-up on flat area of gravity sewer line. | Unknown - private sewer - not District's responsibility | Y | Y | Storm drain to Aliso Creek | Pacific Ocean | N/A | Y | N | N
978-016 | SIRT (FAX) | 1998-06-15 16:35 | Brad Bruington | 949-831-1070 | Moulton Niguel Water | 1998-06-15 14:30 | 1998-06-15 16:30 | 9000 | 0 | County regional park - La Paz Road | Laguna Niguel | OR | 92677 | Recycled water line | 1 | Line break | Sprinkler line in regional park broke in stream. | Closed main valves. Line will be repaired. | Y | N | Sulphur Creek/Aliso Creek | Pacific Ocean | N/A | Y | Y | ? |  | O.C. Health Dept. handles this.
978-017 | SIRT (FAX) | 1998-06-25 10:00 | Brad Bruington | 949-831-1070 | Moulton Niguel Water | 1998-06-25 08:00 | 1998-06-25 08:20 | 200 | 0 | Moulton Pkwy. & Crown Valley Pkwy. | Laguna Niguel | OR | 92677 |  | 1 | Grease, blockage | Partial blockage of 8" sewer - cause unknown | Line jetted and will be inspected with video camera. | Y | Y | Sulphur Creek | Lake at Laguna Niguel Regional Park | N/A | N | N | N/A
978-011 | 619-571-6972 (SIRT) | 1998-04-20 09:00 | MIKE DUNBAR | (949) 499-4555 | SOUTH COAST WATER DISTRICT | 1998-04-19 12:15 | 1998-04-19 13:00 | 2000 | 0 | 32162 PACIFIC COAST HIGHWAY | LAGUNA BEACH | OR | 92651 | MANHOLE | 0 | LINE PLUGGED WITH TREE ROOTS | LINE PLUGGED WITH TREE ROOTS AND RAGS | CLEANED LINE | N: N; N/A: STORM DRAIN; Y: Y; Y: N; N: N | OVERFLOW DID NOT REACH SURFACE WATERS
978040 | Quarterly | Quarterly | Patti S. Page | (760) 723-5640 | Fallbrook Public Utility District | 1998-04-18 20:00 | 1998-04-18 20:35 | 75 | 0 | 1232 Old Stage Road | Fallbrook | SD | 92028 | 4" Cleanout | 1 | Blockage | Unknown Blockage | Flush main line. | N | N | NA | NA | Ran down the side of Old Stage Road 150 ft. and dried up. | N | N | N | NA | Used 50 gallons of wash down water on roadway.
978041 | Quarterly | Quarterly | Patti S. Page | (760) 723-5640 | Fallbrook Public Utility District | 1998-06-17 13:40 | 1998-06-17 14:15 | 8 | 0 | 1448 S. Mission Road | Fallbrook | SD | 92028 | 4" Cleanout | 1 | Other | Sanitary Napkins | Rodded with sewer rodder machine. | N | N | NA | NA | Across blacktop driveway about 60 ft. | N | N | N | NA | Used 30 gallons of wash down water on driveway.
985728 | Fax 571-6972 | 4/02/98 12:45 | R. Parker | 654-4160 | City of San Diego | 4/01/98 17:58 | 4/02/98 08:55 | 26910 | 17850 | Cass St. & Van Nuys St./canyon | San Diego | SD | 92109 | 8" VC sewer main | Three | Vandalism | Vandals opened manhole; filled with rocks | Used fork/tools to remove rocks from manhole; recvr'd part of spill | Y | Y | Van Nuys Creek | Storm Drain | Pacific Ocean | Y | Y | Y | Unknown | 5 signs posted
985818 | Fax 571-6972 | 4/02/98 10:45 | L. Davis | 654-4160 | City of San Diego | 4/02/98 07:50 | 4/02/98 08:50 | 600 | 0 | 11233 Tierrasanta Bl. | San Diego | SD | 92124 | 12" PVC | One | Vandalism | Rocks and roots caused blockage | Machine rodded to remove roots, removed rocks, placed on PM | Y | Y | Storm Drain | Canyon area | Dried in canyon floor | Y | N | N | N/A | N/A
987600 | Fax 571-6972 | 4/14/98 16:45 | L. Finch | 654-4160 | City of San Diego | 4/14/98 09:24 | 4/14/98 12:24 | 180 | 0 | 27th St. & F St. | San Diego | SD | 92102 | 8" VC sewer main | One | Construction | Heavy rocks and dirt caused by construction company | Remv'd rocks/dirt caused by contractor not trapping properly | Y | N | Storm Drain | Soaked into ground | Canyon | Y | N | N | N/A | N/A
987754 | Fax 571-6972 | 4/16/98 15:15 | L. Davis | 654-4160 | City of San Diego | 4/15/98 10:40 | 4/15/98 11:57 | 3850 | 0 | 9100 Friars Rd. | San Diego | SD | 92128 | 16" VC sewer main | One | Vandalism | Debris that entered manhole when lid dislodged | Removed branches, cacti, debris, ref. for manholes to be secured | Y | Y | Storm Drain | San Diego River | Pacific Ocean | Y | Y | Y | Unknown | 24 signs posted
987880 | Fax 571-6972 | 4/16/98 14:00 | L. Finch | 654-4160 | City of San Diego | 4/16/98 09:30 | 4/16/98 10:15 | 22.5 | 0 | 4282 Whittier St. | San Diego | SD | 92107 | 8" VC | One | Grease | Grease stop on 8" VC main | Vacuumed to remove grease, put on PM schedule | Y | N | San Diego River | Pacific Ocean | Dried in street | Y | N | N | N/A | N/A
987928 | Fax 571-6972 | 4/16/98 14:09 | R. Donahue | 654-4160 | City of San Diego | 4/16/98 00:30 | 4/16/98 10:30 | 40800 | 26400 | 4605 Huron St./canyon | San Diego | SD | 92117 | 8" VC | Four | Grvty Mn Brk | Rain storm caused main to wash away | Re-connected main washed out by flooding, secured to wall of trench | Y | Y | Mission Bay | Pacific Ocean | N/A | Y | Y | N | N/A | N/A
987963 | Fax 571-6972 | 4/16/98 20:50 | J. Wilder | 654-4160 | City of San Diego | 4/16/98 16:15 | 4/16/98 18:25 | 390 | 0 | 1665 Sunset Cliffs Bl. | San Diego | SD | 92107 | 6" VC sewer main | One | Grvty Mn Brk | Main break causing sewer to seep up through street | Rod main to open flow until repairs are made | Y | Y | Storm Drain | Pacific Ocean | N/A | Y | N | N | N/A | N/A
988188 | Fax 571-6972 | 4/18/98 12:00 | J.Oropeza | 654-4160 | City of San Diego | 4/18/98 07:35 | 4/18/98 09:15 | 1500 | 0 | Beyer Bl. & Palm Av. | San Diego | SD | 92154 | 10" VC | One | Grease | Heavy grease caused blockage | Relieve stop, ref. to supv. for PM schedule | Y | Y | Storm Drain | SD Bay/Pacific Ocean | N/A | Y | Y | Y | Unknown | 8 signs posted
988227 | Fax 571-6972 | 4/20/98 11:00 | G. Richardson | 654-4160 | City of San Diego | 4/20/98 07:03 | 4/20/98 08:03 | 315 | 0 | Baylor Dr. & Collier Av. | San Diego | SD | 92115 | 6" VC | One | Roots | Roots in main | Removed roots from 6" vc main | Y | Y | Storm Drain | N/A | Storm Drain system | Y | N | N | N/A | N/A
988753 | Fax 571-6972 | 4/23/98 11:30 | L. Davis | 654-4160 | City of San Diego | 4/23/98 06:55 | 4/23/98 07:30 | 450 | 0 | 5011 Waring Rd. | San Diego | SD | 92120 | 8" VC | One | Grease | Grease build-up | Cleared grease stop, place main on PM schedule | Y | Y | Storm Drain | Canyon | Dried up in canyon | Y | N | N | N/A | N/A
989105 | Fax 571-6972 | 4/26/98 11:32 | D. Branco | 654-4160 | City of San Diego | 4/26/98 10:43 | 4/26/98 14:15 | 106 | 0 | 2504 34th St. | San Diego | SD | 92104 | 6" VC | One | Roots | Roots caused blockage | Flushed 6" vc main to relieve stop | Y | N | Soaked into canyon | Chollas Creek/SD Bay | N/A | Y | N | N | N/A | N/A
989616 | Fax 571-6972 | 4/30/98 03:35 | M. Whelan | 654-4160 | City of San Diego | 4/29/98 14:36 | 4/29/98 17:07 | 2265 | 405 | 810 Turquoise St. | San Diego | SD | 92109 | 8" VC | One | Rocks | Roots and rocks | Flushed, vacuumed to remove rocks and roots | Y | Y | Storm Drain | Pacific Ocean | N/A | Y | Y | Y | Unknown | 7 signs posted
989882 | Fax 571-6972 | 5/01/98 10:15 | R. Parker | 654-4160 | City of San Diego | 5/01/98 07:59 | 5/1/98 08:50 | 51 | 0 | 3216 Camto. Eastbluff | San Diego | SD | 92122 | 8" VC | One | Grease | Grease build-up inside main | Flushed main to remove blockage | Y | Y | Curb & storm drain | Rose Creek/Mission Bay/Pacific Ocean | N/A | Y | N | N | N/A | N/A
989953 | Fax 571-6972 | 5/04/98 14:56 | W. Graham | 654-4160 | City of San Diego | 4/30/98 18:30 | 5/01/98 07:30 | 1638000 | 0 | 12101 Lake Dr. | San Diego | SD | 92025 | Sewer Pump Station 77 | One | Force Mn Brk | Footing settled, causing main to break | Took station off-line, executed repair of force main | Y | N | Lake Hodges | N/A | N/A | Y | Y | Y | Five | 4 signs posted
990040 | Fax 571-6972 | 5/02/98 14:05 | D. Branco | 654-4160 | City of San Diego | 5/02/98 08:55 | 5/02/98 09:47 | 520 | 400 | 4559 Hawley Bl. | San Diego | SD | 92116 | 8" VC main | One | Grease | Stoppage caused by grease | Machine rodded to relieve stop, vacuumed pooled spill, ref. for PM | Y | N | Stopped in gutter | SD River/Pacific Ocean | N/A | Y | N | N | N/A | N/A
990078 | Fax 571-6972 | 5/03/98 22:09 | D. Branco | 654-4160 | City of San Diego | 5/03/98 19:08 | 5/03/98 21:10 | 1220 | 0 | 3512 43rd St. | San Diego | SD | 92105 | 8" VC main | One | Grease | Stoppage caused by grease | Machine rodded to relieve stop, ref. for PM | Y | Y | Storm Drain | SD Bay/Pacific Ocean | N/A | Y | Y | N | N/A | N/A
991843 | Fax 571-6972 | 5/15/98 14:10 | R. Bjorkman | 654-4160 | City of San Diego | 5/04/98 06:00 | 5/04/98 12:00 | 9000 | 0 | 15500 Paymogo St. | San Diego | SD | 92129 | Sewer Pump Station 62 | One | Other | Possibly faulty relay | Replaced pump relay switch; investigating alarm failure | Y | Y | Storm Drain | Gravel pit | N/A | Y | Y | Y | Unknown | 5 signs posted
990340 | Fax 571-6972 | 5/05/98 09:30 | G. Richardson | 654-4160 | City of San Diego | 5/05/98 08:27 | 5/05/98 08:50 | 69 | 0 | 4169 Vista Grande | San Diego | SD | 92115 | 6" CP | One | Roots | Roots in main caused overflow | Rodded main to remove roots, cleaned area | Y | Y | Storm Drain | N/A | Storm Drain | Y | N | Y | N/A | N/A
990849 | Fax 571-6972 | 5/08/98 00:47 | M. Whelan | 654-4160 | City of San Diego | 5/07/98 19:44 | 5/07/98 20:39 | 55 | 14 | 5297 Lodi St. | San Diego | SD | 92117 | 8" VC | One | Debris | Debris in manhole caused stoppage | Probed MH, relieved stop, scooped rags, towels, debris from main | Y | Y | Storm Drain | Soaked into ground | N/A | Y | N | N | N/A | N/A
990853 | Fax 571-6972 | 5/08/98 11:30 | L. Finch | 654-4160 | City of San Diego | 5/08/98 06:55 | 5/08/98 08:30 | 47.5 | 0 | Greely Av. & Payne St. | San Diego | SD | 92113 | 8" CI | One | Grease | Stoppage caused by grease | Flushed to relieve stop, deodorized area, advised claims | Y | Y | Storm Drain | Chollas Creek/SD Bay | Storm Drain | Y | N | N | N/A | N/A
991055 | Fax 571-6972 | 5/09/98 13:59 | D. Branco | 654-4160 | City of San Diego | 5/09/98 08:39 | 5/09/98 09:33 | 270 | 0 | 4600 Mt. Etna Dr. | San Diego | SD | 92117 | 8" VC | One | Grease | Stoppage caused by grease | Machine rodded to relieve stop | Y | Y | Storm Drain | Tecolate Creek/Mission Bay | N/A | Y | N | N | N/A | N/A
991336 | Fax 571-6972 | 5/12/98 14:45 | L. Finch | 654-4160 | City of San Diego | 5/12/98 10:07 | 5/12/98 11:43 | 480 | 0 | 2125 Park Bl. | San Diego | SD | 92134 | 6" CP | One | Debris | Debris in sewer main | Relieved stop, ref. for TV | Y | Y | Storm Drain | San Diego Bay | Storm Drain | Y | N | N | N/A | N/A
991382 | Fax 571-6972 | 5/13/98 04:15 | M. Whelan | 654-4160 | City of San Diego | 5/12/98 13:24 | 5/12/98 16:30 | 372 | 0 | Hillside Dr. & Torrey Pines Rd. | San Diego | SD | 92037 | 8" CI sewer main | Two | Roots | Heavy roots in main caused overflow | Rodded main to relieve stop | Y | Y | Storm Drain | Pacific Ocean | N/A | Y | N | Y | Unknown | Unknown
991543 | Fax 571-6972 | 5/13/98 14:45 | R. Parker | 654-4160 | City of San Diego | 5/13/98 12:21 | 5/13/98 13:13 | 2600 | 0 | Carmel Country Rd. & w/b Hwy. 56 | San Diego | SD | 92130 | 10" PVC | One | Debris | Debris build-up caused stoppage | Relieve stop, clean upstream mains, consider for PM site | Y | Y | Storm Drain | Soledad Creek/Pacific Ocean | N/A | Y | Y | Y | Unknown | 5 signs posted
991769 | Fax 571-6972 | 5/15/98 07:30 | M. Whelan | 654-4160 | City of San Diego | 5/14/98 20:55 | 5/15/98 01:55 | 11250 | 0 | 3111 Erie St./canyon | San Diego | SD | 92117 | 10" VC | One | Roots | Roots grew into canyon easement | Hand rod to relieve stop | Y | Y | Canyon | Storm Drain/Mission Bay | N/A | Y | Y | Y | Unknown | 17 signs posted
992084 | Fax 571-6972 | 5/17/98 14:49 | D. Branco | 654-4160 | City of San Diego | 5/17/98 14:46 | 5/17/98 15:20 | 34 | 0 | 6619 Linda Ln. | San Diego | SD | 92120 | 8" VC | One | Roots | Roots caused blockage | Machine rod w/screw to relieve stoppage | N | N | ground & back yard | N/A | Ground & back yard | Y | N | N | N/A | N/A
992092 | Fax 571-6972 | 5/18/98 15:13 | L. Moore | 654-4160 | City of San Diego | 5/17/98 17:49 | 5/18/98 00:45 | 100 | 0 | 1022 Skylark Dr. | San Diego | SD | 92037 | 8" VC | One | Other | Unknown | Unable to locate manhole on 30' deep main; ref to contractor for rprs | Y | Y | Soaked into ground | Canyon storm channel | N/A | Y | N | N | N/A | N/A
992246 | Fax 571-6972 | 5/19/98 04:57 | M. Whelan | 654-4160 | City of San Diego | 5/18/98 17:50 | 5/18/98 21:15 | 102.5 | 0 | 1071 S. 41st St. | San Diego | SD | 92113 | 8" PVC | One | Grease | Grease and rocks in main | Flushed, removed heavy grease from main | Y | Y | Storm Drain | Drainage channel | N/A | Y | N | N | N/A | N/A
992396 | Fax 571-6972 | 5/19/98 04:59 | M. Whelan | 654-4160 | City of San Diego | 5/18/98 21:31 | 5/19/98 24:20 | 845 | 250 | 4297 Cordobes Cv. | San Diego | SD | 92130 | 8" PVC | One | Roots | Roots in buried manhole caused blockage | Locate/dig out manhole, clean 1' of roots from channel to relieve stop | Y | Y | Storm Drain | Drainage ditch | N/A | Y | Y | N | N/A | N/A
992698 | Fax 571-6972 | 5/20/98 01:42 | M. Whelan | 654-4160 | City of San Diego | 5/19/98 20:46 | 5/19/98 22:43 | 351 | 0 | 7247 Arpege Rd. | San Diego | SD | 92119 | 8" PVC | One | Roots | Roots & grease in main/also rootbound manholes | Cleaned rootbound manhole, rodded main to relieve stop | Y | Y | Storm Drain | Soaked into canyon | N/A | Y | N | N | N/A | N/A
993413 | Fax 571-6972 | 5/22/98 15:15 | R, Burton | 654-4160 | City of San Diego | 5/22/98 09:55 | 5/22/98 11:55 | 240 | 235 | 3162 Monroe Av. | San Diego | SD | 92116 | 8" VC | One | Construction | Rocks in 8" VC main | Machine rodded main to relieve stop/removed rocks from 8" vc main | N | N | Dirt around manhole | Vactored up spill | N/A | Y | N | N | N/A | N/A
993592 | Fax 571-6972 | 5/23/98 16:06 | D. Branco | 654-4160 | City of San Diego | 5/23/98 11:39 | 5/23/98 13:01 | 41 | 0 | 3200 Reynard Wy. | San Diego | SD | 92103 | 6" VC | One | Roots | Roots caused blockage | Locate/expose manhole, flush main to remove heavy roots | Y | Y | Storm Drain | SD Bay/Pacific Ocean | N/A | Y | N | N | N/A | N/A
993635 | Fax 571-6972 | 5/25/98 16:00 | J. McPherson | 654-4160 | City of San Diego | 5/25/98 12:16 | 5/25/98 14:16 | 120 | 0 | 2955 Wing St. | San Diego | SD | 92110 | 8" VC | One | Grease | Blockage caused by grease | Removed grease from main to relieve stop | N | N | Dirt around manhole | N/A | N/A | Y | N | N | N/A | N/A
993848 | Fax 571-6972 | 5/27/98 02:52 | M. Whelan | 654-4160 | City of San Diego | 5/26/98 21:37 | 5/26/98 23:07 | 45 | 0 | 5124 Via Cinta | San Diego | SD | 92122 | 8" VC | One | Roots | Roots in easement caused grease build-up | Flushed main to relieve stop | Y | Y | Storm Drain | Soaked into ground | N/A | Y | N | N | N/A | N/A
994128 | Fax 571-6972 | 5/29/98 16:23 | M. Whelan | 654-4160 | City of San Diego | 5/28/98 15:17 | 5/28/98 17:42 | 290 | 0 | 2872 Arbodar Rd. | San Diego | SD | 92154 | 10" VC | One | Grease | Grease in main | Vacuumed heavy grease from main | Y | Y | Dried in Preserve | N/A | N/A | Y | N | N | N/A | N/A
994303 | Fax 571-6972 | 5/29/98 07:03 | M. Whelan | 654-4160 | City of San Diego | 5/28/98 22:11 | 5/29/98 00:32 | 705 | 0 | 3900 Lockridge St. | San Diego | SD | 92102 | 10" VC | One | Vandalism | Vandals and roots caused blockage | Removed heavy debris, roots from main | N | Y | Storm Drain | Soaked into ground | N/A | Y | N | N | N/A | N/A
994368 | Fax 571-6972 | 5/29/98 14:00 | L. Finch | 654-4160 | City of San Diego | 5/29/98 10:20 | 5/29/98 11:10 | 1000 | 0 | 2728 Treat St. | San Diego | SD | 92102 | 8" VC | One | Construction | Construction Co failed to trap construction debris | Cleared debris, advised contractor to use proper trapping techniques | Y | Y | Storm channel | San Diego Bay/Pacific Ocean | Dried in dirt storm channel | Y | Y | N | N/A | N/A
995489 | Fax 571-6972 | 6/04/98 12:10 | C. Bauer | 654-4160 | City of San Diego | 6/04/98 09:29 | 6/04/98 10:36 | 335 | 0 | 10405 San Diego Mission Rd. | San Diego | SD | 92108 | 8" VC | One | Grease | Grease | Flushed 8" vc main to remove stop | Y | Y | Storm Drain | SD River/Pacific Ocean | Storm Drain | Y | N | N | N/A | N/A
998024 | Fax 571-6972 | 6/09/98 13:00 | W. Payne | 654-4160 | City of San Diego | 6/09/98 10:30 | 6/09/98 10:31 | 20 | 0 | 1022 Skylark Dr. | San Diego | SD | 92037 | 8" VC | Two | Construction | Pumping from upstream manhole/bypassing construction | Established bypass pumping system around construction on 8" vc main | N | N | N/A | N/A | Soaked into dirt | Y | N | N | N/A | N/A
996800 | Fax 571-6972 | 6/11/98 05:37 | M. Whelan | 654-4160 | City of San Diego | 6/10/98 21:23 | 6/10/98 23:08 | 525 | 135 | 2548 Reo Dr. | San Diego | SD | 92139 | 8" VC | One | Grease | Grease in main | Vacuum to control overflow on 8" vc main | Y | Y | Storm Drain | N/A | N/A | Y | N | N | N/A | N/A
997138 | Fax 571-6972 | 6/13/98 15:07 | D. Branco | 654-4160 | City of San Diego | 6/13/98 09:52 | 6/13/98 11:45 | 321 | 0 | 6400 Bradford St. | San Diego | SD | 92115 | 8" VC | One | Grease | Blockage caused by grease & roots | Flushed 8" vc main to relieve grease/root stop | Y | Y | Storm Drain | Chollas Creek/San Diego Bay | N/A | Y | N | N | N/A | N/A
997160 | Fax 571-6972 | 6/14/98 15:19 | D. Branco | 654-4160 | City of San Diego | 6/14/98 09:46 | 6/14/98 10:58 | 216 | 0 | 4303 Whittier St. | San Diego | SD | 92107 | 8" VC | Two | Roots | Blockage caused by roots | Flushed 8" vc main to relieve root stop | Y | Y | Storm Drain | San Diego River/Pacific Ocean | N/A | Y | N | N | N/A | N/A
997416 | Fax 571-6972 | 6/16/98 15:42 | L. Moore | 654-4160 | City of San Diego | 6/16/98 09:49 | 6/16/98 12:49 | 1800 | 0 | Mission Center Rd. & Hazard Center Dr. | San Diego | SD | 92108 | 6" PVC | One | Grease | Stoppage caused by grease | Flushed 6" pvc main to relieve stop | Y | Y | Storm Drain | San Diego River | Pacific Ocean | Y | Y | Y | Two | 6 signs posted
997763 | Fax 571-6972 | 6/18/98 13:20 | L. Finch | 654-4160 | City of San Diego | 6/18/98 07:19 | 6/18/98 09:33 | 4020 | 2800 | 1009 Leroy St. | San Diego | SD | 92106 | 8" CP | One | Grvty Main Brk | Pieces of rock, pipe, light roots | Refer for spot repair on 8" cp main | Y | Y | Storm Drain | Storm Drain | N/A | Y | Y | Y | Five | Unknown
997770 | Fax 571-6972 | 6/18/98 16:00 | M. Bedard | 654-4160 | City of San Diego | 6/17/98 09:25 | 6/18/98 13:30 | 33700 | 33700 | 5100 Olvera Av. | San Diego | SD | 92114 | 10" VC | One | Grease | Grease caused blockage | Relieve grease stop on 10" vc main, refer for repair to brick manhole | Y | Y | Storm Drain | Pacific Ocean | N/A | Y | Y | N | N/A | N/A
997785 | Fax 571-6972 | 6/18/98 13:10 | L. Davis | 654-4160 | City of San Diego | 6/18/98 09:40 | 6/18/98 10:35 | 50 | 0 | 17572 Cumana Tr. | San Diego | SD | 92128 | Manhole on 8" PVC | One | Roots | Blockage caused by roots | Relieve root stop on 8" pvc main | Y | Y | Storm Drain | Drainage ditch | Dried in drainage ditch | Y | N | N | N/A | N/A
998146 | Fax 571-6972 | 6/20/98 11:25 | J. Oropeza | 654-4160 | City of San Diego | 6/20/98 09:14 | 6/20/98 10:30 | 152 | 0 | Bunche Av. & Dunant St. | San Diego | SD | 92122 | 8" VC | Two | Grease | Blockage caused by roots and grease | Relieve grease and root stop on 8" vc main | N | Y | Storm Drain | Canyon creek | Soaked into canyon | N | N | N | N/A | N/A
998365 | Fax 571-6972 | 6/22/98 19:55 | M. Whelan | 654-4160 | City of San Diego | 6/22/98 11:00 | 6/22/98 16:15 | 3150 | 400 | 1111 W. Muirlands Dr. | San Diego | SD | 92037 | 8" VC | One | Roots | Blockage caused by roots | Relieve root blockage on 8" vc main | Y | Y | Storm Drain | Pacific Ocean | N/A | Y | Y | Y | Unknown | 7 signs posted
998256 | Fax 571-6972 | 6/23/98 05:40 | M. Whelan | 654-4160 | City of San Diego | 6/22/98 13:33 | 6/22/98 18:30 | 297 | 0 | Front St. & Spruce St./canyon west | San Diego | SD | 92103 | 6" VC | One | Roots | Roots in main | Machine rodded 6" cp main | Y | N | Ground in canyon | N/A | Ground in canyon | Y | N | N | N/A | N/A
999133 | Fax 571-6972 | 6/26/98 09:00 | W. Payne | 654-4160 | City of San Diego | 6/23/98 11:00 | 6/23/98 11:01 | 5 | 0 | 10800 Roselle St. | San Diego | SD | 92121 | 12" DI | Three | Force Main Brk | Break in hi-line to pump station #64 | Shut down pump station until contractor makes repairs | N | N | N/A | N/A | N/A | Y | N | N | N/A | N/A
999185 | Fax 571-6972 | 6/30/98 08:00 | G. Richardson | 654-4160 | City of San Diego | 6/23/98 15:14 | 6/26/98 17:40 | 4405 | 0 | 47th St. & Fairmount Av. | San Diego | SD | 92105 | 8" VC | One | Roots | Blockage caused by grease and roots | Remove root/grease stop from 8" vc main | Y | Y | Dirt ditch | Chollas Creek | Soaked into canyon | Y | Y | N | N/A | N/A
999336 | Fax 571-6972 | 6/27/98 15:05 | J. Oropeza | 654-4160 | City of San Diego | 6/27/98 12:25 | 6/27/98 13:30 | 130 | 85 | 1620 Garnet Av. | San Diego | SD | 92109 | 8" VC | One | Grease | Blockage caused by grease and sludge | Remove grease/sludge from 8" vc main | Y | N | Parking lot at Vons | Mission Bay/Pacific Ocan | Parking lot and grass area | Y | N | N | N/A | N/A
999379 | Fax 571-6972 | 6/29/98 14:20 | L. Finch | 654-4160 | City of San Diego | 6/29/98 09:05 | 6/29/98 10:35 | 180 | 160 | Main St. & Sigsbee St. | San Diego | SD | 92113 | 6" CP | One | Debris | Main filled with pinto beans and grease | Remove grease, food from 6" cp main | Y | N | Recovered most of spill | Dried in street | N/A | Y | N | N | N/A | N/A
999415 | Fax 571-6972 | 6/29/98 18:12 | W. Hampton | 654-4160 | City of San Diego | 6/29/98 07:45 | 6/29/98 16:00 | 742.5 | 600 | 9310 Friars Rd. | San Diego | SD | 92128 | 12" CI | One | Grvty Main Brk | El Nino caused hillside to fall into pipe causing break | Repaired 12" ci main; refer to Engineering for re-routing of creek bed | Y | N | Creek bed | N/A | Pumped back into system | Y | N | N | N/A | N/A
999566 | Fax 571-6972 | 6/30/98 01:58 | M. Whelan | 654-4160 | City of San Diego | 6/29/98 20:30 | 6/29/98 22:11 | 303 | 0 | 47th St. & Dwight St. | San Diego | SD | 92105 | 6" CP | One | Grease | Blockage caused by grease | Rod 6" cp main to relieve stop | Y | Y | Storm Drain | Soaked into ground | N/A | Y | N | N | N/A | N/A
999438 | Fax 571-6972 | 7/01/98 12:45 | L. Finch | 654-4160 | City of San Diego | 6/29/98 06:30 | 6/29/98 10:38 | 2480 | 0 | 2926 Kellogg St. | San Diego | SD | 92106 | 8" VC | One | Roots | Partial root stoppage | Relieve stop on 8" vc main | Y | Y | Storm Drain | San Diego Bay | Pacific Ocean | Y | Y | Y | Three | N/A
978004 | JOHN PHILLIPS | 6/11/1998 8:00AM | KRIS HANBERG | 949/858-4979 | TCWD | 6/10/98 12:00PM | 6/10/98 2:00PM | 24000 | 0 | VIA ALEGRE | TRABUCO CANYON | OR | 92679 | VIA ALEGRE LIFT STATION #04 | 0 | INFILTRATION | CONTRACTORS FLUSHED FIRE HYDRANT INTO SEWER LINE CAUSING HYDRAULIC OVERLOAD TO LIFT STATION | HAD CONTACTED THE CONTRACTOR INSTRUCTED HIM TO STOP AND INFORMED HIM THAT THIS WAS NOT PROPER PROCEDURE | Y | Y | TIJERAS CREEK | OCEAN |  | Y | Y | Y |  | HEALTH DEPT CLOSED BEACH
4079801 | Dan Hoirup | 1998-04-08 13:40 | A J Howard | 949 366-1553 | CSC | 1998-04-07 16:47 | 1998-04-07 17:40 | 700 | 700 | W. Ave. San Gabriel | CSC | OR | 92672 | San Gabriel PS | 0 | Failed Force Main Pipe Joint |  |  | N | N | N/A | N/A | Returned to Collection System downstream of San Gabriel Pump Station | Y | N | N/A | 0 | Crews isolated flows to the station and diverted to coastal trunk line for duration of repairs. Contents that escaped system was confined in adjacent parking lot and removed w/ Vactor
4089801 | Dan Hoirup | 1998-04-08 10:05 | Jay Elston | 949 366-1553 | CSC | 1998-04-08 09:30 | 1998-04-08 10:30 | 4500 | 0 | Esplanade / T-Street | CSC | OR | 92672 | RWW Beach Line to Califia | 2 | Pipe Plugged Failed |  |  | Y | Y | Pacific Ocean |  | Pacific Ocean | Y | N | Y | 1 | Plug installed in reclaimed water line pipe at treatment plant failed. Reclaimed water flowed out onto beach south of T-Street were pipe was damaged winter storm and surf conditions. ON 10 Aor 98 crews installed line valve on RWW line at north Beach
4249801 | John Phillips | 1998-04-24 09:04 | A J Howard | 949 366-1553 | CSC | 1998-04-21 08:00 | 1998-04-23 08:20 | 600 | 0 | Pacific Coast Highway Across from 35105 Doheny Beach Rd. | Dana Point | OR | 92672 | San Clemente Land Outfall line | 0 | Air/Vac Relief Valve |  |  | N | N | N/A | N/A | Pavement/Soil | Y | N | N | N/A | Air/Vac relief valve on Secondary Land Outfall stuck open for short periods then seal. This occurred on 21, 22, 23 Apr 98 @ approx 8:00 hrs ea morning. Discharged secondary effluent wetted street and ground immediately adjacent to the ari/vac station.
98-1 | KRISTIN SCHALL | 1998-05-22 10:00 | JEFF STECHER | 760-753-0155 | LEUCADIA | 1998-05-21 12:15 | 1998-05-21 16:00 | 6000 | 6000 | LA COSTA AVE. & SAXONY RD | CARLSBAD | SD | 92009 | SECONDARY EFFLUENT PIPELINE | 2 | PIPELINE DAMAGED | CONTRACTOR HIT LINE WITH BULLDOZER | DISTRICT CREW REPAIRED LINE AND REVIEWED SOP'S WITH DRIVER | N | N | NA | NA | SEWER LINE | Y | N | N | NA | CONTRACTOR HIT DELINEATED LINE
98-1 |  | 1998-06-06 08:30 | JEFF STECHER | 760-753-0155 | LEUCADIA | 1998-06-06 08:40 | 1998-06-06 09:10 | 750 | 750 | 2804 LA COSTA AVE | CARLSBAD | SD | 92009 | MANHOLE 10-1820 | 3 | ROOTS | 8" GRAVITY SEWER LINE, ROOTS PROTRUDED THROUGH JOINT | ROOT SAW, TV | N | Y | SAN MARCOS CREEK | NA | SAN MARCOS CREEK | Y | N | N | NA | SEWAGE MAINTAINED WITHIN GOLF COURSE
978008 | Not informed | 980602 0630 | City of Laguna Beach | 949 497-0765 | Laguna Beach | 980602 0615 | 980602 0730 | 100 | 50 | Cleo Street Beach | Laguna Beach | Orange | 92651 | Cleo Street Beach | 1 | 8" Siphon Break | The 8" CI Siphon located on the beach was leaking @ high water line, just as it was going in to the wet well. the line is encased in concrete | Crew built a sand berm and recovered 50 gal. We used stop leak material to plug the crack. | Yes | No | Pacific Ocean | None | Pacific Ocean | Yes | No | Yes | 3 | The City is planning to relocate the pipe.
978009 | 619 571-6972 | 980613 1130 | City of Laguna Beach | 949 497-0765 | Laguna Beach | 980613 1100 | 980613 1130 | 1500 | 500 | Shaws Cove | Laguna Beach | Orange | 92651 | Fairview Street Pump Station #14 | 2 | Force Main Break | Force Main Break failure due to old age. 40 yrs. old | An Emergency repair was made on the 6" CI Pipe. This force main will be replaced this month. | Yes | No | Pacific Ocean / Shaws Cove Bch | None | Pacific Ocean | Yes | Yes | Yes | 5 | New Force Main to be constructed
97-8-0007 | FAXED | 10:00AM | Marc Avila | 949-487-1097 | CBWD | Apr.13,6:30pm | Apr.13,6:50pm | 250 | 0 | Camino De Estrella | San Clemente | 0R | 92672 | Manhole | 1 | grease | Grease caused blockage in line | Jetted line clear,continue on preventative maintenance schedule | N | N | N/A | N/A | Asphalt,dissipated,around M.H. | Y | N/A | N/A | N/A
97-8-0008 | FAXED | 12:30PM | Marc Avila | 949-487-1097 | CBWD | Jun.12,12:30pm | Jun.12,12:50pm | 200 | 0 | Fortuna | Capistrano Beach | OR | 92624 | Manhole | 1 | blockage | Roots in line | Jetted line clear,continue preventative maintenance schedule | N | Y | Storm Drain | N/A | Dissipated in storm drain | N | N/A | N/N | N/A
978040 | N/A | N/A | Lance Lauricha | 760-839-4347 | City of Escondido | 4/13/1998 1200 | 4/13/1998 1500 | 35 Gallons | 0 | 1605 Hamilton | Escondido | SD | 92025 | Air-vac | 1 | Broken pipe | corroded copper pipe failed causing leak. | Replaced pipe. | N | N | N/A | N/A | Evaporation/Soil | N | N | N | N/A | No Samples taken.
978041 | Called County Health | 5/2/1998 2400 | Joe Sanchez | 760-839-4347 | City of Escondido | 5/1/1998 900 | 5/2/98 200 | 480 Gallons | 480 Gallons | 510 W. Valley Pkwy. | Escondido | SD | 92025 | Private Cleanout | 0 | Private C.O. | Unknown | Plumber cleared blockage. They also made a service lateral repair. | Y | Y | Storm Drain | Escondido Creek | San Elijo Lagoon | Y | Y | N | N/A | No Samples taken.
978042 | Faxed | 5/7/98 1245 | Lance Lauricha | 760-839-4347 | City of Escondido | 5/7/98 630 | 5/7/98 930 | 9,000 Gallons | 100 Gallons | 475 N. Midway | Escondido | SD | 92026 | Sewer Atlas page 310 Manhole 3266 | 0 | Grease | Excessive grease build-up in main line. | The main line was cleaned and scheduled for CCTV inspection. | Y | Y | Storm Drain | Escondido Creek | San Elijo Lagoon | Y | Y | Y | 4 Days | Samples were taken.
978043 | Called/Faxed | 5/11/98 930 | Lance Lauricha | 760-839-4347 | City of Escondido | 5/9/98 800 | 5/9/98 916 | 3,800 Gallons | 0 | Lincoln and Beech | Escondido | SD | 92026 | Sewer Atlas page 308 Manhole 3077 | 1 | Grease/Debris | Excessive grease build-up in main line. | The main line was cleaned and is scheduled to be upgraded in fiscal year 98-99. Also the Pretreatment Inspector was notified and conducted an investigation. | Y | Y | Storm Drain | Escondido Creek | San Elijo Lagoon | Y | Y | Y | 3 Days | Samples were taken.
978044 | Called/Faxed | 5/14/98 1245 | Lance Lauricha | 760-839-4347 | City of Escondido | 5/13/98 1500 | 5/14/98 1200 | 31,500 Gallons | 0 | 1555 Auto Pkwy. | Escondido | SD | 92027 | Sewer Atlas page 385 Manhole 4228 | 0 | Petroleum grease | Solids and petroleum products formed stoppage in main line. | Pretreatment Inspector was notified and investigated. We plan to continue routine maintenance. | Y | Y | Storm Drain | Escondido Creek | San Elijo Lagoon | Y | Y | Y | 5 Days | Samples were taken.
978045 | Called/Faxed | 5/28/98 1330 | Lance Lauricha | 760-839-4347 | City of Escondido | 5/28/98 945 | 5/28/98 1145 | 8,400 Gallons | 100 Gallons | 475 N. Midway | Escondido | SD | 92026 | Sewer Atlas page 310 Manhole 3266 | 1 | Grease | Excessive grease build-up in main line. | Main line was cleaned, televised, and is currently on a three month cleaning schedule. The Pretreatment Inspector was notified. Public notices were distributed to three apartment complexes in an effort to educate the residents on how grease effects the co | Y | Y | Storm Drain | Escondido Creek | San Elijo Lagoon | Y | Y | Y | 3 Days | Samples were taken.
98004 | N/A | N/A | N/A |  | City of Poway | 05/03/98 - 0730 | 05/04/98 - 0815 | 20 | 5 | 14644 Lake Poway Road | Poway | San Diego | 92064 | Collection System | 1 | Partial main blockage - Roots | Park Ranger notified Water Utilities that sewage was bubbling slowly out of manhole. Vactor crew dispatched to clear blockage. Roots were determined to be cause of blockage. Vactor crew vacuumed up five (5) gallons of spill and sanitized the area. | Removed contaminated soil from the area and replaced with fresh topsoil. Contaminated soil disposed of at City's sludge basin at Hazardous Waste Facility. Main line was video inspected and has been placed on a more frequent maintenance schedule. | No | No | N/A | N/A | Cleaned/sanitized area; replaced soil in spill area with fresh topsoil. | No | No | No | N/A | None
978027 |  |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 4/15/98,8:53:00 PM | 04/15/98, 9:15:00 P.M. | 300 | 0 | ASH ROAD | CAMP PENDLETON | SD | 920555008 | across from wire mountain PX | 1 | BLOCKAGE | GREASE, SOAP AND TRASH BUILDUP CAUSED BLOCKAGE | JETTED LINE TO CLEAR BLOCKAGE | Y | Y | SANTA MARGARITA RIVER | PACIFIC OCEAN |  | Y | NA | N | 0 | SPILL FLOWED FROM MANHOLE 25 FT INTO STORM DRAIN THEN 15 FT INTO DITCH AND PERCOLATED INTO THE GROUND. NEAR A BALLPARK BUT NO PUBLIC CONTACT EXPECTED.
978028 |  |  | DENNIS PINIGIS | 6197259762 | MCB, CAMP PENDLETON | 06/08/98,10:00:00 AM | 06/09/98,10:45:00 A.M. | 100 | 20 | 33 Area Wagon Wheel Street | CAMP PENDLETON | SD | 920555008 |  | 1 | CONSTRUCTION | Contractor cut sewer line while putting in fibre optic cable | break repaired | N | N |  |  | bottom of the trench | Y | NA | N | 0 | NOT IN AN AREA OF EXPECTED PUBLIC CONTACT
978029 | ELECTRONIC QTLY RPT |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 06/26/98,12:00:00 PM | 06/26/98,1:10:00 P.M. | 20 | 0 | BLDG 14137, 16TH STREET | CAMP PENDLETON | SD | 920555008 | CLEANOUT | 1 | OTHER | Cap came off cleanout. Sewage overflowed from cleanout. | Put cap back onto cleanout. Notified pipe shop to inspect and repair as necessary. | Y | N | Pilgrim Creek | San Luis Rey River |  | N | NA | N | 0 | SPILL FLOWED 15 FT FROM CLEANOUT ACROSS DIRT FIELD AND SOAKED INTO THE GROUND. NOT IN AN AREA OF EXPECTED PUBLIC CONTACT.
Note on I752: Changed from "1.64 million" to 1638000 on 12/21/01 per City of San Diego comment
Note on J599: Changed from 1 to 100 on 12/21/01 per City of San Diego comment

## Sheet2 (2)
Tracking No. | Regional Board Contact Notified (Name, or "VOICE MAIL", or "FAX") | Date & Time Reported | Reported By | Phone No. | Agency | Start Date & Time | End Date & Time | Total Overflow Volume (Gallons) | Overflow Volume Recovered (Gallons) | SSO Location -- Street Address | SSO Location -- City | SSO County SD, RV, OR | SSO Zip Code | SSO Structure I.D. | No. of Overflows in past 12 months | SSO Cause (Short Description) | SSO Cause (Detailed Description) | SSO Correction and Prevention | Reach Surface Waters? (Y or N) | Entered Storm Drain? (Y or N) | Initial Receiving Waters | Secondary Receiving Waters | Final Sewage Destination | Local Health Services Agency Notified (Y or N) | OES Notified (Y or N) | Warning Signs Posted (Y or N) | No. of Days Signs Posted | Remarks
968260 | Fax 571-6972 | 12/26/97 16:41 | Hernandez | 6544160 | City of San Diego | 12/22/97 10:30 | 12/26/97 12:15 | 29325 | 100 | 3066 Elm St./from private cleanout | San Diego | SD | 92102 | 8" VC clean out | 1 | Roots | Roots | Hand rodded to remove roots from main causing overflow from c/o | Y | Y | 33rd and E St | San Diego Bay/Pacific Ocean |  | Y | Y | Y | Unknown
955900 | Fax 571-6972 | 10/28/97 12:30 | Richardson | 6544160 | City of San Diego | 10/28/97 09:32 | 10/28/97 10:16 | 88 | 20 | 4536 Craigie St | San Diego | SD | 92102 | Clean out | 1 | Grease | Grease | Flushed to relieve stop | Y | N | 4536 Craigie St - backyard |  | Ground and street | Y | N/A | N
956156 | Fax 571-6972 | 10/29/97 06:40 | Whelan | 6544160 | City of San Diego | 10/29/97 01:00 | 10/29/97 01:00 | 40 | 0 | 5511 Yerba Anita Dr. | San Diego | SD | 92115 | 8" VC sewer main | 1 | Roots | Roots | Surge from stoppage clearing overflowed briefly, receded | Y | N | 5511 Yerba Anita Dr |  | Dried up in street | Y | N | N
978001 | SIRT (FAX) | 1997-07-30 08:45 | James E. Smith | 714-448-4053 | Moulton Niguel Water | 1997-07-30 20:45 | 1997-07-30 21:30 | 1000 | 0 | Moulton Parkway, 300' south of Aliso Creek Road | Laguna Niguel | OR | 92677 | 8" rEcycled water main | 1 | Broken 8" pipeline | An 8-inch recycled water pipeline broke due to corrosion. | The broken pipeline was dug up and replaced. | Y | N | Aliso Creek | Pacific Ocean at Aliso Beach | N/A | Y | N | N | N/A | N/A
978002 | SIRT (FAX) | 1997-08-23 10:00 | James E. Smith | 714-448-4053 | Moulton Niguel Water | 1997-08-23 10:00 | 1997-08-23 11:30 | 500 | 0 | Southwing Lift Station | Aliso Viejo | OR | 92656 | Lift Station | 1 | Automatic reset failed after power outage | Automatic reset device failed after a power outage at the lift station. | An uninterruptible power supply (UPS) has been installed at the lift station. | Y | N | Aliso Creek | Pacific Ocean | N/A | Y | N | N | N/A | N/A
967-003 | Laurie Walsh | 1997-12-04 11:15 | Renzo Marin | (714) 837-7050 | El Toro Water District | 1997-12-03 22:34 | 1997-12-03 22:41 | 350 GAL. | 0 GAL. | 25121 Charlinda | Mission Viejo | OR | 92691 | ETWD Freeway Lift station | 3 | Controller power accidentally shut off. | Pumps Controller power circuit was accidentally turned off by contractor. | Reactivated Controller and pumps. Replaced panel key lock. Requested contractor to obtain district approval prior to entering any district facilities. | Y | Y | Aliso Creek | Aliso Creek | OCEAN | Y | N | N | N/A | Notified all responsible agencies and mailed discharge report.
8 | 6195716972 (FULTON) | 11/10/97 10:20 | MIKE DUNBAR | (714) 499-4555 | SOUTH COAST WATER DISTRICT | 11/09/97 09:00 | 10/09/97 10:00 | 100 | 0 | 21651 WESLEY DRIVE | LAGUNA BEACH | OR | 92651 | MANHOLE | 0 | ROOTS | ROOTS BLOCKED LINE | REMOVED ROOTS AND CLEANED LINE | Y | Y | ALISO CREEK | PACIFIC OCEAN | N/A | Y | N/A | Y AS OF 1:16 PM 11/10/97 |  | CREEK MOUTH ALWAYS POSTED, COUNTY REMOVED BERM ALLOWING FLOW TO OCEAN AT 1:16 PM 11/10/97
978003 | VOICE MAIL-PAUL RICHTOR, FAX | 2/16/98 9:00AM | KRIS HANBERG | 714/858-4979 | TCWD | 2/15/98 5:00AM | 2/16/98 9:00AM | 480000 | 0 | EL TORO/PORTOLA | TRABUCO CANYON | OR | 92679 | EL TORO LIFT STATION | 1 | POWER FAILURE | LOW VOLTAGE RELAY FAILED AND FUSE | LOOKING INTO REDESIGN | Y | Y | ALISO CREEK | OCEAN |  | Y | N | Y | 96 HRS | NONE
967-003 | Laurie Walsh | 1997-12-04 11:15 | Renzo Marin | (714) 837-7050 | El Toro Water District | 1997-12-03 22:34 | 1997-12-03 22:41 | 350 GAL. | 0 GAL. | 25121 Charlinda | Mission Viejo | OR | 92691 | ETWD Freeway Lift station | 3 | Controller power accidentally shut off. | Pumps Controller power circuit was accidentally turned off by contractor. | Reactivated Controller and pumps. Replaced panel key lock. Requested contractor to obtain district approval prior to entering any district facilities. | Y | Y | Aliso Creek | Aliso Creek | OCEAN | Y | N | N | N/A | Notified all responsible agencies and mailed discharge report.
967 -005 | Paul Richter | 1998-02-23 14:35 | Renzo Marin | (714)837-7050 x217 | El Toro Water District | 1998-02-21 16:00 | 02/22098 | 2525 GAL. | 0 GAL. | Avenida Sevilla Bldg. # 643 (Leisure World) | Laguna Hills | OR | 92630 | ETWD Atlas page MD-498, MH 20 | 4 | Tree roots blockage | Tree roots blockage in 6" line. Roots broke pipeline. | Built spill containment area with sand bags. Used Hydrocleaner to break stoppage. Assessed line condition with TV. Exposed and repaired line break. | Y | Y | Aliso Creek | Aliso creek | OCEAN | Y | N | N | N/A | Notified all responsible agencies and mailed discharge report.
978003 | VOICE MAIL-PAUL RICHTOR, FAX | 2/16/98 9:00AM | KRIS HANBERG | 714/858-4979 | TCWD | 2/15/98 5:00AM | 2/16/98 9:00AM | 480000 | 0 | EL TORO/PORTOLA | TRABUCO CANYON | OR | 92679 | EL TORO LIFT STATION | 1 | POWER FAILURE | LOW VOLTAGE RELAY FAILED AND FUSE | LOOKING INTO REDESIGN | Y | Y | ALISO CREEK | OCEAN |  | Y | N | Y | 96 HRS | NONE
978-014 | SIRT (FAX) | 1998-05-11 11:50 | Brad Bruington | 949-831-1070 | Moulton Niguel Water | 1998-05-11 09:15 | 1998-05-11 10:00 | 40000 | ongoing | Oso Pkwy. & Moulton Pkwy. | Laguna Niguel | OR | 92677 |  | 1 | Construction | Contractor hit/broke a 20" abandoned sewer force main that was full of stagnant water. Stagnant water filled trench and went down flood control catch basin. | Line drained and stagnant water vacuumed up and put into sewer. Line will be repaired. | Y | Y | Aliso Creek | None | N/A | Y | Y | Y |  | O.C. Health Dept. handles this
941552 | Fax 571-6972 | 08/19/97 01:52 | Whelan | 6544160 | City of San Diego | 08/18/97 19:20 | 08/18/97 21:00 | 300 | 0 | 7003 Saranac St. | San Diego | SD | 92115 | 6" vc main | 1 | Roots | Roots in main | Flushed, used root saw to clear main | y | y | Alvarado Creek | San Diego River |  | y | n | n
978004 | Voicemail | 1998-02-24 02:00 | Jim Gusman | (760)-726-1340ext1665 | City of Vista | 1998-02-24 00:15 | 1998-02-24 01:30 | 7500 | 0 | Buena Sanitation Trunk Line Easement | Vista | SD | 92083 | B1-2 #101 | 0 | Flood Damage due to rains, Infiltration | High flows at the Buena Pump Station due to very heavy rains. The lowest upstream manhole spilled effluent because the pump station couldn't keep up with the high flows. | All three pumps at the pump station were at high speed,it took over an hour for the pump station to catch up. | Y | N | Aqua Hedionda Creek | Aqua Hedionda Lagoon, Pacific Ocean |  | Y | Y | Y | 10 | Signs posted in the A.M., due to heavy rains and easement access none of the spill was captured. The beach is 8-10 miles from the spill, there was heavy dilution due to the rains. Signs posted on the easement 2 miles downstream.
978005 | Voicemail | 1998-02-24 10:00 | Jim Gusman | (760)-726-1340ext1665 | City of Vista | 1998-02-24 07:50 | 1998-02-24 09:50 | 10500 | 0 | Buena Sanitation Trunk Line Easement | Vista | SD | 92083 | B1-2 #101 | 0 | Flood Damage due to rains, Infiltration | High flows at the Buena Pump Station due to very heavy rains. The lowest upstream manhole spilled effluent because the pump station couldn't keep up with the high flows. | All three pumps at the pump station were at high speed,it took over an hour for the pump station to catch up. | Y | N | Aqua Hedionda Creek | Aqua Hedionda Lagoon, Pacific Ocean |  | Y | Y | Y | 10 | Signs posted in the A.M., due to heavy rains and easement access none of the spill was captured. The beach is 8-10 miles from the spill, there was heavy dilution due to the rains. Signs posted on the easement 2 miles downstream.
954461 | Fax 571-6972 | 10/20/97 14:15 | Richardson | 6544160 | City of San Diego | 10/20/97 11:30 | 10/20/97 12:00 | 30 | 0 | 1935 Leatherwood St. | San Diego | SD | 92154 | 8" PVC | 1 | Grease | Grease | Flushed main to relieve stop | Y | Y | At Curb | Storm Drain | Storm Drain System | Y | N/A | N
975031 | Fax 571-6972 | 02/03/98 19:07 | J.Wilder | 6544160 | City of San Diego | 02/03/98 15:17 | 02/03/98 16:44 | 44 | 10 | 4120 Hillandale Rd. | San Diego | SD | 92116 | 8" VC | One | Roots | Roots | Rodded main/refer for further cleaning | Y | Y | Backyard | N/A | Backyard & vacuumed at gutter | Y | N | N
978002 | FAX | 12/17/97 6:50AM | KRIS HANBERG | 714/858-4979 | TCWD | 12/17/97 6:50AM | 12/17/97 7:15AM | 6000 | 0 | BARNBURG | TRABUCO CANYON | OR | 92679 | BARNEBURG LIFT STATION | 2 | PUMP STATION FAILURE | COMPUTER THAT CONTROLS STATION LOCKED UP | REBOOTED COMPUTER | Y | Y | BELL CANYON CREEK | SAN JUAN CREEK |  | Y | N | N | 0 | NONE
978001 | Left Message | 1997-07-03 08:14 | Jim Gusman | (760)726-1340ext1665 | City of Vista | 1997-07-02 18:45 | 1997-07-02 19:15 | 7500 | 0 | Eucalypus Ave. 300' west of Escondido Ave. | Vista | SD | 92083 | Basin V.22, SMH 96, AP 175-29 | Zero | Grease | Grease Blockage | Cleaned the line downstream two blocks and upstream to the next manhole. | Y | N | Branch of Buena Vista Creek | Buena Vista Creek |  | Y | N | Y | 3 | Washed the area of the spill with 1800 gal of fresh water.
972521 | Fax 571-6972 | 01/23/98 10:10 | G.Richardson | 6544160 | City of San Diego | 01/22/98 19:09 | 01/22/98 21:15 | 504 | 288 | 4125 58th St. | San Diego | SD | 92115 | 8" VC | One | Grvty Main Brk | Break in main | Directed overflow back into manhole/referred to construction crew | Y | Y | Break site between manholes 85 and 86 | Storm Drain | Dissipated into storm drain | Y | N | N
978003 | Carol Tomaki | 1997-10-09 14:00 | Jim Gusman | (760) 726-1340ext1665 | City of Vista | 1997-10-09 12:00 | 1997-10-09 13:30 | 1800 | 500 | 605 W. Vista Way | Vista | SD | 92083 | Private lateral and grease trap | Zero | Grease | Grease trap overflowed across the sidewalk, it also caused a blockage in the lateral which also overflowed across the sidewalk. Both spills followed the gutter about 100' to a catch basin, about 350'-400' north of Buena Vista Creek. | Sewer main was jetted for partial blockage from grease. Sand bags were used to capture still flowing cleanout lateral and grease trap. Vacuum truck captured some of the flow and then a back flush and vacuum of the storm drain was done. | Y | Y | Buena Vista Creek | Buena Vista Lagoon |  | Y | Y | N |  | Washed down the public sidewalk area with fresh water.
978029 |  |  | Jacob DeLa Rosa | 760/966-7868 | Water Utilities Dept. City of Oceanside | 01/06/98 1013 | 01/06/98 1340 | 500 | 0 | 1900 Block of Palmer Drive | Oceanside | SD | 92056 | Manhole | 0 | Roots | Roots in City Main. | Rodded city Main and will monitor quarterly. | Y | Y | Buena Vista Creek | Buena Vista Lagoon | N/A | Y | N/A | N | N/A | Domestic W/W had no solids. Half mile of city gutters before Creek. Public restricted from entering Creek.
978003 | Pam Jackson | 9-25-97 1750 | Orv Salisbury | 760-744-0460 | V.W.D. | 9-25-97 1630 | 9-26-97 0600 | 1500000 | none | easment | Carlsbad | S.D. | 92009 | 24" outfall line | 1 | broken pipe | steel pipe was possibly crushed when installed | engeneering dept is investigating the cause | n | n | canyon | irrigation ponds | La Costa Resort | y | y | y | 14+ | spill was contained
978004 | voice mail | 9-26-97 1000 | Orv Salisbury | 760-744-0460 | V.W.D. | 9-26-97 0900 | 9-26-97 1430 | 942000 | none | easment | Carlsbad | S.D. | 92009 | 24" outfall line | 2 | broken pipe | steel pipe was possibly crushed when installed | engeneering dept is investigating the cause | n | n | canyon | irrigation ponds | La Costa Resort | y | y | y | 14+ | spill was contained
978003 | Pam Jackson | 9-25-97 1750 | Orv Salisbury | 760-744-0460 | V.W.D. | 9-25-97 1630 | 9-26-97 0600 | 1500000 | none | easment | Carlsbad | S.D. | 92009 | 24" outfall line | 1 | broken pipe | steel pipe was possibly crushed when installed | engeneering dept is investigating the cause | n | n | canyon | irrigation ponds | La Costa Resort | y | y | y | 14+ | spill was contained
978004 | voice mail | 9-26-97 1000 | Orv Salisbury | 760-744-0460 | V.W.D. | 9-26-97 0900 | 9-26-97 1430 | 942000 | none | easment | Carlsbad | S.D. | 92009 | 24" outfall line | 2 | broken pipe | steel pipe was possibly crushed when installed | engeneering dept is investigating the cause | n | n | canyon | irrigation ponds | La Costa Resort | y | y | y | 14+ | spill was contained
978006 | fax | 11-13-97 1400 | Cheryl Brandstrom | 760-744-0460 | V.W.D. | 11-10-97 1045 | 11-11-97 1230 | 1500000 | none | easment | Carlsbad | S.D. | 92009 | 24" outfall line | 3 | broken pipe | steel pipe was possibly crushed when installed | in process of replacing bad pipe | n | n | canyon | irrigation ponds | La Costa Resort | y | y | y | 14+ | spill was contained
963459 | Fax 571-6972 | 12/03/97 10:45 | Davis | 6544160 | City of San Diego | 12/02/97 09:05 | 12/02/97 09:55 | 250 | 0 | 18535 Bernardo Trails Dr. | San Diego | SD |  | Storm Culvert/canyon | 1 | Roots | Roots | Machine rodded main | Y | N | Canyon |  | Canyon | Y | N | N
968481 | Fax 571-6972 | 12/28/97 15:36 | Branco | 6544160 | City of San Diego | 12/28/97 10:52 | 12/28/97 12:00 | 204 | 100 | 4920 Imperial Av. | San Diego | SD | 92102 | 6" VC | 1 | Grease | Grease | Flushed main | N | N | Canyon |  | Canyon | Y | N/A | N
978006 | fax | 11-13-97 1400 | Cheryl Brandstrom | 760-744-0460 | V.W.D. | 11-10-97 1045 | 11-11-97 1230 | 1500000 | none | easment | Carlsbad | S.D. | 92009 | 24" outfall line | 3 | broken pipe | steel pipe was possibly crushed when installed | in process of replacing bad pipe | n | n | canyon | irrigation ponds | La Costa Resort | y | y | y | 14+ | spill was contained
978007 | Greg Peters | 02-07-98 1100 | Cheryl Brandstrom | 760-744-0460 | V.W.D. | 02-06-98 1730 | 02-07-98 1400 | 2000000 | none | easement | Carlsbad | S.D. | 92069 | 24" outfall line | 4 | broken pipe | steel pipe was possibly crushed when installed | in process of replacing bad pipe | y | n | canyon | irrigation ponds | La Costa Resort | y | y | y | 14+ | spilled into Batiquitos lagoon Carlsbad
971852 | Fax 571-6972 | 01/21/98 01:30 | M.Whelan | 6544160 | City of San Diego | 01/20/98 15:24 | 01/20/98 20:24 | 300 | 100 | 3206 47th St. | San Diego | SD | 92105 | 8" VC | One | Roots | Heavy roots and grease | Cleaned manhole to remove roots, grease and flushed main | Y | N | Canyon | None | Canyon | Y | N | N
975544 | Fax 571-6972 | 02/06/98 04:53 | M.Whelan | 6544160 | City of San Diego | 02/05/98 18:07 | 02/05/98 20:15 | 6400 | 3800 | 8228 San Vicente St. | San Diego | SD | 92114 | 10" VC | Two | Roots | Roots and grease in main | Rod main and flushed section | Y | Y | Canyon | Jamacha Creek bed |  | Y | Y | N
977532 | Fax 571-6972 | 02/19/98 10:15 | M.Whelan | 6544160 | City of San Diego | 02/18/98 17:28 | 02/18/98 18:58 | 900 | 0 | Herbert Pl. & Pennsylvania Av. | San Diego | SD | 92103 | 8" VC | One | Roots | Roots growing into manhole 593 | Hand rod main/cleaned channels in manhole/refer to manhole crew | Y | N | Canyon | Unknown |  | Y | Y | N
981702 | Fax 571-6972 | 03/14/98 17:45 | M.Bedard | 6544160 | City of San Diego | 03/13/98 08:39 | 03/13/98 20:30 | 4838 | 0 | Cottontail Ln. & Deer Hill Ct./canyon rear | San Diego | SD | 92037 | 8" VC | One | Grvty Mn Brk | Landslides caused section of pipe to break | Replace broken sections | Y | Y | Canyon | Storm Drain | Pacific Ocean | Y | Y | Y | Unknown
982375 | Fax 571-6972 | 03/17/98 15:00 | L.Davis | 6544160 | City of San Diego | 03/17/98 09:45 | 03/17/98 13:30 | 113 | 0 | 8355 Aero Dr. | San Diego | SD | 92123 | MH 151 on 8" VC | One | Roots | Roots | Area will be added to MC site | Y | N | Canyon | Soaked into canyon |  | N | N | N
983776 | Fax 571-6972 | 03/31/98 11:00 | G.Richardson | 6544160 | City of San Diego | 03/23/98 10:18 | 03/23/98 16:35 | 3770 | 0 | 2915 39th St. | San Diego | SD | 92105 | 8" VC | One | Other | Possible main break/rocks & dirt in main | Rodded to relieve overflow/refer to construction and TV sections. | Y | N | Canyon | Chollas Creek | San Diego Bay | Y | Y | Y | Three
991769 | Fax 571-6972 | 5/15/98 07:30 | M. Whelan | 654-4160 | City of San Diego | 5/14/98 20:55 | 5/15/98 01:55 | 11250 | 0 | 3111 Erie St./canyon | San Diego | SD | 92117 | 10" VC | One | Roots | Roots grew into canyon easement | Hand rod to relieve stop | Y | Y | Canyon | Storm Drain/Mission Bay | N/A | Y | Y | Y | Unknown | 17 signs posted
975210 | Fax 571-6972 | 02/04/98 15:30 | G.Richardson | 6544160 | City of San Diego | 02/04/98 10:00 | 02/04/98 11:00 | 12 | 0 | Baja Dr. & Tierra Baja Wy. | San Diego | SD | 92115 | 6" CP | One | Roots | Roots | Rodded to relieve stop | Y | N | Canyon | Pacific Ocean | Dissipated in canyon | Y | N | N
969664 | Fax 571-6972 | 01/06/98 14:50 | L.Finch | 6544160 | City of San Diego | 01/06/98 10:35 | 01/06/98 12:45 | 260 | 0 | 3091 Elm St./canyon | San Diego | SD | 92102 | 8" VC | One | Roots | Roots | Hand rod/refer to TV for pipe integrity | N | N | Canyon bed | Chollas Creek/SD Bay/Pacific Ocean | Contained in canyon | Y | N | N
978009 | Greg Peters | 02-24-98 0930 | Cheryl Brandstrom | 760-744-0460 | V.W.D. | 02-24-98 0700 | 02-25-98 1800 | 5 to 7 mg | none | easement | Carlsbad | S.D. | 92069 | 30" Line | 5 | broken pipe | steel pipe was possibly crushed when installed | in process of replacing bad pipe | y | n | Canyon De Las Encinas Ponds, and stream on golf course. | Batiquitos lagoon | pacific ocean | y | y | y | 14+ | area posted as per health dept.
933615 | Fax 571-6972 | 07/13/97 13:44 | Branco | 6544160 | City of San Diego | 07/13/97 08:24 | 07/13/97 11:15 | 855 | 0 | 1307 Upas St./canyon | San Diego | SD | 92103 | 6" cp main | 1 | Roots | Root blockage | Rodded 6" cp main | y | n | canyon floor | San Diego Bay |  | y | n
932271 | Fax 571-6972 | 07/15/97 14:45 | Gensler | 6544160 | City of San Diego | 07/05/97 17:10 | 07/14/97 19:20 | 36000 | 0 | Mobley St. & Winen Wy./canyon | San Diego | SD | 92123 | 8" vc main | 1 | Roots | Roots, rags, paper towels | Used hand rods, scoop to clear stop | y | n | canyon floor | Pacific Ocean |  | y | y | n
934851 | Fax 571-6972 | 07/18/97 20:22 | Branco | 6544160 | City of San Diego | 07/18/97 18:05 | 07/18/97 18:56 | 510 | 0 | 1301 Dellcrest Ln. | San Diego | SD | 92037 | 8" vc main | 1 | Roots | Root blockage | Machine rodded 8" vc main | y | n | canyon floor | Pacific Ocean |  | y | n | n
907174 | Fax 571-6972 | 07/25/97 16:02 | Harris | 6544160 | City of San Diego | 07/25/97 11:30 | 07/25/97 13:31 | 121 | 0 | 1248 Hayes St. | San Diego | SD | 92103 | 4" unmarked main | 2 | Roots | Roots and debris | Hand rodded 4" unmarked main | y | n | canyon floor | San Diego Bay |  | y | n | n
939877 | Fax 571-6972 | 08/09/97 16:11 | Branco | 6544160 | City of San Diego | 08/09/97 12:20 | 08/09/97 14:50 | 300 | 0 | 6161 Alvarado Rd. | San Diego | SD | 92120 | 8" vc main | 1 | Roots | Root blockage | Machine rodded to clear | y | y | canyon floor | San Diego River | soaked into canyon floor | y | n | n
940089 | Fax 571-6972 | 08/11/97 18:05 | Whelan | 6544160 | City of San Diego | 08/11/97 13:30 | 08/11/97 14:00 | 60 | 0 | I-163 North & Laurel Street (El Prado Bridge) | San Diego | SD | 92101 | 8" vc main | 3 | Construction | Stoppage following main repair | Machine rodded; found pieces of broken main | y | n | canyon floor | Pacific Ocean | dried in canyon | y | n | n
940386 | Fax 571-6972 | 08/20/97 07:45 | Richardson | 6544160 | City of San Diego | 08/12/97 18:12 | 08/12/97 22:52 | 220 | 0 | Altadena Av. & Sterling Ct. | San Diego | SD | 92105 | 8" vc main | 1 | Vandalism | 1' x 1' x 1' concrete block | Removed debris (concrete block) from main | y | n | canyon floor | Pacific Ocean | dried in canyon | y | n | n
942198 | Fax 571-6972 | 08/23/97 14:38 | Branco | 6544160 | City of San Diego | 08/23/97 09:27 | 08/23/97 11:00 | 50 | 0 | 1843 Bancroft St. | San Diego | SD | 92102 | 6" cp main | 1 | Roots | Root blockage | Removed roots from manhole | y | n | canyon floor | San Diego Bay | soaked into canyon floor | y | n | n
942213 | Fax 571-6972 | 08/23/97 17:58 | Branco | 6544160 | City of San Diego | 08/23/97 13:34 | 08/23/97 16:24 | 340 | 210 | 6600 Navajo Rd. | San Diego | SD | 92120 | 8" vc main | 1 | Roots | Root blockage | Rodded to relieve stop, vacuumed portion of spill | y | n | canyon floor | San Diego Bay | soaked into canyon floor | y | n | n
944639 | Fax 571-6972 | 08/31/97 15:30 | Neel | 6544160 | City of San Diego | 08/31/97 11:50 | 08/31/97 13:30 | 100 | 0 | 18535 Bernardo Trails Dr. | San Diego | SD | 92128 | 8" vc main | 1 | Roots | Root blockage | Machine rodded 8" vc main/ref. to area supv. | y | n | canyon floor | Lake Hodges |  | y | n | n
945280 | Fax 571-6972 | 09/05/97 15:06 | Richardson | 6544160 | City of San Diego | 09/05/97 07:47 | 09/05/97 10:40 | 685 | 0 | 3679 Collier Av. | San Diego | SD | 92116 | 8" vc main | 2 | Roots | Root blockage | Relieved stop by rodding/flushing 8" vc main | y | n | canyon floor | Pacific Ocean | soaked into canyon floor | y | n | n
948096 | Fax 571-6972 | 09/19/97 02:55 | Whelan | 6544160 | City of San Diego | 09/18/97 16:34 | 09/18/97 18:15 | 101 | 0 | 5211 Joan Ct. | San Diego | SD | 92115 | 8" vc main | 1 | Roots | Root blockage | Rodded 8" vc main w/screw to clear stop | y | y | canyon floor | Pacific Ocean | dried in canyon | y | n | n
948570 | Fax 571-6972 | 09/20/97 15:26 | Branco | 6544160 | City of San Diego | 09/20/97 09:04 | 09/20/97 11:28 | 72 | 0 | 4421 New Hampshire St. | San Diego | SD | 92108 | 6" cp main | 1 | Roots | Roots, grease | Machine rodded 6" cp main, ref for MC site | y | y | canyon floor | Pacific Ocean | dried in canyon | y | n | n
948574 | Fax 571-6972 | 09/20/97 16:51 | Branco | 6544160 | City of San Diego | 09/20/97 11:09 | 09/20/97 16:30 | 963 | 0 | 2685 Montclair St. | San Diego | SD | 92104 | 10" vc main | 1 | Vandalism | debris dumped in manhole | Ref. to conf. space team to remove rocks, barricades; ref for bucket | y | n | canyon floor | San Diego Bay | dried in canyon | y | n | n
966434 | Fax 571-6972 | 12/17/97 13:15 | Parker | 6544160 | City of San Diego | 12/07/97 00:00 | 12/14/97 18:00 | 60911 | 5950 | 3055 Erie St./canyon | San Diego | SD | 92117 | 8" VC | 3 | Grvty Mn Brk | Line break | Built berm, diverted flow back into broken pipe, ref to constr crew | Y | Y | Canyon floor |  | Mission Bay | Y | Y | Y
967589 | Fax 571-6972 | 12/21/97 18:38 | Branco | 6544160 | City of San Diego | 12/19/97 20:58 | 12/20/97 11:15 | 4285 | 3525 | Albatross St. & Brant St. | San Diego | SD | 92103 | 8" VC | 1 | Other | Unknown | Relieved unknown blockage, recovered 3,525 gals. of overflow | Y | N | Canyon floor | San Diego Bay/Pacific Ocean |  | Y | N/A | N
952126 | Fax 571-6972 | 10/07/97 19:10 | Finch | 6544160 | City of San Diego | 10/07/97 09:24 | 10/07/97 10:34 | 210 | 0 | 3019 Olive St./canyon | San Diego | SD | 92104 | 8" VC Sewer Main | 1 | Rocks | Rocks in Main | Machine rodded 8" vc main | Y | N | Canyon Surface/Soaked into Ground |  | Soaked into the ground |  | N/A | N
951361 | Fax 571-6972 | 10/03/97 06:32 | Whelan | 6544160 | City of San Diego | 10/02/97 21:58 | 10/02/97 23:31 | 23 | 0 | 907 Court Wy. | San Diego | SD | 92103 | 6" CP | 1 | Roots | Roots in Manhole | Hand rod/vacuum/machine rod 6" cp main | Y | Y | Canyon through Storm Drain | San Diego River | Soaked into ground in canyon | Y |  | N
957754 | Fax 571-6972 | 11/06/97 11:00 | Davis | 6544160 | City of San Diego | 11/05/97 18:55 | 11/05/97 19:55 | 6000 | 1500 | 10674 Rancho Carmel Dr. | San Diego | SD | 92128 | 10" PVC | 1 | Roots | Rocks and construction debris | Rodded to relieve stop | Y | Y | Chicarita Creek | Los Penasquitos Creek | Canyon | Y | Y | Y
932333 | Fax 571-6972 | 07/07/97 13:15 | Richardson | 6544160 | City of San Diego | 07/07/97 09:46 | 07/07/97 10:21 | 35 | 0 | Banillo Dr. & Malcolm Dr. | San Diego | SD | 92115 | 6" cp main | 1 | Grease | Grease build-up | Rodded 2 sec. upstream/downstream | y | y | Chollas Creek | San Diego Bay | soaked into creek bed | y | n
933451 | Fax 571-6972 | 07/11/97 21:21 | Branco | 6544160 | City of San Diego | 07/11/97 17:38 | 07/11/97 19:02 | 252 | 0 | 3676 Orange Av. | San Diego | SD | 92105 | 6" vc main | 1 | Grease | Grease and debris | Rodded 6" vc main | y | y | Chollas Creek | San Diego Bay |  | y | n
934093 | Fax 571-6972 | 07/16/97 13:10 | Richardson | 6544160 | City of San Diego | 07/16/97 08:15 | 07/16/97 08:55 | 20 | 20 | 1752 Adams Av. | San Diego | SD | 92116 | 6" cp main | 1 | Roots | Root blockage | Flushed/used root saw on 6" cp main | y | n | Chollas Creek | n/a | returned to syst via MH #382 | y | n | n
938414 | Fax 571-6972 | 08/04/97 11:30 | Richardson | 6544160 | City of San Diego | 08/04/97 07:00 | 08/08/97 09:02 | 6100 | 4000 | 51st St. & Hilltop Dr. | San Diego | SD | 92114 | 21" vc main | 1 | Construction | Rocks in main from construction | Flushed main, vacuumed spill | y | n | Chollas Creek | Pacific Ocean | storm channel/recovered | y | y | n
942208 | Fax 571-6972 | 08/23/97 18:04 | Branco | 6544160 | City of San Diego | 08/23/97 12:10 | 08/23/97 15:30 | 800 | 0 | 330 Willie James Jones St. | San Diego | SD | 92102 | 6" vc main | 1 | Roots | Root blockage | Machine rodded to relieve stop | y | n | Chollas Creek | San Diego Bay | soaked into canyon floor | y | n | n
942225 | Fax 571-6972 | 08/24/97 14:08 | Branco | 6544160 | City of San Diego | 08/24/97 10:15 | 08/24/97 12:30 | 135 | 0 | 2619 Montclair St./canyon | San Diego | SD | 92104 | 6" cp main | 1 | Rocks | Rock blockage | Machine rodded, ref. for PM scheduling | y | n | Chollas Creek | San Diego Bay | soaked into canyon floor | y | n | n
942229 | Fax 571-6972 | 08/24/97 20:26 | Branco | 6544160 | City of San Diego | 08/24/97 17:02 | 08/24/97 19:20 | 690 | 0 | 4942 Lantana Dr. | San Diego | SD | 92105 | 6" vc main | 1 | Roots | Root blockage | Machine rodded 6" vc main, ref. for PM scheduling | y | n | Chollas Creek | San Diego Bay | soaked into canyon floor | y | n | n
950111 | Fax 571-6972 | 09/27/97 12:39 | Branco | 6544160 | City of San Diego | 09/27/97 07:44 | 09/27/97 09:30 | 10600 | 0 | Market St. & Merlin St./under trolley tracks | San Diego | SD | 92114 | 15" vc main | 1 | Rocks | Rock blockage | Machine rod, ref for bucketing to remove add'l rocks | y | y | Chollas Creek | San Diego Bay |  | y | y | n
982018 | Fax 571-6972 | 03/16/98 02:39 | M.Bedard | 6544160 | City of San Diego | 03/15/98 18:37 | 03/16/98 01:00 | 19150 | 0 | 3455 Landis St. | San Diego | SD | 92104 | 15" VC | One | Vandalism | Vandalism-rocks, debris, mattress in manhole | Removed debris/lock down and seal manholes in area | Y | Y | Chollas Creek | San Diego Bay |  | Y | Y | N
1 | PAM | 2/17/98, 23:30 | HENRY MONROE | 728-1178 | RAINBOW MWD | 1998-02-17 10:45 | 2/17/98, 22:00 | 4500 | 0 | OLD RIVER, GOPHER | BONSALL | S.D. | 92008 | M.H. 3P2161 | 0 | POWER FAILURE | BACKUP GENERATOR FAILED TO TURN ON | REPAIR GENERATOR | Y | Y | CREEK | SAN LUIS REY RIVER | PACIFIC OCEAN | Y | Y | N | N/A | NONE
977247 | Fax 571-6972 | 02/17/98 15:05 | W.Graham | 6544160 | City of San Diego | 02/17/98 07:30 | 02/17/98 08:00 | 150 | 0 | 18700 W. Bernardo Dr.** | San Diego | SD | 92128 | SPS 77 | One | Other | Station shut down per Hale Treatment Plant | Turn station back on | Y | N | Creek | Lake Hodges |  | Y | N | Y | Unknown
977344 | Fax 571-6972 | 02/18/98 07:30 | M.Bedard | 6544160 | City of San Diego | 02/17/98 15:09 | 02/18/98 04:30 | 120150 | 0 | 9255 Camino Santa Fe | San Diego | SD | 92121 | 21" CI & VC | Two | Grvty Mn Brk | Deteriorated 21" CI pipe caused rocks in line | Contain overflow/make repairs/line previously submitted for repairs | Y | N | Creek | Penasquitos Lagoon | Pacific Ocean | Y | Y | N
940375 | Fax 571-6972 | 08/13/97 06:19 | Whelan | 6544160 | City of San Diego | 08/12/97 16:18 | 08/12/97 17:45 | 720 | 50 | 60th St. & Fulmar St. | San Diego | SD | 92114 | 8" vc main | 1 | Roots | Heavy roots | Set up pump, vacuumed heavy roots | y | n | creek bed | Pacific Ocean | dried in canyon | y | n | n
940534 | Fax 571-6972 | 08/14/97 15:00 | Richardson | 6544160 | City of San Diego | 08/13/97 10:03 | 08/13/97 03:20 | 25925 | 19200 | 7120 Bullock Dr. | San Diego | SD | 92114 | 10" vc main | 1 | Rocks | Rocks, grease, debris | Rodded 10" vc main to relieve stop, recovered portion of spill | y | n | creek bed | Pacific Ocean | soaked into canyon florr | y | y | n
999415 | Fax 571-6972 | 6/29/98 18:12 | W. Hampton | 654-4160 | City of San Diego | 6/29/98 07:45 | 6/29/98 16:00 | 742.5 | 600 | 9310 Friars Rd. | San Diego | SD | 92128 | 12" CI | One | Grvty Main Brk | El Nino caused hillside to fall into pipe causing break | Repaired 12" ci main; refer to Engineering for re-routing of creek bed | Y | N | Creek bed | N/A | Pumped back into system | Y | N | N | N/A | N/A
985129 | Fax 571-6972 | 03/31/98 11:00 | G.Richardson | 6544160 | City of San Diego | 03/31/98 08:39 | 03/31/98 09:51 | 3600 | 0 | 555 Cadman St. | San Diego | SD | 92114 | 8" VC | One | Other | Possible main break | Rodded main/refer to construction and TV sections | Y | N | Creek in canyon | Chollas Creek | San Diego Bay | Y | Y | Y | One
962653 | Fax 571-6972 | 11/27/97 20:15 | Finch | 6544160 | City of San Diego | 11/27/97 15:02 | 11/27/97 18:32 | 315 | 0 | 8587 Parkbrook St. | San Diego | SD | 92114 | 8" VC | 1 | Roots | Roots | Removed stop, ref to area sprvsr for re-clean, televising | N | N | Curb | San Diego Bay | 8587 & 8589 Parkbrook/yard | Y | N/A | N
989882 | Fax 571-6972 | 5/01/98 10:15 | R. Parker | 654-4160 | City of San Diego | 5/01/98 07:59 | 5/1/98 08:50 | 51 | 0 | 3216 Camto. Eastbluff | San Diego | SD | 92122 | 8" VC | One | Grease | Grease build-up inside main | Flushed main to remove blockage | Y | Y | Curb & storm drain | Rose Creek/Mission Bay/Pacific Ocean | N/A | Y | N | N | N/A | N/A
970317 | Fax 571-6972 | 01/09/98 15:15 | L.Finch | 6544160 | City of San Diego | 01/09/98 08:59 | 01/09/98 12:30 | 2110 | 2110 | 1600 Upas St. | San Diego | SD | 92103 | 6" VC | One | Construction | Contractor's temporary hook-up | Replace 4" hookup with 6" until made permanent when new main laid | Y | N | Curb line on Upas and Herbert | San Diego Bay | Recovered by city crews | N | Y | N
967053 | Fax 571-6972 | 12/17/97 15:30 | Parker | 6544160 | City of San Diego | 12/17/97 07:13 | 12/17/97 10:42 | 1050 | 0 | 3078 Mercer Ln. | San Diego | SD | 92122 | 8" VC | 1 | Debris | Debris | Rodded to relieve stop, ref. for poss. PM site | Y | Y | Curb/storm drain/San Clemente canyon/interc 1 | Mission Bay/Pacific Ocean |  | Y | Y | N
978012 | N/A | 9/24/97 800 | Lance Lauricha | 738-4323 | City of Escondido | 9/24/97 800 | 9/24/97 1045 | 247.5 | 45 | 330 W. Felicita | Escondido | SD | 92027 | Private Cleanout | 1 | Private cleanout | Unknown | Private cleanout, Plumber cleared blockage. | Y | Y | Dead Horse Creek | Lake Hodges | N/A | Y | N | N | N/A
978027 | KATHY STONE-FAX AND CRWQCB | 3/12/98-P.M. | PAT GUEVARA | 760-438-2722 | CARLSBAD MWD | 3/11/98-7:45P | 3/11/98-7:52P | 2000 | 0 | 2700 BLOCK OF AVENIDA DE ANITA | CARLSBAD | SD | 92008 | MANHOLE | 1 | GREASE | GREASE BLOCKAGE UPSTREAM CAME LOOSE AND FORCED @ 2,000 GAL. OUT OF MANHOLE INSTANTANEOUSLY | BLOCKAGE CLEARED ITSELF. THIS AREA IS CURRENTLY ON OUR PREVENTATIVE MAINTENANCE HIGH PRIORITY LIST. | Y | Y | DESILTING BASIN BEHIND VON'S SHOPPING CTR. | BUENA VISTA CREEK AT EL CAMINO REAL | BUENA VISTA LAGOON | Y | Y | N | N/A | ADVISED KATHY STONE ON VOICE MAIL OF OUR FOLLOW UP & INVESTIGATION
978027 | Faxed and Called | 1/20/98 1045 | Todd Anderson | 738-4347 | City of Escondido | 1/20/98 735 | 1/20/98 835 | 12,000 Gallons | 200 Gallons | 1800 Block Citricado Pkwy. | Escondido | SD | 92025 | Manhole, Sewer Atlas Page 444 MH. 3977 | 0 | Roots and Grease | Roots and grease formed stoppage in main line causing it to back-up and overflow. | This is an easement line and has been recommended for replacement. | Y | Y | Did not reach surface waters. | N/A | Open field | Y | Y | Y | Two | No samples taken.
993413 | Fax 571-6972 | 5/22/98 15:15 | R, Burton | 654-4160 | City of San Diego | 5/22/98 09:55 | 5/22/98 11:55 | 240 | 235 | 3162 Monroe Av. | San Diego | SD | 92116 | 8" VC | One | Construction | Rocks in 8" VC main | Machine rodded main to relieve stop/removed rocks from 8" vc main | N | N | Dirt around manhole | Vactored up spill | N/A | Y | N | N | N/A | N/A
993635 | Fax 571-6972 | 5/25/98 16:00 | J. McPherson | 654-4160 | City of San Diego | 5/25/98 12:16 | 5/25/98 14:16 | 120 | 0 | 2955 Wing St. | San Diego | SD | 92110 | 8" VC | One | Grease | Blockage caused by grease | Removed grease from main to relieve stop | N | N | Dirt around manhole | N/A | N/A | Y | N | N | N/A | N/A
999185 | Fax 571-6972 | 6/30/98 08:00 | G. Richardson | 654-4160 | City of San Diego | 6/23/98 15:14 | 6/26/98 17:40 | 4405 | 0 | 47th St. & Fairmount Av. | San Diego | SD | 92105 | 8" VC | One | Roots | Blockage caused by grease and roots | Remove root/grease stop from 8" vc main | Y | Y | Dirt ditch | Chollas Creek | Soaked into canyon | Y | Y | N | N/A | N/A
978018 |  |  | Mike Teem | 7609667868 | Water Utilities Dept. City of Oceanside | 10/13/97 1010 | 10/13/97 1115 | 650 | 0 | 200 Blk. Of Avenida Margarita | Oceanside | SD | 92057 | Manhole | 0 | Grease | Grease & rags in City main caused overflow from manhole. | Vactor truck jet cleaned main. | N | Y | Drainage Ditch | N/A | Soaked into dirt drainage ditch. | Y | N/A | N | N/A | Spill washed down by Vactor truck and paper debris was picked up.
981601 | Fax 571-6972 | 03/13/98 05:48 | M.Whelan | 6544160 | City of San Diego | 03/12/98 18:39 | 03/12/98 21:39 | 540 | 300 | 4403 Cynthia Pl. | San Diego | SD | 92105 | 8" VC | One | Grvty Mn Brk | Main break caused by roots in main | Flushed and rodded main/need to repair pipe | Y | Y | Drainage ditch | Storm channel |  | Y | N | N
954887 | Fax 571-6972 | 10/22/97 12:10 | Finch | 6544160 | City of San Diego | 10/22/97 07:11 | 10/22/97 08:50 | 74 | 0 | 3300 Redwood St. | San Diego | SD | 92104 | 6" CP | 1 | Roots | Roots and Debris | Cleaned main, ref. to TV crew for poss. group job referral | Y | N | Dried along curb and street | San Diego Bay |  | Y | N/A | N
994128 | Fax 571-6972 | 5/29/98 16:23 | M. Whelan | 654-4160 | City of San Diego | 5/28/98 15:17 | 5/28/98 17:42 | 290 | 0 | 2872 Arbodar Rd. | San Diego | SD | 92154 | 10" VC | One | Grease | Grease in main | Vacuumed heavy grease from main | Y | Y | Dried in Preserve | N/A | N/A | Y | N | N | N/A | N/A
954284 | Fax 571-6972 | 10/17/97 13:08 | Finch | 6544160 | City of San Diego | 10/17/97 13:08 | 10/17/97 14:30 | 41 | 0 | 944 Crosby St. | San Diego | SD | 92113 | 6" VC | 1 | Grease | Heavy Grease | Removed stop, placed on PM schedule | Y | Y | Dried in Storm Drain | San Diego Bay |  | Y | N/A | N
954416 | Fax 571-6972 | 10/18/97 13:47 | Branco | 6544160 | City of San Diego | 10/18/97 10:34 | 10/18/97 11:30 | 28 | 0 | Ingraham St. & La Cima St. | San Diego | SD | 92109 | 5" SL | 2 | Roots | Roots | Machine rodded to relieve stop | Y | N | Dried up at curb | Pacific Ocean |  | Y | N/A | N
967944 | Fax 571-6972 | 12/23/97 06:45 | Whelan | 6544160 | City of San Diego | 12/23/97 24:30 | 12/23/97 24:30 | 50 | 0 | 4422 Kansas St. | San Diego | SD | 92104 | 8" VC | 1 | Other | Vactor surcharge | Surcharge from full drain cleaner subsided | Y | N | Dried up in street |  |  | Y | N | N
980624 | Fax 571-6972 | 03/07/98 13:11 | D.Branco | 6544160 | City of San Diego | 03/07/98 10:38 | 03/07/98 11:19 | 20 | 0 | 4400 Del Monte Av. | San Diego | SD | 92107 | 6" CP | One | Grease | Grease | Flushed main/referred to area supervisor for scheduled maintenance | N | N | Dried up in street | N/A | Dried up in street | Y | N | N
933575 | Fax 571-6972 | 07/12/97 09:35 | Kelly | 6544160 | City of San Diego | 07/11/97 21:28 | 07/12/97 00:00 | 46 | 0 | 6526 Lanston St. | San Diego | SD | 92111 | 8" vc main | 1 | Debris | Wastepaper | Rodded 8" vc main to relieve stop, ref. to sup. for eval. | y | y | E. Mission Bay | Pacific Ocean |  | y | n
978025 | (619) 571-6972 | 1998-01-06 08:44 | Patti S. Page | (760) 723-5640 | Fallbrook Public Utility District | 1998-01-05 19:30 | 1998-01-06 00:30 | 1500 | 0 | 1400 Block Mission Rd. | Fallbrook | SD | 92028 | Manhole | 1 | Roots & Grease | Roots and grease plugged line. | Cleaned line, checked all downstream manholes and cleaned lines as needed. | Y | N | Earthen Creek | Fallbrook Creek | NA | Y | N | Y | 3 | Spill percolated quickly into earthen creek bed (dirt culvert) and did not reach Fallbrook Creek.
| BOB BAKER | 1/19/98 1300 | MIKE CALVERT | (909)676-4101 | R.C.W.D. | 1/18/98 2100 | 1/19/98 0900 | 675000 | 0 | 31008 RANCHO CA. ROAD | TEMECULA | RV | 92591 | 12" Reclaimed Reservoir Overflow Line | 0 | TELEMETRY CALIBRATION ERROR | RESERVOIR OVERFLOWED DUE TO THE LEVEL CALIBRATION WAS OFF BY 2' & THE ALTITUDE VALVE SETTING WAS OFF BY 2' | RECALIBRATED LEVEL | N | Yes | EMPIRE CREEK | N/A | EMPIRE CREEK | Yes | No | No | N/A | Spill Contents were fully disinfected Title 22 Effluent
978004 | Called and Faxed | 7/24/97 1630 | John Vaught | 738-4323 | City of Escondido | 7/21/97 600 | 7/24/97 1800 | 4300 | 0 | 1433 N. Broadway | Escondido | SD | 92026 | Private cleanout | 1 | Private cleanout | Private system | Private System | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific | Y | Y | Y | 3
978005 | Called and Faxed | 7/30/97 1020 | Lance Lauricha | 741-4668 | City of Escondido | 7/29/97 500 | 7/30/97 1445 | 3300 | 1500 | 1625 E. Grand Ave. | Escondido | SD | 92026 | Private cleanout | 1 | Private cleanout/grease | Large amounts of grease in private cleanout. | Property owner said they would install additional cleanouts to ensure proper cleaning in the future | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | Y | Y | 5 | Samples were taken.
978006 | Called and Faxed | 8/2/97 1330 | Lucky Bishop | 741-4668 | City of Escondido | 8/1/97 1400 | 8/2/97 1400 | 15720 | 6720 | 725 N. Fig St. | Escondido | SD | 92026 | Private cleanout | 1 | Private cleanout | Private system | Asked property to maintain their system. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | Y | Y | 5 | Samples were taken.
978007 | Called and Faxed | 8/18/97 1330 | Mike Schultz | 738-4347 | City of Escondido | 8/16/97 2323 | 8/16/97 2440 | 1750 | 0 | 802 W. 3rd. | Escondido | SD | 92025 | Sewer Atals PG. 387 MH. 6129 | 1 | Debris/Grease | Build up of grease and other debris caused mainline stoppage. | This line segment has been place on the City's capital improvement plan. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | Y | Y | 5 | Samples were taken.
978009 | N/A | 9/2/97 1350 | Mike Schultz | 738-4347 | City of Escondido | 8/30/97 915 | 8/30/97 1020 | 195 | 50 | 1141 E. Washington | Escondido | SD | 92025 | Private Cleanout | 1 | Private Cleanout | Private cleanout | Elia's Restraunt, possible grease problem. Will be forwarded to Pretreatment Inspector. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | N | N | N/A
978010 | N/A | 9/3/97 1115 | Mike Schultz | 738-4347 | City of Escondido | 8/30/97 ? | 8/31/97 ? | 400 Estimated | 100 | 1629 E. Valley Pkwy. | Escondido | SD | 92027 | Private cleanout | 1 | Private cleanout/Grease | Grease trap which was not being maintained was the cause of the overflow. | The Golden Sun Restaurant was warned by our Pretreatment Inspector/Industrial Waste Inspector of the importance of maintaining his grease trap. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | N | N | N/A
978023 | Faxed | 1/2/1998 1545 | Lance Lauricha | 738-4347 | City of Escondido | 1998-01-02 08:00 | 1/2/98 1500 | 480 gallons | 30 gallons | 1026 E. 5th. Ave. | Escondido | SD | 92026 | Private cleanout | 0 | Unknown | Unknown-Private clean-out | Sewer Dept. cleared the stoppage and installed a cap. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | N | N | N/A | No samples taken.
978025 | Quarterly Report only | N/A | Don Keifer | 741-4668 | City of Escondido | 1/12/98 930 | 1/12/98 1000 | 30 Gallons | 0 | Aldergrove Pl. and Andreason St. | Escondido | SD | 92025 | Manhole, Sewer Atlas Page 384 MH. 4300 | 0 | Roots | Roots in manhole caused stoppage. | Manhole was put on a root inspection schedule. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | N | N | N | N/A | No samples taken.
978029 | Quarterly Report only County Health was notified. | 2/11/98 800 | Lance Lauricha | 738-4347 | City of Escondido | 2/7/98 800 | 2/10/98 1700 | 625 Gallons | 25 Gallons | 520 W. Grand Ave. | Escondido | SD | 92025 | Private cleanout | 0 | Unknown | Unknown-Private clean-out | Plumber cleared private blockage. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | N | N | N/A | No samples taken.
978031 | Quarterly Report only County Health was notified. | 2/14/98 1930 | Julius Turner | 741-4854 | City of Escondido | 2/14/98 1215 | 2/14/98 1630 | 1,275 Gallons | 1,000 Gallons | 729 Chestnut St. | Escondido | SD | 92029 | Overflowing from private clean-out | 0 | Debris | Debris in main line caused waste water to backup into private system resulting in an overflow. | Cleaned main line and continue routine maintenance. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | N | N | N/A | No samples taken.
978032 | Quarterly Report only County Health was notified. | 2/18/98 1430 | John Vaught | 738-4323 | City of Escondido | 2/18/98 700 | 2/18/98 745 | 90 Gallons | 0 | 1564 Tanglewood | Escondido | SD | 92025 | Manhole, Sewer Atlas Page 426 MH. 5803 | 2 | Construction Debris | Some how sand and mud entered the system causing system to back-up. | Cleared blockage, cleaned effected lines as well as C.C.T.V. inspection. The Field inspector was notified. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | N | Y | Three | No samples taken.
978033 | Quarterly Report only County Health was notified. | 3/4/98 1430 | Todd Anderson | 741-4854 | City of Escondido | 3/4/98 1215 | 3/4/98 1223 | 375 Gallons | 0 | 1564 Tanglewood | Escondido | SD | 92025 | Manhole, Sewer Atlas Page 426 MH. 5803 | 3 | Unknown | We suspect that a contractor discharged a large amount of waste water in to our system over taxing it. The Field Inspector was notified and is conducting the investigation. Once again the main lines were televised. No problems were found. | The contractor is being watched! We are also keeping a close eye on this manhole and main line. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | N | Y | two | No samples taken.
978034 | Quarterly Report only County Health was notified. | 3/9/98 945 | Lance Lauricha | 839-4347 | City of Escondido | 3/9/98 807 | 3/9/98 900 | 300 Gallons | 25 Gallons | 1050 Rocksprings | Escondido | SD | 92025 | Private cleanout | 0 | Grease | Grease blockage in apartment service lateral. | Property owner is having a plumbing firm clean all their service laterals. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | N | Y | two | Samples were taken.
978036 | Called and Faxed | 3/17/98 1500 | Lance Lauricha | 839-4347 | City of Escondido | 3/16/98 700 | 3/17/98 1230 | 1,860 Gallons | 500 Gallons | 1236 (A and B) Simpson Way | Escondido | SD | 92025 | Private cleanout | 0 | Rags and toilet paper | Same as short description. | We advised them to clean their system once a year. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | Y | Y | Three | Samples were taken.
978038 | Called and Faxed | 3/28/98 1235 | Lance Lauricha | 839-4347 | City of Escondido | 3/28/98 1215 | 3/28/98 1340 | 3,150 Gallons | 0 | Lincoln Ave. | Escondido | SD | 92026 | Manhole, Sewer Atlas Page 308 MH.3077 | 0 | Grease | Grease blocked main line. | City crew removed stoppage. Will continue routine maintenance. Pretreatment Inspector was notified concerning the grease problem. | Y | Y | Esc. Creek | San Elijo Lagoon | Pacific Ocean | Y | Y | Y | Three | Samples were taken.
978003 | Called and Faxed | 7/19/97 1030 | Joe Sanchez | 739-5538 | City of Escondido | 7/19/97 1000 | 7/19/97 1100 | 3000 | 0 | 223 S. Fig st. | Escondido | SD | 92025 | Sewer Atlas PG.368 MH.6470 | 1 | Roots / Grease | Grease, paper, and roots caused stoppage in sewer mainline. | This mainline was put on a three month cleaning schedule. | Y | Y | Escondido Creek | San Elijo Lagoon | Pacific Ocean | Y | Y | Y | 3 | Samples were taken.
978005 | (619) 571-6972 | 1997-07-28 09:00 | Kyle Drake | (760) 728-1125 | Fallbrook Public Utility District | 1997-07-27 20:00 | 1997-07-27 21:30 | 1300 | 5 | 406 Potter St. | Fallbrook | SD | 92028 | 4" Clay Cleanout | 1 | Grease | Grease, paper, and grit build up in main line. | Rodded from cleanout to main line. Recovered grease, paper, and other objects. Flushed main line. | Y | Y | Fallbrook Creek | Lake O'Neil | N/A | Y | Y | Y | 3 | OES Control # 97-2937.
978007 | (619) 571-6972 | 1997-07-30 10:30 | Patti Page | (760) 723-5640 | Fallbrook Public Utility District | 1997-07-29 12:30 | 1997-07-29 13:00 | 1800 | 50 | 532 E. Fallbrook St. | Fallbrook | SD | 92028 | Cleanout | 1 | Grease | Grease, paper, and grit build-up in main. | Flushed main line. | Y | Y | Fallbrook Creek | Lake O'Neil | N/A | Y | Y | Y | 3 | OES Control # 97-2980. 50 gallons used in wash down. Posted all public access areas along Fallbrook Creek from 532 E. Fallbrook St. to Mission Rd. Attempted to notify Camp Pendleton (no answer for 3 days).
978020 | (619) 467-2952 | 1997-12-09 14:30 | Joel Holt | 7607235640 | Fallbrook Public Utility District | 1997-12-09 04:00 | 1997-12-09 06:00 | 846 | 0 | 1425 S. Alturas | Fallbrook | SD | 92028 | Lift Station #5 | 1 | Pump Station Failure | Pump control system failed. | Reset pump controler. | Y | Y | Fallbrook Creek | Lake O'Neil | NA | Y | N | N | NA
978026 | SWRCB | 1998-01-07 14:45 | Joel Holt | 7607265640 | Fallbrook Public Utility District | 12/24/97 *a.m. | 1998-01-06 15:30 | 5600 | 500 | 433 Fallbrook Street | Fallbrook | SD | 92028 | Lateral | 1 | Line Break | Contractor broke lateral accidentally. They were not aware of it. FPUD discovered sewage in the downstream storm water system. | Repaired line, vacuumed wastewater collected, covered with 2 inches of soil. | Y | Y | Fallbrook Creek | Lake O'Neil | NA | Y | N | Y | 3 | County Health Representatives Kathy Stone and Steven Durham assessed the site. Removed 1/2 yd. of soil that was contaminated and covered spill with 2 inches of soil. FPUD sand bagged creek and recovered as much as possible.
978036 |  |  | Jeremy Kemp | 760/966-7868 | Water Utilities Dept. City of Oceanside | 02/15/98 1250 | 02/15/98 2110 | 800 | 2000 | 2861 Turnbull (easement line) | Oceanside | SD | 92056 | Manhole | 0 | Grease | Grease build up in line through the easement. | Drop chlorine into line for grease prevention. WE NEED A NEW ROAD INTO THE EASEMENT. | N | Y | Flood Control Ditch | Corps of Engineers Detention Pond | N/A | N | N/A | N | N/A
978024 | Fax | 1-5-98, 7:15 am | Woodward | 619-522-7380 | City of Coronado | 1-13-98, 12:00 | 1-14-98, 15:45 | 6,000 gal | 200 gal | Tenth and Glorietta | Coronado | SD | 92118 | Sewer line | 0 | Pipe break | Sewer line collapsed into storm drain | Replaced sewer line over storm drain | N | Y | Glorietta Bay | Pacific Ocean | Sewer line | Y | N | Y | 3
978025 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 07-08-97 | 07-08-97 |  | not known | International Border | San Diego | SD | 92154 | Laureles System | 1 | Line Break |  | spill pumped by City of SD MWWD | Y | N | Goat Creek | None |  | Y | N | N
978026 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 07-09-97 | 07-09-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 2 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978027 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 07-10-97 | 07-10-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 3 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978028 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 07-24-97 | 07-24-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 4 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978029 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-07-97 | 08-07-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 5 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978030 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-08-97 | 08-08-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 6 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978031 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-11-97 | 08-11-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 7 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978032 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-12-97 | 08-12-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 8 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978033 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-13-97 | 08-13-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 9 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978034 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-14-97 | 08-14-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 10 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978035 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-15-97 | 08-15-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 11 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978036 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-16-97 | 08-16-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 12 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978037 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-17-97 | 08-17-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 13 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978038 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-18-97 | 08-18-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 14 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978039 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-19-97 | 08-19-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 15 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978040 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-20-97 | 08-20-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 16 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978041 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-21-97 | 08-21-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 17 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978042 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-22-97 | 08-22-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 18 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978043 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-08-97 | 09-08-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 19 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978044 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-11-97 | 09-11-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 20 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978045 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-12-97 | 09-12-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 21 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978046 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-15-97 | 09-15-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 22 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978047 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-17-97 | 09-17-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 23 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978048 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-18-97 | 09-18-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 24 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978049 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-19-97 | 09-19-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 25 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978050 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-25-97 | 09-25-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 26 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978051 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-26-97 | 09-26-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 27 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
978052 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-29-97 | 09-29-97 |  | 0 | International Border | San Diego | SD | 92154 | Laureles System | 28 | other | overload of collection system |  | Y | N | Goat Creek | None |  | N | N | N
992084 | Fax 571-6972 | 5/17/98 14:49 | D. Branco | 654-4160 | City of San Diego | 5/17/98 14:46 | 5/17/98 15:20 | 34 | 0 | 6619 Linda Ln. | San Diego | SD | 92120 | 8" VC | One | Roots | Roots caused blockage | Machine rod w/screw to relieve stoppage | N | N | ground & back yard | N/A | Ground & back yard | Y | N | N | N/A | N/A
970541 | Fax 571-6972 | 01/11/98 14:42 | D.Branco | 6544160 | City of San Diego | 01/11/98 11:14 | 01/11/98 12:30 | 38 | 0 | 65th St. & Imperial Av. | San Diego | SD | 92114 | 8" VC | One | Roots | Roots | Machine rodded/referred to area supervisor for scheduled PM | N | N | Ground around manhole |  | Dried into ground | Y | N | N
982022 | Fax 571-6972 | 03/16/98 14:30 | G.Richardson | 6544160 | City of San Diego | 03/16/98 06:32 | 03/16/98 10:32 | 240 | 0 | 35th St. & Landis St. | San Diego | SD | 92104 | 8" CP | One | Roots | Roots | Rodded main to relieve stop | Y | N | Ground at spil site | N/A | Soaked into canyon | Y | N | N
979598 | Fax 571-6972 | 03/03/98 09:00 | G.Richardson | 6544160 | City of San Diego | 03/02/98 15:31 | 03/02/98 17:31 | 120 | 0 | 1137 31st St. | San Diego | SD | 92102 | 8" VC | One | Roots | Roots, grease and debris in main | Rodded to relieve stop | Y | N | Ground at spill site | N/A | Soaked into dirt at site | Y | N | N
969976 | Fax 571-6972 | 01/08/98 12:30 | G.Richardson | 6544160 | City of San Diego | 01/07/98 18:31 | 01/07/98 19:05 | 150 | 75 | Imperial Av. & Woodman St./Wideman Park | San Diego | SD | 92114 | 6" VC | One | Roots | Roots | Rodded main/vactored approximately 75 gallons from spill site | N | N | Ground at spill site/manhole #138 |  | Soaked into ground | Y | N | Y | One
998256 | Fax 571-6972 | 6/23/98 05:40 | M. Whelan | 654-4160 | City of San Diego | 6/22/98 13:33 | 6/22/98 18:30 | 297 | 0 | Front St. & Spruce St./canyon west | San Diego | SD | 92103 | 6" VC | One | Roots | Roots in main | Machine rodded 6" cp main | Y | N | Ground in canyon | N/A | Ground in canyon | Y | N | N | N/A | N/A
978031 |  |  | Gary K. Orr | 760/966-4854 | Water Utilities Dept. City of Oceanside | 1998-01-05 | 01/08/98 1515 | 200 | 0 | 217 North Tremont Street | Oceanside | SD | 92054 | Private lateral | 0 | Other | Lateral has blockage & break. Every time commercial washer pumps out, the effluent comes up through cracks in the parking lot in fron of Bell's Liquor Store. |  | N | Y | Gutter | Storm Drain | N/A | N | N/A | N | N/A | Notified landowner (Partners ARO @ 1015 Chestnut Avenue,#A3 @ Carlsbad 92008.
978037 | Called and Faxed | 3/18/98 1834 | Lance Lauricha | 839-4347 | City of Escondido | 3/18/98 1834 | 3/18/98 2040 | 1,800 Gallons | 0 | 222Green Ave. | Escondido | SD | 92029 | Manhole, Sewer Atlas Page 449 MH. 5142 | 0 | Grease | Grease blocked main line. | City crew removed stoppage. Will continue routine maintenance. | Y | Y | Kit Carson or Dead Horse Creek | Lake Hodges | Pacific Ocean | Y | Y | Y | Five | Samples were taken.
989953 | Fax 571-6972 | 5/04/98 14:56 | W. Graham | 654-4160 | City of San Diego | 4/30/98 18:30 | 5/01/98 07:30 | 1638000 | 0 | 12101 Lake Dr. | San Diego | SD | 92025 | Sewer Pump Station 77 | One | Force Mn Brk | Footing settled, causing main to break | Took station off-line, executed repair of force main | Y | N | Lake Hodges | N/A | N/A | Y | Y | Y | Five | 4 signs posted
978001 | quarterly report | n/a | Orv Salisbury | 760-744-0460 | V.W.D. | 7-10-97 1830 | 7-10-97 1915 | 800 | none | 1510 Via Brisa Del Lago | San Marcos | S.D. | 92069 | sewer clean out | 1 | grease | grease blockage in a gravity 8" sewer line | new piping and a new pump station is under const. | y | y | Lake San Marcos | none | Lake San Marcos | y | n | y | 4+ | no body contact in the lake
978001 | quarterly report | n/a | Orv Salisbury | 760-744-0460 | V.W.D. | 7-10-97 1830 | 7-10-97 1915 | 800 | none | 1510 Via Brisa Del Lago | San Marcos | S.D. | 92069 | sewer clean out | 1 | grease | grease blockage in a gravity 8" sewer line | new piping and a new pump station is under const. | y | y | Lake San Marcos | none | Lake San Marcos | y | n | y | 4+ | no body contact in the lake
978012 | Quarterly Report | 05-27-98 0830 | Corey Harrell | 760-744-0460 | V.W.D. | 05-23-98 1030 | 05-23-98 1330 | 900 | none | and Broken Rock | San Marcos | S.D. | 92069 | 8" line | 0 | Roots | Roots in line caused overflow | Have added to our trouble spot list. | n | y | Lake San Marcos | none | Stromdrain | y | n | n | 0 | Contained in Strom drain box
978024 | RICHTER (VOICE MAIL) | 03/03/98, 1720 | SSgt Duke | 6197259762 | MCB, CAMP PENDLETON | 03/03/98, 1440 | 03/03/98, 1630 | 2000 | 0 | 1.5 miles East of Water Well 41618 Las Pulgas Rd | CAMP PENDLETON | SD | 920555008 | Las Flores Creek | 1 | LINE BREAK | Sewer Force main crossing Las Flores Creek from 41300 Lift Station to STP #9 broke because of high flows in creek. | Shut down 41300 Lift Station. Used Pumper trucks to keep wet well pumped down. Short term action - divert creek & repair line. Long term preventative measures - bore line under creek or suspend line over creek. | Y | N | Las Flores Creek | Pacific Ocean | Red Beach | Y | Y | N | 0 | Red Beach is military training area. No bodily contact occurs. No public access.
944680 | Fax 571-6972 | 09/08/97 09:50 | Richardson | 6544160 | City of San Diego | 09/02/97 11:15 | 09/02/97 13:15 | 6000 | 0 | 4290 Polk Av. | San Diego | SD | 92105 | 8" vc main | 1 | Grease | Grease blockage | Rodded 8" vc main, stopped resident from pumping into strm drn | y | y | Lexington Cyn. storm channel | Pacific Ocean | Dried in storm channel | y | y | n
978003 | FAX | 07/21/97 1045 | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 07/20/97 0910 | 07/20/97 1030 | 600 | 0 | Street in front of 2121 Oceanside Blvd. | Oceanside | SD | 92054 | Manhole | 0 | Blockage. | Easement line off Oc'side Blvd. Blocked with sticks, roots, grease, rocks, etc. | Cleaned street with Fire hydrant. | Y | Y | Loma Alta Creek | Loma Alta Slough | N/A | Y | N/A | Y | 2 | Loma Alta Creek is blocked off @ Bucc. Beach. Slough is being pumped into La Salina WWTP for treatment.
978027 |  |  | Norm Crum | 760/966-7868 | Water Utilities Dept. City of Oceanside | 01/03/98 2245 | 01/03/98 2330 | 350+ | 0 | 1999 So. El Camino Real | Oceanside | SD | 92054 | 4" Air Release Valve | 0 | Vandalism | Motor Vehicle crashed into Air Release Valve, over Forse Main from Buena Vista Lift Station. | Repaired Valve. Steel pipe posts will be installed to prevent damage from another crash. | Y | Y | Loma Alta Creek | Loma Alta Slough | Pacific Ocean | Y | N/A | Y | 2 | Spill occurred during storm. Creek running full, anyway!.
978037 | Voice Mail | 02/24/98 0430 | Paul Hojo | 760/966-4870 | Water Utilities Dept. City of Oceanside | 02/24/98 0030 | 02/24/98 0330 | 7500 | 0 | 1330 South Tait Street (La Salina WWTP) | Oceanside | SD | 92054 | Load Equalization Tank | 0 | Infiltration | Heavy rain infiltration caused increased raw sewage flow into headworks. LET exceeded max. level of 10 Ft. to 10.5 Ft. Flow spilled fm two gaps in concrete wall. | Fill in the two gaps with concrete. | Y | Y | Loma Alta Creek | Pacific Ocean | N/A | Y | Y | Y | 2 | Extremely heavy rain fm 2000 to 0230.
978038 |  |  | Gary K. Orr | 760/966-4854 | Water Utilities Dept. City of Oceanside | 02/26/98 0800 | 02/26/98 0830 | 3000 | 0 | 1330 South Tait Street (La Salina WWTP) | Oceanside | SD | 92054 | Force Main | 0 | Equipment Failure | Fitting broke or seperated underground. | Replace fitting and fill hole. | Y | Y | Loma Alta Creek | Pacific Ocean | N/A | Y | Y | Y | 2 | Occurred during high tide. No chance of public contact.
943106 | Fax 571-6972 | 08/28/97 11:00 | Bauer | 6544160 | City of San Diego | 08/28/97 09:04 | 08/28/97 09:48 | 440 | 0 | 15603 Caldas de Reyes | San Diego | SD | 92128 | 8" pvc main | 1 | Grease | Grease blockage | Flushed 8" pvc main | y | y | Los Penasquitos Cnyn | Cypress Creek | dried in storm drain | y | n | n
940367 | Fax 571-6972 | 08/13/97 05:23 | Whelan | 6544160 | City of San Diego | 08/12/97 15:38 | 08/13/97 00:30 | 978 | 90 | 5366 Santa Margarita St. | San Diego | SD | 92114 | 8" vc main | 1 | Grease | Grease blockage | Rodded 8" vc main | y | y | Market St. Creek | San Diego Bay |  | y | y | n
932274 | Fax 571-6972 | 07/05/97 23:30 | Oropeza | 6544160 | City of San Diego | 07/05/97 18:01 | 07/05/97 19:45 | 105 | 0 | 2404 Loring St. | San Diego | SD | 92037 | 8" vc main | 1 | Grvty Mn Brk | Broken main | Dig out/repair main | y | y | Mission Bay | Pacific Ocean | soil ditch/Pico & Garnet | y | n
941305 | Fax 571-6972 | 08/16/97 15:26 | Branco | 6544160 | City of San Diego | 08/16/97 13:22 | 08/16/97 14:10 | 24 | 0 | S. Crown Pt. Park & Corona Orente Rd. | San Diego | SD | 92109 | 8" vc main | 1 | Roots | Root blockage | Machine rodded 8" vc main | y | n | Mission Bay | Pacific Ocean | soaked into ground around MH | y | n | n
941872 | Fax 571-6972 | 08/21/97 13:30 | Parker | 6544160 | City of San Diego | 08/21/97 08:29 | 08/21/97 10:10 | 101 | 101 | 3954 Hains St./alley | San Diego | SD | 92109 | 8" vc main | 1 | Roots | Root stoppage | Rodded main by machine/spill captured by interceptor | y | y | Mission Bay | Pacific Ocean |  | y | n | n
975913 | Fax 571-6972 | 02/09/98 15:30 | W.Payne | 6544160 | City of San Diego | 02/09/98 10:34 | 02/09/98 10:39 | 250 | 0 | 4605 Huron Av./canyon | San Diego | SD | 92117 | 8" VC | Two | Grvty Mn Brk | Major flooding of dirt storm channel | Replace VC pipe with PVC pipe | Y | Y | Mission Bay | Pacific Ocean |  | Y | N | Y | Unknown
977660 | Fax 571-6972 | 02/25/98 09:00 | W.Payne | 6544160 | City of San Diego | 02/16/98 22:00 | 02/18/98 10:05 | 43300 | 0 | 4605 Huron Av./canyon | San Diego | SD | 92117 | 8" VC/PVC | Three | Grvty Mn Brk | Flood damage due to heavy rains | Re-connect 8" PVC to 8" VC main/sandbag to protect until rains stop. | Y | Y | Mission Bay | Pacific Ocean |  | Y | Y | N
987928 | Fax 571-6972 | 4/16/98 14:09 | R. Donahue | 654-4160 | City of San Diego | 4/16/98 00:30 | 4/16/98 10:30 | 40800 | 26400 | 4605 Huron St./canyon | San Diego | SD | 92117 | 8" VC | Four | Grvty Mn Brk | Rain storm caused main to wash away | Re-connected main washed out by flooding, secured to wall of trench | Y | Y | Mission Bay | Pacific Ocean | N/A | Y | Y | N | N/A | N/A
940894 | Fax 571-6972 | 08/15/97 04:46 | Whelan | 6544160 | City of San Diego | 08/14/97 15:13 | 08/14/97 16:32 | 79 | 0 | 54th St. & Montezuma Rd. | San Diego | SD | 92115 | 8" vc main | 1 | Grvty Mn Brk | main break or offset joint | Rodded 8" vc main to relieve stop | y | y | Montezuma Creek | Pacific Ocean | dissipated in drainage ditch | y | n | n
942266 | Fax 571-6972 | 08/15/97 04:49 | Whelan | 6544160 | City of San Diego | 08/14/97 16:35 | 08/14/97 16:45 | 100 | 0 | 54th St. & Baja Dr. | San Diego | SD | 92115 | 8" vc main | 2 | Roots | secondary spill as a result of clearing the above spill | Ovrflw subsided after post-stoppage removal surcharge | y | y | Montezuma Creek | Pacific Ocean | dissipated in drainage ditch | y | n | n
976074 | Fax 571-6972 | 02/10/98 04:30 | M.Bedard | 6544160 | City of San Diego | 02/09/98 21:15 | 02/10/98 03:10 | 17750 | 0 | Murray Ridge Rd. & Fireside Av./canyon | San Diego | SD | 92123 | 10" VC | One | Other | Rain washed out manhole cone/rocks in main | Hand rod main/cleaned base of manhole/rebuild manhole | Y | N | Murray Canyon Creek | San Diego River | Pacific Ocean at Dog Beach | Y | Y | N
978006 | Voice Mail | 1998-02-24 | Steve Polzin | (909)676-4101 | R.C.W.D. | 02/24/98 0035 | 02/24/98 1226 | 1800000 | 0 | 26266 Washington | Murrieta | RV | 92562 | Secondary Effluent Equalization Basin | none | Vandalism Manhole | Manhole Cover Removed | Raised Manhole Cover and Locking Lid Installed | Y | Yes | Murrieta Creek | Santa Margarita River | Santa Margarita River | Yes | No | No | N/A
978007 | Voice Mail | 1998-03-09 | Bob Olds | (909)676-4101 | R.C.W.D. | 03/07/98 1824 | 03/08/98 0630 | 1000000 | 0 | 26266 Washington | Murrieta | RV | 92562 | Secondary Effluent Equalization Basin | One | Operator Error | Alarm Reset Error | New Alarms Installed | Y | Yes | Murrieta Creek | Santa Margarita River | Santa Margarita River | Yes | No | No | N/A
978001 | N/A | 7/2/97 1200 | Mike Schultz | 760-738-4347 | City of Escondido | 7/1/97 1015 | 7/1/97 1515 | 600 | 0 | La Honda Dr. | Escondido | SD | 92027 | Sewer Atlas PG. 251 MH.1174 | 1 | Vandalism | Vandalism, rocks, sticks,charcoal. | A locking manhole cover was installed. | N | N | N/A | N/A | Ground Absorption | Y | N | N | N/A
978008 | N/A | 9/2/97 1550 | Mike Schultz | 738-4347 | City of Escondido | 1997-08-29 | 8/29/97 1705 | 120 | 50 | 1605 Hamlton | Escondido | SD | 92025 | Sewer Atlas PG.486 Airvac. | 1 | Air release valve malfunctioned. | Malfunctioning air release value. | Remove unit cleaned, inspected. then reinstalled. | N | N | N/A | N/A | N/A | Y | N | N | N/A
978001 | Quarterly Report | 07/17/97; 14:30 | Richard Andrews | 619 755-3294 | City of Del Mar | 07/15/97; 20:22 | 07/16/97; 08:30 | 50 gallons | 0 | 119 11th Street | Del Mar | SD | 92014 | City Manhole No. 13 | 0 | Construction Defect | Incorrect connection lateral to main allowed leakage when lateral pressurized by basement ejector pump. | Rodded main which was clear. Contacted contractor ID fix connection. | N | N | N/A | N/A | dissipated @ road edge & storm drain system | Y | NA | N | NA | NA
978002 | Quarterly Report | 07/27/97; 17:15 | Richard Andrews | 619 755-3294 | City of Del Mar | 07/25/97; 16:50 | 07/25/97; 18:00 | 350 gallons | 0 | 200 Block Stratford Court, West Bluff | Del Mar | SD | 92014 | City Manhole No. 4 | 0 | Roots and Debris | Roots, Debris, and paper | Rodded Main to Clear Blockage | N | Y | N/A | N/A | Dirt next to manhole and dirt east of RR | Y | NA | N | NA | NA
978003 | Quarterly Report | 07/28/97; 13:45 | Richard Andrews | 619 755-3294 | City of Del Mar | 07/27/97; 15:30 | 07/28/97; 09:30 | 600 gallons | 0 | 390 Stratford Court | Del Mar | SD | 92014 | Private Lateral Clean Out | 0 | Roots | Roots in private lateral caused backup and overflow from residents cleanout. | Plumber contracted by owner and cleared. | N | Y | N/A | N/A | Ran down street leached into ground at bluff drainage swale est of RR | Y | NA | N | NA | Resident called PW answering machine (Sunday PM) to report a water leak at meter box. Did not call emergency number given in message. PW investigation Monday morning revealed private sewer company.
978005 | Quarterly Report | 10/02/97; 14:00 | Richard Andrews | 619 755-3294 | City of Del Mar | 09/27/97; 10:37 | 09/27/97; 11:50 | 146 gallons | 0 | 310 La Amatista Road | Del Mar | SD | 92014 | City Manhole Grid B 10 17 | 0 | Roots | Plumber clearing private lateral pushed roots into City main caused the blockage and overflow. | Rodded main to clear blockage. Continue preventative rodding. | N | Y | N/A | N/A | Road edge, gutter and drain. | Y | NA | N | NA | NA
978001 | none | none | D.Catone |  | L.G.Sanitation Dist. | 09/12/97 09:00 | 1997-09-12 13:00 | 2400 GA | 2400 GA | Lemon Grove Ave between Canton and Viewcrest | Lemon Grove | San Diego | 91945 | 8" main | 0 | line break to roots in main | line break due to tree roots in main | Repaired pipe | NO | NO | N/A | N/A | some soaked in to surrounding soil. Most was contained with dam & pumped back into system. Line was pumped on bypass during repair. | N | N/A | N | 0 | breakage was on side of main traveled way.
978006 | ELECTRONIC QTRLY RPT |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 08/09/97 | 18:00 | 300 | 175 | Bldg 43535, BEQ | SD | 920555008 | cleanout AT BLDG 43535 | 2 | BLOCKAGE | paper towels and roots caused blockage causing overflow from cleanout | Used jetter to clear blockage. Informed duty to tell tenants to stop flushing paper towels into sewer. | N | N | n/a | n/a | ponded around cleanout | Y | NA | N | 0 |  | SPILL OVERFLOWED FROM CLEANOUT AND PONDED INTO A POOL 10 FT ACROSS.
97001 | N/A | N/A | N/A |  | City of Poway | 01/07/97 - 0730 | 01/07/97 - 0810 | 40 | 0 | 17924 St. Andrews Drive | Poway | San Diego | 92064 | Collection System | 1 | Roots in main | 0730-Notified by residents manhole in front of home bubbling sewage. Dispatched Vactor crew to site at 0732. Vactor crew and Utilities Operations Supervisor met at site at 0747. Sewage was bubbling from manhole access in front of residence. Found 8" m | Placed this section of the collection system in the quarterly maintenance file. A video inspection has been scheduled to determine extent of root infiltration. | No | No | N/A | N/A | Cleaned up | No | No | No | N/A | None
978004 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 07/27/97 1445 | 07/27/97 1500 | 50 | 0 | Mission & Frontier | Oceanside | SD | 92054 | Manhole | 9 | Line Break. | CalTrans contractor crushed lateral. | CalTrans will order repairs when they get around to it. | N | N | N/A | N/A | Soaked into soil. | N | N/A | N | N/A | Ongoing problem. Needs to be fixed, ASAP!
978006 |  |  | Ira Black | 7609667868 | Water Utilities Dept. City of Oceanside | 07/29/97 1330 | 07/29/97 1345 | 15 | 0 | 710 Neptune | Oceanside | SD | 92054 | Cleanout | 1 | Roots. | Roots in the City Main. | "Rod " manhole every 30 days. | N | N | N/A | N/A | Soaked into soil. | N | N/A | N | N/A
978008 |  |  | Jeremy Kemp | (760)966-7868 | Water Utilities Dept. City of Oceanside | 08/03/97 1150 | 08/03/97 1220 | 40 | 0 | Mission & Frontier | Oceanside | SD | 92054 | Manhole | 10 | Line Break. | CalTrans contractor crushed lateral. | CalTrans will order repairs when they get around to it. | N | N | N/A | N/A | Soaked into soil. | N | N/A | N | N/A | Ongoing problem. Needs to be fixed, ASAP!
978009 |  |  | Steve | (760)966-7868 | Water Utilities Dept. City of Oceanside | 08/10/97 0745 | 08/10/97 0755 | 100 | 0 | Mission & Frontier | Oceanside | SD | 92054 | Manhole | 11 | Line Break. | CalTrans contractor crushed lateral. | CalTrans will order repairs when they get around to it. | N | N | N/A | N/A | Soaked into soil. | N | N/A | N | N/A | Ongoing problem. Needs to be fixed, ASAP!
978010 |  |  | Norm Crum | 7609667868 | Water Utilities Dept. City of Oceanside | 08/14/97 0830 | 08/14/97 0930 | 500 | 0 | Behind 725 Los Arbolitos | Oceanside | SD | 92056 | Air Relief Valve | 0 | Leaky Valve | Tapping Valve on 24 inch force main would not close completely, during time it took to clean grease and debris from air valve. | valve to be placed on air vent riser pipe, prior to the air vent itself. | N | N | N/A | N/A | Soaked into soil. | N | N/A | N | N/A | Repairs will be made A.S.A.P!
978011 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 08/17/97 1218 | 08/17/97 1250 | 300 | 0 | Mission & Frontier | Oceanside | SD | 92054 | Manhole | 12 | Line Break. | CalTrans contractor crushed lateral. | CalTrans will order repairs when they get around to it. | N | N | N/A | N/A | Soaked into soil. | N | N/A | N | N/A | Ongoing problem. Needs to be fixed, ASAP!
978012 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 08/24/97 0800 | 08/24/97 0810 | 25 | 0 | Mission & Frontier | Oceanside | SD | 92054 | Manhole | 13 | Line Break. | CalTrans contractor crushed lateral. | We are "vactoring" out of the manhole three (3) times a day. | N | N | N/A | N/A | Soaked into soil. | N | N/A | N | N/A | Ongoing problem. Needs to be fixed, ASAP!
978014 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 09/07/97 1200 | 09/07/97 1230 | 100 | 0 | Mission & Frontier | Oceanside | SD | 92054 | Manhole | 14 | Line Break. | CalTrans contractor crushed lateral. | CalTrans will order repairs when they get around to it. | N | N | N/A | N/A | Soaked into soil. | N | N/A | N | N/A | Vactor is down for repairs. Scavenger not keeping up w/flow. Called out "Atlas" 3000 Gal. Tanker.
978015 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 09/14/97 1415 | 09/14/97 1440 | 70 | 0 | Mission & Frontier | Oceanside | SD | 92054 | Manhole | 15 | Line Break. | CalTrans contractor crushed lateral. | CalTrans will order repairs when they get around to it. | N | N | N/A | N/A | Soaked into soil. | N | N/A | N | N/A | Ongoing problem. Needs to be fixed, ASAP!
978001 |  |  | Joel Holt | (760) 723-5640 | Fallbrook Public Utility District | 1997-07-02 11:50 | 1997-07-02 12:20 | 25 | 0 | 645 Minnesota | Fallbrook | SD | 92028 | 6" VCP | 1 | Roots | Eucaplyptus Roots | Rodded with small rodder and opened 15' into 6" lateral. Problem area will be replaced. | N | N | N/A | N/A | Ice Plant on bank. | N | N | N | N/A | No overflow was recovered due to ground cover (Ice Plant), debris was picked up.
978002 |  |  | Joel Holt | (760) 723-5640 | Fallbrook Public Utility District | 1997-07-02 18:30 | 7/2/97 1900 | 30 | 5 | 410 E. Fallbrook St. | Fallbrook | SD | 92028 | 6" VCP | 4 | Grease Blockage | Grease & baby wipes. | Flushed lines, ran 6" cutter in cleanout all the way to main. Recovered solids toilet paper, baby wipes, string and other foreign materials. | N | N | N/A | N/A | Around cleanout on grass & asphalt. | N | N | N | N/A | Did not reach storm drain. Cleaned up all debris.
978003 |  |  | Joel Holt | (760) 723-5640 | Fallbrook Public Utility District | 1997-07-18 11:20 | 1997-07-18 11:45 | 5 | 0 | 131 W. Beech St. | Fallbrook | SD | 92028 | 4" Clay Pipe | 1 | Other | Unknown. | Rodded lateral until water went down. Main line needs to be flushed. | N | N | N/A | N/A | Dirt around cleanout. | N | N | N | N/A
978004 |  |  | Joel Holt | (760) 723-5640 | Fallbrook Public Utility District | 1997-07-20 08:30 | 1997-07-20 09:00 | 250 | 0 | 700 Block of Shady Lane | Fallbrook | SD | 92028 | Lift Station | 1 | Power Failure | Power failure. Generator didn't start. | Posted area. Covered area with dirt, and made sure lift station was operational. | N | N | N/A | N/A | Empty/open field that is fenced on all four sides. | N | N | Y | 3
978006 | (619) 571-6972 | 1997-08-01 09:45 | Joel Holt | (760) 723-5640 | Fallbrook Public Utility District | 1997-07-28 13:00 | 7/28/97 16:30 | 1050 | 0 | 2141 S. Mission | Fallbrook | SD | 92028 | 18" Recycled Water Line | 1 | Line Break | Small break in the recycled water main line. | N/A | N | N | N/A | N/A | Absorbed into the ground just adjascent to an approved recycled water user. | Y | N | N | N/A | Spill was Title 22, recycled water.
978008 |  |  | Joel Holt | (760) 723-5640 | Fallbrook Public Utility District | 1997-08-10 20:41 | 1997-08-10 21:10 | 1 | 0 | 229 W. Alavarado | Fallbrook | SD | 92028 | Cleanout | 2 | Roots | Roots possibly offset joint in lateral. Also clogged with toilet paper. | Rodded lateral from open cleanout. Check on monthly basis and rod with root cutter. | N | N | N/A | N/A | Inside cleanout - only 1 gallon overflowed. | N | N | N | N/A
978009 |  |  | Joel Holt | (760) 723-5640 | Fallbrook Public Utility District | 1997-08-11 09:00 | 1997-08-11 09:25 | 20 | 10 | 1062 Via Unidos | Fallbrook | SD | 92028 | 4" Clay Cleanout | 1 | Roots | Roots in main line. | Flushed main line and rodded cleanout to main. Recovered roots, solids, and toilet paper. Removed contaminated soil around cleanout box and replaced with clean soil. | N | N | N/A | N/A | Dirt around cleanout. | N | N | N | N/A
978011 |  |  | Joel Holt | (760) 723-5640 | Fallbrook Public Utility District | 1997-08-18 08:30 | 1997-08-19 14:00 | 50 | 40 | 550 Industrial Way | Fallbrook | SD | 92028 | 6" Clay Pipe | 1 | Line break | Pipe was broken by backhoe operator. | Section was in 6" piece of pipe. Removed approximately 2 yards of contaminated soil around pipe. | N | N | N/A | N/A | Recovered spill by vactor truck from bell hole ditch. | N | N | N | N/A
97002 | N/A | N/A | N/A |  | City of Poway | 09/07/97 - 1400 | 09/07/97 - 1445 | 40 | 16 | 12957 Sagewood Drive | Poway | San Diego | 92064 | Collection System | 1 | Roots in main | 1400 - Resident called in report of overflow. Dispatched Vactor crew to site. Found 8" main partially blocked with tree roots. Cleared roots from pipe and performed clean up procedures. Approximate loss of 40 gallons calculated. | Placed section of collection system in PM database. | No | No | N/A | N/A | Cleaned up | No | No | No | N/A | None
97003 | N/A | N/A | N/A |  | City of Poway | 11/27/97 - 0930 | 11/27/97 - 0950 | 45 | 15 | 13441 Sagewood Drive | Poway | San Diego | 92064 | Collection System | 1 | Partial main blockage | 0900 - Resident called water treatment plant to report sewer bubbling out of clean-out. Water Utilities crews called in. Cleared partial blockage in the 8" sewer main caused by grease build up. Used Vactor to vacuum 15 gallons of spill; disinfected and | Video inspection scheduled to determine maintenance needs; placed in cardfile. | No | No | N/A | N/A | Disinfected and spread topsoil | No | No | No | N/A | None
957874 | Fax 571-6972 | 11/06/97 13:55 | Bauer | 6544160 | City of San Diego | 11/06/97 09:46 | 11/06/97 11:50 | 580 | 0 | 7564 Rainswept Ln. | San Diego | SD | 92119 | 8" PVC | 1 | Roots | Roots | Flushed/cleaned main with root cutter | N | N | N/A | Storm drain/SD River | Ground around manhole | Y | N/A | N
969415 | Fax 571-6972 | 12/22/97 11:20 | Galinzoga | 6544160 | City of San Diego | 12/22/97 08:50 | 12/22/97 09:15 | 175 | 0 | 18695 Pomerado Rd.** | San Diego | SD |  | Bldg # 1329 | 1 | Debris | Rocks & debris in suction line | Removed debris/rocks from suction line to pumps in PS #76 | Y | N | N/A | N/A | Station grounds | Y | N/A | Y
| SIRT (Attn: Gloria Fulton) | 1997-10-01 11:00 | James E. Smith | 714-448-4053 | Moulton Niguel Water | 1997-10-01 10:30 | 1997-10-01 10:32 | 100-200 | 100-200 | End of Alipaz | San Juan Capistrano | OR | 92675 | 3A Effluent Pipeline | 1 | Construction | Grading contractor for Pepper Tree Estates hit the buried 20" effluent pipeline that transports secondary effluent to the Chiquita Land outfall. The 3A plant was processing only recycled water, so the only water in the pipeline was residual effluent. | What water that escaped from the pipeline percolated into the ground. | N | N | N/A | NA | Ground | Y | N | N | N/A
| SIRT (Attn: Gloria Fulton) | 1997-12-16 10:45 | Property Manager | 714-448-0061 | Moulton Niguel Water | 1997-12-16 10:00 | 1997-12-16 11:00 | 300 | 0 | 23932 Aliso Creek Rd. | Laguna Niguel | OR | 92677 | Sectional map E-19, MH #2 | 1 | Grease | Cause is unknown. Sewer is from business park only. Partial blockage | Sewer lines were jetted and will be videoed in the next few days. | Y | N | N/A | Pacific Ocean | N/A | Y | N | N | N/A | The pipelines leading from the commercial area will be videoed to see if there is a problem with the sewer or manholes.
978019 |  |  | Norman Crum | 7609667868 | Water Utilities Dept. City of Oceanside | 10/16/97 1700 | 10/16/97 1730 | 100 | 0 | 3207 Roymar Road | Oceanside | SD | 92056 | Manhole | 0 | Grease | Build up of grease in city main. | Main was "jet rodded". | N | Y | N/A | N/A | Soaked into dirt drainage ditch. | Y | N/A | N | N/A | No "solids" escaped manhole. No "public contact" was evident, or likely.
978021 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 11/02/97 0930 | 11/02/97 1000 | 80 | 0 | Mission & Frontier | Oceanside | SD | 92056 | Manhole | 14 | Line Break | Sewer Lateral was crushed by contractor for CalTrans while working on #76. | CalTrans will fix it, when they get around to it. | N | N | N/A | N/A | Soaked into dirt drainage ditch. | N | N/A | N | N/A | Atlas was hired to remove 3,800 gallons.
978022 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 11/09/97 0840 | 11/09/97 0905 | 100 | 0 | Mission & Frontier | Oceanside | SD | 92056 | Manhole | 15 | Line Break | Sewer Lateral was crushed by contractor for CalTrans while working on #76. | CalTrans will fix it, when they get around to it. | N | N | N/A | N/A | Soaked into dirt drainage ditch. | Y | N/A | N/A | N/A | Flow is also coming out of a CalTrans "pull" box for traffic signals, etc.
978023 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 11/16/97 1250 | 11/16/97 1320 | 80 | 0 | Mission & Frontier | Oceanside | SD | 92056 | Manhole | 16 | Line Break | Sewer Lateral was crushed by contractor for CalTrans while working on #76. | CalTrans will fix it, when they get around to it. | N | N | N/A | N/A | Soaked into dirt drainage ditch. | Y | N/A | N/A | N/A | Flow is also coming out of a CalTrans "pull" box for traffic signals, etc.
978025 |  |  | Ira Black | 7609667868 | Water Utilities Dept. City of Oceanside | 12/18/97 0930 | 12/18/97 1030 | 200 | 150 | 2209 Valley Road | Oceanside | SD | 92056 | Private Cleanout | 0 | Roots | Sewer Lateral "backed up" because of root bound City Main. | City Main put on monthly "Rodding" schedule. | N | N | N/A | N/A | Front Yard | Y | N/A | N/A | N/A | Property has yard drain illegally hooked to sewer lateral.
978026 |  |  | Ed Calhoun | 7609667868 | Water Utilities Dept. City of Oceanside | 12/26/97 0830 | 12/26/97 1530 | 50 | 0 | 143 Harrison Street | Oceanside | SD | 92057 | Private Cleanout | 0 | Blockage | City Main "running free". Private lateral has blockage. | Advised renter to call plumber. | N | N | N/A | N/A | Front Yard | N | N/A | N/A | N/A
97003 | N/A | N/A | N/A |  | City of Poway | 11/27/97 - 0930 | 11/27/97 - 0950 | 45 | 15 | 13441 Sagewood Drive | Poway | San Diego | 92064 | Collection System | 1 | Partial main blockage | 0900 - Resident called water treatment plant to report sewer bubbling out of clean-out. Water Utilities crews called in. Cleared partial blockage in the 8" sewer main caused by grease build up. Used Vactor to vacuum 15 gallons of spill; disinfected and | Video inspection scheduled to determine maintenance needs; placed in cardfile. | No | No | N/A | N/A | Disinfected and spread topsoil | No | No | No | N/A | None
978028 |  |  | Ira Black | 760/966-7868 | Water Utilities Dept. City of Oceanside | 01/06/98 1030 | 01/06/98 1100 | 150 | 0 | 3685 Vista Campana North & "W" | Oceanside | SD | 92056 | Manhole | 0 | Roots | Roots in City Main. | Rodded City Main and washed down. | N | N | N/A | N/A | Street & Gutters | Y | N/A | N | N/A
978030 |  |  | Ed Calhoun | 760/966-7868 | Water Utilities Dept. City of Oceanside | 01/07/98 0845 | 01/07/98 0930 | 200 | 0 | 1619 Loretta Street | Oceanside | SD | 92054 | Manhole | 0 | Debris | Found paper towels & rags & grease plugging the City Main. | Routine Rodding Schedule. | N | Y | N/A | N/A | Street & Gutters | N | N/A | N | N/A | Aprox. 1/4 of mile from storm system.
978032 |  |  | Ed Calhoun | 760/966-7868 | Water Utilities Dept. City of Oceanside | 1/15/98 0730 | `01/15/98 0800 | 100 | 0 | 1968 College Blvd.,#163 | Oceanside | SD | 92056 | Manhole | 1 | Debris | Found paper towels & rags & grease plugging the City Main. | Routine Rodding Schedule. | N | Y | N/A | N/A | Street & Gutters | N | N/A | N | N/A
978033 |  |  | Ed Calhoun | 760/966-7868 | Water Utilities Dept. City of Oceanside | 1/17/98 1130 | 1/17/998 1200 | 200 | 0 | 1217 Holly Street | Oceanside | SD | 92054 | Private lateral | 0 | Other | City opened "cleanout" in house lateral to relieve pressure on downstairs area from flooding further. | City Main ;has been cleared and is on a monthly "Jetter" schedule. | N | N | N/A | N/A | Private Property | N | N/A | N | N/A
978034 |  |  | Norm Crum | 760/966-7868 | Water Utilities Dept. City of Oceanside | 1/29/98 1915 | 1/29/98 2015 | 150 | 0 | 2209 Valley Road | Oceanside | SD | 92054 | Yard Drain | 2 | Blockage in City Main | Owner should receive letter requesting them to install a backwater valve in their lateral. |  | N | N | N/A | N/A | Front & Side Yards | N | N/A | N | N/A | Orr to order their yard drain disconnected from lateral.
978035 |  |  | Norm Crum | 760/966-7868 | Water Utilities Dept. City of Oceanside | 2/11/98 1720 | 2/11/98 1830 | 55 | 0 | 2434 Vista Way | Oceanside | SD | 92054 | Manhole | 0 | Grease | Grease build up in City Main. | Preventative Maint. Scheduleing for Jetter" | N | Y | N/A | N/A | Unknown | N | N/A | N | N/A
978039 |  |  | Mark Levine | 760/966-7868 | Water Utilities Dept. City of Oceanside | 03/18/98 0715 | 03/18/98 0740 | 50 | 0 | 3100 Block of Alto Street | Oceanside | SD | 92054 | Manhole | 0 | Roots | Roots in City Main. | Rodded line with large cutter blade. | N | N | N/A | N/A | Gutter | N | N/A | N | N/A
978010A | Quarterly Report | 03-03-98 0800 | Ted Powell | 760-744-0460 | V.W.D. | 03-02-98 1100 | 03-02-98 1130 | 450 | none | Lake San Marcos Golf Course | San Marcos | S.D. | 92069 | 8" line | 1 | roots | Roots in line due to large tree next to line. | engineering will talk to golf course about tree removal. | n | n | n/a | n/a | n/a | y | n | n | 0 | spill was contained
978008 | Quarterly Report | 1998-02-02 12:30 | Richard Andrews | 619 755-3294 | City of Del Mar | 02/02/98; 09:00 | 02/02/98; 09:50 | 500 gallons | 250 gallons | 600 Blk Camino Del Mar, East side | Del Mar | SD | 92014 | City Manhole No. 15 sewer block map b-10 | 0 | Roots / Blockage | Roots and Paper | Ran 388' of rod from 600 block of Stratford. Found roots and paper. Travel Vac used to catch overflow and returned. | n | y | n/a | n/a | Retrieved back to system 50%, other soaked into dirt drainage ditches next to railroad tracks. | y | n/a | n | n/a | Sewage caught before reaching ocean, all streets cleaned.
978009 | Quarterly Report | 1998-03-04 18:00 | Richard Andrews | 619 755-3294 | City of Del Mar | 1998-03-04 14:30 | 3/4/1998; 14:30 | 300 gallons | none | Carmel Valley @ Portofino | San Diego | SD | 92014 | Force Main | 0 | Construction | Contractor excavating at south edge Carmel Valley @ intersection w/ Portofino, struck and damaged force main. |  | n | n | n/a | n/a | Road edge weeds and bushes at edge | y | n/a | n | n/a | none
978002 | NO | n/a | n/a | 619-464-6934 | Lemon Grove | 112797*10:30 | 112797*14:30 | 20-25 gal | 0 | 7923 Nichals St | Lemon Grove | San Diego | 91945 | Rear easement | 0 | roots,grease | combination of roots & grease constricted flow | 6" line jetted,stoppage removed/area sanitized | N | N | N/A | N/A | Small amount around manhole, rear easement, area sanitized | N | N | N | N/A | none
978003 | NO | n/a | b/a | 619-464-6934 | Lemon Grove | 022498*2:30 | 022498*6:30 | backup into home | all | 1758 Colfax St | Lemon Grove | San Diego | 91945 | Into residence | 0 | backup into home | No problem in main located | Installed p/l backflow. Home sanitized | N | N | N/A | N/A | Private property. Sewer system | N | N | N | N/A | none
978004 | NO | n/a | n/a | 619-464-6934 | Lemon Grove | 033198*19:00 | 033198*23:00 | 2 to 4 gal | all | 1467 Madera | Lemon Grove | San Diego | 91945 | none | 0 | line blockage | not determined | jetted line. Small spill swept back into sewer | N | N | N/A | N/A | Small amt swept back into sewer | N | N | N | N/A | none
978024 | Quarterly Report only | N/A | Don Keifer | 741-4668 | City of Escondido | 1/11/98 1400 | 1/11/98 1600 | 120 Gallons | 120 Gallons | 701 E. 7th. Ave. | Escondido | SD | 92025 | Private cleanout | Unknown | Unknown | Unknown-Private clean-out | Property owner cleared stoppage. City sewer crew cleared the area of wastewater debris. | N | N | N/A | N/A | Recovered | N | N | N | N/A | No samples taken.
978026 | Quarterly Report only County Health was notified. | 1/17/98 1130 | Todd Anderson | 741-4668 | City of Escondido | 1/16/98 2100 | 1/17/98 900 | 760 Gallons | 25 Gallons | Jesmondene Park | Escondido | SD | 92025 | Waste water storage tank | 0 | Tank overflowed due to stuck urinal valve. | Same as short description. | Valve was repaired, effected area was vacuumed and disinfected. Signs were posted. | N | N/A | N/A | N/A | Grass area | Y | N | Y | Two | No samples taken.
978035 | Quarterly Report only | 3/12/98 1315 | Lance Lauricha | 839-4347 | City of Escondido | 3/12/98 1300 | 3/12/89 1530 | 25 Gallons | 0 | 112 S. Grape St. | Escondido | SD | 92026 | Private cleanout | 0 | Roots | Service lateral blocked with roots. | Private system. | N | N | N/A | N/A | N/A | N | N | N | N/A | No samples taken.
978039 | Quarterly Report only | 3/30/98 1848 | Jim Miller | 839-4347 | City of Escondido | 3/30/1998 1848 | 3/30/98 2040 | 40 Gallons | 20 Gallons | Mission at Centre City Pkwy. | Escondido | SD | 92026 | Private cleanout | 0 | Roots and Grease | Private system. | Advised property manager to perform preventive maintenance. | N | N | N/A | N/A | N/A | N | N | N/A | N/A | No samples taken.
978040 |  |  | Mark Patnode | 760/966-7868 | Water Utilities Dept. City of Oceanside | 04/13/98 0000 | 04/13/98 1645 | 200 | 160 | 3000 Guajome Lake Road | Oceanside | SD | 92057 | Sewer Lateral | 0 | Line Break | "CalTras" Contractor hit 8" private lateral while breaking up the surface of the road. | Spoke with the contractor. They repaired the break. | N | N | N/A | N/A | Contained within the trench line. | N | N | N | N/A | I notified the Park Ranger @ 14/1100Apr98.
978041 |  |  | E.C. Calhoun | 760/966-7868 | Water Utilities Dept. City of Oceanside | 04/15/98 1035 | 04/15/98 1059 | 150 | 0 | 2900 Blk of Fire Mountain Road | Oceanside | SD | 92054 | Manhole | 0 | Roots | Roots, paper towels and wire caught in manhole. | Quarterly rodding schedule | N | Y | N/A | N/A | Soaked into mud & debris in basin. | N | N/A | N | N/A | Was overdue on the rodding schedule. Heavy workload.
978044 |  |  | Jeremy Kemp | 760/966-7868 | Water Utilities Dept. City of Oceanside | 04/26/98 1330 | 04/26/98 1400 | 50 | 0 | Mission & Frontier | Oceanside | SD | 92056 | Manhole | 17 | Line Break | "CalTrans" Contractor broke Drive-Inn Theater lateral last year, and has not gotten around to fixing it. | We use Vactor to remove contents of line every Friday, Saturday, Sunday, & Monday. | N | N | N/A | N/A | Soaked into the ground @ site. | N | N/A | N | N/A | `
978045 |  |  | Jeremy Kemp | 760/966-7868 | Water Utilities Dept. City of Oceanside | 05/17/98 1140 | 05/17/98 1200 | 250 | 0 | Mission & Frontier | Oceanside | SD | 92056 | Manhole | 18 | Line Break | "CalTrans" Contractor broke Drive-Inn Theater lateral last year, and has not gotten around to fixing it. | We use Vactor to remove contents of line every Friday, Saturday, Sunday, & Monday. | N | N | N/A | N/A | Soaked into the ground @ site. | N | N/A | N | N/A | Needs to be fixed, please.
978047 |  |  | Jeremy Kemp | 760/966-7868 | Water Utilities Dept. City of Oceanside | 06/07/98 1300 | 06/07/98 1345 | 300 | 0 | Mission & Frontier | Oceanside | SD | 92054 | Manhole | 20 | Line Break | "CalTrans" Contractor broke Drive-Inn Theater lateral last year, and has not gotten around to fixing it. | We use Vactor to remove contents of line every Friday, Saturday, Sunday, & Monday. | N | N | N/A | N/A | Soaked into the ground @ site. | N | N/A | N | N/A | …Also, yesterday there was a heavy gasoline smell and oil residue in the hole.
978048 |  |  | Norm Crum | 760/966-7868 | Water Utilities Dept. City of Oceanside | 06/18/98 1830 | 06/18-98 1930 | 100 | 0 | 1015 Eucalyptus | Oceanside | SD | 92054 | Manhole | 0 | Grease | Grease build up in City Main. | Site will be ckecked periodically for two weeks. | N | Y | N/A | N/A | Debris in Storm Drain. | N | N/A | N | N/A
998024 | Fax 571-6972 | 6/09/98 13:00 | W. Payne | 654-4160 | City of San Diego | 6/09/98 10:30 | 6/09/98 10:31 | 20 | 0 | 1022 Skylark Dr. | San Diego | SD | 92037 | 8" VC | Two | Construction | Pumping from upstream manhole/bypassing construction | Established bypass pumping system around construction on 8" vc main | N | N | N/A | N/A | Soaked into dirt | Y | N | N | N/A | N/A
999133 | Fax 571-6972 | 6/26/98 09:00 | W. Payne | 654-4160 | City of San Diego | 6/23/98 11:00 | 6/23/98 11:01 | 5 | 0 | 10800 Roselle St. | San Diego | SD | 92121 | 12" DI | Three | Force Main Brk | Break in hi-line to pump station #64 | Shut down pump station until contractor makes repairs | N | N | N/A | N/A | N/A | Y | N | N | N/A | N/A
4079801 | Dan Hoirup | 1998-04-08 13:40 | A J Howard | 949 366-1553 | CSC | 1998-04-07 16:47 | 1998-04-07 17:40 | 700 | 700 | W. Ave. San Gabriel | CSC | OR | 92672 | San Gabriel PS | 0 | Failed Force Main Pipe Joint |  |  | N | N | N/A | N/A | Returned to Collection System downstream of San Gabriel Pump Station | Y | N | N/A | 0 | Crews isolated flows to the station and diverted to coastal trunk line for duration of repairs. Contents that escaped system was confined in adjacent parking lot and removed w/ Vactor
4249801 | John Phillips | 1998-04-24 09:04 | A J Howard | 949 366-1553 | CSC | 1998-04-21 08:00 | 1998-04-23 08:20 | 600 | 0 | Pacific Coast Highway Across from 35105 Doheny Beach Rd. | Dana Point | OR | 92672 | San Clemente Land Outfall line | 0 | Air/Vac Relief Valve |  |  | N | N | N/A | N/A | Pavement/Soil | Y | N | N | N/A | Air/Vac relief valve on Secondary Land Outfall stuck open for short periods then seal. This occurred on 21, 22, 23 Apr 98 @ approx 8:00 hrs ea morning. Discharged secondary effluent wetted street and ground immediately adjacent to the ari/vac station.
97-8-0007 | FAXED | 10:00AM | Marc Avila | 949-487-1097 | CBWD | Apr.13,6:30pm | Apr.13,6:50pm | 250 | 0 | Camino De Estrella | San Clemente | 0R | 92672 | Manhole | 1 | grease | Grease caused blockage in line | Jetted line clear,continue on preventative maintenance schedule | N | N | N/A | N/A | Asphalt,dissipated,around M.H. | Y | N/A | N/A | N/A
978040 | N/A | N/A | Lance Lauricha | 760-839-4347 | City of Escondido | 4/13/1998 1200 | 4/13/1998 1500 | 35 Gallons | 0 | 1605 Hamilton | Escondido | SD | 92025 | Air-vac | 1 | Broken pipe | corroded copper pipe failed causing leak. | Replaced pipe. | N | N | N/A | N/A | Evaporation/Soil | N | N | N | N/A | No Samples taken.
98004 | N/A | N/A | N/A |  | City of Poway | 05/03/98 - 0730 | 05/04/98 - 0815 | 20 | 5 | 14644 Lake Poway Road | Poway | San Diego | 92064 | Collection System | 1 | Partial main blockage - Roots | Park Ranger notified Water Utilities that sewage was bubbling slowly out of manhole. Vactor crew dispatched to clear blockage. Roots were determined to be cause of blockage. Vactor crew vacuumed up five (5) gallons of spill and sanitized the area. | Removed contaminated soil from the area and replaced with fresh topsoil. Contaminated soil disposed of at City's sludge basin at Hazardous Waste Facility. Main line was video inspected and has been placed on a more frequent maintenance schedule. | No | No | N/A | N/A | Cleaned/sanitized area; replaced soil in spill area with fresh topsoil. | No | No | No | N/A | None
978014 |  |  | Joel Holt | 7607235640 | Fallbrook Public Utility District | 1997-11-14 13:42 | 1997-11-14 14:05 | 50 | 5 | 2613 Buena Rosa | Fallbrook | SD | 92028 | Cleanout | 1 | Blockage | Toilet paper and foreign material. | Rodded line until it was clear. Picked up solids and other objects. | N | N | NA | NA | Lawn and sidewalk. | N | N | N | NA | None.
978015 |  |  | Joel Holt | 7607235640 | Fallbrook Public Utility District | 1997-11-17 14:00 | 1997-11-17 14:35 | 5 | 5 | 800 E. Porter | Fallbrook | SD | 92028 | Cleanout | 1 | Roots | Roots in cleanout. | Rodded line with bullet and 4" cutter. Recovered 5 gallons of paper, roots, and solids. | N | N | NA | NA | Ground around cleanout. | N | N | N | NA | None.
978016 |  |  | Joel Holt | 7607235640 | Fallbrook Public Utility District | 1997-11-20 16:15 | 1997-11-20 16:30 | 15 | 0 | 500 Ammunition Rd. | Fallbrook | SD | 92028 | Manhole | 1 | Grease | Grease plugging line. | Flushed line. | N | N | NA | NA | Gutter and street. | N | N | N | NA | None.
978017 |  |  | Joel Holt | 7607235640 | Fallbrook Public Utility District | 1997-11-23 02:23 | 1997-11-23 02:50 | 50 | 0 | 400 Block W. Aviation | Fallbrook | SD | 92028 | Manhole | 1 | Grease | There was alot grease in the line. | Flushed line twice. | N | N | NA | NA | On blacktop and cement driveway (about 200 ft.). | N | N | N | NA | Unable to get access to location due to locked gate, which made initial recovery of spill difficult.
978018 | SDCnty - K. Stone | 1997-12-06 10:00 | Joe Polzin | 7607235640 | Fallbrook Public Utility District | 1997-12-05 17:00 | 1997-12-06 08:00 | 27000 | 0 | 700 Block Shady Lane | Fallbrook | SD | 92028 | Lift Station | 2 | Pump Station Failure | Both pumps at the Lift Station tripped out. | Reset both breakers. Cleaned the bubbler tube and watched it run through several cycles. | N | N | NA | NA | Ran into open field with no public access. | Y | N | Y | 3 | Unable to recover any of spill - quicly ran into open field and percolated into ground.
978021 |  |  | Joel Holt | 7607235640 | Fallbrook Public Utility District | 1997-10-21 08:50 | 1997-10-21 11:00 | 240 | 200 | Beech Street | Fallbrook | SD | 92028 | 8" Mainline | 1 | Roots | Roots in mainline. | Dug up line, replaced line and installed 6" cleanout. Removed contaminated soil (approx. 1 yd.). | N | N | NA | NA | Percolated into ground. | N | N | N | NA | Sequential Tracking # does not correspond to dating sequence, due to the fact that this report was not forwarded to appropriate personnel in proper sequence.
978022 |  |  | Joel Holt | 7607235640 | Fallbrook Public Utility District | 1997-12-09 12:00 | 1997-12-09 12:30 | 15 | 10 | 445 Linden Lane | Fallbrook | SD | 92028 | Cleanout | 1 | Other | Paper towels obstruction in off-set joint of mainline. | Cleaned up site and flushed mainline to open blockage. | N | N | NA | NA | Percolated into ground around cleanout. | N | N | N | NA
978023 |  |  | Joel Holt | 7607235640 | Fallbrook Public Utility District | 1997-12-17 18:35 | 1997-12-17 19:00 | 15 | 0 | 232 E. Kalmia | Fallbrook | SD | 92028 | Cleanout | 1 | Blockage | Unknown blockage - possibly roots or grease. | Ran cutter through 4" cleanout and flushed easement main line. | N | N | NA | NA | Dried up along cement driveway and in Kalmia Street. | N | N | N | NA
978027 |  |  | Joel Holt | 7607235640 | Fallbrook Public Utility District | 1997-12-11 11:00 | 1997-12-11 11:05 | 40 | 0 | 1425 S. Alturas | Fallbrook | SD | 92028 | Sludge Bed | 1 | Blockage | While cleaning up sludge spill, catch basin overflowed. While staff was hosing down and cleaning up. |  | N | * | NA | NA | * Spill went partially into Plant contained storm drain (returned to headworks) & remainder percolated into soil on Naval Weapons Station Property in an isolated area. | N | N | N | NA | Sequential Tracking # does not correspond to dating sequence, due to the fact that this report was not forwarded to appropriate personnel in proper sequence.
978017 | county health | 12-9-97 945 | Lance Lauricha | 738-4348 | City of Escondido | 12-9-97 915 | 12-9-97 1115 | 100 | 100 | 1203 S. Maple | Escondido | SD | 92026 | Private Cleanout | 0 | Private Cleanout / unknown | unknown | Plumber cleared blockage | n | n | na | na | na | y | n | n | na
978022 | none | na | na | 738-4353 | City of Escondido | 12-25-97 900 | 12-25-97 1130 | 100 | 100 | 1103 E. 5th. | Escondido | SD | 92025 | MH 3684, Sewer atlas 369 | 0 | Roots | Roots | Cleared stoppage and put manhole on scheduled root inspection. | n | n | na | na | na | n | n | n | na
978024 | Quarterly |  | Joel V. Holt | (760) 723-5640 | Fallbrook Public Utility District | 1998-01-05 09:15 | 1998-01-05 10:30 | 20 | 20 | Fallbrook & Elbrook Streets | Fallbrook | SD | 92028 | 8" Main Line | 1 | Construction | Contractor broke the pipe with backhoe. | Vacuumed 20 gallons of wastewater from along pipe. Also hauled away 3/4 yards of contaminated dirt. | N | N | NA | NA | Ditch beside pipeline | N | N | N | NA
978029 | Quarterly |  | Joel V. Holt | (760) 723-5640 | Fallbrook Public Utility District | 1998-01-25 14:45 | 1998-01-25 15:00 | 60 | 50 | 1309 Via Del Oro | Fallbrook | SD | 92028 | 4" Cleanout | 1 | Blockage | Unknown blockage. | Flushed main line and unblocked. | N | N | NA | NA | Percolated into ground. | N | N | N | NA | Main line was draining slowly and that is why it wasn't overflowing when crew arrived on site.
978031 | Quarterly |  | Joel V. Holt | (760) 723-5640 | Fallbrook Public Utility District | 1998-02-07 12:00 | 1998-02-07 13:00 | 40 | 0 | 314 Calle de la Paloma | Fallbrook | SD | 92028 | Cleanout | 1 | Grease | Grease and grit blockage. | Flushed line from Fallbrook Street. Need to raise manholes under blacktop. | N | N | NA | NA | Percolated into gravel area. | N | N | N | NA | Washed down gravel area.
978035 | Quarterly |  | Joel V. Holt | (760) 723-5640 | Fallbrook Public Utility District | 1998-03-20 09:20 | 1998-03-20 10:00 | 15 | 5 | 2537 Buena Rosa | Fallbrook | SD | 92028 | Cleanout | 1 | Other | Foreign paper products clogging line. | Rodded line until open, about 20 feet. | N | N | NA | NA | Around cleanout box | N | N | N | NA
978036 | Quarterly |  | Joel V. Holt | (760) 723-5640 | Fallbrook Public Utility District | 1998-03-21 15:01 | 1998-03-21 16:00 | 15 | 7 | 2355 S. Stagecoach | Fallbrook | SD | 92028 | 4" Cleanout | 1 | Other | Foreign paper products clogging line. | Rodded 4" cleanout and unplugged stoppage. Primary male resident informed others in household not to flush "problem" items down toilet any more. | N | N | NA | NA | Around cleanout box | N | N | N | NA
978037 | Quarterly |  | Joel V. Holt | (760) 723-5640 | Fallbrook Public Utility District | 1998-03-23 09:47 | 1998-03-23 10:35 | 30 | 0 | 1708 E. Mission Rd. | Fallbrook | SD | 92028 | 4" Cleanout | 1 | Roots | Roots primary problem. Foreign paper products secondary problem. | Rodded line 3 times and removed all roots. Should be dug up and replaced with new pipe in near future. | N | N | NA | NA | Dried up on roadway (100 ft.). | N | N | N | NA
978038 | County SD | 1998-03-30 10:55 | Patti S. Page | (760) 723-5640 | Fallbrook Public Utility District | 1998-03-29 16:00 | 1998-03-29 17:30 | 1400 | 0 | 529 Debby Street - Pump Station | Fallbrook | SD | 92028 | Lift Station | 1 | Pump Station Failure | Pump Failure. | Removed and repaired pumps. | N | N | NA | NA | Empty field - fenced with restricted access. | Y | N | Y | 3
978039 | Quarterly |  | Joel V. Holt | (760) 723-5640 | Fallbrook Public Utility District | 1998-03-29 13:30 | 1998-03-29 15:00 | 5 | 0 | 1338 E. Fallbrook St. | Fallbrook | SD | 92028 | 4" Cleanout | 1 | Blockage | Roots or offset pipe, can't tell with out digging up. | Homeowner is going to remove trees. | N | N | NA | NA | Percolated into ground around cleanout | N | N | N | NA
978040 | Quarterly | Quarterly | Patti S. Page | (760) 723-5640 | Fallbrook Public Utility District | 1998-04-18 20:00 | 1998-04-18 20:35 | 75 | 0 | 1232 Old Stage Road | Fallbrook | SD | 92028 | 4" Cleanout | 1 | Blockage | Unknown Blockage | Flush main line. | N | N | NA | NA | Ran down the side of Old Stage Road 150 ft. and dried up. | N | N | N | NA | Used 50 gallons of wash down water on roadway.
978041 | Quarterly | Quarterly | Patti S. Page | (760) 723-5640 | Fallbrook Public Utility District | 1998-06-17 13:40 | 1998-06-17 14:15 | 8 | 0 | 1448 S. Mission Road | Fallbrook | SD | 92028 | 4" Cleanout | 1 | Other | Sanitary Napkins | Rodded with sewer rodder machine. | N | N | NA | NA | Across blacktop driveway about 60 ft. | N | N | N | NA | Used 30 gallons of wash down water on driveway.
98-1 | KRISTIN SCHALL | 1998-05-22 10:00 | JEFF STECHER | 760-753-0155 | LEUCADIA | 1998-05-21 12:15 | 1998-05-21 16:00 | 6000 | 6000 | LA COSTA AVE. & SAXONY RD | CARLSBAD | SD | 92009 | SECONDARY EFFLUENT PIPELINE | 2 | PIPELINE DAMAGED | CONTRACTOR HIT LINE WITH BULLDOZER | DISTRICT CREW REPAIRED LINE AND REVIEWED SOP'S WITH DRIVER | N | N | NA | NA | SEWER LINE | Y | N | N | NA | CONTRACTOR HIT DELINEATED LINE
01-978 | No | N/A | N/A | N/A | City of El Cajon | 3/15/98 1245 | 3/15/98 1345 | 35 | 0 | 253 CUYMACA ST. | RUSSEL RD. |  | 92020 | HOUSE/GARAGE | 1 | ROOTS | ROOTS PARTIALLY BLOCKED LINE. | PLACED ON CLEANING SCHEDULE. |  | NO | NO | NO | HOUSE OR GARAGE | NO | NO | NO | N/A | FIRST PROBLEM AT THIS LOCATION
02-978 | yes | 6/16/98 1233 | E. Donnelly | 441-1658 | City of El Cajon | 6/15/98 2030 | 6/15/98 2130 | 500 | 0 | 355 S. WESTWIND | EL CAJON | SD | 92020 | CLEANOUT | 1 | ROOTS | ROOT INFILTRATION CAUSED BLOCKAGE | PLACED ON CLEANING SCHEDULE. | NO | NO | NO | NO | ABSORBED IN | YES | NO | NO | N/A | FIRST PROBLEM AT
978001 | N/A | N/A | N/A | N/A | N/A | 7-20-97, 10:50 | 7-20-97, 11:45 | 25 GALLONS | 25 GALLONS | 420 ADELLA LANE | CORONADO | SD | 92118 | SEWER LINE |  | ROOTS | ROOTS IN SEWER LINE | CLEARED WITH VACTOR/RODDER | N | N | NONE | NONE | SEWER LINE | N | N/A | N | N
978002 | N/A | N/A | N/A | N/A | N/A | 8-3-97, 2:20 | 8-3-97, 2:00 | 25 GALLONS | 25 GALLONS | 10TH/I-J ALLEY | CORONADO | SD | 92118 | SEWER LINE |  | ROOTS | FOREIGN MATTER IN ROOTS | CLEARED WITH VACTOR/RODDER | N | N | NONE | NONE | SEWER LINE | N | N/A | N | N
978003 | N/A | N/A | N/A | N/A | N/A | 8-8-97, 9:30 | 8-8-97, 11:00 | 250 GALLONS | 250 GALLONS | VENT VAULT, SR 75 | CORONADO | SD | 92118 | SEWER LINE |  | VENT VALVE FAILURE | VENT VALVE ON FORCE MAIN FAILED | REPLACED VENT VALVE | N | N | NONE | NONE | SEWER LINE | N | N/A | N | N
978004 | N/A | N/A | N/A | N/A | N/A | 8-13-97, 1:30 | 8-13-97, 2:30 | 30 GALLONS | 30 GALLONS | FIRST/G-H ALLEY | CORONADO | SD | 92118 | SEWER LINE |  | GREASE | GREASE BUILD-UP IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N/A | N | N
978005 | N/A | N/A | N/A | N/A | N/A | 9-2-97, 8:00 | 9-2-97, 9:00 | 25 GALLONS | 25 GALLONS | 555 D AVENUE | CORONADO | SD | 92118 | SEWER LINE |  | FOREIGN MATTER | PLASTIC MATERIAL IN SEWER | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N/A | N | N
978006 | N/A | N/A | N/A | N/A | N/A | 9-2-97, 9:30 | 9-2-97, 10:30 | 150 GALLONS | 150 GALLONS | 340 B AVENUE | CORONADO | SD | 92118 | SEWER LINE |  | ROOTS | ROOTS IN SEWER LINE | CLEARED WITH VACTOR/RODDER | N | N | NONE | NONE | SEWER LINE | N | N/A | N | N
978007 | N/A | N/A | N/A | N/A | N/A | 9-4-97,12:30 | 9-4-97, 1:30 | 40 GALLONS | 40 GALLONS | A AND ORANGE | CORONADO | SD | 92118 | SEWER LINE |  | GREASE | MASSIVE AMOUNT OF GREASE IN SEWER | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N/A | N | N
978008 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-30-97 | 09-30-97 |  | 0 | International Border | San Diego | SD | 92154 | Canyon del Sol | 3 | other | overload of collection system |  | N | N | None | None |  | N | N | N
4 | GLORIA FULTON | 09/22/97 07:30 | MIKE DUNBAR | (714) 499-4555 | SOUTH COAST WATER DISTRICT | 09/22/97 07:30 | 09/22/97 08:30 | 4000 | 0 | VALIDO WAY & TOTO LOMA LANE | LAGUNA BEACH | OR | 92977 | MANHOLE | 0 | ROOTS / DEBRIS / BLOCKAGE | MANHOLE PLUGGED UP WITH ROOTS AND RAGS | CLEANED MANHOLE | N | Y | NONE | NONE | SAND | Y | N/A | N | N/A
978003 | Kathy Stone | 12/9/97 8am | Bill Wiltse | 6198744082 | SD County | 11/08/97 2030 | 11/08/97 2210 | 300 | 0 | 10105 Toledo | Spring Valley | SD | 91977 | 501-180-198T | 0 | Roots | Roots caused paper and grease to block line | Special Maintenance Line, Clean every 3 months | N | N | none | none | Perc into meadow | Y | Y | N | 0 | Televised line, good condition
978009 | N/A | N/A | N/A | N/A | N/A | 10-6-97, 1200 | 10-6-97, 1315 | 50 GAL | 50 GAL | 203 SIXTH STREET | CORONADO | SD | 92118 | SEWER LINE | 0 | FOREIGN OBJECT | ROOTS AND OBJECT IN SEWER LINE | CLEARED WITH RODDER | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978010 | N/A | N/A | N/A | N/A | N/A | 10-9-97, 1015 | 10-9-97, 1130 | 25 GAL | 25 GAL | 100 BLOCK D ALLEY | CORONADO | SD | 92118 | SEWER LINE | 2 | GREASE | GREASE IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978011 | N/A | N/A | N/A | N/A | N/A | 10-14-97, 1345 | 10-14-97, 1415 | 25 GAL | 25 GAL | 945 I AVENUE | CORONADO | SD | 92118 | SEWER LINE | 1 | ROOTS | ROOTS IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978012 | N/A | N/A | N/A | N/A | N/A | 10-17-97, 911 | 10-17-97, 1100 | 25 GAL | 25 GAL | 600 BLOCK J ALLEY | CORONADO | SD | 92118 | SEWER LINE | 0 | ROOTS | ROOTS IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978013 | N/A | N/A | N/A | N/A | N/A | 10-21-97, 1400 | 10-21-97, 1500 | 50 GAL | 50 GAL | 500 BLOCK B/C ALLEY | CORONADO | SD | 92118 | SEWER LINE | 1 | GREASE | GREASE IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978014 | N/A | N/A | N/A | N/A | N/A | 10-27-97, 2030 | 10-27-97, 2130 | 25 GAL | 25 GAL | 750 COUNTRY CLUB LANE | CORONADO | SD | 92118 | SEWER LINE | 0 | DEBRIS | FOREIGN DEBRIS IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978015 | N/A | N/A | N/A | N/A | N/A | 10-29-97, 1750 | 10-29-97, 2000 | 80 GAL | 80 GAL | 600 BLOCK E/F ALLEY | CORONADO | SD | 92118 | SEWER LINE | 0 | SAND | SAND IN SEWER | CLEARED WITH RODDER | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978016 | N/A | N/A | N/A | N/A | N/A | 10-30-97, 1030 | 10-30-97, 1430 | 25 GAL | 25 GAL | 205 SIXTH STREET | CORONADO | SD | 92118 | SEWER LINE | 1 | ROOTS | FOREIGN ROOTS IN SEWER | CLEARED WITH RODDER | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978017 | N/A | N/A | N/A | N/A | N/A | 11-1-97, 1015 | 11-1-97, 1145 | 50 GAL | 50 GAL | FOURTH, BET H/I | CORONADO | SD | 92118 | SEWER LINE | 3 | GREASE | GREASE IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978018 | N/A | N/A | N/A | N/A | N/A | 11-17-97, 945 | 11-17-97,1130 | 50 GAL | 50 GAL | 820 ADELLA AVENUE | CORONADO | SD | 92118 | SEWER LINE | 1 | ROOTS | ROOTS IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978019 | N/A | N/A | N/A | N/A | N/A | 11-27-97, 1015 | 11-27-97, 1130 | 25 GAL | 25 GAL | 200 BLOCK A/B ALLEY | CORONADO | SD | 92118 | SEWER LINE | 2 | ROOTS | ROOTS IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978020 | N/A | N/A | N/A | N/A | N/A | 11-27-97, 1402 | 11-27-97, 1515 | 25 GAL | 25 GAL | 500 BLOCK G/H ALLEY | CORONADO | SD | 92118 | SEWER LINE | 1 | ROOTS | ROOTS AND GREASE IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
978021 | N/A | N/A | N/A | N/A | N/A | 12-31-97, 2050 | 12-31-97, 2145 | 25 GAL | 25 GAL | 417 EIGHTH STREET | CORONADO | SD | 92118 | SEWER LINE | 0 | FOREIGN OBJECT | FOREIGN OBJECTS (PLASTIC MATERIAL) IN SEWER LINE | CLEARED WITH VACTOR | N | N | NONE | NONE | SEWER LINE | N | N | N | N/A
953167 | Fax 571-6972 | 10/13/97 12:30 | Davis | 6544160 | City of San Diego | 10/13/97 09:40 | 10/13/97 11:00 | 1600 | 900 | 12760 Rancho Penasquitos Bl. | San Diego | SD | 92129 | 12" VC | 1 | Grease | Grease | Cleaned extensively to remove grease | Y | Y | None | None | Canyon | Y |  | N
978003 | No, spill totalled 50 gallons. Kathy Stone, County of San Diego contacted via fax. | October 29, 1997; 11:00 am | DENNIS K. QUILLEN | -541 | RAMONA WATER DISTRICT | October 29, 1997; 11:00 am | October 29, 1997; 11:05 am | 50 | 0 | Barona Mesa Road | RAMONA | SD | 92065 | Lift Station no. 2 | 0 | Electrician failed to shut-down lift station 1 while performing mainternance on pump station no. 2 | Pump station no. 1 operated on auto, and began pumping into station no. 2. Sewage spilled onto ground surface while pump station no. 1 was being shut-off. | Electrician instructed to shut-down lift station no. 1 anytime pump station no. 2 is being maintained. | NO | No | None | None | No solids, all liquid waste which was diluted with water | Yes | NA | NO | N/A | All liquid waste, diluted with water
6 | GLORIA FULTON | 10/15/97 07:30 | MIKE DUNBAR | (714) 499-4555 | SOUTH COAST WATER DISTRICT | 10/13/97 12:15 | 10/13/97 12:30 | 100 | 80 | PACIFIC COAST HWY & RITZ COVE DR | DANA POINT | OR | 92629 | 6" DIP FORCE MAIN | 1 | CONSTRUCTION | CONTRACTOR SNAGGED 6" DIP FORCE MAIN WHILE TRENCHING FOR NEW 12" PVC LINE | 80% OF DISCHARGE WAS DIVERTED BACK INTO NEW PIPELINE ALREADY IN PLACE, REPAIR CLAMP PLACED ON 6" DIP LINE, HTH SPRINKLED IN TRENCH AND ON SOIL REMOVED | N | N | NONE | NONE | 8' DEEP TRENCH WITH ROCK BASE | Y | N/A | N | N/A
7 | 6195716972 (FULTON) | 10/16/97 08:20 | MIKE DUNBAR | (714) 499-4555 | SOUTH COAST WATER DISTRICT | 10/15/97 16:30 | 10/15/97 17:15 | 500 | 0 | 31672 SCENIC DR | LAGUNA BEACH | OR | 92677 | MAIN LINE | 0 | ROOTS | BLOCKAGE AT MAINLINE CAME OUT OF CUSTOMER CLEAN-OUT, ROOTS WERE THE CAUSE | CLEANED OUT MAIN LINE WITH RODDING MACHINE | N | Y | NONE | NONE | SAND | Y | N/A | N | N/A
978008 | Quarterly Report | 02-18-98 1200 | Ted Powell | 760-744-0460 | V.W.D. | 02-17-98 1430 | 02-17-98 1445 | 950 | none | Field | San Marcos | S.D. | 92009 | 8" line | 1 | surcharging | surcharging due to heavy rains | cut back on pumping to Treatment plant in heavy rains | n | n | none | none | n/a | y | n | n | 0 | absorbed into ground at m/h
97-98-01 | Mailed Report | Jan22,7:40am | Marc Avila | 714 248-3940 | CBWD | Jan21,2:35pm | Jan21,3:00pm | 75 | 0 | Camino De Los Mares | Capistrano Beach | OR | 92624 | Manhole | 0 | Grease | Grease in upstream manhole,flow caused bubbling at manhole. | Vactor jetted line clear, scheduled to do follow up and is cleaned on regular P&M schedule | no | yes | None | None | Curb and Gutter | Yes | N | No | N/A | Reported to Monica Mazur OCHD
97-98-05 | Faxed | March14,9:30am | Chris Goodchild | 714 487-1097 | CBWD | March14,NA | Mar14,11:30am | 75 | 0 | Pacific Coast Hwy | Capistrano Beach | OR | 92624 | service lateral | 1 | OTHER | Heavy rainstorm event caused hillside to slide and break line. | Contractor repaired line | no | no | none | none | soil | yes |  | no | N/A | Approx. 50 gallons entered storm drain of the 300
978018 | ELECTRONIC QTLY RPT |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 01/28/98, 1200 | 02/05/98, 1000 | 200 | 0 | BUILDING 2378 | CAMP PENDLETON | SD | 920555008 | SEWER LATERAL FROM BUILDING | 1 | CONSTRUCTION | EXISTING SEWER LATERALS FROM BUILDING WERE NOT CONNECTED TO NEW SEWER MAIN BEFORE EXISTING SEWER MAIN WAS DEMOLISHED |  | N | N | NONE | NONE | PERCOLATION SITE AROUND PIPE. | N | NA | N | N/A | SPILL OCCURRED AT CONSTRUCTION SITE. NOT IN AN AREA OF EXPECTED PUBLIC CONTACT.
978022 | N/A | N/A | N/A | N/A | City of Coronado | 1-2-98, 8:45 | 1-2-98, 10:30 | 50 gal | 50 gal | 100 block F/G alley | Coronado | SD | 92118 | Sewer line | 2 | Roots | Roots and debris in sewer line | Cleared with Vactor | N | N | None | None | Sewer line | N | N | N | N/A
978023 | N/A | N/A | N/A | N/A | City of Coronado | 1-10-98, 10:30 | 1-10-98, 12:00 | 60 gal | 60 gal | Third and Orange | Coronado | SD | 92118 | Sewer line | 1 | Debris | Plastic debris in sewer line | Cleared with Vactor | N | N | None | None | Sewer line | N | N | N | N/A
978025 | N/A | N/A | N/A | N/A | City of Coronado | 1-20-98, 21:35 | 1-20-98, 23:00 | 50 gal | 50 gal | 8th and I/J alley | Coronado | SD | 92118 | Sewer line | 1 | Roots | Roots and debris in sewer line | Cleared with Vactor | N | N | None | None | Sewer line | N | N | N | N/A
978026 | N/A | N/A | N/A | N/A | City of Coronado | 1-23-98, 19:00 | 1-23-98, 22:00 | 100 gal | 100 gal | 555 D Avenue | Coronado | SD | 92118 | Sewer line | 2 | Debris/grease | Debris and grease in sewer line | Cleared with Vactor | N | N | None | None | Sewer line | N | N | N | N/A
978027 | N/A | N/A | N/A | N/A | City of Coronado | 2-16-98, 9:15 | 2-16-98, 12:00 | 75 gal | 75 gal | Ninth and B | Coronado | SD | 92118 | Sewer line | 0 | Roots | Roots and debris in sewer line | Cleared with Vactor | N | N | None | None | Sewer line | N | N | N | N/A
975987 | Fax 571-6972 | 02/10/98 04:59 | M.Whelan | 6544160 | City of San Diego | 02/09/98 17:22 | 02/09/98 19:00 | 980 | 800 | 1010 W. San Ysidro Bl. | San Diego | SD | 92173 | 8" VC | One | Grease | Grease | Flush main to remove grease | N | N | None | None | Soaked up along I-5 | Y | Y | N
979589 | Fax 571-6972 | 03/03/98 05:55 | M.Whelan | 6544160 | City of San Diego | 03/02/98 14:31 | 03/02/98 19:30 | 224 | 0 | 6471 Norman Ln. | San Diego | SD | 92120 | 8" VC | One | Roots | Roots | Clean main to clear roots | N | N | None | Soaked into hillside |  | Y | N | N
978011 | Quarterly Report | 05-18-98 1400 | Ted Powell | 760-744-0460 | V.W.D. | 05-18-98 0920 | 05-18-98 0930 | 900 | none | Rancho Santa Fe Rd. | San Marcos | S.D. | 92069 | 8" line | 2 | surcharging | To much flow for in line | Cut flow back to handle peak flows during the day. | n | n | none | none | n/a | y | n | n | 0 | absorbed into ground at M/H
978002 | Fax | 1998-04-22 12:00 | Dave Seymour | 9494596540 | Santa Margarita Water District | 1998-04-21 12:00 | 1998-04-21 12:00 | 3000 | 0 | South Bend Road | Coto de Caza | OR | 92679 | Wetwell | 1 | Construction | Contractor illegally pumped out wet well and dumped it onto nearby ground. Found wet area and signs of sewage (plastics and rubber goods). Cleaned up the site. Questioning of employees and pump truck driver failed to reveal who performed the dumping. |  | N | N | None | None | N/A | Y | Y | N | N/A
978004 | ELECTRONIC QTLY RPT |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 07/29/97 | 15:00 | 600 | 0 | Bldg 51096, Burger King | SD | 920555008 | Grease Trap | 1 | GREASE | Grease trap exit pipe backed up due to grease and debris | notified tenant to have grease trap cleaned. Used ramjet to clear line | Y | Y | San Onofre Creek/ESTUARY | none (see remarks) |  | Y | NA | Y | 3 |  | FLOWED 60' OVER PARKING LOT TO STORM DRAIN, 300' UNDER PARKING LOT TO EDGE OF CANYON, 400' TO SAN ONOFRE CREEK. CREEK IS NOT FLOWING BUT HAS WATER POOLED UNDER FREEWAY. ESTUARY MOUTH BLOCKED BY SANDBAR.
978004 | Quarterly Report | 08/12/97; 13:30 | Richard Andrews | 619 755-3294 | City of Del Mar | 08/12/97; 10:30 | 08/12/97; 11:45 | 900 gallons | 0 | 12th Street and Maiden Lane | Del Mar | SD | 92014 | Manholes grid B8 81, 17, 18 | 0 | Roots | Roots blocking 8" sewer main. | Rodded main to clear roots. Continue preventative rodding. | Y | Y | Ocean | N/A |  | Y | NA | Y | 1 | Two signs posted north and 2 south 50 yards either side of spill.
1110971 | VM/FAX | 11/10/97, 13:20 | Jay Elston | 714 366-1553 | CITY OF SAN CLEMENTE | 11/10/97, 10:30 | 11/10/97, 11:10 | 900 gal | 0 | Cascadita / Montego | San Clemente | OR | 92672 | SMHB5434 | 0 | Roots |  |  | Y | Y | Ocean |  | Pacific Ocean | Y | N | Y | 2 Days | Roots caused blockage at intersection of Cascadita / montego. Area not root problem. Blockage may be a result of homeowner cleaning house lateral. County posted beaches and sampled.
1124971 | Rebecca Stewart | 1997-11-24 | A J Howard | 714 366-1553 | CITY OF SAN CLEMENTE | 11/21/97, 12:00 | 11/22/97, 16:00 | 2300 gal | 0 | 380 Ave Pico | San Clemente | OR | 92672 | RWW Yard Pipe | 0 | Corroded Line |  |  | Y | Y | Ocean |  | Pacific Ocean | Y | N | N | NA | Reclaimed water line for irrigation corroded. Leak initially thought to be domestic fire service line. Crews ID line as RWW and repairs began next day. A new line is being installed.
978024 |  |  | Ed Calhoun | 7609667868 | Water Utilities Dept. City of Oceanside | 11/21/97 1430 | 11/21/97 1500 | 100 | 0 | 1200 North Harbor | Oceanside | SD | 92054 | Manhole | 0 | Roots | Sewer Lateral belonging to Oceanside Marina Towers became "root bound" by their trees. | Management of "Towers" was requested to keep their lateral free of roots. | Y | Y | Oceanside Harbor | Pacific Ocean | N/A | Y | N/A | Y | 2
978028 | Quarterly Report only County Health was notified. | 1/30/98 1055 | Todd Anderson | 741-4854 | City of Escondido | 1/30/98 1050 | 1/30/98 1055 | 125 Gallons | 50 Gallons | 1564 Tanglewood | Escondido | SD | 92025 | Manhole, Sewer Atlas Page 426 MH. 5803 | 1 | Roots | Stoppage could have formed due to roots in main line and manhole. | Roots were removed and main lines were cleaned. Televising of main revealed no major structural problem. | Y | Y | Open culvert then to soil. | N/A | N/A | Y | N | Y | Two | No samples taken.
| SIRT (FAX) | 1998-02-18 15:00 | Brad Bruington | 714-425-3514 | Moulton Niguel Water | 1998-02-16 11:30 | 1998-02-16 15:30 | 3600 | 0 | Camino Capistrano | Laguna Niguel | OR | 92677 | 30" steel line | 1 | Line break | Ground sliding into river cracked 30" steel secondary effluent outfall line, plant off, drained line. | Line repaired by welder. Tested with flow. | Y | N | Oso Creek | Pacific Ocean | NA | Y | N | Y | TBD | O.C. Health Dept. posted beaches
| SIRT (FAX) | 1998-02-18 15:00 | Brad Bruington | 714-425-3514 | Moulton Niguel Water | 1998-02-18 12:00 | 1998-02-18 17:00 | 1200 | 0 | Camino Capistrano | Laguna Niguel | OR | 92677 | pipeline | 2 | Line break | Second break at land slide area. | Drain and weld line. | Y | N | Oso Creek | Pacific Ocean | N/A | Y | N | Y | TBD | O.C. Health Dept. posted beaches
978010 | (619) 571-6972 | 1997-08-17 11:30 | Mitch Pierson | (760) 723-5640 | Fallbrook Public Utility District | 1997-08-16 23:00 | 1997-08-17 01:00 | 195000 | 0 | 2575 Olive Hill Rd. | Fallbrook | SD | 92028 | 6" Pipeline @ Meter | 1 | Line break. | Truck hit 6" recycled water meter pipeline. | Pipeline was valved off until the repair is complete. | Y | N | Ostrich Creek | San Luis Rey River | N/A | Y | Y | N | N/A | Signs were not posted as per OES, David Cammal. Spill was Title 22, recycled water.
978012 | (619) 467-2952 | 1997-09-29 11:45 | Joel Holt | (760) 723-5640 | Fallbrook Public Utility District | 1997-09-29 05:00 | 1997-09-29 09:30 | 62330 | 0 | Overland Trail | Fallbrook | SD | 92028 | Effluent Line - Plant 2 | 1 | Line Break | Break in pressure line, effluent from Plant 2. | Secured pumps and repaired line. | Y | N | Ostrich Creek | San Luis Rey River | N/A | Y | Y | Y | 3 | Spill was secondary effluent.
978013 | 619-467-2952 | 1997-10-13 14:00 | Joel Holt | 7607235640 | Fallbrook Public Utility District | 1997-10-13 04:00 | 1997-10-13 08:00 | 4000 | 0 | 2800 Overland Trail | Fallbrook | SD | 92028 | Effluent Line-Plant2 | 2 | Line Break | Pressure line sustained a hole. | Secured pumps and repaired the line. | Y | N | Ostrich Creek | San Luis Rey River | NA | Y | Y | Y | 3 | Secondary Effluent
978019 | SDCnty - K. Stone | 1997-12-08 12:40 | Patti Page | 7607235640 | Fallbrook Public Utility District | 1997-12-07 14:00 | 1997-12-07 14:45 | 300 | 0 | 990 E. Mission | Fallbrook | SD | 92028 | Manhole | 1 | Blockage | Stick and mud in manhole. | Flushed and recovered paper and ground cover. Replaced ground cover of surrounding area and posted sign. | Y | Y | Ostrich Creek | San Luis Rey River | NA | Y | N | Y | 3 | Picked up a yard of ground cover for replacement at spill location. Spill ran along side of road and into storm drain to Ostrich Creek.
978034 | County SD | 1998-03-23 10:45 | Patti S. Page | (760) 723-5640 | Fallbrook Public Utility District | 1998-03-17 13:30 | 1998-03-17 14:30 | 40 | 5 | 904 S. Main St. | Fallbrook | SD | 92028 | Cleanout | 1 | Grease | Cleanout plug full of grease. | Rodded line all the way to main. Flushed main line. | Y | Y | Ostrich Creek | San Luis Rey River | NA | N | N | N | NA | Washed down and disinfected immediate area around cleanout.
987006 | QUARTERLY REPORT | 10-2-97; 14:30 | RICHARD ANDREWS | 6197553294 | CITY OF DEL MAR | 10-2-97; 10:15 | 10-2-97;13:45 | 840 | 0 | 1247 CAMINO DEL MAR | DEL MAR | SD | 92014 | CLEANOUT | 0 | GREASE |  | ADVISED OWNER TO HAVE LATERAL CLEAN SEMIANNUALLY | Y | Y | PACIFIC |  |  | Y | N | Y | 1 | NA
978003 | ELECTRONIC QTLY RPT |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 07/15/97 | 16:25 | 25 | 10 | Bldg 520450 | SD | 920555008 | cleanout | 4 | ROOTS | paper towels and roots in manhole | replaced broken pipe. | Y | N | San Onofre Creek | Pacific Ocean |  | N | NA | N | 0 |  | SPILL FLOWED 15' INTO A DRY GRASS AREA. NOT IN AN AREA OF EXPECTED PUBLIC CONTACT.
978005 | ELECTRONIC QTLY RPT |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 08/01/97 | 18:00 | 30 | 10 | Bldg 62520 | SD | 920555008 | cleanout on main line | 1 | ROOTS | roots and towels caused blockage resulting in sewage overflowing from cleanout | used jetter to clear stoppage | Y | N | San Mateo Creek | Pacific Ocean |  | N | NA | N | 0 |  | SPILLED FLOWED 5' FROM CLEANOUT OVER SIDEWALK 30' INTO GRASSY AREA
978007 | ELECTRONIC QRTLY RPT |  | KARL VOGEL | 6197259762 | MCB, CAMP PENDLETON | 08/15/97 | 18:30 | 500 | 150 | BLDG 43402 | SD | 920555008 | Grease TRAP MESS HALL | 3 | GREASE | Grease trap stopped up WITH GREASE causing OVERFLOW of cleanout | contact food services, advised to check grease trap enzyme program for proper application. cleaned out trap. | Y | Y | Las Flores Creek | Pacific Ocean |  | Y | NA | N | 0 |  | SPILL FLOWED 200' ACROSS A PARKING LOT INTO STORM DRAIN, 100' DOWN CEMENT LINED DITCH, SOAKED INTO DIRT AND WEEDS IN BOTTOM OF DITCH.
978008 | ELECTRONIC QTRLY RPT |  | KARL VOGEL | 6197259762 | MCB, CAMP PENDLETON | 08/17/97 | 10:30 | 30 | 0 | BLDG 43402 | SD | 920555008 | Grease Trap Mess Hall | 4 | GREASE | grease trap STOPPED UP WITH GREASE resulted in overflow | Ramjet used to clear line, will notify food services to treat. Check enzyme program for proper application | Y | Y | Las Flores Creek | Pacific Ocean |  | Y | NA | N | 0 |  | SPILL FLOWED 200 FT DOWN STREET AND 50 FT INTO STORM DRAIN. PERCOLATED IN CEMENT LINED DITCH THAT HAS DIRT AND WEEDS IN BOTTOM.
978009 | ELECTRONIC QTRLY RPT |  | KARL VOGEL | 6197259762 | MCB, CAMP PENDLETON | 08/26/97 | 17:30 | 950 | 0 | LIFT STATIONS 51050 & 51054 BASILONE RD | SD | 920555008 | MH FOR 51050 WET WELL AND MH FOR 51054 WET WELL | 1 | OTHER | POWER SECURED AT 51050, TO REPAIR AIR-VAC VALVE ON FORCE MAIN TO STP 11. FLOW WENT FROM 51050 TO 51054- ADDITIONAL FLOW TO 51054 CAUSED FLOW OUT MAN HOLES AT BOTH STATIONS WHEN 51054 COULD NOT KEEP UP |  | Y | Y | SAN ONOFRE CREEK | PACIFIC OCEAN |  | Y | NA | N | 0 |  | SPILL FLOWED FROM BOTH MH51050=110 FT AND MH51054=55FT INTO STORM DRAIN, FLOW TRAVELLED APPROX 1/4 MILE TO UNDEVELOPED FIELD AN PERCOLATED INTO SOIL.NOT IN AN AREA OF EXPECTED PUBLIC CONTACT.
97810 | ELECTRONIC QTRLY RPT |  | KARL VOGEL | 6197259762 | MCB, CAMP PENDLETON | 08/26/97 | 14:00 | 900 | 0 | BasIlone Rd. | SD | 920555008 | Air-Vac on forced main | 2 | OTHER | Air-Vac jammed open, venting to atmosphere | Secured PUMP STATION 51050 TO SECURE Air-Vac and installed new one. | Y | Y | San Onofre Creek | Pacific Ocean |  | Y | NA | N | 0 |  | SPILL FLOWED 30 FT DOWN ROAD INTO CULVERT, 20 FT UNDER ROAD, PERCOLATED IN SAND 10 FT FROM END OF CULVERT. TOTAL OF 60 FT. SPILL OCCURED IN SEMI-WILDERNESS, NOT EXPECTED TO HAVE PUBLIC CONTACT.
987012 | QTLY RPT TO RWQCB |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 09/16/97 | 20:30 | 200 | 50 | Bldg 520450 | SD | 920555008 | C/O main | 12 | OTHER | manhole overflowed due to jetting equipment when clearing roots from the sewer line. | Preventative maintenance program of clearing roots from the lines | Y | Y | San Onofre Creek (dry) | Pacific Ocean |  | N | NA | N | 0 |  | SPILL FLOWED FROM MANHOLE 150 FT INTO STORM DRAIN ON BASILONE RD THEN INTO SAN ONOFRE CREEK (DRY). TOTAL DISTANCE 530 FT
978013 | G. FULTON VOICEMAIL | 13:45 | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 09/16/97 | 17:30 | 1800 | 1000 | Intersection of Eliason and Angel | SD | 920555008 | MANHOLE | 1 | GREASE | Grease caused blockage which caused overflow from manhole | Ramjetted blockage. Recovered 1000 gallons with Super Vac truck | Y | Y | Santa Margarita | Pacific Ocean |  | Y | Y | N | 0 |  | Spill flowed 65' from manhole to storm drain on Eliason THEN INTO CANYON. TOTAL DISTANCE 650 FT INTO THE CANYON. SPILL FLOWED TO AREA OF NO EXPECTED PUBLIC CONTACT
968496 | Fax 571-6972 | 12/28/97 21:22 | Branco | 6544160 | City of San Diego | 12/28/97 15:45 | 12/28/97 19:40 | 235 | 0 | 242 Prospect St. | San Diego | SD | 92037 | 6" VC | 1 | Other | Faulty pipe | Faulty slipline pipe connection pried open | Y | Y | Pacific Ocean |  | Pacific Ocean | Y | N/A | Y
9 | 6195716972 (FULTON) | 12/08/97 12:30 | MIKE DUNBAR | (714) 499-4555 | SOUTH COAST WATER DISTRICT | 12/06/97 12:43 | 12/06/97 14:00 | 130000-150000 | 0 | ALISO CREEK | LAGUNA BEACH | OR | 92651 | SEWAGE LIFT STATION | 0 | INFILTRATION | INFILTRATION OF SURFACT FLOOD WATER COMING FROM ALISO CREEK PUMPS COULD NOT HANDLE VOLUME | FLOWS DIVERTED INTO ABANDONED OUTFALL LINE PUMPS WERE BACK ON LINE AS SOON AS MANHOLE COVERS COULD BE REACHED AND PLACED BACK IN POSITION | Y | N | PACIFIC OCEAN | NONE | N/A | Y | Y | Y | UNKNOWN AT THIS TIME | ALISO CREEK IMPACTED BY HEAVY SURFACE RUNOFF ORIGINATING INLAND
10 | 6195716972 (FULTON) | 02/17/98 10:30 | MIKE DUNBAR | (714) 499-4555 | SOUTH COAST WATER DISTRICT | 02/17/98 05:15 | 02/17/98 08:40 | 11286 | 0 | ALISO PKWY & AWMA ROAD | LAGUNA NIGUEL | OR | 92677 | EAST EXPORT SLUDGE BARREL | 0 | LINE BREAK | CREEK EROSION DUE TO HEAVY STORM RUNOFF CAUSED EMBANKMENT FAILURE | FIX LINE BREAK | Y | N | PACIFIC OCEAN | NONE | N/A | Y | Y | Y |  | SIGNS ALREADY POSTED DUE TO SPILL FROM TRABUCO CANYON WATER DISTRICT
1109801 | R.Stewart | 1/10/1998; 17:30 | A J Howard | 714 366-1553 | CSC | 1/10/1998; 900 | 1/10/1998; 1400 | 6000 | 0 | 100 Ave Rosa/Alley | San Clemente | OR | 92691 | SMHD721 | 0 | Contractor Trench collapse displaced sewer line | Contractor Trench collapse displaced sewer line |  | Y | Y | Pacific Ocean |  | Pacific Ocean | Y | N | Y | 5 | Contractor cited by City Inspector to protect all utilities before proceeding. City inspector to continue to monitor contractor.
1309801 | SiRT | 1/30/1998; 17:00 | Jay Elston | 714 366-1553 | CSC | 1/30/1998; 1605 | 1/30/1998; 1715 | 7,500 Gal | 0 | Avenida Califia | San Clemente | OR | 92691 | SMHD725 | 0 | Grease/Roots | Grease/Roots |  | Y | Y | Pacific Ocean |  | Pacific Ocean | Y | N | Y | 4
2269801 | R. Stewart | 2/26/1998; 17:30 | A J Howard | 714 366-1553 | CSC | 2/26/1998; 800 | 2/26/1998; 1730 | 50000 | 0 | Esplanade/Trafalgar | San Clemente | OR | 92691 | RWW Beach | 0 | High Tide/Storm; Surf condition eroded 6ft. soil | High Tide/Storm; Surf condition eroded 6ft. soil |  | Y | Y | Pacific Ocean |  | Pacific Ocean | Y | N | Y | 1 | Combination of high tide and extremely heavy storm surf conditions eroded beach up to the RR tracks exposing and undermining RWW line. Line was isolated at plant on 25 Feb 98 and pumped until loss of suction.
3199801 | N/A |  |  |  |  | 3/19/1998; 815 | 3/19/1998; 930 | <500 Gallons | 0 | Esplanade/Trafalgar | San Clemente | OR | 92691 | RWW Beach | 0 | Line out of service; line plug leaking | Line out of service; line plug leaking |  | Y | Y | Pacific Ocean |  | Pacific Ocean | Y | N | Y | 0 | Off duty operator observed RWW line leaking<3gpm at 08:15; Monica Mazur, OC DOHS also reported at 900; Spoke w/ Monica advise crew was resetting plug at plant; Crew pumped down sump and hard pipe air line to pulg; EST lost < 500 gallons RWW soaked in sand
3259801 | Craig | 3/25/1998; 1310 | Jay Elston | 714 366-1553 | CSC | 3/25/1998; 1210 | 3/25/1998; 1313 | 200Gallons | 0 | Victoria/Del Mar | San Clemente | OR | 92691 | SMHC708 | 0 | 3" Rainfall in less than 3 hrs. Trunk line under 8ft water upstream | 3" Rainfall in less than 3 hrs. Trunk line under 8ft water upstream |  | Y | Y | Pacific Ocean |  | Pacific Ocean | Y | N | Y |  | Unusually high level of precipitation in short period time flooded beach trunk line south of Pier. Inflows Subsided within 30 minutes, pump stations recovered within 90 minutes.
3259802 | Craig | 3/25/1998; 1310 | Jay Elston | 714 366-1553 | CSC | 3/25/1998; 1330 | 3/25/1998; 1410 | 1,200 Gallons | 0 | Boca De La Playa | San Clemente | OR | 92691 | SMHD8713 | 0 | 3" Rainfall in less than 3 hrs. Trunk line under 8ft water upstream | 3" Rainfall in less than 3 hrs. Trunk line under 8ft water upstream |  | Y | Y | Pacific Ocean |  | Pacific Ocean | Y | N | Y |  | Unusually high level of precipitation in short period time flooded beach trunk line south of Pier. Inflows Subsided within 30 minutes, pump stations recovered within 90 minutes.
97-98-03 | Faxed | Feb 15,9:00pm | Chris Goodchild | 714 487-1097 | CBWD | Feb 14,1:00pm | Feb14,4:00pm | 4500 | 0 | Pacific Coas Hwy | Capistrano Beach | OR | 92624 | Manhole | 1 | OTHER | Heavy rainstorm event caused hydraulic surcharge on our system.PCH stormdrain on hillside broken also. | Storm finally stopped, jetted lines as precaution due to tremendous amount of surface water infiltration | no | yes | Pacific Ocean | none | Ocean | yes |  | yes | OCH | Reported to OCHD
97-98-02 | Faxed | Feb 2,10:30am | Larry Fregin | 714496-1324 | CBWD | Feb 3,10:30am | Feb 3,11:30am | 6750 | 0 | Pacific Coast Hwy | Capistrano Beach | OR | 92624 | Manhole | 0 | OTHER | Heavy rainstorm event caused hydraulic surcharge on our system. | Follow up inspection, El Nino storm event | no | yes | Pacific Ocean | none | Ocean | yes |  | yes | OCH | Larry Honeyborne was in area,showed up to location
97-98-04 | Faxed | Feb22,5:30pm | Geoffrey Cook | 714 487-1097 | CBWD | Feb22,3:45pm | Feb 22,4:05pm | 500 | 0 | Pacific Coast Hwy | Capistrano Beach | OR | 92624 | Manhole | 2 | OTHER | Continuous storm events continue to cause hydraulic overloads on system. | Continue to monitor system | no | yes | Pacific Ocean | none | Ocean | yes |  | yes | OCH | El Nino heavy rain, causing us surcharge.005-
4089801 | Dan Hoirup | 1998-04-08 10:05 | Jay Elston | 949 366-1553 | CSC | 1998-04-08 09:30 | 1998-04-08 10:30 | 4500 | 0 | Esplanade / T-Street | CSC | OR | 92672 | RWW Beach Line to Califia | 2 | Pipe Plugged Failed |  |  | Y | Y | Pacific Ocean |  | Pacific Ocean | Y | N | Y | 1 | Plug installed in reclaimed water line pipe at treatment plant failed. Reclaimed water flowed out onto beach south of T-Street were pipe was damaged winter storm and surf conditions. ON 10 Aor 98 crews installed line valve on RWW line at north Beach
978008 | Not informed | 980602 0630 | City of Laguna Beach | 949 497-0765 | Laguna Beach | 980602 0615 | 980602 0730 | 100 | 50 | Cleo Street Beach | Laguna Beach | Orange | 92651 | Cleo Street Beach | 1 | 8" Siphon Break | The 8" CI Siphon located on the beach was leaking @ high water line, just as it was going in to the wet well. the line is encased in concrete | Crew built a sand berm and recovered 50 gal. We used stop leak material to plug the crack. | Yes | No | Pacific Ocean | None | Pacific Ocean | Yes | No | Yes | 3 | The City is planning to relocate the pipe.
978009 | 619 571-6972 | 980613 1130 | City of Laguna Beach | 949 497-0765 | Laguna Beach | 980613 1100 | 980613 1130 | 1500 | 500 | Shaws Cove | Laguna Beach | Orange | 92651 | Fairview Street Pump Station #14 | 2 | Force Main Break | Force Main Break failure due to old age. 40 yrs. old | An Emergency repair was made on the 6" CI Pipe. This force main will be replaced this month. | Yes | No | Pacific Ocean / Shaws Cove Bch | None | Pacific Ocean | Yes | Yes | Yes | 5 | New Force Main to be constructed
978003 | 619 571-6972 | 970918 1020 | City of Laguna Beach | 714 497-0765 | Laguna Beach | 970918 1020 | 970918 1040 | 100 | None | 647 S. Coast Hwy | Laguna Beach | Orange | 92651 | 647 S. Coast Hwy | 1 | Grease | 8" Sewer Main Line on Sleepy Hollow | Jetter machine used to open up the | Yes | No | Pacific Ocean / Sleepy Hollow | None | Same | Yes | No | Yes | 4 | Posting was done by Orange County Health Dept. Beach closed from
978-001 | Kristin Schwall | 1998-02-15 11:15 | City of Encinitas Lifeguard | (760)753-6203 | City of Encinitas | 1998-02-15 11:15 | 1998-02-15 12:45 | 85000 | 0 | 301 Third Street | Encinitas | SD | 92024 | Moonlight Beach Pump Station | 0 | Infiltration/ Pump Station Failure | Inflow exceeded pump capacity and submerged level sensor which gave inaccurate level data. Caused eratic pump operation and failure to match flow. All data was lost. Pumps shut down causing spill. High wetwell alarm went unreported. | Manually started pumps, cleaned level sensor and reset system. Notified alarm company. Clean-up initiated. Spill and debris completely cleaned using vaccon. | y | y | Pacific Ocean/ Moonlight Beach |  |  | y | n | y | n/a
978005 | 619 571-6972 | 080224 1500 | City of Laguna Beach | 714 497-0765 | Laguna Beach | 980223 1800 | 980224 1430 | 200000 | None | 2556 Temple Hills Drive | Laguna Beach | Orange | 92651 | 2556 Temple Hills/Swr Easement | 1 | Heavy Rain | Due to extremely heavy rain, the hillside gave way | City Crew replaced the missing pipe with pvc | Yes | Yes | Pacific Ocean/Cleo Street Beach | None | Same | Yes | No | Yes | On Going | Due to storm water and sewer spill, all of our beaches were contaminated.
978004 | 619 571-6972 | 971212 0700 | City of Laguna Beach | 714 497-0765 | Laguna Beach | 971211 1055 | 971211 1120 | 250 | None | 100 Blk. S. Coast Hwy | Laguna Beach | Orange | 92651 | 100 Blk. S. Coast Hwy Manhole #3 | 1 | Grease | Grease build-up caused the flow to | Broke stoppage using the Jetter. Need | Yes | Yes | Pacific Ocean/Main Beach | None | Same | Yes | No | Yes | 4 | Signs were still up from previous spill on 12/6
978006 | 619 571-6972 | 980317 0905 | City of Laguna Beach | 714 497-0765 | Laguna Beach | 980317 0900 | 980317 1030 | 10000 | None | Fairview Street | Laguna Beach | Orange | 92651 | Fairview Street Pump Station | 1 | Force Main Break | Failure of 6" Force Main just outside the pump station. This force main is 40 yrs old. | Repaired with a clamp, pipe has a 4" long crack. This main wil be replace by May 98. | Yes | Yes | Pacific Ocean/Shaws Cove Bch | No | Pacific Ocean | Yes | No | Yes | 5 | Number of posted days are estimates
978158 | Fax 571-6972 | 02/14/98 19:33 | M.Bedard | 6544160 | City of San Diego | 02/14/98 15:00 | 02/14/98 15:10 | 50 | 50 | 2211 Avenida de la Playa** | San Diego | SD | 92037 | SPS 27 | One | Power Outage | Power outage caused by storm | Power returned and spill vacuumed up; area hosed & cleaned | N | N | Parking garage | Tennis Club |  | Y | N | N
999336 | Fax 571-6972 | 6/27/98 15:05 | J. Oropeza | 654-4160 | City of San Diego | 6/27/98 12:25 | 6/27/98 13:30 | 130 | 85 | 1620 Garnet Av. | San Diego | SD | 92109 | 8" VC | One | Grease | Blockage caused by grease and sludge | Remove grease/sludge from 8" vc main | Y | N | Parking lot at Vons | Mission Bay/Pacific Ocan | Parking lot and grass area | Y | N | N | N/A | N/A
977424 | Fax 571-6972 | 02/19/98 09:30 | G.Richardson | 6544160 | City of San Diego | 02/18/98 13:41 | 02/18/98 14:10 | 10 | 10 | 4121 Camino del Rio S. | San Diego | SD | 92115 | 8" VC | One | Debris | Debris | Flushed to relieve stop. Flushed main for city protection | Y | N | Pavement at manhole 231 | N/A | Recovered by Vactor | Y | N | N
975957 | Fax 571-6972 | 02/09/98 13:00 | J.McPherson | 6544160 | City of San Diego | 02/08/98 12:00 | 02/09/98 08:00 | 1200 | 0 | 11388 Sorrento Valley Rd. | San Diego | SD | 92121 | 2" air valve | One | Debris | Debris | Put air valve on regular maintenance program | Y | Y | Penasquitos Lagoon | Pacific Ocean |  | Y | Y | N
978026 | ELECTRONIC QTLY RPT |  | KARL VOGEL | 6197259762 | MCB, CAMP PENDLETON | 03/23/98, 0730 | 03/23/98, 1000 | 500 | 0 | F STREET, AT MESSHALL BLDG 14036 | CAMP PENDLETON | SD | 920555008 | Grease Trap | 1 | GREASE | animal fat BUILD UP CAUSED BLOCKAGE IN OUTLET PIPES OF GREASE TRAP DUE TO MISSING SANITARY TEE'S (FOUND IN BOTTOM OF TANK). |  | y | Y | PILGRAM CREEK | SAN LUIS REY RIVER | Earthen diTCH ADJACENT F Street and Messhall. | Y | NA | N | 0 | FLOW TRAVELLED: CONCRETE SWALE (30FT) EARTHEN DITCH (250FT) AND PERCOLATED AFTER MINOR PONDING. NO EXPECTED PUBLIC CONTACT IN AREA OF OVERFLOW. HOT WATER AND DEGREASER USED TO CLEAN/DISINFECT AREA ADJACENT THE MESSHALL.
978014 | CAROL TAMAKI | 12:00 | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 09/28/97 | 19:30 | 09/29/97 | 16,000 | 1,000 | Behind 243 Holt Court (SERRA MESA HOUSING AREA) | SD | 920555008 | M/H 2Y112, 2Y113 | 1 | VANDALISM | Bowling ball size rocks in bottom of manhole causED pipe blockage. DURING THE CLEARING PROCESS ONE OF THE ROCKS ROLLED DOWN THE PIPE AND CAUSED A BREAKAGE. | Ramjetted manhole and recovered large rocks. One of the rocks slipped through line and caused a breakage near m/h 2Y110. Repaired line and pumped 1,000 gallons back into m/h 2Y110. | Y | N | Pilgrim Creek | San Luis Rey River |  | Y | Y | Y | 3 | SPILL FLOWED OUT OF M/H 500' TO PILGRIM CREEK THEN APPROX 1 MILE AND PERCOLATED IN CREEK BED
978029 | ELECTRONIC QTLY RPT |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 06/26/98,12:00:00 PM | 06/26/98,1:10:00 P.M. | 20 | 0 | BLDG 14137, 16TH STREET | CAMP PENDLETON | SD | 920555008 | CLEANOUT | 1 | OTHER | Cap came off cleanout. Sewage overflowed from cleanout. | Put cap back onto cleanout. Notified pipe shop to inspect and repair as necessary. | Y | N | Pilgrim Creek | San Luis Rey River |  | N | NA | N | 0 | SPILL FLOWED 15 FT FROM CLEANOUT ACROSS DIRT FIELD AND SOAKED INTO THE GROUND. NOT IN AN AREA OF EXPECTED PUBLIC CONTACT.
978010B | Voice mail | 03-21-98 1325 | Cheryl Brandstrom | 760-744-0460 | V.W.D. | 03-21-98 1000 | 03-21-98 1200 | 239000 | none | Canyon Easement SE of El Camino Real & Palomar Airport Rd. | Carlsbad | S.D. | 92009 | 24" line | 6 | broken pipe | Steel pipe was possibly crushed when installed. | In process of replacing bad pipe. | n | n | Pond on golf course | n/a | Series of ponds on golf course | y | y | y | 14+ | area posted as per health dept.
978003 | KATHY STONE-FAX | 8/5/97-11:03 A | PAT GUEVARA | 438-2722 X134 | CARLSBAD MWD | 8/2/97-11:30 A | 8/2/97-1:15 P | 150-250 | 0 | MEDFORD CT. | CARLSBAD | SD | 92008 | SEWER MAIN DEAD-END CLEANOUT | 1 | UNKNOWN BLOCKAGE |  | USED VACTOR TO JET ROD PLUGGED SEWER MAIN. RAN JET RODDER THRU PROBLEM AREA SEVERAL TIMES TO INSURE BLOCKAGE WAS COMPLETELY CLEARED | Y | Y | POWER LINE EASEMENT, CALAVERA HILLS (NATURAL DRAINAGE BASIN) |  |  | Y | N | N | N/A | CHECKED DRAIN AREA AT CHESTNUT CROSSING POINT, FOUND NO EVIDENCE OF WASTEWATER AT THAT POINT.
970674 | Fax 571-6972 | 01/13/98 05:05 | M.Whelan | 6544160 | City of San Diego | 01/12/98 15:45 | 01/12/98 16:45 | 300 | 250 | 40th St. 1800' n. of Adams Av. | San Diego | SD | 92116 | 8" VC | Three | Vandalism | Rocks and debris buildup from vandalism | Rocks removed from manhole/cleaned manhole | Y | Y | Pumped overflow into manhole | Storm drain/San Diego River |  | Y | N | N
999379 | Fax 571-6972 | 6/29/98 14:20 | L. Finch | 654-4160 | City of San Diego | 6/29/98 09:05 | 6/29/98 10:35 | 180 | 160 | Main St. & Sigsbee St. | San Diego | SD | 92113 | 6" CP | One | Debris | Main filled with pinto beans and grease | Remove grease, food from 6" cp main | Y | N | Recovered most of spill | Dried in street | N/A | Y | N | N | N/A | N/A
978002 | 619 571-6972 | 970831 1030 | City of Laguna Beach | 714 497-0765 | Laguna Beach | 970831 0930 | 970831 1100 | 40000 | None | 412 N. Coast Hwy | Laguna Beach | Orange | 92651 | 412 N. Coast Hwy. Bathrooms | 1 | Paper/Rags/roots | 8" Sewer Main Line was plugged up | Jetter machine used to open up the | Yes | Yes | Rockpile Beach | None | Rockpile Beach | Yes | No | Yes | 4 | Posting was done by Laguna Beach Lifeguards at the small coves
963237 | Fax 571-6972 | 12/01/97 15:40 | Parker | 6544160 | City of San Diego | 12/01/97 13:50 | 12/01/97 15:10 | 800 | 200 | 4258 Robbins St. | San Diego | SD | 92122 | 8" VC | 1 | Roots | Roots | Cleared roots on 8" vc main | Y | Y | Rose Canyon Creek/Interc 1/M.Bay |  |  | Y | N/A | N
975877 | Fax 571-6972 | 02/11/98 14:00 | J.McPherson | 6544160 | City of San Diego | 02/08/98 15:25 | 02/10/98 09:00 | 24955 | 0 | I-805 & Railroad Tracks @ Rose Canyon | San Diego | SD | 92122 | 15" VC | One | Surcharge | Line surcharge | Will investigate to find out problem & correct | Y | Y | Rose Canyon/Mission Bay | Pacific Ocean |  | Y | Y | N
945143 | Fax 571-6972 | 09/04/97 15:30 | Parker | 6544160 | City of San Diego | 09/04/97 12:48 | 09/04/97 14:10 | 82 | 0 | Cobb Dr. & Cobb Pl./canyon | San Diego | SD | 92117 | 8" vc main | 1 | Roots | Root blockage | Cleared stop on 8" vc main | y | y | Rose Creek | Mission Bay |  | y | n | n
977216 | Fax 571-6972 | 02/19/98 09:00 | R.Parker | 6544160 | City of San Diego | 02/17/98 08:00 | 02/18/98 08:00 | 36000 | 0 | I-805 & Railroad Tracks @ Rose Canyon | San Diego | SD | 92122 | 15" VC | Two | Surcharge | Infiltration inside 15" VC sewer main | Find points of infiltration and plug | Y | Y | Rose Creek & I-805 to Mission Bay | Mission Bay/Pacific Ocean |  | Y | Y | Y | Unknown
978353 | Fax 571-6972 | 02/24/98 12:00 | R.Parker | 6544160 | City of San Diego | 02/20/98 10:30 | 02/20/98 17:30 | 10500 | 0 | I-805 & Railroad Tracks @ Rose Canyon | San Diego | SD | 92122 | 15" VC | Three | Surcharge | Infiltration inside 15" VC sewer main | Find points of infiltration and flow to stop inflow | Y | Y | Rose Creek to Mission Bay | Mission Bay/Pacific Ocean |  | Y | Y | Y | Unknown
978363 | Fax 571-6972 | 02/24/98 14:00 | R.Parker | 6544160 | City of San Diego | 02/24/98 08:30 | 02/25/98 08:00 | 35250 | 0 | I-805 & Railroad Tracks @ Rose Canyon | San Diego | SD | 92122 | 15" VC | Four | Surcharge | Infiltration inside 15" VC | Find points of infiltration and repair to stop inflow | Y | Y | Rose Creek to Mission Bay | Mission Bay to Pacific Ocean |  | Y | Y | Y | Unknown
978005 | Greg Peters | 10-06-97 1030 | Ted Powell | 760-744-0460 | V.W.D. | 10-6-97 0810 | 10-6-97 0850 | 2000 | none | Discovery St. | San Marcos | S.D. | 92069 | S4C-Q15-M6 | 1 | grease | grease blockage in the 8" sewer line | we will include this on the trouble spot list | y | n | S.M. creek | Lake San Marcos | n/a | y | y | y | 5 | area posted as per health dept. no body contact in lake.
978005 | Greg Peters | 10-06-97 1030 | Ted Powell | 760-744-0460 | V.W.D. | 10-6-97 0810 | 10-6-97 0850 | 2000 | none | Discovery St. | San Marcos | S.D. | 92069 | S4C-Q15-M6 | 1 | grease | grease blockage in the 8" sewer line | we will include this on the trouble spot list | y | n | S.M. creek | Lake San Marcos | n/a | y | y | y | 5 | area posted as per health dept. no body contact in lake.
| SIRT (Attn: Gloria Fulton) | 1997-12-10 12:00 | James E. Smith | 714-448-4053 | Moulton Niguel Water | 1997-12-06 10:45 | 1997-12-06 11:00 | 3000 | 0 | Niguel Road, near Club House Drive | Laguna Niguel | OR | 92677 | Upper Salada Lift Station | 1 | Infiltration | This particular lift station has two force mains leading from the station. The rains on Saturday morning were very heavy, and we had only one force main in operation. Approx. 3,000 gallaons spilled while we were opening the 2nd force main. | Both force mains will remain open during the winter months. | Y | Y | Salt Creek | Pacific Ocean |  | Y | N | N | N/A
5 | GLORIA FULTON | 10/06/97 15:00 | MIKE DUNBAR | (714) 499-4555 | SOUTH COAST WATER DISTRICT | 10/06/97 14:00 | 10/06/97 15:30 | 500-1000 | 0 | LINKS GOLF COURSE | DANA POINT | OR | 92629 | FORCE MAIN | 0 | CONSTRUCTION | CONTRACTOR HIT AIR LINE HOOKED UP TO FORCE MAIN (BROKE FITTING) | 500-1000 GALLONS CONTAINED IN DITCH (SEEPING INTO GROUND) 50 GALLONS WENT INTO OCEAN | Y | Y | SALT CREEK | PACIFIC OCEAN | N/A | Y |  | Y | 3 DAYS | POSTED AT MOUTH OF CREEK
978003 | GLORIA FULTON FAX | 1997-09-05 | BRIAN WALTHER | 691-5027 | CITY OF CHULA VISTA | 1997-09-05 10:00 | 1997-09-05 11:00 | 1500 | 0 | SOUTH END OF HUNTE PARKWAY | CITY OF CHULA VISTA | SD | 91910 | ORANGE AVENUE FORCE MAIN CLEANOUT | 0 | FORCEMAIN CLEANOUT FAILED | FORCEMAIN CLEANOUT FAILED DUE TO IMPROPER INSTALLATION AT TIME OF CONSTRUCTION | CHECKED OTHER FORCEMAIN CLEANOUTS AND FOUND HALF TO HAVE BEEN IMPROPERLY CONSTRUCTED. ORIGINAL CONTRACTOR REPAIRED ALL OTHERS | Y | Y | SALT CREEK | NONE | UPPER REACH OF SALT CREEK | Y | N | N | 0 | THE AREA WHERE THE SEWEAGE FLOWED INTO SALT CREEK IS IN ACCESSESSIBLE. THERE WAS NO VISABLE FLOW IN THE CREEK AT THE TIME
978004 | GLORIA FULTON FAX | 1997-09-09 13:00 | EASTLAKE PROPERTY MANAGER | 421-0127 | CITY OF CHULA VISTA | 1997-09-09 13:00 | 1997-09-09 14:00 | 800 | 0 | HUNTE PARKWAY APPROXIMATELY 1000 FEETSOUTH OF OTAY LAKES ROAD | CITY OF CHULA VISTA | SD | 91910 | MANHOLE | 0 | CONTRACTOR HIT MANHOLE COVER | DIRT FELL INTO MANHOLE AFTER COVER HIT AND PLUGGED THE LINE | USED OUR VACCON AND REMOVED DIRT AND DEBRIS FROM THE MANHOLE AND MAIN. RARE OCCURRENCE, NO PREVENTATIVE MEASURES REQUIRED. | N | Y | SALT CREEK | N/A | UPPER REACH OF SALT CREEK | Y | N | N | 0 | THE AREA WHERE THE SEWEAGE FLOWED INTO SALT CREEK IS IN ACCESSESSIBLE. THERE WAS NO VISABLE FLOW IN THE CREEK AT THE TIME
| SIRT (FAX) | 1998-02-14 15:00 | Brad Bruington | 714-425-3514 | Moulton Niguel Water | 1998-02-14 10:50 | 1998-02-14 11:15 | 500 | 0 | Upper Salada Pump Station, Niguel Rd. | Laguna Niguel | OR | 92677 | Upper Salada Pump Station | 2 | Pump Station Failure | Heavy rains calling on all pumps. One pump check valve stuck open, returning flow to wet well. | Check valve cleaned and repaired | Y | N | Salt Creek | Pacific Ocean | N/A | Y | N/A | Y | TBD | O.C. Health Dept. posted beaches
973995 | Fax 571-6972 | 01/30/98 10:15 | L.Davis | 6544160 | City of San Diego | 01/30/98 07:15 | 01/30/98 07:30 | 60 | 0 | Mercury Ct. & Mercury Dr.** | San Diego | SD | 92111 | Manhole | One | Other | Pump station failure | Referred to an electrician for repairs | Y | Y | San Clemente Canyon | Rose Creek |  | Y | N | N
978151 | Fax 571-6972 | 02/10/98 14:45 | G.Himaka | 6544160 | City of San Diego | 02/07/98 15:00 | 02/09/98 14:15 | 950 | 0 | 5240 Convoy St. (Metro Biosolids Center) | San Diego | SD | 92123 | 4" blow-off valve | One | Construction | 4" blow-off valve left open | Closed valve/initiating clean up | Y | N | San Clemente Canyon | N/A | Canyon floor | Y | N | N
968516 | Fax 571-6972 | 12/29/97 12:30 | Parker | 6544160 | City of San Diego | 12/29/97 10:35 | 12/29/97 11:06 | 395 | 0 | 5972 Kantor St. | San Diego | SD | 92122 | 8" VC | 1 | Roots | Roots | Rodded 8" vc main to relieve stop | Y | Y | San Clemente Canyon/Highway 52 | Creek/Mission Bay/Pacific Ocean |  | Y | N/A | N
931991 | Fax 571-6972 | 07/03/97 12:40 | Harris,L | 6544160 | City of San Diego | 07/03/97 06:00 | 07/03/97 11:00 | 150 | 40 | 3762 Main St. | San Diego | SD | 92136 | 8" vc main | 1 | Other | Heavy sludge | Rodded main w/4" screw | y | n | San Diego Bay | Pacific Ocean | soaked into ground @ MH | y | n
932428 | Fax 571-6972 | 07/08/97 14:15 | Finch | 6544160 | City of San Diego | 07/07/97 16:29 | 07/08/97 12:00 | 585 | 45 | 3144 Quimby St. | San Diego | SD | 92106 | 6" cp main | 1 | Roots | Partial root stop | Rodded up/downstream w/root cutter | y | y | San Diego Bay | Pacific Ocean | San Diego Bay | y | n | n
932762 | Fax 571-6972 | 07/11/97 07:15 | Finch | 6544160 | City of San Diego | 07/08/97 21:31 | 07/09/97 09:09 | 115 | 0 | 30th St. & Olive St. | San Diego | SD | 92104 | 6" cp main | 1 | Roots | Root blockage | Machine rodded to relieve stop | y | n | San Diego Bay | Pacific Ocean | Soaked into ground | y | n
934500 | Fax 571-6972 | 07/21/97 14:30 | Payne | 6544160 | City of San Diego | 07/14/97 12:00 | 07/18/97 16:30 | 975 | 82 | I-163 North & Laurel Street (El Prado Bridge) | San Diego | SD | 92101 | 8" cp main | 1 | Grvty Mn Brk | Deterioration of cp main | Remv'd blockage from 8" vc main, recovered 106 gallons | y | y | San Diego Bay | Pacific Ocean |  | y | y | n
938376 | Fax 571-6972 | 08/02/97 20:35 | Branco | 6544160 | City of San Diego | 08/02/97 18:33 | 08/02/97 19:30 | 570 | 0 | 5450 University Av. | San Diego | SD | 92105 | 8" vc main | 1 | Roots | Root blockage | Flushed line to relieve stop | y | y | San Diego Bay | Pacific Ocean | storm drain | y | n | n
939326 | Fax 571-6972 | 08/11/97 12:00 | Senior | 6544160 | City of San Diego | 08/07/97 13:21 | 08/07/97 19:30 | 730 | 650 | I-163 North & Laurel Street (El Prado Bridge) | San Diego | SD | 92101 | 8" cp main | 2 | Grvty Mn Brk | Concrete main deterioration | Replace main from MH 17 to MH 16 | y | y | San Diego Bay | Pacific Ocean |  | y | n | n
939907 | Fax 571-6972 | 08/10/97 18:27 | Branco | 6544160 | City of San Diego | 08/10/97 15:55 | 08/10/97 17:20 | 85 | 0 | 6292 Lolly Ln. | San Diego | SD | 92114 | 8" pvc main | 1 | Grease | Grease blockage | Machine rodded 8" pvc main | y | y | San Diego Bay | Pacific Ocean |  | y | n | n
941783 | Fax 571-6972 | 08/21/97 04:25 | Whelan | 6544160 | City of San Diego | 08/20/97 17:58 | 08/20/97 19:35 | 388 | 0 | Palm Av. & 18th St. | San Diego | SD | 92154 | 8" vc main | 1 | Grease | Grease accumulation | Rodded 8" vc main | y | y | San Diego Bay | Pacific Ocean |  | y | n | n
946547 | Fax 571-6972 | 09/11/97 16:45 | Finch | 6544160 | City of San Diego | 08/11/97 12:00 | 09/10/97 16:00 | 217200 | 0 | 10th Av. & A St. | San Diego | SD | 92101 | 6" vc main | 1 | Grease | Grease blockage caused backup thru abandoned lateral | Flushed to relieve stop, plugged abandoned lateral | y | y | San Diego Bay | Pacific Ocean |  | y | y | n
946873 | Fax 571-6972 | 09/12/97 15:00 | Finch | 6544160 | City of San Diego | 09/12/97 09:09 | 09/12/97 11:20 | 615 | 0 | Canon St. & Evergreen St. | San Diego | SD | 92106 | 6" cp main | 1 | Grease | Grease and rocks | Cleared stop, ref. to FEWD | y | y | San Diego Bay | Pacific Ocean |  | y | n | n
947203 | Fax 571-6972 | 09/13/97 14:31 | Branco | 6544160 | City of San Diego | 09/13/97 08:45 | 09/13/97 10:40 | 230 | 0 | 2997 Marquette St. | San Diego | SD | 92110 | 8" vc main | 1 | Roots | Root blockage | Machine rodded 8" vc main, ref. for MC site | y | y | San Diego Bay | Pacific Ocean |  | y | n | n
946895 | Fax 571-6972 | 09/18/97 08:50 | Finch | 6544160 | City of San Diego | 09/12/97 10:12 | 09/17/97 17:58 | 3948 | 0 | 2431 Willow St./canyon | San Diego | SD | 92106 | 6" cp main | 1 | Roots | Heavy roots | Cleared stop, TV'd for integrity, ref. for Group Job repl. | n | n | San Diego Bay | Pacific Ocean |  | y | y | y | unk
948220 | Fax 571-6972 | 09/19/97 14:00 | Finch | 6544160 | City of San Diego | 09/19/97 09:51 | 09/19/97 11:05 | 2220 | 1110 | Canon St. & Evergreen St. | San Diego | SD | 92135 | 6" pvc main | 2 | Grease | Grease and roots | Cleared stop, ref to be TV'd for pipe integrity | y | y | San Diego Bay | Pacific Ocean |  | y | y | y | 3
978008 | FAX | 10-6-97, 1402 | D. WOODWARD | 619-522-7380 | CITY OF CORONADO | 10-6-97, 1110 | 10-6-97, 1125 | 350 GAL | 80 GAL | 200 BLOCK A/B ALLEY | CORONADO | SD | 92118 | SEWER LINE | 0 | ROOTS | ROOTS AND DEBRIS IN SEWER LINE | CLEARED WITH VACTOR | N | Y | SAN DIEGO BAY | PACIFIC OCEAN | SEWER LINE | Y | N | Y | 3
951096 | Fax 571-6972 | 10/02/97 04:10 | McPherson | 6544160 | City of San Diego | 09/30/97 13:12 | 10/02/97 20:00 | 25200 | 0 | Bessemer St. & Scott St. | San Diego | SD |  | 18" VC Sewer Main | 1 | Grvty Mn Break | Hole in 18" VC Sewer Pipe | Repaired 18" vc main | Y | N | San Diego Bay | Pacific Ocean |  | Y | Y | Y
955539 | Fax 571-6972 | 10/30/97 05:15 | Whelan | 6544160 | City of San Diego | 10/27/97 09:16 | 10/29/96 16:30 | 3315 | 0 | 3606 Pennsylvania Av. | San Diego | SD | 92103 | 8" VC | 1 | Roots | Roots | Removed stop, ref. for re-evaluation of cleaning freq. | N | N | San Diego Bay | Pacific Ocean | Ground in canyon | Y | Y | N
981292 | Fax 571-6972 | 03/12/98 08:40 | L.Finch | 6544160 | City of San Diego | 03/11/98 09:16 | 03/11/98 15:00 | 516 | 450 | 4279 Pacific Hy./RR tracks east | San Diego | SD | 92110 | 8" VC | One | Grease | Grease | Add to 36 month cleaning schedule | N | N | San Diego Bay | Pacific Ocean | Soaked into ground | Y | N | N
933396 | Fax 571-6972 | 07/11/97 19:25 | Branco | 6544160 | City of San Diego | 07/11/97 11:54 | 07/11/97 17:30 | 6720 | 0 | 5980 Mission Center Rd. | San Diego | SD | 92123 | 8" vc main | 1 | Debris | Broken screws/hand rod | Removed broken hand-rod screw, debris from 8" vc main | y | y | San Diego River | Pacific Ocean |  | y | y | y | unk
934967 | Fax 571-6972 | 07/19/97 10:58 | Branco | 6544160 | City of San Diego | 07/19/97 08:55 | 07/19/97 09:55 | 60 | 0 | 1502 Minden Dr. | San Diego | SD | 92111 | 8" vc main | 1 | Roots | Root blockage | Machine rodded 8" vc main | y | n | San Diego River | Pacific Ocean |  | y | n | n
936081 | Fax 571-6972 | 07/24/97 00:00 | Whelan | 6544160 | City of San Diego | 07/23/97 19:36 | 07/23/97 20:50 | 296 | 36 | 4671 Terrace Dr. | San Diego | SD | 92116 | 8" pvc main | 2 | Grease | Grease blockage | Rodded 8" pvc main, vacuumed 36 gallons of spill | y | y | San Diego River | Pacific Ocean |  | y | n | n
936661 | Fax 571-6972 | 07/27/97 12:55 | Branco | 6544160 | City of San Diego | 07/27/97 09:49 | 07/27/97 10:39 | 500 | 0 | 10035 Rue Chantemar | San Diego | SD | 92131 | 8" pvc main | 1 | Grease | Grease blockage | Machine rodded 8" pvc main | y | y | San Diego River | Pacific Ocean |  | y | n | n
937620 | Fax 571-6972 | 07/31/97 02:05 | Whelan | 6544160 | City of San Diego | 07/30/97 22:25 | 07/30/97 23:02 | 925 | 0 | 4600 Collwood Ln. | San Diego | SD | 92115 | 12" vc main | 1 | Roots | Root blockage | Rodded 12" vc main to relieve stop | y | y | San Diego River | Pacific Ocean |  | y | y | n
987880 | Fax 571-6972 | 4/16/98 14:00 | L. Finch | 654-4160 | City of San Diego | 4/16/98 09:30 | 4/16/98 10:15 | 22.5 | 0 | 4282 Whittier St. | San Diego | SD | 92107 | 8" VC | One | Grease | Grease stop on 8" VC main | Vacuumed to remove grease, put on PM schedule | Y | N | San Diego River | Pacific Ocean | Dried in street | Y | N | N | N/A | N/A
982004 | Fax 571-6972 | 03/15/98 15:00 | D.Branco | 6544160 | City of San Diego | 03/14/98 22:55 | 03/15/98 12:30 | 8150 | 0 | 7970 Sevan Ct./canyon | San Diego | SD | 92123 | 8" VC | Two | Grvty Mn Brk | Rocks, roots and debris in main | Flushed and rodded main/refer to construction and TV section | Y | Y | San Diego River/Pacific Ocean |  |  | Y | Y | Y | Unknown
978007 | QUARTERLY REPORT | 11-17-97;16:02 | RICHARD ANDREWS | 6197553294 | CITY OF DEL MAR | 10-27-97:13:00 | 11-16-97; 13:00 | 6400 | 0 | 2900 CAMINO DEL MAR | DEL MAR | SD | 92014 | PUMP DISCHARGE | 0 | CONSTRUCTION |  | TOLD CONTRACTOR TO POTHOLE UTILITIES BEFORE BORING | Y | Y | SAN DIEGUITO RIVER | PACIFIC |  | Y | Y | N | N/A | NA
978001 | Kristin Schwall | 1998-02-09 11:00 | Gary Masters | (760)753-6203 | San Elijo Joint Powers Authority | 1998-02-06 16:00 | 1998-02-06 16:05 | <250 gallons | 0 gallons | 2695 Manchester Avenue | Cardiff | SD | 92007 | Plant Headworks | 0 | Infiltration | Heavy rain caused infiltration at the Olivenhain Pump Station and the Solana Beach Pump Station. The momentary high peak flow caused the spill an the plant's headworks. | Infiltration at both pump stations will be investigated. | Y | Y | San Elijo Lagoon | Pacific Ocean |  | Y | NA | N | NA
| SIRT (Attn: Gloria Fulton) | 1997-12-10 16:45 | James E. Smith | 714-448-4053 | Moulton Niguel Water | 1997-12-07 01:00 | 1997-12-07 06:00 | 248000 | 0 | One mile south of Del Obispo & Camino Capistrano | San Juan Capistrano | OR | 92713 | 20" effluent line | 1 | Line break | Contractor dropped rip rap on our outfall line during emergency repairs to the San Juan Creek channel. The contractor was doing the emergency work for the County of Orange. The effluent was secondary treated effluent, not chlorinated. | The plant and the valves were shut down prior to breaking the effluent line, however, line is a gravaity line with the high point near Oso Road. The portion of the line from Oso Road to the break drains by gravity. | Y | N | San Juan Creek | Pacific Ocean | N/A | Y | Y | Y | N/A
| SIRT (FAX) | 1998-02-26 10:00 | Brad Bruington | 714-425-3514 | Moulton Niguel Water | 1998-02-25 20:30 | 1998-02-25 23:30 | 3500 | 0 | 400 yds. south of Del Obispo (San Juan River) | San Juan Capistrano | OR | 92675 | 21" secondary effluent outfall line | 1 | Line break | Contractor placing rip rap on San Juan Creek punctured 21" secondary effluent outfall line. | Crew repaired punctured area. | Y | N | San Juan Creek | Pacific Ocean | N/A | Y | N | Y | TBD | O.C. Health Dept. posted beaches.
978002 | ELECTRONIC QTLY RPT |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 07/13/97 | 15:30 | 150 | 0 | 205 ABeyta, Sierra Mesa | SD | 920555008 | 2Y152 | 1 | BLOCKAGE | Chunks of grease and soap caused blockage which resulted in overflow from manhole | cleared with jetter. | Y | N | Pilgrim Creek | San Luis Rey River |  | Y | NA | N | 0 |  | SPILL FLOWED FROM MANHOLE 30' TO CANYON THEN 10' INTO CANYON AND PERCOLATED. NOT IN AN AREA OF EXPECTED PUBLIC CONTACT
978011 | ELECTRONIC QTLY RPT |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 09/04/97 | 11:30 | 800 | 0 | Bldg 1795 | SD | 920555008 | Z-Y-128 Officers Club | 1 | ROOTS | roots caused a blockage which caused sewage to overflow from manhole | used cutting head to cut out roots | Y | N | Pilgrim Creek | San Luis Rey River |  | Y | NA | N | 0 |  | SPILL FLOWED APPROX. 880' FROM MANHOLE INTO DITCH AND PERCOLATED INTO THE GROUND. SLOW LEAK WAS NOT CALLED IN TO MAINTENANCE UNTIL THE DAY AFTER IT STARTED.
978002 | Called and Faxed | 7/8/97 730 | J. Vaught/L. Bishop | 741-4668 | City of Escondido | 7/8/97 730 | 7/8/97 1015 | 22600 | 8600 | 1750 W. El Norte Pkwy. | Escondido | SD | 92026 | 8" Forcemain | 2 | Forcemain break | 10' cracked 8" pipe. | Repair was made with a higher rated pipe. | Y | Y | San Marcos Creek | Lake San Marcos | Pacific Ocean | Y | Y | Y | 7 | Samples were taken.
978011 | N/A | 9/18/1997 1430 | Mike Schultz | 738-4347 | City of Escondido | 9/18/97 845 | 9/18/97 930 | 90 | 0 | W. El Norte Pkwy. at Rees Rd. | Escondido | SD | 92026 | Airvac. Sewer Atlas PG. 264 | 2 | Airvac Malfunction | Air release valve malfunctioned allowing wastewater to trickle. | The valve was removed and clean, inspected, then reinstalled. | Y | Y | San Marcos Creek | Lake San Marcos | N/A | Y | N | N | N/A
98-1 |  | 1998-06-06 08:30 | JEFF STECHER | 760-753-0155 | LEUCADIA | 1998-06-06 08:40 | 1998-06-06 09:10 | 750 | 750 | 2804 LA COSTA AVE | CARLSBAD | SD | 92009 | MANHOLE 10-1820 | 3 | ROOTS | 8" GRAVITY SEWER LINE, ROOTS PROTRUDED THROUGH JOINT | ROOT SAW, TV | N | Y | SAN MARCOS CREEK | NA | SAN MARCOS CREEK | Y | N | N | NA | SEWAGE MAINTAINED WITHIN GOLF COURSE
978025 | ELECTRONIC QTLY RPT |  | SSgt Duke | 6197259762 | MCB, CAMP PENDLETON | 03/11/98, 1930 | 03/11/98, 2230 | 150 | 0 | 702 Erskine San Onofre I Housing | CAMP PENDLETON | SD | 920555008 | Man Hole HY-184 | 1 | GREASE | Animal fat build up, broom handle and sticks FOUND IN MANHOLE | Put GREASE cutter head on jetter and PM'D lines on Erskine to Torrey. REMOVED Animal fat CLUMPS AND sticks FOR DISPOSAL. | Y | Y | San Mateo Creek | Pacific Ocean |  | Y | NA | N | 0 | NO DISINFECTION OF STREET BUT HOSED DOWN AREA OF CONTACT. SPILL Did not ACTUALLY reach surface waterS. Went 424 DOWN STREET GUTTER,500' down storm drain, 50' DOWN EARTHEN DITCH BY 61 AREA AG FIELD AND Percolated into SOIL.
978001 | VOICE MAIL | 21:00 | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 07/06/97 | 15:40 | 25000 | 19200 | Carnes Road | SD | 920555008 | MANHOLE 13Y28 | 2 | BLOCKAGE | solids and debris in line caused overflow from manhole. | cleared sewer line with jet-TRUCK. | Y | Y | STP #13 OXIDATION/PERC. POND | Santa Margarita River |  | Y | Y | Y | 3 |  | SPILL TRAVELED 1/2 MILE FROM MANHOLE-ACROSS ROAD TO CANYON ALONG CARNES RD UNDER ASH RD TO VANDERGRIFT INTO CULVERT TO STP #13 TWIN LAKES TREATED EFFLUENT POND TO PERCOLATE ADJACENT SANTA MARGARITA RIVER.
978015 | VOICE MAIL | 10/04/97,1400 | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 10/04/97,0840 | 10/04/97,1230 | 9000 | 000 | 509 Parker (Stuart Mesa Housing) | CAMP PENDLETON | SD | 920555008 | unknown manhole | 1 | PUMP STATION FAILURE | BREAKER ON SEWAGE LIFT STATION PUMP TRIPPED. THIS CAUSED THE PUMP TO FAIL AND SEWAGE TO OVERFLOW FROM MANHOLE | REPAIRED ELECTRICAL SYSTEM AT LIFT STATION. WASTEWATER SHOP IS MONITORING LIFT STATION TO AVERT POSSIBLE SPILL. TWO WARNING SIGNS POSTED ALONG PARKER STREET. | Y | Y | SANTA MARGARITA RIVER | PACIFIC OCEAN |  | Y | Y | Y | 3 | SPILL FLOWED 60' FROM MANHOLE ACROSS STREET DOWN GUTTER INTO STORM DRAIN THEN 600' TO CANYON AND PERCOLATED INTO THE GROUND. POTENTIAL PUBLIC CONTACT IN STUART MESA HOUSING AREA.
978016 | ELECTRONIC QTLY RPT |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 10/07/97,1420 | 10/07/97,1500 | 25 | 3 | Wire Mountain elementary school | CAMP PENDLETON | SD | 920555008 | c/o | 1 | BLOCKAGE | blockage in lateral caused cleanout to backup | adviced school faculty to ensure students only put toilet paper into toilets. | Y | N | SANTA MARGARITA RIVER | PACIFIC OCEAN |  | N | NA | N | 0 | SPILL OCCURED IN FACULTY PARKING LOT. NOT IN PLAY AREA.
978017 | DAT QUACH VOICEMAIL | 11/18/97,1345 | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 11/18/97,0800 | 11/18/97,1545 | 10,400 | 7,000 | PIPE NEXT TO Twin Lakes. ALSO LIFT ST. 31220 | CAMP PENDLETON | SD | 920555008 | PIPE PRIOR TO STP 13. ALSO M/H AT LIFT ST. 31220. | 1 | CONSTRUCTION | Contractor backhoe punched hole in pipe. | Prevented additional spillage by turnING off WATER SUPPLY AND lift stations 31220 and 31227. PUMPER TRUCKS PUMPED OUT WET WELL AT LIFT STATION 31227. COLIFORM SAMPLING TAKEN AT S.M. RIVER AND BEACH | Y | N | Santa Margarita River | Pacific Ocean |  | Y | Y | N | 0 | 9,500 gallons spilled from hole in pipe, of which 7,000 gallons was recovered. THIS SPILL FLOWED INTO TWIN LAKES (OUTFALL TO SAN. MARG. RIVER). 900 gallons spilled from manhole at lift station 31220 AND FLOWED INTO NEWTON CANYON POND (NO
978019 | PETERS (VOICE MAIL) | 02/13/98, 1420 | Karl Vogel | 6197259762 | MCB, CAMP PENDLETON | 02/11/98, 1800 | 02/11/98, 1915 | 2000 | 0 | 2250 Lift Station | CAMP PENDLETON | SD | 920555008 | 3Y174 | 1 | PUMP STATION FAILURE | Booster pumps not operational, excess flow from bldg 2252 to wet well. | Pumper utilized while booster pumps are being repaired. Cause of excess flow from bldg 2252 repaired. | Y | Y | SANTA MARGARITA RIVER | PACIFIC OCEAN |  | Y | Y | N | 0
978020 | PETERS, VOICE MAIL | 02/13/98, 1505 | KARL VOGEL | 6197259762 | MCB, CAMP PENDLETON | 02/13/98, 1000 | 02/13/98, 1300 | 1800 | 0 | Bldg 140210 | CAMP PENDLETON | SD | 920555008 | 1 Y 14 | 1 | BLOCKAGE | Manhole cover found in adjacent manhole in combination with heavy grease and wood causing blockage. This manhole did not overflow. | Remove cover from manhole and repair /reset ring with cover. | Y | Y | Santa Margarita River | Pacific Ocean |  | Y | Y | N | 0 | Only paper solids had to be disposed of
978021 | GREG PETERS | 02/13/98, 1510 | KARL VOGEL | 6197259762 | MCB, CAMP PENDLETON | 02/13/98, 1130 | 02/14/98, 1730 | 22,800 | 7,800 | South of Stuart Mesa Bridge | CAMP PENDLETON | SD | 920555008 | 6" Force Sewer Main | 1 | CONSTRUCTION | Contractor nicked 6" Force Sewer Main when paving the road. Additional overflow to adjacent wetlands occured when repairs effected. | When leak began an Earthen impound was dug to capture the flow while broken sewer line was repaired. | Y | N | Santa Margarita River | Pacific Ocean |  | Y | Y | Y | 8 | No public access to wetlands. Signs posted at Del Mar Beach (3/4 of a mile south of San. Mar. River) will remain up until sampling results confirm acceptable coliform levels.
978027 |  |  | DENNIS PINIGIS | 6197259761 | MCB, CAMP PENDLETON | 4/15/98,8:53:00 PM | 04/15/98, 9:15:00 P.M. | 300 | 0 | ASH ROAD | CAMP PENDLETON | SD | 920555008 | across from wire mountain PX | 1 | BLOCKAGE | GREASE, SOAP AND TRASH BUILDUP CAUSED BLOCKAGE | JETTED LINE TO CLEAR BLOCKAGE | Y | Y | SANTA MARGARITA RIVER | PACIFIC OCEAN |  | Y | NA | N | 0 | SPILL FLOWED FROM MANHOLE 25 FT INTO STORM DRAIN THEN 15 FT INTO DITCH AND PERCOLATED INTO THE GROUND. NEAR A BALLPARK BUT NO PUBLIC CONTACT EXPECTED.
975844 | Fax 571-6972 | 02/07/98 15:38 | D.Branco | 6544160 | City of San Diego | 02/07/98 13:28 | 02/07/98 14:35 | 34 | 0 | 3912 Lomaland Dr. | San Diego | SD | 92106 | 8" VC | One | Roots | Roots | Machine rod/refer to area supervisor for scheduled maintenance | N | N | Seepage around manhole |  | Dried up around manhole | Y | N | N
968918 | Fax 571-6972 | 12/31/97 13:00 | Richardson | 6544160 | City of San Diego | 12/31/97 10:10 | 12/31/97 11:00 | 100 | 100 | 3450 College Av. | San Diego | SD | 92115 | 8" VC | 1 | Grease | Grease | Rodded 8" vc main, recovered total volume of spill | N | N | Service Tunnel under the mall |  | Sewer recovered | Y | N/A | N
989001 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 07-08-97 | 07-08-97 |  | 0 | 2121 Monument Road | San Diego | SD | 92154 | Smuggler Gulch | 1 | other | overload of collection system |  | Y | N | Smuggler Gulch | None |  | N | N | N
989002 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-12-97 | 08-12-97 |  | 0 | 2121 Monument Road | San Diego | SD | 92154 | Smuggler Gulch | 2 | other | overload of collection system |  | Y | N | Smuggler Gulch | None |  | N | N | N
989003 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-12-97 | 09-12-97 |  | 0 | 2121 Monument Road | San Diego | SD | 92154 | Smuggler Gulch | 3 | other | overload of collection system |  | Y | N | Smuggler Gulch | None |  | N | N | N
989004 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-25-97 | 09-25-97 |  | 0 | 2121 Monument Road | San Diego | SD | 92154 | Smuggler Gulch | 4 | other | overload of collection system |  | Y | N | Smuggler Gulch | None |  | N | N | N
989005 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-26-97 | 09-26-97 |  | 0 | 2121 Monument Road | San Diego | SD | 92154 | Smuggler Gulch | 5 | other | overload of collection system |  | Y | N | Smuggler Gulch | None |  | N | N | N
968185 | Fax 571-6972 | 12/25/97 02:57 | Whelan | 6544160 | City of San Diego | 12/24/97 14:16 | 12/24/97 16:24 | 128 | 0 | 7068 Everglades Av. | San Diego | SD | 92119 | 8" VC sewer main | 1 | Roots | Roots | Rodded main to relieve stop | N | N | Soaked in ground in backyard |  | Soaked into ground in backyard | Y | N | N
967514 | Fax 571-6972 | 12/29/97 14:00 | McPherson | 6544160 | City of San Diego | 12/19/97 15:16 | 12/21/97 14:00 | 11662 | 3000 | 4409 New Hampshire St. | San Diego | SD |  | 6" CP | 1 | Grvty Mn Brk | Line break | Made temporary main repairs, ref. for contractor for perm. rprs. | N | N | Soaked into canyon | Hoffman Canyon |  | Y | Y | N
968824 | Fax 571-6972 | 12/31/97 12:00 | Whelan | 6544160 | City of San Diego | 12/30/97 17:00 | 12/31/97 09:15 | 975 | 0 | Cedar St. & Gregory St./canyon | San Diego | SD | 92102 | 6" CP easement main | 1 | Roots | Roots | Hand rodded, ref for TV to determine extent of root blockage | N | N | Soaked into canyon |  |  | Y | N | N
971178 | Fax 571-6972 | 01/15/98 01:02 | M.Whelan | 6544160 | City of San Diego | 01/14/98 16:21 | 01/14/98 17:38 | 77 | 34 | 5203 S. Thorn St. | San Diego | SD | 92105 | 6" VC | One | Roots | Roots | Rodded main/checked easement manhole; referred to be strapped | Y | Y | Soaked into canyon |  |  | Y | N | N
989105 | Fax 571-6972 | 4/26/98 11:32 | D. Branco | 654-4160 | City of San Diego | 4/26/98 10:43 | 4/26/98 14:15 | 106 | 0 | 2504 34th St. | San Diego | SD | 92104 | 6" VC | One | Roots | Roots caused blockage | Flushed 6" vc main to relieve stop | Y | N | Soaked into canyon | Chollas Creek/SD Bay | N/A | Y | N | N | N/A | N/A
954415 | Fax 571-6972 | 10/18/97 13:55 | Branco | 6544160 | City of San Diego | 10/18/97 10:28 | 10/18/97 11:30 | 620 | 0 | 3705 Albatross St./canyon | San Diego | SD | 92103 | 6" CP | 1 | Roots | Roots | Machine rodded to relieve stop | Y | N | Soaked into Canyon Floor | SD Bay/Pacific Ocean |  | Y | N/A | N
983574 | Fax 571-6972 | 03/20/98 21:53 | D.Branco | 6544160 | City of San Diego | 03/20/98 16:11 | 03/20/98 20:41 | 1350 | 0 | 3300 Euclid Av. | San Diego | SD | 92105 | 8" VC | One | Roots | Roots | Hand rodded main/refer to area supervisor for PM maintenance | Y | N | Soaked into canyon floor | San Diego Bay/Pacific Ocean |  | Y | Y | N
968808 | Fax 571-6972 | 12/31/97 06:15 | Whelan | 6544160 | City of San Diego | 12/30/97 16:18 | 12/30/97 16:18 | 190 | 0 | 2255 Camino del Rio So. | San Diego | SD | 92108 | 8" VC sewer main | 1 | Roots | Roots | Rodded 8" vc main to relieve stop | Y | Y | Soaked into ground |  |  | Y | N | N
992092 | Fax 571-6972 | 5/18/98 15:13 | L. Moore | 654-4160 | City of San Diego | 5/17/98 17:49 | 5/18/98 00:45 | 100 | 0 | 1022 Skylark Dr. | San Diego | SD | 92037 | 8" VC | One | Other | Unknown | Unable to locate manhole on 30' deep main; ref to contractor for rprs | Y | Y | Soaked into ground | Canyon storm channel | N/A | Y | N | N | N/A | N/A
974710 | Fax 571-6972 | 02/02/98 22:34 | J.Wilder | 6544160 | City of San Diego | 02/02/98 15:20 | 02/02/98 16:55 | 380 | 0 | 5884 Madra Av. | San Diego | SD | 92120 | 8" VC | One | Roots | Roots | Rodded main to clean section | N | N | Soaked into hillside | N/A | Soaked into hillside | Y | N | N
990040 | Fax 571-6972 | 5/02/98 14:05 | D. Branco | 654-4160 | City of San Diego | 5/02/98 08:55 | 5/02/98 09:47 | 520 | 400 | 4559 Hawley Bl. | San Diego | SD | 92116 | 8" VC main | One | Grease | Stoppage caused by grease | Machine rodded to relieve stop, vacuumed pooled spill, ref. for PM | Y | N | Stopped in gutter | SD River/Pacific Ocean | N/A | Y | N | N | N/A | N/A
978001 | fax | 1997-09-11 13:00 | Denis Pollak | 7607530155 | Leucadia County Water District | 9-11-97 700 | 9-11-97 830 | 3600 | 2500 | 50 yards south of 6200 Avenida Encinas | Carlsbad | SD | 92009 | 16" DIP failsafe pipeline | 0 | leak in DIP pipeline | corrosion of pip material | Spot repair of pipline, inspection of condition and extent of corrosion to pipe material | y | y | Storm channel | marsh area | Marsh area | y | n | n | n/a | Spill was of highly treated secondary effluent not raw sewage.
944658 | Fax 571-6972 | 09/01/97 14:00 | Kelly | 6544160 | City of San Diego | 09/01/97 08:26 | 09/01/97 10:42 | 680 | 0 | Romero Dr. & Romero Ct. | San Diego | SD | 92037 | 8" vc main | 3 | Roots | Root blockage | Rodded 8" vc main | y | n | storm channel | Pacific Ocean |  | y | n | n
963844 | Fax 571-6972 | 12/05/97 13:00 | Richardson | 6544160 | City of San Diego | 12/03/97 11:35 | 12/03/97 12:50 | 3750 | 3000 | 2181 Avnda. del Mexico | San Diego | SD | 91911 | 12" VC | 1 | Grease | Grease | Flushed 12" vc main to relieve stop | Y | N | Storm channel | San Diego Bay | Storm channel | Y | Y | Y | 3
967646 | Fax 571-6972 | 01/05/98 09:30 | Richardson | 6544160 | City of San Diego | 12/22/97 08:10 | 12/22/97 09:12 | 310 | 0 | 5474 Reservoir Dr. | San Diego | SD | 92120 | 10" VC | 1 | Roots | Roots | Rodded main to relieve stop | Y | N | Storm channel | Alvarado Creek | Pacific Ocean |  | N/A | N
994368 | Fax 571-6972 | 5/29/98 14:00 | L. Finch | 654-4160 | City of San Diego | 5/29/98 10:20 | 5/29/98 11:10 | 1000 | 0 | 2728 Treat St. | San Diego | SD | 92102 | 8" VC | One | Construction | Construction Co failed to trap construction debris | Cleared debris, advised contractor to use proper trapping techniques | Y | Y | Storm channel | San Diego Bay/Pacific Ocean | Dried in dirt storm channel | Y | Y | N | N/A | N/A
978002 | quarterly report | n/a | Orv Salisbury | 760-744-0460 | V.W.D. | 7-16-97 2000 | 7-16-97 2200 | 1800 | 1000 | Liberty St. | San Marcos | S.D. | 92069 | sewer manhole | 1 | grease | heavy grease from low income apartments | we will include this site on our trouble spot list | y | y | Storm drain | S.M. Creek | open channel | y | n | y | 4 | spill was contained and recovered
978002 | quarterly report | n/a | Orv Salisbury | 760-744-0460 | V.W.D. | 7-16-97 2000 | 7-16-97 2200 | 1800 | 1000 | Liberty St. | San Marcos | S.D. | 92069 | sewer manhole | 1 | grease | heavy grease from low income apartments | we will include this site on our trouble spot list | y | y | Storm drain | S.M. Creek | open channel | y | n | y | 4 | spill was contained and recovered
978001 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 07/06/97 1730 | 07/06/97 1830 | 150 | 0 | 4200 Via Rancho Road & Cassanna Way | Oceanside | SD | 92056 | Manhole | 0 | Debris | Eight inch "screw plug" stuck in mouth of channel. | Removed it. | N | Y | Storm Drain | N/A | Dried up quickly. | N | N/A | N | N/A
978002 |  |  | Ira Black | 7609667868 | Water Utilities Dept. City of Oceanside | 07/14/97 0945 | 07/14/97 1030 | 500 | 0 | 2861 Turnbull Street Easement | Oceanside | SD | 92054 | Manhole | 0 | Vandalism. | Fence poles, sand, boards, and rocks. | Put a "lock down" lid on the manhole and check it once a week. | N | Y | Storm Drain | N/A | `Storm Drain | Y | N/A | Y | 2 | Did not go to surface water, but we'll sign anyway.
978005 | Tape Recorder | 07/29/97 2353 | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 07/29/97 2000 | 07/29/97 2240 | 15000 | 0 | 5565 Old Ranch Road | Oceanside | SD | 92054 | Manhole | 0 | Debris. | Grease and Rags and Construction Wood. | Put a "lock down" lid on the manhole and check it once a week. | Y | Y | Storm Drain | Storm Drain Channel | Storm Drain Channel | Y | Y | Y | 5 | "Spill" did not reach Guajome Lake, as previously reported. All soaked into the sides and bottom of channel.
978007 |  |  | Ira Black | 7609667868 | Water Utilities Dept. City of Oceanside | 07/31/97 1250 | 07/31/97 1300 | 50 | 0 | Lynn Court & Henie Hills | Oceanside | SD | 92054 | Manhole | 2 | Roots. | Roots in the City Main. | "Rod " manhole every 30 days. | N | Y | Storm Drain | N/A | Soaked into soil. | N | N/A | N | N/A
978013 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 08/26/97 1232 | 08/26/97 1250 | 25 | 0 | 1400 Pacific Street | Oceanside | SD | 92054 | Manhole | 0 | Grease. | Grease plugged City Main. | Dropped 100 lbs. Of Chlorine in sewer main to eat grease. | Y | Y | Storm Drain | Loma Alta Slough | N/A | N | N/A | N | N/A
978016 |  |  | Jeremy Kemp | 7609667868 | Water Utilities Dept. City of Oceanside | 09/14/97 2020 | Ongoing | 5-75 GPM | 0 | 515 Greenbrier | Oceanside | SD | 92054 | Private Cleanouts | 0 | Blockage. | Unknown. Private plumbing problem inside building. | Could not contact manager of complex, until 15/0930. | Y | Y | Storm Drain | Loma Alta Slough | Pacific Ocean | Y | N/A | N | N/A | "Cartage Apts." owned by Clifton Warren Investments of Hermosa Beach, CA. (310)372-5774.
978017 |  |  | Mike Teem | 7609667868 | Water Utilities Dept. City of Oceanside | 09/23/97 ?? | Ongoing | 1-2 GPM | 0 | 814 Missouri | Oceanside | SD | 92054 | Private Cleanouts | 1 | Blockage. | Unknown. Private plumbing problem inside building. | Notified Fran Banks (Chamberlain Prop. Manage.) @ 24/1100Sep97. | N | N | Storm Drain | N/A | Soaked into soil. | N | N/A | N | N/A | Peppertree Apts. Owned by Jdames F. Weber of 580 Beech Street, Carlsbad.
953700 | Fax 571-6972 | 10/16/97 15:15 | Finch | 6544160 | City of San Diego | 10/15/97 08:20 | 10/16/97 10:50 | 31800 | 20300 | 3617 Curlew St. | San Diego | SD | 92103 | 6" CP | 1 | Roots | Root Ball | Rodded/cleaned main, ref. for TV | Y | Y | Storm Drain | San Diego Bay |  | Y | Y | Y | Unknown
959555 | Fax 571-6972 | 11/16/97 | McPherson | 6544160 | City of San Diego | 11/16/97 21:31 | 11/16/97 23:45 | 4690 | 0 | Renaissance Av. & Towne Centre Dr. | San Diego | SD |  | 8" VC | 1 | Grease | Grease | Flushed 8" vc main | Y | Y | Storm drain |  | Rose Canyon/Dried in dirt | Y | Y | N
958286 | Fax 571-6972 | 11/09/97 21:24 | Branco | 6544160 | City of San Diego | 11/09/97 14:57 | 11/09/97 18:26 | 4180 | 500 | Carmel Valley Rd. w. of I-5/on hillside | San Diego | SD | 92014 | 8" VC | 1 | Roots | Roots | Machine rodded to relieve stop | Y | Y | Storm drain | Soledad Creek/Pacific Ocean |  | Y | Y | N
957073 | Fax 571-6972 | 11/03/97 11:46 | Kelly | 6544160 | City of San Diego | 11/02/97 22:12 | 11/02/97 23:20 | 2720 | 0 | 4356 30th St./alley | San Diego | SD | 92116 | 10" VC | 1 | Grease | Grease | Flushed 10" vc main to relieve stop | N | Y | Storm drain | San Diego Bay | Soaked in canyon | Y | Y | N
951690 | Fax 571-6972 | 10/05/97 16:18 | Branco | 6544160 | City of San Diego | 10/05/97 13:38 | 10/05/97 14:03 | 2500 | 0 | I-163 south of Robinson Av. exit | San Diego | SD | 92103 | 12" VC | 1 | Roots | Roots | Flushed to relieve root stop | Y | Y | Storm Drain | Drainage Channel |  | Y | Y | N
953596 | Fax 571-6972 | 10/14/97 23:55 | Whelan | 6544160 | City of San Diego | 10/14/97 16:09 | 10/14/97 18:16 | 1905 | 1200 | 1333 Hotel Circle S. | San Diego | SD | 92108 | 12" VC Main | 1 | Roots | Roots | Vacuumed overflow, hand rodded main to relieve stop | Y | Y | Storm Drain |  | Soaked into ground | Y | Y | N
965108 | Fax 571-6972 | 12/09/97 11:44 | Burton | 6544160 | City of San Diego | 12/09/97 07:07 | 12/09/97 08:07 | 1500 | 0 | 49th St. & Logan Av. | San Diego | SD | 92114 | 10" VC | 1 | Grease | Grease | Machine rodded 10" vc main | Y | Y | Storm drain | San Diego Bay | Dried up in canyon | Y | Y | N
963088 | Fax 571-6972 | 11/30/97 11:57 | Branco | 6544160 | City of San Diego | 11/29/97 09:37 | 11/30/97 10:25 | 1488 | 0 | 4311 Hortensia St. | San Diego | SD | 92103 | 6" CP | 1 | Roots | Roots | Machine rodded to clear stop; ref for possible MC site | Y | Y | Storm drain | San Diego Bay/Pacific Ocean |  | Y | Y | N
960214 | Fax 571-6972 | 11/09/97 00:02 | Whelan | 6544160 | City of San Diego | 11/08/97 15:35 | 11/08/97 17:55 | 1400 | 1000 | 347 S. Royal Oak Dr. | San Diego | SD | 92114 | 8" VC | 1 | Grease | Grease | Rodded main to relieve stop | Y | Y | Storm drain | Storm drain | Storm drain | Y | N | N
960881 | Fax 571-6972 | 11/20/97 11:40 | Finch | 6544160 | City of San Diego | 11/20/97 06:25 | 11/20/97 09:05 | 1050 | 0 | 3174 Falcon St. | San Diego | SD | 92101 | 6" CP | 1 | Roots | Roots | Removed root stoppage, ref for televising | Y | Y | Storm drain | San Diego Bay |  | Y | Y | Y | 1
967474 | Fax 571-6972 | 12/20/97 17:29 | Branco | 6544160 | City of San Diego | 12/19/97 11:32 | 12/20/97 10:30 | 689 | 0 | 6394 Elmhurst Dr. | San Diego | SD | 92120 | 8" VC | 1 | Roots | Roots | Hand rodded easement main to remove roots | Y | Y | Storm drain | San Diego River/Pacific Ocean |  | Y | N/A | N
958251 | Fax 571-6972 | 11/08/97 16:27 | Branco | 6544160 | City of San Diego | 11/08/97 11:12 | 11/08/97 12:10 | 580 | 0 | 2330 F St. | San Diego | SD | 92102 | 8" PVC | 1 | Construction | Collapsed pipe | Rodded to clear line, ref for repairs | Y | Y | Storm drain | SD Bay/Pacific Ocean |  | Y | N/A | N
965699 | Fax 571-6972 | 12/11/97 12:20 | Finch | 6544160 | City of San Diego | 12/11/97 08:45 | 12/11/97 09:40 | 550 | 525 | Chatsworth Bl. & James St. | San Diego | SD | 92106 | 8" CP | 1 | Roots | Roots | Relieved stop, placed main on PM schedule | Y | Y | Storm drain | San Diego Bay | Dried in storm drain | Y | N/A | N
962335 | Fax 571-6972 | 11/26/97 07:30 | Parker | 6544160 | City of San Diego | 11/25/97 19:11 | 11/25/97 21:55 | 492 | 300 | 3124 Carnegie Ct. | San Diego | SD | 92122 | 8" VC | 2 | Rocks | Roots | Removed roots from MH, ref for consideration as MC site | Y | Y | Storm drain | San Clemente Canyon/Rose Canyon/Mission Bay |  | Y | N | N
965109 | Fax 571-6972 | 12/09/97 11:30 | Parker | 6544160 | City of San Diego | 12/09/97 07:00 | 12/09/97 11:10 | 450 | 300 | Playa del Sur & Neptune Pl. | San Diego | SD | 92037 | 4" hi-line | 1 | Other | Break in hi-line | Contained majority of overflow, contractor switched to new frc main | Y | Y | Storm drain | Pacific Ocean |  | Y | N/A | Y | Unknown
956226 | Fax 571-6972 | 10/29/97 15:30 | Parker | 6544160 | City of San Diego | 10/29/97 10:47 | 10/29/97 13:47 | 360 | 0 | 5895 Camto. Empressa | San Diego | SD | 92109 | 8" VC | 1 | Grease | Grease | Relieved stop, consider for PM site | Y | Y | Storm drain | Pacific Ocean |  | Y | N | N
957066 | Fax 571-6972 | 11/02/97 18:21 | Branco | 6544160 | City of San Diego | 11/02/97 12:46 | 11/02/97 13:55 | 345 | 0 | 7422 Conestoga Wy. | San Diego | SD | 92120 | 12" VC | 1 | Roots | Roots | Machine rodded 12" vc main | Y | Y | Storm drain | SD River/Pacific Ocean |  | Y | N/A | N
955318 | Fax 571-6972 | 10/24/97 06:25 | Whelan | 6544160 | City of San Diego | 10/23/97 21:29 | 10/23/97 22:10 | 246 | 0 | 5227 University Av. | San Diego | SD | 92105 | 8" VC | 1 | Grease | Grease | Rodded 8" vc main to relieve stop | Y | Y | Storm Drain | Storm Drain system |  | Y | N | N
958333 | Fax 571-6972 | 11/10/97 14:10 | Hoyer | 6544160 | City of San Diego | 11/10/97 11:18 | 11/10/97 11:50 | 184 | 0 | Hillside Dr. & Torrey Pines Rd. | San Diego | SD | 92037 | 8" CI | 1 | Roots | Roots | Rodded main to remove roots | Y | Y | Storm drain | Pacific Ocean |  | Y | N/A | N
963288 | Fax 571-6972 | 12/01/97 20:47 | Wilder | 6544160 | City of San Diego | 12/01/97 15:32 | 12/01/97 16:30 | 174 | 100 | Copley Av. & Oregon St. | San Diego | SD | 92116 | 6" VC | 1 | Grvty Mn Brk | Line break | Repair 6" vc main | Y | Y | Storm drain | Canyon |  | Y | N/A | N
953151 | Fax 571-6972 | 10/12/97 15:52 | Branco | 6544160 | City of San Diego | 10/12/97 13:17 | 10/12/97 14:32 | 150 | 0 | Paradise Valley Rd. & Woodman St. | San Diego | SD | 92114 | 8" PVC | 1 | Grease | Grease | Flushed to relieve grease blockage | Y | Y | Storm Drain | Sweetwater River/SD Bay |  | Y | N/A | N
963985 | Fax 571-6972 | 12/04/97 05:00 | Whelan | 6544160 | City of San Diego | 12/03/97 17:06 | 12/03/97 19:36 | 150 | 10 | 6401 Linda Vista Rd. | San Diego | SD | 92111 | 8" VC sewer main | 1 | Grease | Grease | Rodded 8" vc main | Y | Y | Storm drain |  |  | Y | N | N/A
961705 | Fax 571-6972 | 11/22/97 17:13 | Branco | 6544160 | City of San Diego | 11/22/97 10:41 | 11/22/97 15:27 | 143 | 0 | 47th St. & Quince St. | San Diego | SD | 92105 | 8" PVC | 1 | Roots | Roots | Machine rodded 8" pvc main, ref for MC site | Y | Y | Storm drain | Chollas Creek/San Diego Bay |  | Y | N/A | N
963161 | Fax 571-6972 | 12/01/97 12:15 | Finch | 6544160 | City of San Diego | 12/01/97 09:25 | 12/01/97 10:10 | 135 | 0 | 2748 30th St./alley west | San Diego | SD | 92104 | 6" VC | 1 | Grease | Grease | Flushed 6" vc main | Y | Y | Storm drain | San Diego Bay | Dried & soaked in ground | Y | N/A | N
954438 | Fax 571-6972 | 10/19/97 13:04 | Branco | 6544160 | City of San Diego | 10/19/97 09:51 | 10/19/97 10:15 | 120 | 0 | 1735 Midvale Dr. | San Diego | SD | 92105 | 8" VC | 1 | Roots | Roots | Machine rodded to relieve root stop | Y | Y | Storm Drain | Chollas Creek/SD Bay |  | Y | N/A | N
951700 | Fax 571-6972 | 10/05/97 22:29 | Branco | 6544160 | City of San Diego | 10/05/97 20:49 | 10/05/97 21:45 | 112 | 0 | 11381 Turtleback Ln. | San Diego | SD | 92127 | 8" PVC | 1 | Grease | Grease | Flushed to relieve stop, ref. for PM | Y | Y | Storm Drain | Lusardi Creek/SD River |  | Y | N/A | N
955643 | Fax 571-6972 | 10/28/97 08:40 | Finch | 6544160 | City of San Diego | 10/27/97 15:58 | 10/27/97 16:45 | 94 | 0 | Newton Av. & S. 16th St. | San Diego | SD | 92113 | 6" CP Sewer Main | 1 | Grease | Grease | Hand rodded 29' of 6" cp main | Y | Y | Storm Drain | San Diego Bay | Storm drain system | N | N/A | N
958090 | Fax 571-6972 | 11/07/97 15:00 | Finch | 6544160 | City of San Diego | 11/07/97 11:45 | 11/07/97 12:30 | 80 | 0 | 21st St. & F St. | San Diego | SD | 92102 | 6" VC | 1 | Construction | Bricks, rocks, concrete | Removed debris, put area on MC site | Y | Y | Storm drain | Dried in storm drain | dried in storm drain | Y | N/A | N
966385 | Fax 571-6972 | 12/13/97 14:18 | Branco | 6544160 | City of San Diego | 12/13/97 10:32 | 12/13/97 11:00 | 56 | 50 | 5800 Santa Fe St. | San Diego | SD | 92109 | 8" VC | 1 | Grease | Grease, rocks and dirt | Flushed line to relieve stop | N | Y | Storm drain | N/A | Interceptor I | Y | N/A | N
967533 | Fax 571-6972 | 12/19/97 19:59 | Branco | 6544160 | City of San Diego | 12/19/97 17:02 | 12/19/97 18:30 | 44 | 0 | 2545 G St. | San Diego | SD | 92102 | 6" CP | 1 | Grease | Grease | Flushed main to relieve stop | Y | Y | Storm drain | San Diego Bay/Pacific Ocean |  | Y | N/A | N
952610 | Fax 571-6972 | 10/09/97 05:45 | Whelan | 6544160 | City of San Diego | 10/08/97 23:05 | 10/08/97 23:39 | 25 | 0 | 3511 Oliphant St. | San Diego | SD | 92106 | 6" CP | 1 | Other | Unknown | Unknown cause, self-clearing stop, main 10-34 upon arrival | Y | Y | Storm Drain |  | Storm Drain | Y | N/A | N
978014 | none | na | na | 738-4323 | City of Escondido | 10-22-97 900 | 10-22-97 1730 | 50 | 30 | 2500 S. Esc. Blvd. | Escondido | SD | 92025 | Private Grease Trap | 1 | Grease | Private grease trap overflow | Grease trap cleaned and reported to out pretreatment inspector | y | y | Storm Drain | Deadhorse Creek | Lake Hodges | n | n | n | na
978015 | called / faxed | 11-21-97 1115 | Jim Miller | 741-4668 | City of Escondido | 11-21-97 715 | 11-21-97 754 | 1950 | 0 | N. Centre City Pkwy. @ Country Club Ln. | Escondido | SD | 92026 | MH 245, Sewer atlas p. 245 | 0 | Grease | Grease and rags | Line was placed on 3-month cleaning schedule | y | y | Storm Drain | Reidy Creek | Esc. Creek | y | y | y | 3 | samples were taken
978016 | called / faxed | 11-25-97 1330 | Lance Lauricha | 738-4347 | City of Escondido | 11-18-97 700 | 11-25-97 1300 | 1890 | 0 | 1032 N. Gamble | Escondido | SD | 92026 | Private Cleanout | 0 | Private cleanout / Broken | Contractor broke sewer line | A plumber opened stoppage while city inspector scheduled the contractor to make repairs | y | y | Storm Drain | Esc. Creek | San Elijo Lagoon | y | y | y | 4 | samples were taken
978018 | called / faxed | 12-14-97 1320 | Lance Lauricha | 738-4349 | City of Escondido | 12-7-97 ? | 12-14-97 1415 | 3150 | 0 | 610 E. Washington | Escondido | SD | 92026 | Private Cleanout | 0 | Private Cleanout | Plastic bags | Private system | y | y | Storm Drain | Esc. Creek | San Elijo Lagoon | y | y | n | na
978019 | county health | 12-16-97 745 | Lance Lauricha | 738-4350 | City of Escondido | 12-15-97 1330 | 12-15-97 1600 | 750 | 400 | 1960 W. Mission | Escondido | SD | 92025 | Private Cleanout | 0 | Private Cleanout / unknown | Unknown | Plumber cleared blockage | y | y | Storm Drain | Esc. Creek | San Elijo Lagoon | y | n | n | na
978020 | called / faxed | 12-19-97 1530 | Lance Lauricha | 738-4351 | City of Escondido | 12-18-97 700 | 12-19-97 1200 | 6300 | 500 | 1670 El Norte Pkwy | Escondido | SD | 92027 | Private Cleanout | 0 | Private Cleanout / unknown | Rags | Plumber cleared blockage | y | y | Storm Drain | Esc. Creek | San Elijo Lagoon | y | y | y | 3 | samples were taken
978021 | county health | 12-23-97 1300 | Lance Lauricha | 738-4352 | City of Escondido | 12-23-97 900 | 12-23-97 1230 | 420 | 50 | 204 E. Second Ave. | Escondido | SD | 92026 | Private Cleanout | 2 | Private Cleanout | Paper towels | Plumber cleared blockage | y | y | Storm Drain | Esc. Creek | San Elijo Lagoon | y | n | n | na
967- 001 | Whitney Ghoram | 8/12/96 8:20 | Renzo Marin | (714) 837-7050 | El Toro Water District | 8/10/96 17:45 | 8/10/96 18:05 | 600 GAL. | 0 GAL. | 25011 El Toro Rd. | Laguna Hills | OR | 92630 | Oso Sta. Wet Well | 1 | State Wide Power Outage and failure of the Transfer Switch. | The Automatic Transfer Switch "Power Sensing Relay" was wired incorrectly, it did not allow the switch to transfer the pumps to the Emergency Power source, leaving the station pumps inoperable. | Rewired "Power Sensing Relay" to prevent failure of the ATS control system. | Y | Y | Storm drain | Aliso creek | OCEAN | Y | N | Y | ? | OCHD placed the warning signs and monitored water quality.
967- 002 | Susan Pease | 2/7/97 13:30 | Renzo Marin | (714) 837-7050 | El Toro Water District | 2/7/97 11:20 | 2/7/97 11:45 | 500 GAL. | 0 GAL. | B - 607 U Avenida Sevilla | Laguna Hills | OR | 92630 | ETWD Atlas page ME-497, MH 14 | 2 | Sticks and rocks. | Sticks and rocks blockage in 6" gravity main line. | Used the Hydrocleaner to break stoppage. Clean up spill and washed down with 4,000 gallons of potable water. Relayed to maintenance crew for routine inspection. | Y | Y | Storm drain | Aliso creek | OCEAN | Y | N | N | N/A | Notified all responsible agencies and mailed discharge report.
978020 |  |  | Mike Teem | 7609667868 | Water Utilities Dept. City of Oceanside | 10/27/97 0715 | 10/27/97 0815 | 275 | 0 | 4221 Thomas Street | Oceanside | SD | 92054 | Manhole | 0 | Grease | Heavy blockage of grease in city main. | Line was "jet rodded" after breaking up stoppage, also chlorine will be dropped in the line to dissolve grease. | N | Y | Storm Drain | N/A | Storm Drain. | N | N/A | N | N/A | Spill area was washed down with water.
97-98-06 | Faxed | Mar.18,9:15pm | Geoffrey Cook | 714-487-1097 | CBWD | Mar.18,9:15pm | Mar.18,10:10pm | 300 | 0 | Calle Paloma | Capistrano Beach | OR | 92624 | Manhole | 1 | Grease | Grease in upstream manhole,flow caused bubbling at manhole. | Jetted line clear, schedule follow up and review next scheduled cleaning on regular scheduled cleaning. | no | yes | storm drain | none | storm drain | yes |  | no | N/A
969183 | Fax 571-6972 | 01/01/98 14:00 | J.Grable | 6544160 | City of San Diego | 01/01/98 10:30 | 01/01/98 13:00 | 750 | 0 | Falcon Fire Wy. & Jacmar Av. | San Diego | SD | 92114 | 8" VC | One | Grease | Grease | Rodded main/refer for pm and grease treatment schedule | N | Y | Storm Drain | Pacific Ocean | Soaked into ground | Y | N | N
969365 | Fax 571-6972 | 01/03/98 14:24 | D.Branco | 6544160 | City of San Diego | 01/03/98 09:36 | 01/03/98 11:00 | 168 | 0 | 3996 Hatton St. | San Diego | SD | 92111 | 8" VC | One | Debris | Roots/Heavy paper buildup | Machine rodded/referred to area supervisor for scheduled PM | Y | Y | Storm Drain | Mission Bay/Pacific Ocean |  | Y | N | N
969380 | Fax 571-6972 | 01/03/98 22:50 | D.Branco | 6544160 | City of San Diego | 01/03/98 20:52 | 01/03/98 22:05 | 730 | 0 | 2331 Galveston St. | San Diego | SD | 92110 | 8" VC | One | Roots | Roots | Machine rodded/referred to area supervisor for scheduled PM | Y | Y | Storm Drain |  | Mission Bay/Pacific Ocean | Y | N | Y | Unknown
970299 | Fax 571-6972 | 01/09/98 06:35 | M.Whelan | 6544160 | City of San Diego | 01/08/98 19:08 | 01/08/98 21:38 | 150 | 15 | 1180 S. Valencia Py. | San Diego | SD | 92114 | 8" VC | One | Grease | Grease | Rod main/cleaned and vacuumed manhole/vacuumed puddle | Y | Y | Storm Drain | Dissipated in storm drain system |  | Y | N | N
971258 | Fax 571-6972 | 01/15/98 01:00 | M.Whelan | 6544160 | City of San Diego | 01/14/98 19:38 | 01/14/98 22:08 | 450 | 0 | 6474 El Cajon Bl. | San Diego | SD | 92115 | 8" VC | One | Roots | Roots | Rod main/trace out overflow | Y | Y | Storm Drain | Dissipated in storm drain |  | Y | N | N
971662 | Fax 571-6972 | 01/17/98 17:12 | D.Branco | 6544160 | City of San Diego | 01/17/98 09:01 | 01/17/98 10:30 | 455 | 0 | 4575 Arizona St. | San Diego | SD | 92104 | 8" VC | One | Grease | Grease | Machine Rodded/referred to area supervisor for scheduled PM | Y | Y | Storm Drain | San Diego Bay/Pacific Ocean |  | Y | N | N
971668 | Fax 571-6972 | 01/17/98 17:06 | D.Branco | 6544160 | City of San Diego | 01/17/98 10:06 | 01/17/98 11:07 | 122 | 0 | El Amigo & Nob Av. | San Diego | SD | 92014 | 8" VC | One | Roots | Roots | Flushed main to relieve stop/refer to area supervisor for scheduled PM | Y | Y | Storm Drain | Pacific Ocean |  | Y | N | N
971701 | Fax 571-6972 | 01/17/98 23:55 | J.McPherson | 6544160 | City of San Diego | 01/17/98 20:52 | 01/17/98 23:00 | 68 | 2 | 1018 Bangor St. | San Diego | SD | 92106 | 6" CP | One | Roots | Roots | Rodded easement line to remove blockage | Y | Y | Storm Drain | Pacific Ocean |  | Y | N | N
971737 | Fax 571-6972 | 01/19/98 15:00 | J.McPherson | 6544160 | City of San Diego | 01/19/98 12:33 | 01/19/98 14:33 | 600 | 0 | 168 Kenyatta Dr. | San Diego | SD | 92114 | 8" VC | One | Grease | Heavy grease | Referred to area supervisor for main cleaning schedule | Y | Y | Storm Drain | Chollas Creek |  | Y | N | N
971748 | Fax 571-6972 | 01/19/98 20:30 | J.McPherson | 6544160 | City of San Diego | 01/19/98 16:04 | 01/19/98 17:00 | 56 | 0 | 4432 Pacific Hy. | San Diego | SD | 92140 | 8" VC | One | Debris | Rags in main | Added to cleaning schedule | Y | Y | Storm Drain | San Diego Bay | Dried in storm drain | Y | N | N
971823 | Fax 571-6972 | 01/21/98 01:27 | M.Whelan | 6544160 | City of San Diego | 01/20/98 13:37 | 01/20/98 17:05 | 1040 | 400 | Calle Cristobal & Corley Ct. | San Diego | SD | 92126 | 8" VC | One | Grease | Heavy grease mixed with roots | Flushed main/cleaned manholes | Y | Y | Storm Drain | None | Dried in canyon | Y | Y | N
972348 | Fax 571-6972 | 01/22/98 19:55 | M.Whelan | 6544160 | City of San Diego | 01/22/98 13:48 | 01/22/98 15:03 | 150 | 74 | 5005 Texas St. | San Diego | SD | 92108 | 8" VC | One | Roots | Heavy roots and heavy grease | Machine rodded main/cleaned out manhole of very heavy roots | Y | Y | Storm Drain | Soaked into ground in drainage ditch |  | Y | N | N
972712 | Fax 571-6972 | 01/24/98 12:00 | D.Branco | 6544160 | City of San Diego | 01/24/98 08:40 | 01/24/98 09:17 | 74 | 0 | 40th St. & T St. | San Diego | SD | 92113 | 8" VC | One | Grease | Grease | Flushed main/referred to area supervisor for scheduled PM | Y | Y | Storm Drain | San Diego Bay/Pacific Ocean |  | Y | N | Y
972745 | Fax 571-6972 | 01/25/98 02:15 | L.Finch | 6544160 | City of San Diego | 01/24/98 22:14 | 01/25/98 00:20 | 630 | 0 | Swift Av. & Wightman St./alley east | San Diego | SD | 92104 | 6" VC | One | Debris | Vandalism/manhole deterioration | Refer to area supervisor for maintenance scheduling | Y | Y | Storm Drain | San Diego Bay/Pacific Ocean |  | Y | N | N
975021 | Fax 571-6972 | 01/25/98 22:20 | L.Finch | 6544160 | City of San Diego | 01/25/98 16:00 | 01/25/98 20:20 | 260 | 0 | 5005 Texas St. | San Diego | SD | 92108 | 8" VC | Two | Grease | Heavy grease | Clean and TV main for evaluation for shorter maintenance site | Y | Y | Storm Drain | Soaked into ground |  | Y | N | N
973179 | Fax 571-6972 | 01/27/98 15:30 | L.Finch | 6544160 | City of San Diego | 01/27/98 13:56 | 01/27/98 14:40 | 88 | 0 | 21st St. & F St. | San Diego | SD | 92102 | 6" CP | Two | Debris | Rags and paper | Re-evaluation main and MC site | Y | Y | Storm Drain | San Diego Bay | Dissipated in storm drain | Y | N | N
974119 | Fax 571-6972 | 01/31/98 09:05 | M.Bedard | 6544160 | City of San Diego | 01/30/98 18:45 | 01/31/98 01:00 | 2505 | 480 | Roselle St. & Sorrento Valley Bl.** | San Diego | SD | 92121 | SPS 65 force main | Two | Construction | Sewer plug lost seal causing leak | Vactor flow/shut down SPS 65 | Y | Y | Storm Drain | Pacific Ocean |  | Y | Y | N
974463 | Fax 571-6972 | 02/01/98 17:39 | D.Branco | 6544160 | City of San Diego | 02/01/98 09:29 | 02/01/98 12:55 | 412 | 0 | 2757 K St. | San Diego | SD | 92102 | 6" CP | One | Grease | Grease | Machine rodded/referred to area supervisor for scheduled PM | Y | Y | Storm Drain | San Diego Bay/Pacific Ocean |  | Y | N | N
975167 | Fax 571-6972 | 02/04/98 14:00 | L.Finch | 6544160 | City of San Diego | 02/04/98 08:11 | 02/04/98 09:10 | 680 | 500 | Rosecrans St. & Zola St. | San Diego | SD | 92133 | 8" CP | One | Debris | Paper towels and other debris | Machine rodded main/adding to MC site | Y | Y | Storm Drain | San Diego Bay/Pacific Ocean |  | Y | N | Y | Three
976079 | Fax 571-6972 | 02/10/98 13:30 | L.Finch | 6544160 | City of San Diego | 02/10/98 05:44 | 02/10/98 09:00 | 3920 | 0 | 2648 E St./alley north | San Diego | SD | 92102 | 6" CP | One | Construction | Construction debris | Cleaned main/advised contractor to trap better & keep traps clean | Y | Y | Storm Drain | San Diego Bay |  | Y | Y | N
978992 | Fax 571-6972 | 02/27/98 10:19 | M.Dawson | 6544160 | City of San Diego | 02/27/98 07:26 | 02/27/98 08:56 | 90 | 0 | Chamoune Av. & Dwight St. | San Diego | SD | 92105 | 6" CP | One | Grease | Grease | Flushed to relieve stop/referred to FEWD | N | Y | Storm Drain | Chollas Creek | San Diego Bay | Y | N | N
979415 | Fax 571-6972 | 02/28/98 13:56 | D.Branco | 6544160 | City of San Diego | 02/28/98 10:29 | 02/28/98 14:21 | 116 | 0 | 4236 Venus St. | San Diego | SD | 92110 | 8" VC | One | Grvty Mn Brk | Main collapsed cuasing system to back-up | Repaired collapsed main | Y | Y | Storm Drain | San Diego River/Pacific Ocean |  | Y | N | N
979557 | Fax 571-6972 | 03/02/98 14:00 | G.Richardson | 6544160 | City of San Diego | 03/02/98 12:46 | 03/02/98 13:03 | 85 | 0 | Altadena Av. & Wightman St. | San Diego | SD | 92105 | 8" VC | One | Grease | Grease | Rodded main to relieve stop | Y | Y | Storm Drain | Chollas Creek | San Diego Bay | Y | N | N
979929 | Fax 571-6972 | 03/04/98 15:00 | L.Davis | 6544160 | City of San Diego | 03/04/98 06:59 | 03/04/98 08:30 | 4500 | 1500 | 6449 Bell Bluff Av. | San Diego | SD | 92123 | 12" VC | One | Roots | Roots and rocks in the main | Bucketing main to remove rocks/putting main on 36 month PM schedule | Y | Y | Storm Drain | Pond area | Pond area | Y | Y | Y | Unknown
980102 | Fax 571-6972 | 03/05/98 15:15 | G.Richardson | 6544160 | City of San Diego | 03/04/98 10:49 | 03/04/98 17:50 | 432000 | 9000 | Kostner Av. & Marge Wy. | San Diego | SD | 91911 | 8" VC | One | Grvty Mn Brk | Storm Drain failure | Referred to construction for repairs | Y | Y | Storm Drain | Tijuana River | Pacific Ocean | Y | N | Y | One
980448 | Fax 571-6972 | 03/06/98 06:00 | M.Whelan | 6544160 | City of San Diego | 03/05/98 18:34 | 03/05/98 22:04 | 315 | 0 | 4036 S. Hampstead Cir. | San Diego | SD | 92116 | 6" CP | One | Grease | Grease | Rod section to relieve stop. Rod to clean section | Y | Y | Storm Drain | Soaked into ground in canyon |  | Y | N | N
980652 | Fax 571-6972 | 03/07/98 18:55 | D.Branco | 6544160 | City of San Diego | 03/07/98 16:46 | 03/07/98 17:40 | 108 | 0 | 6170 Dunant St. | San Diego | SD | 92122 | 8" VC | One | Grease | Grease | Flushed main/referred to area supervisor for scheduled maintenance | Y | Y | Storm Drain | Rose Canyon/Mission Bay |  | Y | N | N
980700 | Fax 571-6972 | 03/09/98 11:30 | R.Parker | 6544160 | City of San Diego | 03/09/98 06:07 | 03/09/98 09:00 | 865 | 0 | David St. & Ulric St./on Ulric s/o David | San Diego | SD | 92111 | 18" VC | One | Other | Sludge build-up caused back-up | Flushed main/possibly place on scheduled maintenance | Y | Y | Storm Drain | San Diego River/Pacific Ocean |  | Y | N | Y | Unknown
980706 | Fax 571-6972 | 03/09/98 07:51 | L.Davis | 6544160 | City of San Diego | 03/09/98 07:44 | 03/09/98 09:00 | 380 | 100 | Lake Murray Bl. & Lynn Haven Ln. | San Diego | SD | 92119 | 8" VC | One | Roots | Roots and grease | Machine flushed, cleaned up spill site | Y | Y | Storm Drain | Trench in canyon | Soaked into open trench | Y | N | N
981068 | Fax 571-6972 | 03/12/98 14:15 | R.Parker | 6544160 | City of San Diego | 03/05/98 09:00 | 03/12/98 12:35 | 122360 | 21840 | 7970 Sevan Ct./canyon | San Diego | SD | 92123 | 8" VC | One | Grvty Mn Brk | Heavy rains exposed pipe/heavy rocks falling | Rodded and repaired main | Y | Y | Storm Drain | Murray Canyon/ San Diego River/ Pacific Ocean |  | Y | Y | Y | Unknown
981490 | Fax 571-6972 | 03/12/98 13:10 | G.Richardson | 6544160 | City of San Diego | 03/12/98 10:55 | 03/12/98 12:02 | 134 | 0 | 2282 Leighton Ct. | San Diego | SD | 92139 | 8" VC | One | Roots | Roots and grease | Rodded main to relieve stop | Y | Y | Storm Drain | N/A | Dissipated in Storm Drain | Y | N | N
981687 | Fax 571-6972 | 03/13/98 11:20 | L.Davis | 6544160 | City of San Diego | 03/13/98 08:50 | 03/13/98 09:15 | 300 | 0 | 10265 Pinetree Dr. | San Diego | SD | 92131 | 8" VC | One | Roots | Root build-up | Cleaned manhole and easement/place on scheduled maintenance | Y | Y | Storm Drain | Drainage Ditch |  | Y | N | Y | Unknown
982116 | Fax 571-6972 | 03/16/98 14:55 | M.Bedard | 6544160 | City of San Diego | 03/16/98 08:00 | 03/16/98 08:32 | 450 | 450 | Cottontail Ln. & Deer Hill Ct./canyon rear | San Diego | SD | 92037 | 8" VC | One | Other | Bypass pumping temporarily failed | Set up additional measures to by-pass pump | Y | Y | Storm Drain | Canyon Creek | Storm Drain/open manhole | Y | N | N
983589 | Fax 571-6972 | 03/20/98 21:57 | D.Branco | 6544160 | City of San Diego | 30/20/98 18:04 | 30/20/98 20:15 | 131 | 0 | 2362 Hartford St. | San Diego | SD | 92110 | 8" VC | One | Roots | Roots | Flushed main/refer to area supervisor for scheduled PM maintenance | N | Y | Storm Drain | Interceptor I-2 |  | Y | N | N
983739 | Fax 571-6972 | 03/22/98 11:10 | D.Branco | 6544160 | City of San Diego | 03/22/98 08:38 | 03/22/98 09:33 | 550 | 0 | College Av. & Lance St. | San Diego | SD | 92120 | 8" VC | One | Roots | Roots | Rodded main/refer to area supervisor to review cleaning schedule | Y | Y | Storm Drain | San Diego River/Pacific Ocean |  | Y | N | N
983849 | Fax 571-6972 | 03/23/98 10:30 | E.Semo | 6544160 | City of San Diego | 03/23/98 09:18 | 03/23/98 10:12 | 112 | 0 | 4836 Mt. Frissell Dr. | San Diego | SD | 92117 | 8" VC | One | Grease | Grease | Rod main/add to flush PM schedule | Y | Y | Storm Drain | Pacific Ocean |  | Y | N | N
984173 | Fax 571-6972 | 03/25/98 04:37 | M.Whelan | 6544160 | City of San Diego | 03/24/98 16:47 | 03/24/98 17:52 | 33 | 0 | 1740 Midvale Dr. | San Diego | SD | 92105 | 8" VC | One | Debris | Debris | Rodded and flushed main/vacummed overflow | Y | Y | Storm Drain | Storm Drain |  | Y | N | N
984850 | Fax 571-6972 | 03/29/98 16:31 | D.Branco | 6544160 | City of San Diego | 03/29/98 13:33 | 03/29/98 14:20 | 470 | 0 | 65th St. & Benson Av. | San Diego | SD | 92114 | 8" VC | One | Grease | Grease | Machine rodded/refer to area supervisor for scheduled PM maintenance | Y | Y | Storm Drain | San Diego Bay/Pacific Ocean |  | Y | N | N
967- 001 | Whitney Ghoram | 1996-08-12 08:20 | Renzo Marin | (714) 837-7050 | El Toro Water District | 1996-08-10 17:45 | 1996-08-10 18:05 | 600 GAL. | 0 GAL. | 25011 El Toro Rd. | Laguna Hills | OR | 92630 | Oso Sta. Wet Well | 1 | State Wide Power Outage and failure of the Transfer Switch. | The Automatic Transfer Switch "Power Sensing Relay" was wired incorrectly, it did not allow the switch to transfer the pumps to the Emergency Power source, leaving the station pumps inoperable. | Rewired "Power Sensing Relay" to prevent failure of the ATS control system. | Y | Y | Storm drain | Aliso creek | OCEAN | Y | N | Y | ? | OCHD placed the warning signs and monitored water quality.
967- 002 | Susan Pease | 1997-02-07 13:30 | Renzo Marin | (714) 837-7050 | El Toro Water District | 1997-02-07 11:20 | 1997-02-07 11:45 | 500 GAL. | 0 GAL. | B - 607 U Avenida Sevilla | Laguna Hills | OR | 92630 | ETWD Atlas page ME-497, MH 14 | 2 | Sticks and rocks. | Sticks and rocks blockage in 6" gravity main line. | Used the Hydrocleaner to break stoppage. Clean up spill and washed down with 4,000 gallons of potable water. Relayed to maintenance crew for routine inspection. | Y | Y | Storm drain | Aliso creek | OCEAN | Y | N | N | N/A | Notified all responsible agencies and mailed discharge report.
978042 |  |  | Jeremy Kemp | 760/966-7868 | Water Utilities Dept. City of Oceanside | 04/21/98 1912 | 04/21/98 2030 | 600 | 0 | 1905 Comanche | Oceanside | SD | 92056 | Manhole | 2 | Grease | Grease built up in the line through the easement. | We have been dropping chlorine in this area to control the grease problem. | N | Y | Storm Drain | Loma Alta Creek | N/A | Y | N/A | N | N/A | Diluted spill with 500 Gallons of fresh water.
978043 | Voice Mail | 04/26/98 1535 | Jeremy Kemp | 760/966-7868 | Water Utilities Dept. City of Oceanside | 04/26/98 1105 | 04/26/98 1240 | 2300 | 0 | Capistrano & San Jose Easement | Oceanside | SD | 92054 | Manhole | 0 | Blockage | Lots of rags in line. | This easement is rodded on quarterly basis. | Y | Y | Storm Drain | San Luis Rey River | N/A | Y | Y | N | N/A | Easement was due next month for quarterly rodding.
978004 | Mail | 1998-05-12 09:00 | Steve Francis | 9494596540 | Santa Margarita Water District | 1998-05-11 16:00 | 1998-05-11 17:00 | 600 | 0 | Vista del Lago | Mission Viejo | OR | 92690 | Manhole | 1 | Roots | Root intrusion into 8" VCP sewer line. | Cut out root ball and removed from sewer line. Area was disinfected with chlorine and washed into manhole. | Y | Y | Storm Drain | Los Alisos Creek | Aliso Beach | Y | Y | N | N/A
978005 | Fax | 1998-06-27 14:00 | Steve Francis | 9494596539 | Santa Margarita Water District | 1998-06-27 12:30 | 1998-06-27 12:50 | 300 | 0 | Puerte de Luz | Mission Viejo | OR | 92691 | Manhole | 1 | Power Failure | Power Failure caused wetwell to fill and overflow before crew could arrive with Vactor. |  | Y | Y | Storm Drain | Los Alisos Creek | Aliso Beach | Y | N | N | N/A
978030 | CLAY CLIFTON-PHONE & FAX | 6/10/98-11:15 A | DON WASKO/PAT GUEVARA | 760-438-2722 | CARLSBAD MWD | 6/10/98-9:20 A | 6/10/98-10:10 A | 1500 | 0 | 2805 OCEAN ST. | CARLSBAD | SD | 92008 | 4" SEWER CLEANOUT (2) | 1 | CONSTRUCTION DEBRIS | MAJOR CONSTRUCTION OCCURING ACROSS THE STREET FROM 2805 OCEAN ST.. DEBRIS INCLUDED SOIL, BRICK PIECES, PIPE SCRAPS. | VACTOR TRUCK USED TO CLEAR SEWER MAIN. ENSURE CONSTRUCTION DEBRIS NEVER ENTERS SEWER SYSTEM. | Y | Y | STORM DRAIN | PACIFIC OCEAN | PACIFIC OCEAN/BEACH AREA | Y | Y | Y | 2 | NANCY ANSON W/ENCINA WWA DISPATCHED JEFF PARKS (ENCINA) TO TAKE WATER SAMPLES. SAMPLES PROVED NEGATIVE. SIGNS WERE THEN REMOVED FROM BEACH AREA.
985818 | Fax 571-6972 | 4/02/98 10:45 | L. Davis | 654-4160 | City of San Diego | 4/02/98 07:50 | 4/02/98 08:50 | 600 | 0 | 11233 Tierrasanta Bl. | San Diego | SD | 92124 | 12" PVC | One | Vandalism | Rocks and roots caused blockage | Machine rodded to remove roots, removed rocks, placed on PM | Y | Y | Storm Drain | Canyon area | Dried in canyon floor | Y | N | N | N/A | N/A
987600 | Fax 571-6972 | 4/14/98 16:45 | L. Finch | 654-4160 | City of San Diego | 4/14/98 09:24 | 4/14/98 12:24 | 180 | 0 | 27th St. & F St. | San Diego | SD | 92102 | 8" VC sewer main | One | Construction | Heavy rocks and dirt caused by construction company | Remv'd rocks/dirt caused by contractor not trapping properly | Y | N | Storm Drain | Soaked into ground | Canyon | Y | N | N | N/A | N/A
987754 | Fax 571-6972 | 4/16/98 15:15 | L. Davis | 654-4160 | City of San Diego | 4/15/98 10:40 | 4/15/98 11:57 | 3850 | 0 | 9100 Friars Rd. | San Diego | SD | 92128 | 16" VC sewer main | One | Vandalism | Debris that entered manhole when lid dislodged | Removed branches, cacti, debris, ref. for manholes to be secured | Y | Y | Storm Drain | San Diego River | Pacific Ocean | Y | Y | Y | Unknown | 24 signs posted
988188 | Fax 571-6972 | 4/18/98 12:00 | J.Oropeza | 654-4160 | City of San Diego | 4/18/98 07:35 | 4/18/98 09:15 | 1500 | 0 | Beyer Bl. & Palm Av. | San Diego | SD | 92154 | 10" VC | One | Grease | Heavy grease caused blockage | Relieve stop, ref. to supv. for PM schedule | Y | Y | Storm Drain | SD Bay/Pacific Ocean | N/A | Y | Y | Y | Unknown | 8 signs posted
988227 | Fax 571-6972 | 4/20/98 11:00 | G. Richardson | 654-4160 | City of San Diego | 4/20/98 07:03 | 4/20/98 08:03 | 315 | 0 | Baylor Dr. & Collier Av. | San Diego | SD | 92115 | 6" VC | One | Roots | Roots in main | Removed roots from 6" vc main | Y | Y | Storm Drain | N/A | Storm Drain system | Y | N | N | N/A | N/A
988753 | Fax 571-6972 | 4/23/98 11:30 | L. Davis | 654-4160 | City of San Diego | 4/23/98 06:55 | 4/23/98 07:30 | 450 | 0 | 5011 Waring Rd. | San Diego | SD | 92120 | 8" VC | One | Grease | Grease build-up | Cleared grease stop, place main on PM schedule | Y | Y | Storm Drain | Canyon | Dried up in canyon | Y | N | N | N/A | N/A
989616 | Fax 571-6972 | 4/30/98 03:35 | M. Whelan | 654-4160 | City of San Diego | 4/29/98 14:36 | 4/29/98 17:07 | 2265 | 405 | 810 Turquoise St. | San Diego | SD | 92109 | 8" VC | One | Rocks | Roots and rocks | Flushed, vacuumed to remove rocks and roots | Y | Y | Storm Drain | Pacific Ocean | N/A | Y | Y | Y | Unknown | 7 signs posted
990078 | Fax 571-6972 | 5/03/98 22:09 | D. Branco | 654-4160 | City of San Diego | 5/03/98 19:08 | 5/03/98 21:10 | 1220 | 0 | 3512 43rd St. | San Diego | SD | 92105 | 8" VC main | One | Grease | Stoppage caused by grease | Machine rodded to relieve stop, ref. for PM | Y | Y | Storm Drain | SD Bay/Pacific Ocean | N/A | Y | Y | N | N/A | N/A
991843 | Fax 571-6972 | 5/15/98 14:10 | R. Bjorkman | 654-4160 | City of San Diego | 5/04/98 06:00 | 5/04/98 12:00 | 9000 | 0 | 15500 Paymogo St. | San Diego | SD | 92129 | Sewer Pump Station 62 | One | Other | Possibly faulty relay | Replaced pump relay switch; investigating alarm failure | Y | Y | Storm Drain | Gravel pit | N/A | Y | Y | Y | Unknown | 5 signs posted
990340 | Fax 571-6972 | 5/05/98 09:30 | G. Richardson | 654-4160 | City of San Diego | 5/05/98 08:27 | 5/05/98 08:50 | 69 | 0 | 4169 Vista Grande | San Diego | SD | 92115 | 6" CP | One | Roots | Roots in main caused overflow | Rodded main to remove roots, cleaned area | Y | Y | Storm Drain | N/A | Storm Drain | Y | N | Y | N/A | N/A
990849 | Fax 571-6972 | 5/08/98 00:47 | M. Whelan | 654-4160 | City of San Diego | 5/07/98 19:44 | 5/07/98 20:39 | 55 | 14 | 5297 Lodi St. | San Diego | SD | 92117 | 8" VC | One | Debris | Debris in manhole caused stoppage | Probed MH, relieved stop, scooped rags, towels, debris from main | Y | Y | Storm Drain | Soaked into ground | N/A | Y | N | N | N/A | N/A
990853 | Fax 571-6972 | 5/08/98 11:30 | L. Finch | 654-4160 | City of San Diego | 5/08/98 06:55 | 5/08/98 08:30 | 47.5 | 0 | Greely Av. & Payne St. | San Diego | SD | 92113 | 8" CI | One | Grease | Stoppage caused by grease | Flushed to relieve stop, deodorized area, advised claims | Y | Y | Storm Drain | Chollas Creek/SD Bay | Storm Drain | Y | N | N | N/A | N/A
991055 | Fax 571-6972 | 5/09/98 13:59 | D. Branco | 654-4160 | City of San Diego | 5/09/98 08:39 | 5/09/98 09:33 | 270 | 0 | 4600 Mt. Etna Dr. | San Diego | SD | 92117 | 8" VC | One | Grease | Stoppage caused by grease | Machine rodded to relieve stop | Y | Y | Storm Drain | Tecolate Creek/Mission Bay | N/A | Y | N | N | N/A | N/A
991336 | Fax 571-6972 | 5/12/98 14:45 | L. Finch | 654-4160 | City of San Diego | 5/12/98 10:07 | 5/12/98 11:43 | 480 | 0 | 2125 Park Bl. | San Diego | SD | 92134 | 6" CP | One | Debris | Debris in sewer main | Relieved stop, ref. for TV | Y | Y | Storm Drain | San Diego Bay | Storm Drain | Y | N | N | N/A | N/A
991382 | Fax 571-6972 | 5/13/98 04:15 | M. Whelan | 654-4160 | City of San Diego | 5/12/98 13:24 | 5/12/98 16:30 | 372 | 0 | Hillside Dr. & Torrey Pines Rd. | San Diego | SD | 92037 | 8" CI sewer main | Two | Roots | Heavy roots in main caused overflow | Rodded main to relieve stop | Y | Y | Storm Drain | Pacific Ocean | N/A | Y | N | Y | Unknown | Unknown
991543 | Fax 571-6972 | 5/13/98 14:45 | R. Parker | 654-4160 | City of San Diego | 5/13/98 12:21 | 5/13/98 13:13 | 2600 | 0 | Carmel Country Rd. & w/b Hwy. 56 | San Diego | SD | 92130 | 10" PVC | One | Debris | Debris build-up caused stoppage | Relieve stop, clean upstream mains, consider for PM site | Y | Y | Storm Drain | Soledad Creek/Pacific Ocean | N/A | Y | Y | Y | Unknown | 5 signs posted
992246 | Fax 571-6972 | 5/19/98 04:57 | M. Whelan | 654-4160 | City of San Diego | 5/18/98 17:50 | 5/18/98 21:15 | 102.5 | 0 | 1071 S. 41st St. | San Diego | SD | 92113 | 8" PVC | One | Grease | Grease and rocks in main | Flushed, removed heavy grease from main | Y | Y | Storm Drain | Drainage channel | N/A | Y | N | N | N/A | N/A
992396 | Fax 571-6972 | 5/19/98 04:59 | M. Whelan | 654-4160 | City of San Diego | 5/18/98 21:31 | 5/19/98 24:20 | 845 | 250 | 4297 Cordobes Cv. | San Diego | SD | 92130 | 8" PVC | One | Roots | Roots in buried manhole caused blockage | Locate/dig out manhole, clean 1' of roots from channel to relieve stop | Y | Y | Storm Drain | Drainage ditch | N/A | Y | Y | N | N/A | N/A
992698 | Fax 571-6972 | 5/20/98 01:42 | M. Whelan | 654-4160 | City of San Diego | 5/19/98 20:46 | 5/19/98 22:43 | 351 | 0 | 7247 Arpege Rd. | San Diego | SD | 92119 | 8" PVC | One | Roots | Roots & grease in main/also rootbound manholes | Cleaned rootbound manhole, rodded main to relieve stop | Y | Y | Storm Drain | Soaked into canyon | N/A | Y | N | N | N/A | N/A
993592 | Fax 571-6972 | 5/23/98 16:06 | D. Branco | 654-4160 | City of San Diego | 5/23/98 11:39 | 5/23/98 13:01 | 41 | 0 | 3200 Reynard Wy. | San Diego | SD | 92103 | 6" VC | One | Roots | Roots caused blockage | Locate/expose manhole, flush main to remove heavy roots | Y | Y | Storm Drain | SD Bay/Pacific Ocean | N/A | Y | N | N | N/A | N/A
993848 | Fax 571-6972 | 5/27/98 02:52 | M. Whelan | 654-4160 | City of San Diego | 5/26/98 21:37 | 5/26/98 23:07 | 45 | 0 | 5124 Via Cinta | San Diego | SD | 92122 | 8" VC | One | Roots | Roots in easement caused grease build-up | Flushed main to relieve stop | Y | Y | Storm Drain | Soaked into ground | N/A | Y | N | N | N/A | N/A
994303 | Fax 571-6972 | 5/29/98 07:03 | M. Whelan | 654-4160 | City of San Diego | 5/28/98 22:11 | 5/29/98 00:32 | 705 | 0 | 3900 Lockridge St. | San Diego | SD | 92102 | 10" VC | One | Vandalism | Vandals and roots caused blockage | Removed heavy debris, roots from main | N | Y | Storm Drain | Soaked into ground | N/A | Y | N | N | N/A | N/A
995489 | Fax 571-6972 | 6/04/98 12:10 | C. Bauer | 654-4160 | City of San Diego | 6/04/98 09:29 | 6/04/98 10:36 | 335 | 0 | 10405 San Diego Mission Rd. | San Diego | SD | 92108 | 8" VC | One | Grease | Grease | Flushed 8" vc main to remove stop | Y | Y | Storm Drain | SD River/Pacific Ocean | Storm Drain | Y | N | N | N/A | N/A
996800 | Fax 571-6972 | 6/11/98 05:37 | M. Whelan | 654-4160 | City of San Diego | 6/10/98 21:23 | 6/10/98 23:08 | 525 | 135 | 2548 Reo Dr. | San Diego | SD | 92139 | 8" VC | One | Grease | Grease in main | Vacuum to control overflow on 8" vc main | Y | Y | Storm Drain | N/A | N/A | Y | N | N | N/A | N/A
997138 | Fax 571-6972 | 6/13/98 15:07 | D. Branco | 654-4160 | City of San Diego | 6/13/98 09:52 | 6/13/98 11:45 | 321 | 0 | 6400 Bradford St. | San Diego | SD | 92115 | 8" VC | One | Grease | Blockage caused by grease & roots | Flushed 8" vc main to relieve grease/root stop | Y | Y | Storm Drain | Chollas Creek/San Diego Bay | N/A | Y | N | N | N/A | N/A
997160 | Fax 571-6972 | 6/14/98 15:19 | D. Branco | 654-4160 | City of San Diego | 6/14/98 09:46 | 6/14/98 10:58 | 216 | 0 | 4303 Whittier St. | San Diego | SD | 92107 | 8" VC | Two | Roots | Blockage caused by roots | Flushed 8" vc main to relieve root stop | Y | Y | Storm Drain | San Diego River/Pacific Ocean | N/A | Y | N | N | N/A | N/A
997416 | Fax 571-6972 | 6/16/98 15:42 | L. Moore | 654-4160 | City of San Diego | 6/16/98 09:49 | 6/16/98 12:49 | 1800 | 0 | Mission Center Rd. & Hazard Center Dr. | San Diego | SD | 92108 | 6" PVC | One | Grease | Stoppage caused by grease | Flushed 6" pvc main to relieve stop | Y | Y | Storm Drain | San Diego River | Pacific Ocean | Y | Y | Y | Two | 6 signs posted
997763 | Fax 571-6972 | 6/18/98 13:20 | L. Finch | 654-4160 | City of San Diego | 6/18/98 07:19 | 6/18/98 09:33 | 4020 | 2800 | 1009 Leroy St. | San Diego | SD | 92106 | 8" CP | One | Grvty Main Brk | Pieces of rock, pipe, light roots | Refer for spot repair on 8" cp main | Y | Y | Storm Drain | Storm Drain | N/A | Y | Y | Y | Five | Unknown
997770 | Fax 571-6972 | 6/18/98 16:00 | M. Bedard | 654-4160 | City of San Diego | 6/17/98 09:25 | 6/18/98 13:30 | 33700 | 33700 | 5100 Olvera Av. | San Diego | SD | 92114 | 10" VC | One | Grease | Grease caused blockage | Relieve grease stop on 10" vc main, refer for repair to brick manhole | Y | Y | Storm Drain | Pacific Ocean | N/A | Y | Y | N | N/A | N/A
997785 | Fax 571-6972 | 6/18/98 13:10 | L. Davis | 654-4160 | City of San Diego | 6/18/98 09:40 | 6/18/98 10:35 | 50 | 0 | 17572 Cumana Tr. | San Diego | SD | 92128 | Manhole on 8" PVC | One | Roots | Blockage caused by roots | Relieve root stop on 8" pvc main | Y | Y | Storm Drain | Drainage ditch | Dried in drainage ditch | Y | N | N | N/A | N/A
998146 | Fax 571-6972 | 6/20/98 11:25 | J. Oropeza | 654-4160 | City of San Diego | 6/20/98 09:14 | 6/20/98 10:30 | 152 | 0 | Bunche Av. & Dunant St. | San Diego | SD | 92122 | 8" VC | Two | Grease | Blockage caused by roots and grease | Relieve grease and root stop on 8" vc main | N | Y | Storm Drain | Canyon creek | Soaked into canyon | N | N | N | N/A | N/A
998365 | Fax 571-6972 | 6/22/98 19:55 | M. Whelan | 654-4160 | City of San Diego | 6/22/98 11:00 | 6/22/98 16:15 | 3150 | 400 | 1111 W. Muirlands Dr. | San Diego | SD | 92037 | 8" VC | One | Roots | Blockage caused by roots | Relieve root blockage on 8" vc main | Y | Y | Storm Drain | Pacific Ocean | N/A | Y | Y | Y | Unknown | 7 signs posted
999566 | Fax 571-6972 | 6/30/98 01:58 | M. Whelan | 654-4160 | City of San Diego | 6/29/98 20:30 | 6/29/98 22:11 | 303 | 0 | 47th St. & Dwight St. | San Diego | SD | 92105 | 6" CP | One | Grease | Blockage caused by grease | Rod 6" cp main to relieve stop | Y | Y | Storm Drain | Soaked into ground | N/A | Y | N | N | N/A | N/A
999438 | Fax 571-6972 | 7/01/98 12:45 | L. Finch | 654-4160 | City of San Diego | 6/29/98 06:30 | 6/29/98 10:38 | 2480 | 0 | 2926 Kellogg St. | San Diego | SD | 92106 | 8" VC | One | Roots | Partial root stoppage | Relieve stop on 8" vc main | Y | Y | Storm Drain | San Diego Bay | Pacific Ocean | Y | Y | Y | Three | N/A
97-8-0008 | FAXED | 12:30PM | Marc Avila | 949-487-1097 | CBWD | Jun.12,12:30pm | Jun.12,12:50pm | 200 | 0 | Fortuna | Capistrano Beach | OR | 92624 | Manhole | 1 | blockage | Roots in line | Jetted line clear,continue preventative maintenance schedule | N | Y | Storm Drain | N/A | Dissipated in storm drain | N | N/A | N/N | N/A
978041 | Called County Health | 5/2/1998 2400 | Joe Sanchez | 760-839-4347 | City of Escondido | 5/1/1998 900 | 5/2/98 200 | 480 Gallons | 480 Gallons | 510 W. Valley Pkwy. | Escondido | SD | 92025 | Private Cleanout | 0 | Private C.O. | Unknown | Plumber cleared blockage. They also made a service lateral repair. | Y | Y | Storm Drain | Escondido Creek | San Elijo Lagoon | Y | Y | N | N/A | No Samples taken.
978042 | Faxed | 5/7/98 1245 | Lance Lauricha | 760-839-4347 | City of Escondido | 5/7/98 630 | 5/7/98 930 | 9,000 Gallons | 100 Gallons | 475 N. Midway | Escondido | SD | 92026 | Sewer Atlas page 310 Manhole 3266 | 0 | Grease | Excessive grease build-up in main line. | The main line was cleaned and scheduled for CCTV inspection. | Y | Y | Storm Drain | Escondido Creek | San Elijo Lagoon | Y | Y | Y | 4 Days | Samples were taken.
978043 | Called/Faxed | 5/11/98 930 | Lance Lauricha | 760-839-4347 | City of Escondido | 5/9/98 800 | 5/9/98 916 | 3,800 Gallons | 0 | Lincoln and Beech | Escondido | SD | 92026 | Sewer Atlas page 308 Manhole 3077 | 1 | Grease/Debris | Excessive grease build-up in main line. | The main line was cleaned and is scheduled to be upgraded in fiscal year 98-99. Also the Pretreatment Inspector was notified and conducted an investigation. | Y | Y | Storm Drain | Escondido Creek | San Elijo Lagoon | Y | Y | Y | 3 Days | Samples were taken.
978044 | Called/Faxed | 5/14/98 1245 | Lance Lauricha | 760-839-4347 | City of Escondido | 5/13/98 1500 | 5/14/98 1200 | 31,500 Gallons | 0 | 1555 Auto Pkwy. | Escondido | SD | 92027 | Sewer Atlas page 385 Manhole 4228 | 0 | Petroleum grease | Solids and petroleum products formed stoppage in main line. | Pretreatment Inspector was notified and investigated. We plan to continue routine maintenance. | Y | Y | Storm Drain | Escondido Creek | San Elijo Lagoon | Y | Y | Y | 5 Days | Samples were taken.
978045 | Called/Faxed | 5/28/98 1330 | Lance Lauricha | 760-839-4347 | City of Escondido | 5/28/98 945 | 5/28/98 1145 | 8,400 Gallons | 100 Gallons | 475 N. Midway | Escondido | SD | 92026 | Sewer Atlas page 310 Manhole 3266 | 1 | Grease | Excessive grease build-up in main line. | Main line was cleaned, televised, and is currently on a three month cleaning schedule. The Pretreatment Inspector was notified. Public notices were distributed to three apartment complexes in an effort to educate the residents on how grease effects the co | Y | Y | Storm Drain | Escondido Creek | San Elijo Lagoon | Y | Y | Y | 3 Days | Samples were taken.
977994 | Fax 571-6972 | 02/21/98 13:00 | J.Oropeza | 6544160 | City of San Diego | 02/21/98 10:28 | 02/21/98 11:50 | 82 | 0 | 7590 Windy Ridge Rd. | San Diego | SD | 92126 | 8" PVC | One | Other | Sand & Rocks | Refer to area supervisor to possibly add to PM schedule | N | Y | Storm drain | Los Penasquitos Canyon Preserve | Soaked into canyon | Y | N | N
978008 | Fax 571-6972 | 02/21/98 17:35 | J.Oropeza | 6544160 | City of San Diego | 02/21/98 14:40 | 02/21/98 16:00 | 80 | 30 | 3504 La Cima Dr. | San Diego | SD | 92109 | 8" VC | One | Roots | Heavy grease and roots | Refer to area supervisor to add to PM site | Y | Y | Storm drain | Mission Bay | Mission Bay/Storm Drain | Y | N | Y | Unknown
987963 | Fax 571-6972 | 4/16/98 20:50 | J. Wilder | 654-4160 | City of San Diego | 4/16/98 16:15 | 4/16/98 18:25 | 390 | 0 | 1665 Sunset Cliffs Bl. | San Diego | SD | 92107 | 6" VC sewer main | One | Grvty Mn Brk | Main break causing sewer to seep up through street | Rod main to open flow until repairs are made | Y | Y | Storm Drain | Pacific Ocean | N/A | Y | N | N | N/A | N/A
967 -004 | Whitney Ghoram | 1997-12-13 11:55 | Renzo Marin | (714) 837-7050 | El Toro Water District | 1997-12-13 09:15 | 1997-12-13 16:55 | 225,660 GAL. | 94,660 GAL. | 24206 Twig st. and 25121 Charlinda | Mission Viejo | OR | 92691 | 12” Force main and Freeway Sta. MH-5 | 4 | 12” Force main break. | 12" Freeway force main was cracked by tree roots growing around the pipeline. | Performed permanent repairs of pipeline break. Built containment area for sewage spill and recovery. Diluted spill with potable water. Cleaned and wash down area. | Y | Y | Storm drain and Aliso creek | Aliso creek | OCEAN | Y | Y | Y | N/A | Notified all responsible agencies and mailed discharge report.
967 -004 | Whitney Ghoram | 1997-12-13 11:55 | Renzo Marin | (714) 837-7050 | El Toro Water District | 1997-12-13 09:15 | 1997-12-13 16:55 | 225,660 GAL. | 94,660 GAL. | 24206 Twig st. and 25121 Charlinda | Mission Viejo | OR | 92691 | 12” Force main and Freeway Sta. MH-5 | 4 | 12” Force main break. | 12" Freeway force main was cracked by tree roots growing around the pipeline. | Performed permanent repairs of pipeline break. Built containment area for sewage spill and recovery. Diluted spill with potable water. Cleaned and wash down area. | Y | Y | Storm drain and Aliso creek | Aliso creek | OCEAN | Y | Y | Y | N/A | Notified all responsible agencies and mailed discharge report.
956158 | Fax 571-6972 | 10/29/97 06:25 | Whelan | 6544160 | City of San Diego | 10/28/97 15:00 | 10/28/97 20:00 | 75 | 0 | 5959 Cornerstone Ct. | San Diego | SD | 92121 | 10" PVC sewer main | 1 | Roots | Roots | Removed roots, rodded main | Y | Y | Storm drain in parking lot |  | Dried up in storm drain | Y | N | N
951223 | Fax 571-6972 | 10/02/97 15:30 | Davis | 6544160 | City of San Diego | 10/02/97 12:12 | 10/02/97 13:15 | 600 | 260 | 7751 Mission Gorge Rd./drainage ditch n. | San Diego | SD | 92120 | 8" VC Sewer Main | 1 | Roots | Tree Roots | Rodded 8" vc main | N | Y | Storm Drain North of Mission Gorge | San Diego River | Storm Drain and Drainage Ditch | Y | N/A | N
978-015 | SIRT (FAX) | 1998-05-14 13:00 | Brad Bruington | 949-831-1070 | Moulton Niguel Water | 1998-05-14 09:15 | 1998-05-14 09:30 | 100 | 0 | David Phillips Buick - 24888 Alicia Parkway | Laguna Hills | OR | 92653 | 6" gravity sewer | 1 | Debris, grease, blockage | heavy grease build-up on flat area of gravity sewer line. | Unknown - private sewer - not District's responsibility | Y | Y | Storm drain to Aliso Creek | Pacific Ocean | N/A | Y | N | N
978046 | Voice Mail | 05/31/98 1950 | Jeremy Kemp | 760/966-7868 | Water Utilities Dept. City of Oceanside | 05/31/98 1147 | 05/31/98 1830 | 18000 | 4000 | 770 Capistrano Drive | Oceanside | SD | 92054 | Manholes | 0 | Vandalism | "kids" or "homeless" removed manhole cover and dropped 5 buckets of rocks into the channel. Manhole is in remote easement, down by river. | Supervisor is ordering "locking" manhole covers to be installed, ASAP. | Y | Y | Storm Drain. | San Luis Rey River | N/A | Y | Y | Y | 2 | Posted temporary signs at river mouth. Additional samples were ordered from Lab.
978028 | KATHY STONE-FAX | 4/21/98-3:45 P | PAT GUEVARA | 760-438-2722 | CARLSBAD | 4/17/98-1:00 P | 4/17/98-1:35 P | 100 | 100 | 1860 MARRON RD. | CARLSBAD | SD | 92008 | PRIV. MANHOLE | 1 | GREASE | GREASE TRAP POSSIBLY NOT SERVICED ADEQUATELY | GREASE TRAPS SHOULD BE CHECKED ONCE A WEEK BY RESPONSIBLE PARTY | Y | Y | STORM DRAIN/CULVERT | NONE | VACTOR TRUCK RECOVERED | Y | N | N | N | DISINFECTED AREA.
951051 | Fax 571-6972 | 10/01/97 14:44 | Graham | 6544160 | City of San Diego | 10/01/97 09:15 | 10/01/97 09:25 | 100 | 50 | 2799 Carleton St. | San Diego | SD |  | MH # 71 | 1 | Grease | Grease Blockage in 27" Main | Relieved grease stop, vacuumed sewage from street, flushed lines | Y | Y | Storm Drain/SD harbor |  |  | Y | N/A | Y
978030 | Quarterly Report only County Health was notified. | 2/13/98 930 | Todd Anderson | 738-4347 | City of Escondido | 2/13/98 930 | 2/13/98 1000 | 30 Gallons | 0 | Amarillo and Brotherton | Escondido | SD | 92025 | Manhole, Sewer Atlas Page 468 MH. 4617 | 0 | Grease | Grease blockage in main line. | Continue routine maintenance. | Y | Y | Storm system | Felectia Creek | Lake Hodges | Y | N | N | N/A | No samples taken.
957136 | Fax 571-6972 | 11/03/97 10:45 | Richardson | 6544160 | City of San Diego | 11/03/97 09:30 | 11/03/97 09:50 | 20 | 0 | 5940 University Av. | San Diego | SD | 92115 | 6" VC | 1 | Roots | Roots and grease | Rodded to relieve stop | Y | N | Street | N/A | Dried in the street | Y | N/A | N
968920 | Fax 571-6972 | 12/31/97 13:00 | Richardson | 6544160 | City of San Diego | 12/31/97 09:15 | 12/31/97 09:35 | 20 | 20 | 893 Leppert St. | San Diego | SD | 92113 | 8" VC | 1 | Roots | Roots | Rodded 8" pvc main, recovered total volume of spill | Y | N | Street and curb |  | Dried up in the street | Y | N/A | N
978-017 | SIRT (FAX) | 1998-06-25 10:00 | Brad Bruington | 949-831-1070 | Moulton Niguel Water | 1998-06-25 08:00 | 1998-06-25 08:20 | 200 | 0 | Moulton Pkwy. & Crown Valley Pkwy. | Laguna Niguel | OR | 92677 |  | 1 | Grease, blockage | Partial blockage of 8" sewer - cause unknown | Line jetted and will be inspected with video camera. | Y | Y | Sulphur Creek | Lake at Laguna Niguel Regional Park | N/A | N | N | N/A
978-016 | SIRT (FAX) | 1998-06-15 16:35 | Brad Bruington | 949-831-1070 | Moulton Niguel Water | 1998-06-15 14:30 | 1998-06-15 16:30 | 9000 | 0 | County regional park - La Paz Road | Laguna Niguel | OR | 92677 | Recycled water line | 1 | Line break | Sprinkler line in regional park broke in stream. | Closed main valves. Line will be repaired. | Y | N | Sulphur Creek/Aliso Creek | Pacific Ocean | N/A | Y | Y | ? |  | O.C. Health Dept. handles this.
968519 | Fax 571-6972 | 12/29/97 14:45 | Hernandez | 6544160 | City of San Diego | 12/29/97 10:08 | 12/29/97 11:35 | 80 | 0 | Brighton Av. & Long Branch Av./alley | San Diego | SD |  | 6" VC | 1 | Roots | Roots | Relieved stop on 6" vc main | N: Y; None: Surface street/curb; None: Pacific Ocean; Y: Y; N: N
948590 | Fax 571-6972 | 09/20/97 19:23 | Branco | 6544160 | City of San Diego | 09/20/97 15:52 | 09/20/97 18:08 | 260 | 0 | 6320 Potomac St. | San Diego | SD | 92139 | 8" vc main | 1 | Grease | Grease blockage | Vacuumed/flushed 8" vc main, ref for MC site | y | y | Sweetwater River | San Diego Bay | dried in storm drain | y | n | n
949948 | Fax 571-6972 | 09/26/97 19:48 | Branco | 6544160 | City of San Diego | 09/26/97 15:35 | 09/26/97 18:30 | 875 | 0 | 6528 Bougainvillea Rd. | San Diego | SD | 92139 | 8" vc main | 1 | Grease | Grease blockage | Machine rodded 8" vc main | y | y | Sweetwater River | San Diego Bay |  | y | n | n
972765 | Fax 571-6972 | 01/25/98 21:12 | D.Branco | 6544160 | City of San Diego | 01/25/98 12:41 | 01/25/98 18:10 | 1645 | 0 | 4310 Mt. Elbrus Ct. | San Diego | SD | 92117 | 8" VC | One | Roots | Roots | Hand rodded main/refer to area supervisor for scheduled PM | Y | N | Tecolate Canyon | Mission Bay/Pacific Ocean | Canyon Floor | Y | Y | N
935540 | Fax 571-6972 | 07/24/97 13:30 | Parker | 6544160 | City of San Diego | 07/22/97 20:11 | 07/22/97 21:41 | 1165 | 350 | 3510 Auburndale St. | San Diego | SD | 92111 | 8" vc main | 1 | Roots | Heavy roots | Rodded 267' of 8" vc main | y | y | Tecolote Creek | Mission Bay |  | y | y | n
937419 | Fax 571-6972 | 07/31/97 09:45 | Parker | 6544160 | City of San Diego | 07/29/97 21:40 | 07/29/97 23:02 | 852 | 0 | 6434 Camto. Listo | San Diego | SD | 92111 | 8" pvc main | 1 | Grease | Grease blockage | Relieved stop, ref. for stepped-up PM, ref. for TV | y | y | Tecolote Creek | Mission Bay | soaked into hillside | y | n | n
944931 | Fax 571-6972 | 09/03/97 14:00 | Parker | 6544160 | City of San Diego | 09/03/97 10:05 | 09/03/97 11:35 | 180 | 0 | Tecolote Canyon Park 1/2 mi. e. of gate | San Diego | SD | 92109 | 10" vc main | 1 | Roots | Root blockage | Cleared stop, ref. for poss. MC site | y | n | Tecolote Creek | Mission Bay |  | y | n | n
980722 | Fax 571-6972 | 03/11/98 09:00 | W.Payne | 6544160 | City of San Diego | 03/09/98 12:00 | 03/09/98 12:36 | 3600 | 3400 | 4177 Mt Ashmun Dr. | San Diego | SD | 92111 | 15"VC | One | Grvty Mn Brk | Soil erosion caused rocks to break main | Pipe repaired and backfilled | Y | N | Tecolote Creek |  |  | Y | Y | N
| Mr. Chang | 1998-05-06 10:00 | Anne Briggs | (909) 928-3777 | E.M.W.D. | 1998-05-06 08:03 | 1998-05-06 08:26 | 4025 | None | Overland Trail & Redhawk Parkway | Temecula | Riverside | 92590 | Manhole | 3 | Obstruction | Construction Debris - Plastic Sheeting in Pipe | Remove debris from line and will perform inspections of the area to determine source of construction debris | Y | Y | Temecula Creek | Santa Margarita River |  | Y | N | N | N/A | All solids were picked up
978001 | 619 571-6972 | 970801 0800 | City of Laguna Beach | 714 497-0765 | Laguna Beach | 970801 0800 | 970801 0830 | 1000 | 1000 gals. | Temple Hills Drive | Laguna Beach | Orange | 92651 | Temple Hills Drive Manhole #69 | 1 | Roots/Rocks | Main Line was blocked with debris | Main Line jetted/vacuumed to remove | No | No | Temple Hills Dr./Storm Drain | None | Temple Hills Drive | No | No | No |  | The main was jetted/vacuumed to remove all debris and a T.V.
978004 | JOHN PHILLIPS | 6/11/1998 8:00AM | KRIS HANBERG | 949/858-4979 | TCWD | 6/10/98 12:00PM | 6/10/98 2:00PM | 24000 | 0 | VIA ALEGRE | TRABUCO CANYON | OR | 92679 | VIA ALEGRE LIFT STATION #04 | 0 | INFILTRATION | CONTRACTORS FLUSHED FIRE HYDRANT INTO SEWER LINE CAUSING HYDRAULIC OVERLOAD TO LIFT STATION | HAD CONTACTED THE CONTRACTOR INSTRUCTED HIM TO STOP AND INFORMED HIM THAT THIS WAS NOT PROPER PROCEDURE | Y | Y | TIJERAS CREEK | OCEAN |  | Y | Y | Y |  | HEALTH DEPT CLOSED BEACH
978001 | FAX | 11/21/97 @ 18:45 | Cheryl Neal | 619-423-8311 | City of Imperial Beach | 11/21/97 @ 15:33 | 11/21/97 @ 16:00 | <50 | 0 | 542 Elm Avenue | Imperial Beach | SD | 91932 | MH #85 | 0 | Blockage in main | Blockage in main line. | Cleaned up w/vactor but <50 gallons went into stormdrain. Check main line regularly. | Y | Y | Tijuana Estuary | N/A | Tijuana Estuary | Y | N | N | N/A
978002 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-27-97 | 08-27-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 1 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978003 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-30-97 | 08-30-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 2 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978004 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 08-31-97 | 08-31-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 3 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978005 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-04-97 | 09-04-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 4 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978006 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-05-97 | 09-05-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 5 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978007 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-06-97 | 09-06-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 6 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978008 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-07-97 | 09-07-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 7 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978009 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-10-97 | 09-10-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 8 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978010 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-12-97 | 09-12-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 9 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978011 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-13-97 | 09-13-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 10 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978012 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-14-97 | 09-14-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 11 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978013 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-15-97 | 09-15-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 12 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978014 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-16-97 | 09-16-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 13 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978015 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-17-97 | 09-17-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 14 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978016 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-18-97 | 09-18-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 15 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978017 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-19-97 | 09-19-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 16 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978018 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-20-97 | 09-20-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 17 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978019 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-25-97 | 09-25-97 |  | 0 | 5000 Monument Road | San Diego | SD | 92173 | Stewarts Drain | 1 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978020 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-25-97 | 09-25-97 |  | 0 | International Border | San Diego | SD | 92154 | Silva Drain | 1 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978021 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-25-97 | 09-25-97 |  | 0 | International Border | San Diego | SD | 92154 | Canyon del Sol | 1 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978022 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-25-97 | 09-25-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 18 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978023 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-26-97 | 09-26-97 |  | 0 | 5000 Monument Road | San Diego | SD | 92173 | Stewarts Drain | 2 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978024 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-26-97 | 09-26-97 |  | 0 | International Border | San Diego | SD | 92154 | Canyon del Sol | 2 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978025 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-26-97 | 09-26-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 19 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978026 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-27-97 | 09-27-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 20 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978027 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-28-97 | 09-28-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 21 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
978028 | N/A | N/A | Dion McMicheaux | 6196627600 | IBWC | 09-29-97 | 09-29-97 |  | 0 | International Border | San Diego | SD | 92173 | Tijuana River | 22 | other | overload of collection system |  | Y | N | Tijuana River | None |  | N | N | N
971580 | Fax 571-6972 | 01/16/98 19:00 | J.McPherson | 6544160 | City of San Diego | 01/16/98 13:30 | 01/16/98 14:15 | 450 | 0 | Roselle St. & Sorrento Valley Bl.** | San Diego | SD | 92121 | 24" Plug | One | Force Main Brk | Leak on 24" plug at end of force main | Shut off force main/pumping through new #65 Station | Y | Y | Torrey Pines State Reserve | Pacific Ocean |  | Y | N | N
978001 | FAX | 1997-12-20 | Dave Seymour | 714 459-6540 | SMWD | 12/20/97 10:00am | 1997-12-20 17:00 | 900 gal | 0 | Seacountry Lane | Rancho Santa Margarita | OR | 92688 | Manhole | 0 | Construction debri | Construction debri, rocks, wood and mud blocked downstream of manhole causing spill | Removed debri, vactored solids and cleaned section of line effected by blockage | y | y | Trabuco Creek |  |  | Y | Y | N |  | Contained spill upon arrival, washed down area with chlorine solution and vactored remaining spill
| SIRT (Attn:Gloria Fulton) | 1997-10-03 16:45 | James E. Smith | 714-448-4053 | Moulton Niguel Water | 1997-10-03 11:00 | 1997-10-03 14:00 | 32000 | 0 | End of Alipaz | San Juan Capistrano | OR | 92675 | 3A Effluent Pipeline | 1 | Construction | Grading contractor for Pepper Tree Estates hit the effluent pipeline that transports secondary effluent to the Chiquita Land Outfall. The pipeline fracture was on the side of the pipe, causing a hole 3" wide X 6" long. | Effluent was contained on the site, however, the majority escaped to Trabuco Creek. | Y | N | Trabuco Creek | San Juan Creek | NA | Y | N | N | N/A
| SIRT (FAX) | 1998-02-25 | Brad Bruington | 714-425-3514 | Moulton Niguel Water | 1998-02-24 08:00 | 1998-02-25 12:30 | 3000000 | 0 | Camino Capistrano/Junipero Serra | San Juan Capistrano | OR | 92675 | 39" pipeline | 1 | Line break | Trabuco Creek broke 39" concrete-encased sewer line under creek | Bypass pipe and put pumps in place. Was in place and operational by 2/25/98 14:00 hours | Y | N | Trabuco Creek | Pacific Ocean | N/A | Y | Y | Y | TBD | O.C. Health Dept. is sampling and posting beaches.
978001 | LINDA PARDY, VOICE MAIL | 1/24/97 0930 | CUSTOMER | NO PHONE | TCWD | 9/24/97 0915 | 1/24/97 1000 | 8000 | 0 | PLANO/ SANTA MARGRETTA | TRABUCO CANYON | OR | 92679 |  | 1 | BLOCKAGE | BLOCKAGE IN BYPASS TO SMWD | UNCLOGGED BLOCKAGE | Y | Y | TRABUCO CREEK | SAN JUAN CREEK | OCEAN | Y | N | Y | 2 HOURS | NONE
978003 | Fax | 1998-05-04 11:00 | Dave Seymour | 9494596540 | Santa Margarita Water District | 1998-05-04 06:00 | 1998-05-04 07:45 | 600 | 150 | Seacountry Lane | Rancho Santa Margarita | OR | 92688 | Manhole | 2 | Construction | Construction debris plugged line. |  | Y | Y | Trabuco Creek | None | N/A | Y | Y | N | N/A
978-013 | SIRT (FAX) | 1998-04-04 | Brad Bruington | 949-831-1070 | Moulton Niguel Water | 1998-04-04 10:00 | 1998-04-04 13:00 | 75000 | 0 | Camino Capistrano/Juniper Serra | San Juan Capistrano | OR | 92675 |  | 2 | Line break/flood damage | Unknown pump or increased sewer flow problem at temporary pump station at Trabuco Creek sewer line break. | More flow diverted above pump station and all pumps checked for proper operation. | Y | N | Trabuco Creek | Pacific Ocan | N/A | Y | Y | Y |  | O.C. Health Dept. handles this
972858 | Fax 571-6972 | 01/26/98 16:10 | L.Finch | 6544160 | City of San Diego | 01/26/98 12:40 | 01/26/98 13:30 | 150 | 100 | 1694 Main St. | San Diego | SD | 92113 | 6" CP | One | Rocks | Rocks | Clean area and re-evaluate cleaning schedule | Y | N | Vactored street | San Diego Bay |  | Y | N | N
936631 | Fax 571-6972 | 07/26/97 15:51 | Branco | 6544160 | City of San Diego | 07/26/97 09:38 | 07/26/97 12:30 | 86 | 0 | 6102 La Pintura Dr. | San Diego | SD | 92037 | 8" vc main | 1 | Roots | Root blockage | Machine rodded 8" vc main | y | n | Van Nuys canyon | Pacific Ocean |  | y | n | n
976068 | Fax 571-6972 | 02/17/98 08:00 | W.Payne | 6544160 | City of San Diego | 02/09/98 20:10 | 02/10/98 12:00 | 23500 | 0 | 1000 Van Nuys St./canyon | San Diego | SD | 92109 | 8" VC | One | Grvty Mn Brk | Rains washed out pipe causing rocks in main | Repaired main/pumped & cleaned ponded areas back into system | Y | Y | Van Nuys Canyon | Storm Drain | Pacific Ocean | Y | Y | N
985240 | Fax 571-6972 | 03/31/98 20:50 | R.Parker | 6544160 | City of San Diego | 03/31/98 14:30 | 03/31/98 18:38 | 248 | 0 | Paseo Bonita & Rutgers Rd./canyon | San Diego | SD | 92037 | 8" VC | One | Roots | Roots | Hand rodded manhole to relieve stop | Y | Y | Van Nuys Canyon | Storm Drain/Pacific Ocean |  | Y | N | N
977272 | Fax 571-6972 | 02/19/98 10:00 | R.Parker | 6544160 | City of San Diego | 02/17/98 17:34 | 02/18/98 16:04 | 27000 | 3600 | 1000 Van Nuys St./canyon | San Diego | SD | 92109 | 8" VC | Two | Grvty Mn Brk | Line washed away causing rocks in pipe | Rodded main and made repairs | Y | Y | Van Nuys Canyon creek/Storm Drain | Pacific Ocean |  | Y | Y | Y | Unknown
985728 | Fax 571-6972 | 4/02/98 12:45 | R. Parker | 654-4160 | City of San Diego | 4/01/98 17:58 | 4/02/98 08:55 | 26910 | 17850 | Cass St. & Van Nuys St./canyon | San Diego | SD | 92109 | 8" VC sewer main | Three | Vandalism | Vandals opened manhole; filled with rocks | Used fork/tools to remove rocks from manhole; recvr'd part of spill | Y | Y | Van Nuys Creek | Storm Drain | Pacific Ocean | Y | Y | Y | Unknown | 5 signs posted
977001 | Voice Mail | 7/10/97 1330 PM | Mike M. Calvert | 9096764101 | Rancho California Water District | 7/10/97 0700 AM | 7/10/97 0745 AM | 2250 | 0 | Washington & Brown | Murrieta | RV | 92562 | 24" CML-CMC pipe | 1 | Vandalism | A new 12" valve was put on a 24" line and during the night vandals opened the line.
978001 | KATHY STONE-FAX | 7/14/97-2:00P | PAT GUEVARA | 438-2722 X134 | CARLSBAD MWD | 7/14/97-8:30A | 7/14/97-9:30 A | 60 | 30 | SHUTTLE RD/FINCH/KINGFISHER | CARLSBAD | SD | 92009 | MANHOLE | 2 | ROCKS/DEBRIS/BLOCKAGE |  | ROUTINELY CHECK MANHOLES IN AREA DURING CONSTRUCTION PERIOD | N | N |  |  | 1/2 WAS VACTORED UP, REMAINING FLOWED TO DIRT PILES | Y | N | N | N/A | DISINFECTED AREA. AREA STILL UNDER CONSTRUCTION.
978002 | N/A | N/A | N/A | N/A | PRIVATE | 7/22/97-12:00 P | 7/22/97-2:00 P | 1 TO 5 | 0 | 3180 CANYON | CARLSBAD | SD | 92008 | CLEANOUT | 1 | UNKNOWN BLOCKAGE |  |  | N | N |  |  | SEWER CLEANOUT AREA | N | N | N | N/A | DISINFECTED AREA.
978004 | N/A | N/A | N/A | N/A | PRIVATE | 8/11/97-8:00 A | 8/11/97-9:00A | 1 TO 5 | 0 | 7260 MIMOSA DR. | CARLSBAD | SD | 92009 | CLEANOUT | 3 | UNKNOWN BLOCKAGE |  | USED RODDING MACHINE TO CLEAR STOPPAGE. T.V. INSPECTED LATERAL. WILL SCHEDULE FOR LATERAL REPLACEMENT | N | N |  |  | SEWER CLEANOUT AREA | N | N | N | N/A | DISINFECTED AREA.
978005 | N/A | N/A | N/A | N/A | PRIVATE | 8/13/97-7:00 P | 8/13/97-9:30 P | 5 TO 10 | 0 | 3883 WOODVALE | CARLSBAD | SD | 92008 | CLEANOUT | 1 | ROOTS & HAIR |  | USED RODDING MACHINE TO CLEAR STOPPAGE | N | N |  |  | SEWER CLEANOUT AREA | N | N | N | N/A | DISINFECTED AREA.
978006 | N/A | N/A | N/A | N/A | PRIVATE | 8/19/97-4:40 P | 8/19/97-6:15 P | 2 | 0 | 330 REDWOOD | CARLSBAD | SD | 92008 | CLEANOUT | 1 | UNKNOWN BLOCKAGE |  | USED DRAIN KING TO CLEAR STOPPAGE | N | N |  |  | SEWER CLEANOUT AREA | N | N | N | N/A | DISINFECTED AREA
978007 | N/A | N/A | N/A | N/A | PRIVATE | 9/16/97-8:15 P | 9/16/97-10:00P | 1 TO 2 | 0 | 2074 AVE OF THE TREES | CARLSBAD | SD | 92008 | CLEANOUT | 1 | UNKNOWN BLOCKAGE |  | USED RODDING MACHINE TO CLEAR STOPPAGE | N | N |  |  | SEWER CLEANOUT AREA | N | N | N | N/A | DISINFECTED AREA
978001 | VOICE MAIL | 7/07/97 11:00AM | ROBERT BRAUN | (619) 874-4087 | COUNTY OF SAN DIEGO | 7/04/97 4:15PM | 7/4/97 5:00PM | 300 | NONE | 604 GALAPAGO ST. | SPRING VALLEY | SD | 91977 | MANHOLE COVER | 0 | GREASE | GREASE BUILDED UP IN 8 INCH. SEWER MAIN CAUSING SEWER TO BACK UP IN MANHOLE | SEWER LINE WILL GO ON SPECIAL MAINTENANCE - RODDED 4 TIMES A YEAR | N | Y |  | SWEETWATER RIVER | OCEAN | Y | N | N | NONE | LINE NOW ON SPECIAL MAINTENANCE 4 TIMES YEAR
978002 | VOICE MAIL | 8/23/97 930A | ROBERT BRAUN | (619) 874-4082 | CO OF SAN DIEGO | 8/23/97 0930 | 8/23/97 1015A | 750 | NONE | 4306 VISTA WAY | SP VALLEY | SD | 91977 | MANHOLE COVER | 0 | ROOTS | ROOTS BLOCKING OUTLET SIDE OF MANHOLE | SPECIAL MAINTENANCE, CLEAN 4 TIMES YEARLY | N | N |  |  | DRY CREEK | Y | N | N | NONE | SPECIAL MAINITENANCE
931472 | Fax 571-6972 | 07/01/97 10:31 | Gensler | 6544160 | City of San Diego | 07/01/97 07:40 | 07/01/97 09:05 | 170 | 0 | Calamar Dr. & Inverno Dr. | San Diego | SD | 92124 | 8" vc main | 1 | Roots | Root blockage | Rodded/flushed 2 sections | n | n |  |  | dissipated in storm drain | y | n | n
931567 | Fax 571-6972 | 07/02/97 03:59 | Whelan | 6544160 | City of San Diego | 07/01/97 14:33 | 07/01/97 20:30 | 714 | 180 | 1552 Tarbox St. | San Diego | SD | 92114 | 8" vc main | 1 | Grease | Grease blockage | Rodded, vacuumed overflow | n | n |  |  | dried in gutter | y | n | n
931583 | Fax 571-6972 | 07/02/97 03:57 | Whelan | 6544160 | City of San Diego | 07/01/97 16:09 | 07/01/97 17:09 | 120 | 0 | 1712 Gateway Dr. | San Diego | SD | 92105 | 8" vc main | 1 | Roots | Root blockage | Rodded main, ref for MH location | N: n; N: n; N/A: dried in gutter; Y: y; Y: n
931620 | Fax 571-6972 | 07/03/97 03:53 | Whelan | 6544160 | City of San Diego | 07/02/97 15:50 | 07/02/97 16:30 | 24500 | 7000 | 3296 Talbot St. | San Diego | SD | 92106 | 8" cp main | 2 | Grvty Mn Brk | Gravity Main Break | Rodded main, ref for televising | N: n; N: n; N/A: back into manhole; Y: y; Y: n
931702 | Fax 571-6972 | 07/02/97 16:12 | Gensler | 6544160 | City of San Diego | 07/02/97 12:26 | 07/02/97 14:26 | 60 | 0 | 6218 Calle Empinada Dr. | San Diego | SD | 92120 | 8" vc main | 1 | Roots | Root stop in MH #138 | Rodded/flushed to relieve stop | y | y |  | Pacific Ocean | dried in storm drain | y | n
931705 | Fax 571-6972 | 07/02/97 15:00 | Richardson | 6544160 | City of San Diego | 07/02/97 13:29 | 07/02/97 14:20 | 51 | 20 | 3312 Madison Av. | San Diego | SD | 92116 | 6" vc main | 1 | Construction | So-Cal Constr. broke off 200' of PVC in main | Flushed to relieve, retrieve pipe | N: n; N: n; N/A: dried at curb; Y: y; Y: n
931793 | Fax 571-6972 | 07/03/97 03:30 | Whelan | 6544160 | City of San Diego | 07/02/97 18:57 | 07/02/97 20:30 | 490 | 0 | Florida St. & Lincoln Av. | San Diego | SD | 92104 | 8" vc main | 1 | Grease | Grease caused blockage | Flushed to relieve stop | y | y |  | Pacific Ocean | dried in storm drain | y | n
933103 | Fax 571-6972 | 07/10/97 14:20 | Galinzoga | 6544160 | City of San Diego | 07/10/97 10:57 | 07/10/97 11:22 | 250 | 0 | 8540 Camino Santa Fe** | San Diego | SD | 92121 | 10" pvc main | 1 | Other | Bubbler failure @ P.S. #51 | Repaired failed bubbler on PS #51 | y | y |  | Pacific Ocean | Dissipated in storm drain | y | n
933617 | Fax 571-6972 | 07/13/97 13:52 | Branco | 6544160 | City of San Diego | 07/13/97 09:10 | 07/13/97 11:45 | 465 | 0 | 4910 Pacifica Dr. | San Diego | SD | 92109 | 8" vc main | 1 | Roots | Heavy roots caused blockage | Machine rodded 8" vc main to remove heavy roots | N: n; N: y; N/A: Interceptor V760; Y: y; Y: n
936410 | Fax 571-6972 | 07/26/97 08:00 | Mickelson | 6544160 | City of San Diego | 07/25/97 11:00 | 07/25/97 17:00 | 90 | 0 | 3205 Edith Ln. | San Diego | SD | 92106 | 6" cp main | 1 | Roots | Root blockage | Vacuumed manhole on 6" cp main | n | n |  |  | soaked into ground | y | n | n
937041 | Fax 571-6972 | 07/29/97 03:58 | Whelan | 6544160 | City of San Diego | 07/27/97 13:00 | 07/28/97 20:50 | 5730 | 200 | 7258 Romero Dr. | San Diego | SD | 92037 | 8" vc main | 1 | Roots | Root blockage | Rodded 8" vc main | y | y |  | Pacific Ocean | storm drain | y | y | n
937668 | Fax 571-6972 | 08/01/97 10:05 | Payne | 6544160 | City of San Diego | 07/31/97 06:00 | 07/31/97 10:30 | 5400 | 2000 | 11600 Flintkote Av. | San Diego | SD | 92121 | 6" ci main | 1 | Force Mn Brk | Break on 6" return line from surge tank | Repaired 6" ci main | n | n |  |  | holding pond | y | y | n
939925 | Fax 571-6972 | 08/11/97 15:00 | Davis,L | 6544160 | City of San Diego | 08/11/97 08:00 | 08/11/97 10:30 | 300 | 0 | Bernardo Center Dr. & Bernardo Center Ct. | San Diego | SD | 92128 | 8" vc main | 1 | Roots | Roots and grease in main | Rodded 8" vc main | y | y |  | Pacific Ocean | dried in storm drain | y | n | n
940384 | Fax 571-6972 | 08/13/97 06:15 | Whelan | 6544160 | City of San Diego | 08/12/97 17:40 | 08/12/97 18:25 | 90 | 80 | 4540 51st St. | San Diego | SD | 92115 | 6" cp main | 2 | Grease | Grease blockage | Rodded main to relieve stop, recovered most of spill | n | n |  |  | vacuumed some, rest soaked into ground | y | n | n
941809 | Fax 571-6972 | 08/21/97 04:30 | Whelan | 6544160 | City of San Diego | 08/20/97 15:14 | 08/20/97 18:33 | 50 | 0 | 2504 San Marcos St. | San Diego | SD | 92104 | 6" cp main | 1 | Roots | Roots in main | Hand rodded 6" cp main | n | n |  |  | soaked into ground | y | n | n
942010 | Fax 571-6972 | 08/22/97 05:25 | Whelan | 6544160 | City of San Diego | 08/21/97 22:51 | 08/22/97 01:13 | 2130 | 2130 | 1820 Midway Dr. | San Diego | SD | 92110 | 6" vc main | 1 | Grease | Grease stoppage | Flushed/vacuumed spill/rest captured by interceptor | y | y |  |  | Interceptor #10 | y | n | n
942030 | Fax 571-6972 | 08/22/97 14:00 | Finch | 6544160 | City of San Diego | 08/22/97 08:41 | 08/22/97 10:15 | 10 | 0 | Del Mar Av. & Guizott St. | San Diego | SD | 92107 | 6" cp main | 1 | Roots | Light roots | Removed stop (main scheduled for Group Job Replacement) | n | n |  |  | dried at curb | y | n | n
942041 | Fax 571-6972 | 08/22/97 12:30 | Parker | 6544160 | City of San Diego | 08/22/97 09:40 | 08/22/97 10:00 | 500 | 0 | Bonair St. & Tyrian St. | San Diego | SD | 92037 | 21" vc main | 1 | Construction | Contractor caused/bypass pumping | Washed street, posted signs, notified lifeguard | y | y |  | Pacific Ocean |  | y | n | n
943215 | Fax 571-6972 | 08/29/97 06:10 | Whelan | 6544160 | City of San Diego | 08/28/97 17:55 | 08/28/97 19:18 | 9 | 9 | 4146 33rd St. | San Diego | SD | 92104 | 8" vc main | 1 | Grease | Grease blockage | Rodded 8" vc main to relieve blockage | n | n |  |  | recovered from around manhole | y | n | n
946908 | Fax 571-6972 | 09/12/97 15:00 | Sackett | 6544160 | City of San Diego | 09/12/97 10:38 | 09/12/97 12:01 | 180 | 0 | I-163 & Laurel St. /under bridge | San Diego | SD | 92101 | 6" cp main | 2 | Debris | debris, deteriorating main | Cleared stop; this main scheduled for Group Job repl. | n | n |  |  | soaked into ground | y | n | n
946659 | Fax 571-6972 | 09/11/97 15:10 | Finch | 6544160 | City of San Diego | 09/11/97 09:28 | 09/11/97 11:28 | 240 | 0 | 4445 Logan Av. | San Diego | SD | 92113 | 6" vc main | 1 | Grease | Heavy grease | Cleared stop, ref. to FEWD | n | n |  |  | soaked into ground in dirt lot | y | n | n
947198 | Fax 571-6972 | 09/13/97 13:29 | Branco | 6544160 | City of San Diego | 09/13/97 07:30 | 09/13/97 08:50 | 80 | 0 | 14004 Rue St. Raphael | San Diego | SD | 92014 | 8" vc main | 1 | Roots | Root blockage | Machine rodded 8" vc main, ref. for MC site | y | y |  | Pacific Ocean |  | y | n | n
947242 | Fax 571-6972 | 09/14/97 20:16 | Branco | 6544160 | City of San Diego | 09/14/97 15:53 | 09/14/97 18:30 | 314 | 314 | 3769 Promontory St. | San Diego | SD | 92109 | 8" vc main | 1 | Grease | Grease, plastic bags | Rodded to clear stop; spill captured by interceptor V70 | n | y |  |  | Interceptor V-70 | y | n | n
948225 | Fax 571-6972 | 09/19/97 15:25 | Finch | 6544160 | City of San Diego | 09/19/97 09:54 | 09/19/97 10:34 | 80 | 60 | 4000 Santa Cruz Av. | San Diego | SD | 92107 | 6" cp main | 1 | Roots | Root blockage | Machine rodded to clear, recovered 60 gal. | N: n; N: n; N/A: dried in street; Y: n; Y: n
948287 | Fax 571-6972 | 09/19/97 19:49 | Branco | 6544160 | City of San Diego | 09/19/97 12:25 | 09/19/97 17:24 | 50 | 0 | 5620 Trinidad Wy. | San Diego | SD | 92114 | 6" cp main | 1 | Roots | Root blockage | Machine rodded 6" cp main, deodorize, ref. for MC site | n | n |  |  | soaked into ground | y | n | n
948742 | Fax 571-6972 | 09/23/97 02:48 | Parker | 6544160 | City of San Diego | 09/22/97 16:13 | 09/22/97 17:52 | 990 | 0 | 4735 Boxwood Dr./easement behind | San Diego | SD | 92117 | 10" vc main | 1 | Roots | Root blockage | Rodded to relieve stop | n | n |  |  | dried around manhole | y | y | n
948633 | Fax 571-6972 | 09/22/97 13:25 | Harris,L | 6544160 | City of San Diego | 09/22/97 09:35 | 09/22/97 11:05 | 45 | 45 | 2778 Treat St. | San Diego | SD | 92102 | 6" cp main | 3 | Grease | Grease blockage - heavy | Cleared stop on 6" cp main | y | y |  | Pacific Ocean | recovered from storm drain | y | n | n
949716 | Fax 571-6972 | 09/25/97 23:35 | Whelan | 6544160 | City of San Diego | 09/25/97 15:55 | 09/25/97 17:04 | 690 | 0 | 8353 Menkar Rd. | San Diego | SD | 92126 | 8" vc main | 1 | Grease | Grease blockage | Rodded 8" vc main to relieve stop | y | y |  | Pacific Ocean |  | y | n | n
950558 | Fax 571-6972 | 09/30/97 18:50 | Davis | 6544160 | City of San Diego | 09/29/97 09:00 | 09/30/97 13:30 | 17100 | 1000 | 9770 Carroll Centre Rd. | San Diego | SD | 92145 | 10" vc main | 1 | Grvty Main Brk | Blockage downstrm from main brk | Flushed 407' of 10" vc main | y | y |  | private pond |  | y | y | n
829971 |  |  |  |  | City of San Clemente | 8/29/97, 10:05 | 8/29/97, 10:25 | 50 gal | 0 | 110 Balboa | San Clemente | OR | 92672 | SMHD6624 | 0 | Roots |  |  | N | Y |  |  | Absorbed in Canyon Floor | N | N | N | NA
OCT-DEC '97
978002 | NO |  |  |  | City of Vista | 1997-10-06 16:00 | 1997-10-06 16:00 | <200 | 0 | 2525 Lupine Hills Drive | Vista | SD | 92083 | Shadowridge Water Reclamation Plant | Zero | Inadvertent valve closure | While draining the splitter box the surface drain valve was mistakenly closed discharging partially treated wastewater down the storm water drainage system | [10 empty] | The total area affected was less than square feet. It absorbed into the ground within minutes. | bar: N; Y to N
956452 | Fax 571-6972 | 10/30/97 15:20 | Finch | 6544160 | City of San Diego | 10/30/97 09:59 | 10/30/97 12:59 | 90 | 0 | 2600 Golf Course Dr. (hole #4) | San Diego | SD | 92102 | 6" CP | 1 | Grvty Mn Brk | Break in line | Relieved root blockage in broken main, ref. to constr. crew | N | N |  | San Diego Bay | Settle in canyon area | Y | N/A | N
957953 | Fax 571-6972 | 11/06/97 | West | 6544160 | City of San Diego | 11/06/97 14:15 | 11/06/97 15:00 | 23 |  | 989 Sunset Cliffs Bl.** | San Diego | SD |  |  | 1 | Surcharge | Main break | Discontinued bypass pumping into collapsed manhole | Y | N |  |  | Sand and dirt | Y | N | N
978008 | N/A | N/A | N/A | N/A | PRIVATE | 10/2/97-3:15 P | 10/2/97-4:30 P | LESS THAN 1 | 0 | 3190 CANYON | CARLSBAD | SD | 92008 | CLEANOUT | 1 | UNKNOWN |  | RODDED LATERAL TO CLEAR STOPPAGE | N | N |  |  | CLEANOUT | N | N | N | N/A | DISINFECTED AREA
978009 | N/A | N/A | N/A | N/A | CARLSBAD MWD | 10/6/97-12:30 P | 10/6/97-2:00 P | 10 | 10 | 2410 BUENA VISTA CR | CARLSBAD | SD | 92008 | DEAD-END CLEANOUT | 1 | UNKNOWN |  | CLEARED SEWER MAIN WITH VACTOR. | N | N |  |  | STREET SURFACE | N | N | N | N/A | DISINFECTED AREA
978010 | N/A | N/A | N/A | N/A | PRIVATE | 10/13/97-5:35 P | 10/13/97-7:10 P | 3 TO 5 | 0 | 2598 JEFFERSON | CARLSBAD | SD | 92008 | CLEANOUT | 1 | UNKNOWN |  | RODDED LATERAL TO CLEAR STOPPAGE | N | N |  |  | CLEANOUT | N | N | N | N/A | DISINFECTED AREA
978011 | N/A | N/A | N/A | N/A | CARLSBAD MWD | 11/6/97-3:11 P | 11/6/97-4:15 P | 1 TO 5 | 0 | PIO PICO,N OF TAMARACK | CARLSBAD | SD | 92008 | MANHOLE | 1 | GREASE |  | CLEARED SEWER MAIN WITH VACTOR. | N | N |  |  | STREET SURFACE | N | N | N | N/A | DISINFECTED AREA
978012 | N/A | N/A | N/A | N/A | CARLSBAD MWD | 11/7/97-2:49 P | 11/7/97-4:15 P | 1 TO 5 | 0 | 260 NORMANDIE | CARLSBAD | SD | 92008 | CLEANOUT | 2 | GREASE |  | RODDED MAIN LINE TO CLEAR STOPPAGE. MAIN LINE TOO SMALL FOR VACTOR. | N | N |  |  | STREET SURFACE | N | N | N | N/A | DISINFECTED AREA
978013 | N/A | N/A | N/A | N/A | CARLSBAD MWD | 11/8/97-2:30 P | 11/8/97-3:00 P | 20 | 0 | 5192 CARLSBAD BLVD. | CARLSBAD | SD | 92008 | MANHOLE | 1 | ROOTS/PLASTIC BAGS |  | CLEARED SEWER MAIN WITH VACTOR. | N | N |  |  | STREET SURFACE | N | N | N | N/A | DISINFECTED AREA
978014 | KATHY STONE-FAX | 11/18/97-4:30 P | PAT GUEVARA | 438-2722 X132 | CARLSBAD MWD | 11/16/97-10:30 A | 11/16/97-1:00 P | 120 | 0 | 3183 JEFFERSON | CARLSBAD | SD | 92008 | CLEANOUT | 1 | UNKNOWN |  | CLEARED SEWER MAIN WITH VACTOR. FLAT AREA IN MAIN LINE. WILL SCHEDULE TO CLEAN THIS LINE EVERY 6 MONTHS. | N | N |  |  | INSIDE APT. UNITS AND WALKWAY IN FRONT OF APTS. | Y | N | N | N/A | DISINFECTED AREA
978015 | N/A | N/A | N/A | N/A | PRIVATE | 11/24/97-8:30 A | 11/24/97-10:30 A | 1 TO 5 | 0 | 1271 TAMARACK | CARLSBAD | SD | 92008 | CLEANOUT | 1 | UNKNOWN |  | RODDED LATERAL TO CLEAR STOPPAGE | N | N |  |  | CLEANOUT | N | N | N | N/A | DISINFECTED AREA
978016 | KATHY STONE-FAX | 12/2/97-? | PAT GUEVARA | 438-2722 X132 | CARLSBAD MWD | 11/28/97-9:45 A | 11/28/97-11:15 A | 50 | 40 | TYLER & PINE | CARLSBAD | SD | 92008 | CLEANOUT | 1 | POSSIBLY GREASE |  | CLEARED SEWER MAIN WITH VACTOR. | N | N |  |  | EMPTY LOT ON TYLER | Y | N | N | N/A | DISINFECTED AREA
978017 | N/A | N/A | N/A | N/A | PRIVATE | 12/6/97-1:30 P | 12/6/97-1:55 P | 20 | 15 | 4205 CLEARVIEW | CARLSBAD | SD | 92008 | BATHROOMS INSIDE HOUSE | 2 | ROOTS |  | CLEARED LATERAL WITH RODDING MACHINE | N | N |  |  | BATHROOMS IN HOUSE | N | N | N | N/A | CUSTOMER CLEANED UP INSIDE HOUSE.
978018 | N/A | N/A | N/A | N/A | PRIVATE | 12/13/97-5:55 P | 12/13/97-7:35 P | 1 TO 5 | 0 | 1123 CAMEO DEL SOL | CARLSBAD | SD | 92008 | CLEANOUT | 1 | ROOTS |  | CLEARED LATERAL WITH RODDING MACHINE | N | N |  |  | CLEANOUT | N | N | N | N/A | DISINFECTED AREA
97019 | N/A | N/A | N/A | N/A | CARLSBAD MWD | 12/23/97-1:15 P | 12/23/97-2:30 P | 5 TO 10 | 0 | 237 NORMANDIE | CARLSBAD | SD | 92008 | CLEANOUT | 3 | BROKEN CUTTER |  | CLEARED MAIN LINE W/RODDING MACHINE | N | N |  |  | STREET SURFACE | N | N | N | N/A | DISINFECTED AREA
JAN-MAR '98
978020 | N/A | N/A | N/A | N/A | CARLSBAD MWD | 1/2/98-9:08 A | 1/2/98-12:30 P | 5 TO 10 | 5 TO 10 | 260 NORMANDIE | CARLSBAD | SD | 92008 | CLEANOUT | 4 |  | PIECE OF RODDING MACHINE BROKE OFF IN MAIN | CLEARED OBSTRUCTION AND WILL INCREASE PREVENTATIVE MAINTENANCE IN THIS AREA DUE TO GREASE PROBLEMS | N | N |  |  | STREET SURFACE | N | N | N | N/A | VACUUMED UP WATER THAT SPILLED AND DISINFECTED AREA.
978021 | N/A | N/A | N/A | N/A | CARLSBAD MWD | 1/10/98-11:30 A | 1/10/98-11:50 A | 5 | 0 | 1113 CAMINO DEL SOL CIRCLE | CARLSBAD | SD | 92008 | CLEANOUT | 1 | TREE ROOTS |  | RODDED LATERAL WITH RODDING MACHINE, CLEARED LINE. | N | N |  |  | AREA AROUND CLEANOUT | N | N | N | N/A | DISINFECTED AREA AROUND CLEANOUT
978022 | KATHY STONE-FAX | 1/15/98-A.M. | DON WASKO | 760-438-2722 | CARLSBAD MWD | 1/14/98-7:00A | 1/14/98-8:00A | 50 | 50 | 1275 YOURELL | CARLSBAD | SD | 92008 | INSIDE HOUSE | 1 | TREE ROOTS |  | RODDED LATERAL WITH RODDING MACHINE, CLEARED LINE. | N | N |  |  | FAMILY ROOM INSIDE HOUSE | N | N | N | N/A | RESIDENT CLEANED UP SEWAGE
978023 | N/A | N/A | N/A | N/A | CARLSBAD MWD | 1/14/98-8:00A | 1/14/98-9:30A | 30 | 30 | IMPALA @ PALMER WAY | CARLSBAD | SD | 92008 | PRIVATE PUMP STATION | 2 |  | POWER FAILURE, PUMP STATION FAILURE AT PRIVATE PUMP STATION LOCATED ON PROPERTY. | REITERATED TO MANAGEMENT COMPANY (MULLER CO.) THE IMPORTANCE OF PREVENTATIVE MAINTENANCE ON PUMP STATION | N | N |  |  | STREET SURFACE | N | N | N | N/A | VACUUMED UP WATER THAT SPILLED AND DISINFECTED AREA.
978024 | KATHY STONE-FAX | 1/19/98-A.M. | PAT GUEVARA | 760-438-2722 | CARLSBAD MWD | 1/17/98-10:30 A | 1/17/98-11:30 A | 100 | 100 | 2445 PIO PICO | CARLSBAD | SD | 92008 | INSIDE HOUSE | 1 |  | SEWER MAIN STOPPAGE ON PIO PICO, BETWEEN BUENA VISTA WAY & KNOWLES | CLEARED OBSTRUCTION IN SEWER MAIN WITH VACTOR | N | N |  |  | INSIDE HOUSE | N | N | N | N/A | RESIDENT HIRED CONTRACTOR TO CLEAN UP SEWAGE
978025 | N/A | N/A | N/A | N/A | CARLSBAD MWD | 1/21/98-3:00P | 1/21/98-4:00P | 20 | 0 | 7201 TANAGER | CARLSBAD | SD | 92009 | MANHOLE | 1 |  | PIPE OBSTRUCTION AT MANHOLE (DEBRIS) | CLEARED BLOCKAGE WITH VACTOR | N | N |  |  | AREA AROUND MANHOLE | N | N | N | N/A | DISINFECTED AREA AROUND MANHOLE
978026 | N/A | N/A | N/A | N/A | CARLSBAD MWD | 1/23/98-9:04 A | 1/23/98-11:30 A | 1 TO 5 | 0 | 3898 WESTHAVEN | CARLSBAD | SD | 92008 | CLEANOUT | 1 | TREE ROOTS |  | RODDED LATERAL WITH RODDING MACHINE, CLEARED LINE. | N | N |  |  | AREA AROUND CLEANOUT | N | N | N | N/A | DISINFECTED AREA AROUND CLEANOUT
967-001 | Kristin Schwall | 1997-04-25 10:00 | Shawn Atherton | 753-5018 | City of Encinitas | 1997-01-25 14:15 | 1997-01-25 15:15 | 400 | 0 | 801 Birmingham (Cardiff) | Encinitas | SD | 92024 | Crdf 16 mh121 | 0 | Tree Roots | Nearby tree roots growing into side of m.h. and down into the waters, causing blockage in the channel of the m.h. | Nearby trees were removed from the easement by the property owner. | n | y |  |  | Ocean (4 miles from source) | y | n | n | n/a | It was raining at the time of the blocakge. We also flushed additional 1,000 gal. of water into storm drain. Sewage was well diluted by the time it reached the ocean.
978022 | GREG PETERS | 02/13/98, 1510 | Karl Vogel | 6197259762 | MCB, CAMP PENDLETON | 02/13/98, 1445 | 02/14/98, 1730 | 90,000 | 0 | East of Stuart Mesa road, North of San. Mar. River | CAMP PENDLETON | SD | 920555008 | Lift Station # 31-220 | 1 | LINE BREAK | Lift Station secured to prevent further damage to 6" Force Main until repairs effected. |  | N | N |  |  | Abandoned sewage lagoon. | Y | Y | N | 0
978023 | ELECTRONIC QTLY RPT |  | Karl Vogel | 6197259762 | MCB, CAMP PENDLETON | 02/18/98, 0400 | 02/18/98, 0900 | 900 | 850 | LCAC area, ajacent Fire station | CAMP PENDLETON | SD | 920555008 | Lift station # 31-0924 | No | LINE BREAK | Cause undetermined | Discharge line repaired will monitor for any sign of problems. | N | N |  |  | Grass adjacent Lift station. | Y | NA | N | 0 | Area is grassy and level. Spill spead 20" around station percolated/ponded and was pumped. Reached no surface waters.
APR-JUN, '98
978029 | N/A | N/A | N/A | N/A | CARLSBAD | 6/8/98-9:45 A | 6/8/98-10:30 A | 5 TO 10 | 5 TO 10 | 380 CHRISTIANSEN | CARLSBAD | SD | 92008 | PRIV. CLEANOUT | 1 | ROOTS |  |  | N | N |  |  |  | N | N | N/A | N/A | DISINFECTED AREA.
978-011 | 619-571-6972 (SIRT) | 1998-04-20 09:00 | MIKE DUNBAR | (949) 499-4555 | SOUTH COAST WATER DISTRICT | 1998-04-19 12:15 | 1998-04-19 13:00 | 2000 | 0 | 32162 PACIFIC COAST HIGHWAY | LAGUNA BEACH | OR | 92651 | MANHOLE | 0 | LINE PLUGGED WITH TREE ROOTS | LINE PLUGGED WITH TREE ROOTS AND RAGS | CLEANED LINE | N: N; N/A: STORM DRAIN; Y: Y; Y: N; N: N | OVERFLOW DID NOT REACH SURFACE WATERS
978028 |  |  | DENNIS PINIGIS | 6197259762 | MCB, CAMP PENDLETON | 06/08/98,10:00:00 AM | 06/09/98,10:45:00 A.M. | 100 | 20 | 33 Area Wagon Wheel Street | CAMP PENDLETON | SD | 920555008 |  | 1 | CONSTRUCTION | Contractor cut sewer line while putting in fibre optic cable | break repaired | N | N |  |  | bottom of the trench | Y | NA | N | 0 | NOT IN AN AREA OF EXPECTED PUBLIC CONTACT
Note on I157: Changed from "1.64 million" to 1638000 on 12/21/01 per City of San Diego comment
Note on J33: Changed from 1 to 100 on 12/21/01 per City of San Diego comment